## Summary
Hornsund photovoltaic capacity factor
Site | Hornsund
Latitude [deg] | 76.9667
Longitude [deg E] | 15.7167
Surface tilt [deg] | 60
Surface azimuth [deg] | 0
Minimum ground albedo [-] | 0.2
Maximum ground albedo [-] | 0.8
Albedo model | rho(t) from 2015 Hornsund/Fuglebekken snow-cover reference
2015 snow-cover points | 17 May 90%; 10 Jun 75%; 15 Jun 50%; 20 Jun 25%; 27 Jun 10%; 06 Jul <2%
Interpolation | Linear between observed 2015 SCE points
Before 17 May | SCE = 1.0 -> rho = rho_max
From 06 July onward | SCE = 0.0 -> rho = rho_min; autumn return not imposed
Derating factor [-] | 0.82
Hourly conversion | linear
Direct input interpretation | BHI
Temperature correction | ON - SEKLIMA hourly air temperature
NOCT [°C] | 45
Temperature coefficient [1/°C] | -0.0035
Reference cell temperature [°C] | 25
NOCT reference ambient temperature [°C] | 20
NOCT reference irradiance [W/m²] | 800
Temperature source UTC offset [h] | 1
Year | Processed hours | Specific production (kWh/kWp) | Mean CF | Maximum CF | Mean POA irradiance (W/m²)
2016 | 8784 | 578.9532 | 0.06591 | 0.77775 | 76.8134

## Hourly 2016
Date and time UTC | GHI horizontal (W/m²) | DHI horizontal (W/m²) | BHI horizontal / source Direct (W/m²) | Derived DNI (W/m²) | Solar declination (°) | Hour angle (°) | Solar zenith (°) | Solar elevation (°) | Solar azimuth (°) | PV incidence angle (°) | POA direct (W/m²) | POA diffuse (W/m²) | Ground albedo rho(t) (-) | Snow cover fraction - 2015 reference (-) | POA ground reflected (W/m²) | POA global (W/m²) | Air temperature (°C) | Cell temperature (°C) | Temperature factor (-) | Capacity factor (kW/kWp)
2016-01-01 | 0 | 0 | 0 | 0 | -23.0953 | -164.9533 | 125.6257 | -35.6257 | -162.9153 | 164.6053 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-01-01 01:00 | 0 | 0 | 0 | 0 | -23.0923 | -149.958 | 124.1727 | -34.1727 | -146.1774 | 151.1745 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-01-01 02:00 | 0 | 0 | 0 | 0 | -23.0893 | -134.9627 | 121.9149 | -31.9149 | -129.9325 | 137.4076 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.7 | 2.7 | 1.078 | 0
2016-01-01 03:00 | 0 | 0 | 0 | 0 | -23.0863 | -119.9673 | 119.0546 | -29.0546 | -114.2646 | 123.637 | 0 | 0 | 0.8 | 1 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-01-01 04:00 | 0 | 0 | 0 | 0 | -23.0833 | -104.972 | 115.8213 | -25.8213 | -99.1487 | 109.9823 | 0 | 0 | 0.8 | 1 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-01-01 05:00 | 0 | 0 | 0 | 0 | -23.0803 | -89.9767 | 112.4475 | -22.4475 | -84.4883 | 96.5482 | 0 | 0 | 0.8 | 1 | 0 | 0 | 3.2 | 3.2 | 1.0763 | 0
2016-01-01 06:00 | 0 | 0 | 0 | 0 | -23.0772 | -74.9814 | 109.1542 | -19.1542 | -70.157 | 83.475 | 0 | 0 | 0.8 | 1 | 0 | 0 | 3.2 | 3.2 | 1.0763 | 0
2016-01-01 07:00 | 0 | 0 | 0 | 0 | -23.0741 | -59.986 | 106.1435 | -16.1435 | -56.0302 | 70.9863 | 0 | 0 | 0.8 | 1 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-01-01 08:00 | 0 | 0 | 0 | 0 | -23.0711 | -44.9907 | 103.5941 | -13.5941 | -42.0049 | 59.4704 | 0 | 0 | 0.8 | 1 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-01-01 09:00 | 0 | 0 | 0 | 0 | -23.068 | -29.9954 | 101.6559 | -11.6559 | -28.011 | 49.6245 | 0 | 0 | 0.8 | 1 | 0 | 0 | 5 | 5 | 1.07 | 0
2016-01-01 10:00 | 0 | 0 | 0 | 0 | -23.0649 | -15 | 100.4432 | -10.4432 | -14.013 | 42.6332 | 0 | 0 | 0.8 | 1 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-01-01 11:00 | 0 | 0 | 0 | 0 | -23.0618 | -0.0047126 | 100.0284 | -10.0284 | -0.0044032 | 40.0284 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.7 | 1.7 | 1.0816 | 0
2016-01-01 12:00 | 0 | 0 | 0 | 0 | -23.0586 | 14.9906 | 100.4364 | -10.4364 | 14.0045 | 42.6242 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-01-01 13:00 | 0 | 0 | 0 | 0 | -23.0555 | 29.986 | 101.6425 | -11.6425 | 28.0037 | 49.6093 | 0 | 0 | 0.8 | 1 | 0 | 0 | 4.2 | 4.2 | 1.0728 | 0
2016-01-01 14:00 | 0 | 0 | 0 | 0 | -23.0523 | 44.9813 | 103.5742 | -13.5742 | 41.9993 | 59.452 | 0 | 0 | 0.8 | 1 | 0 | 0 | 3.8 | 3.8 | 1.0742 | 0
2016-01-01 15:00 | 0 | 0 | 0 | 0 | -23.0492 | 59.9766 | 106.1173 | -16.1173 | 56.0266 | 70.9667 | 0 | 0 | 0.8 | 1 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-01-01 16:00 | 0 | 0 | 0 | 0 | -23.046 | 74.972 | 109.1218 | -19.1218 | 70.1557 | 83.4555 | 0 | 0 | 0.8 | 1 | 0 | 0 | 3.4 | 3.4 | 1.0756 | 0
2016-01-01 17:00 | 0 | 0 | 0 | 0 | -23.0428 | 89.9673 | 112.4091 | -22.4091 | 84.4891 | 96.5298 | 0 | 0 | 0.8 | 1 | 0 | 0 | 3.6 | 3.6 | 1.0749 | 0
2016-01-01 18:00 | 0 | 0 | 0 | 0 | -23.0396 | 104.9627 | 115.7768 | -25.7768 | 99.1512 | 109.9659 | 0 | 0 | 0.8 | 1 | 0 | 0 | 4 | 4 | 1.0735 | 0
2016-01-01 19:00 | 0 | 0 | 0 | 0 | -23.0364 | 119.958 | 119.004 | -29.004 | 114.2679 | 123.6236 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-01-01 20:00 | 0 | 0 | 0 | 0 | -23.0331 | 134.9534 | 121.8581 | -31.8581 | 129.935 | 137.3987 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-01-01 21:00 | 0 | 0 | 0 | 0 | -23.0299 | 149.9487 | 124.1097 | -34.1097 | 146.1775 | 151.1732 | 0 | 0 | 0.8 | 1 | 0 | 0 | 3.7 | 3.7 | 1.0745 | 0
2016-01-01 22:00 | 0 | 0 | 0 | 0 | -23.0266 | 164.9441 | 125.5566 | -35.5566 | 162.911 | 164.6215 | 0 | 0 | 0.8 | 1 | 0 | 0 | 3.7 | 3.7 | 1.0745 | 0
2016-01-01 23:00 | 0 | 0 | 0 | 0 | -23.0233 | 179.9394 | 126.0567 | -36.0567 | 179.9311 | 173.9431 | 0 | 0 | 0.8 | 1 | 0 | 0 | 4.2 | 4.2 | 1.0728 | 0
2016-01-02 | 0 | 0 | 0 | 0 | -23.02 | -165.0652 | 125.558 | -35.558 | -163.0483 | 164.7282 | 0 | 0 | 0.8 | 1 | 0 | 0 | 4 | 4 | 1.0735 | 0
2016-01-02 01:00 | 0 | 0 | 0 | 0 | -23.0167 | -150.0699 | 124.1118 | -34.1118 | -146.3131 | 151.2855 | 0 | 0 | 0.8 | 1 | 0 | 0 | 4.3 | 4.3 | 1.0724 | 0
2016-01-02 02:00 | 0 | 0 | 0 | 0 | -23.0134 | -135.0745 | 121.8597 | -31.8597 | -130.0683 | 137.5101 | 0 | 0 | 0.8 | 1 | 0 | 0 | 4 | 4 | 1.0735 | 0
2016-01-02 03:00 | 0 | 0 | 0 | 0 | -23.0101 | -120.0791 | 119.0033 | -29.0033 | -114.3988 | 123.7319 | 0 | 0 | 0.8 | 1 | 0 | 0 | 4.3 | 4.3 | 1.0724 | 0
2016-01-02 04:00 | 0 | 0 | 0 | 0 | -23.0068 | -105.0838 | 115.7719 | -25.7719 | -99.28 | 110.0695 | 0 | 0 | 0.8 | 1 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-01-02 05:00 | 0 | 0 | 0 | 0 | -23.0034 | -90.0884 | 112.3981 | -22.3981 | -84.6164 | 96.6264 | 0 | 0 | 0.8 | 1 | 0 | 0 | 3.9 | 3.9 | 1.0738 | 0
2016-01-02 06:00 | 0 | 0 | 0 | 0 | -23 | -75.093 | 109.1028 | -19.1028 | -70.2817 | 83.5422 | 0 | 0 | 0.8 | 1 | 0 | 0 | 3.6 | 3.6 | 1.0749 | 0
2016-01-02 07:00 | 0 | 0 | 0 | 0 | -22.9967 | -60.0977 | 106.0885 | -16.0885 | -56.1513 | 71.039 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2 | 2 | 1.0805 | 0
2016-01-02 08:00 | 0 | 0 | 0 | 0 | -22.9933 | -45.1023 | 103.5343 | -13.5343 | -42.1222 | 59.503 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-01-02 09:00 | 0 | 0 | 0 | 0 | -22.9899 | -30.1069 | 101.5901 | -11.5901 | -28.1243 | 49.6283 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-01-02 10:00 | 0 | 0 | 0 | 0 | -22.9864 | -15.1115 | 100.371 | -10.371 | -14.1219 | 42.5979 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-01-02 11:00 | 0 | 0 | 0 | 0 | -22.983 | -0.11617 | 99.9497 | -9.9497 | -0.10858 | 39.9498 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-01-02 12:00 | 0 | 0 | 0 | 0 | -22.9796 | 14.8792 | 100.3515 | -10.3515 | 13.9052 | 42.5133 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2 | 2 | 1.0805 | 0
2016-01-02 13:00 | 0 | 0 | 0 | 0 | -22.9761 | 29.8746 | 101.5518 | -11.5518 | 27.909 | 49.4832 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.1 | 2.1 | 1.0801 | 0
2016-01-02 14:00 | 0 | 0 | 0 | 0 | -22.9726 | 44.87 | 103.4788 | -13.4788 | 41.9087 | 59.3222 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-01-02 15:00 | 0 | 0 | 0 | 0 | -22.9692 | 59.8654 | 106.0181 | -16.0181 | 55.9392 | 70.8383 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-01-02 16:00 | 0 | 0 | 0 | 0 | -22.9657 | 74.8607 | 109.02 | -19.02 | 70.0699 | 83.3307 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2 | 2 | 1.0805 | 0
2016-01-02 17:00 | 0 | 0 | 0 | 0 | -22.9621 | 89.8561 | 112.3059 | -22.3059 | 84.403 | 96.4094 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-01-02 18:00 | 0 | 0 | 0 | 0 | -22.9586 | 104.8515 | 115.6735 | -25.6735 | 99.0627 | 109.8505 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.1 | 2.1 | 1.0801 | 0
2016-01-02 19:00 | 0 | 0 | 0 | 0 | -22.9551 | 119.8469 | 118.9019 | -28.9019 | 114.1747 | 123.5138 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.6 | 2.6 | 1.0784 | 0
2016-01-02 20:00 | 0 | 0 | 0 | 0 | -22.9515 | 134.8423 | 121.7587 | -31.7587 | 129.8349 | 137.2959 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-01-02 21:00 | 0 | 0 | 0 | 0 | -22.948 | 149.8377 | 124.0146 | -34.0146 | 146.0688 | 151.0809 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.4 | 1.4 | 1.0826 | 0
2016-01-02 22:00 | 0 | 0 | 0 | 0 | -22.9444 | 164.8331 | 125.4672 | -35.4672 | 162.7931 | 164.5541 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-01-02 23:00 | 0 | 0 | 0 | 0 | -22.9408 | 179.8285 | 125.9741 | -35.9741 | 179.8048 | 174.0237 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-01-03 | 0 | 0 | 0 | 0 | -22.9372 | -165.1761 | 125.4827 | -35.4827 | -163.1806 | 164.8529 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-01-03 01:00 | 0 | 0 | 0 | 0 | -22.9336 | -150.1807 | 124.0433 | -34.0433 | -146.4488 | 151.3964 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.7 | 2.7 | 1.078 | 0
2016-01-03 02:00 | 0 | 0 | 0 | 0 | -22.9299 | -135.1853 | 121.7967 | -31.7967 | -130.2046 | 137.6116 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.5 | 2.5 | 1.0788 | 0
2016-01-03 03:00 | 0 | 0 | 0 | 0 | -22.9263 | -120.1899 | 118.9443 | -28.9443 | -114.5338 | 123.8252 | 0 | 0 | 0.8 | 1 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-01-03 04:00 | 0 | 0 | 0 | 0 | -22.9226 | -105.1945 | 115.715 | -25.715 | -99.4124 | 110.1544 | 0 | 0 | 0.8 | 1 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-01-03 05:00 | 0 | 0 | 0 | 0 | -22.919 | -90.1991 | 112.341 | -22.341 | -84.7455 | 96.7018 | 0 | 0 | 0.8 | 1 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-01-03 06:00 | 0 | 0 | 0 | 0 | -22.9153 | -75.2037 | 109.0438 | -19.0438 | -70.4072 | 83.6059 | 0 | 0 | 0.8 | 1 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-01-03 07:00 | 0 | 0 | 0 | 0 | -22.9116 | -60.2082 | 106.026 | -16.026 | -56.273 | 71.0874 | 0 | 0 | 0.8 | 1 | 0 | 0 | 3.4 | 3.4 | 1.0756 | 0
2016-01-03 08:00 | 0 | 0 | 0 | 0 | -22.9079 | -45.2128 | 103.4668 | -13.4668 | -42.2399 | 59.5304 | 0 | 0 | 0.8 | 1 | 0 | 0 | 3.6 | 3.6 | 1.0749 | 0
2016-01-03 09:00 | 0 | 0 | 0 | 0 | -22.9042 | -30.2174 | 101.5168 | -11.5168 | -28.2375 | 49.626 | 0 | 0 | 0.8 | 1 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-01-03 10:00 | 0 | 0 | 0 | 0 | -22.9004 | -15.222 | 100.2912 | -10.2912 | -14.2303 | 42.5556 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.5 | 2.5 | 1.0788 | 0
2016-01-03 11:00 | 0 | 0 | 0 | 0 | -22.8967 | -0.22657 | 99.8634 | -9.8634 | -0.21185 | 39.864 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.5 | 2.5 | 1.0788 | 0
2016-01-03 12:00 | 0 | 0 | 0 | 0 | -22.8929 | 14.7689 | 100.259 | -10.259 | 13.8073 | 42.3957 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-01-03 13:00 | 0 | 0 | 0 | 0 | -22.8892 | 29.7643 | 101.4538 | -11.4538 | 27.8162 | 49.3518 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-01-03 14:00 | 0 | 0 | 0 | 0 | -22.8854 | 44.7597 | 103.3761 | -13.3761 | 41.8204 | 59.1884 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.7 | 1.7 | 1.0816 | 0
2016-01-03 15:00 | 0 | 0 | 0 | 0 | -22.8816 | 59.7551 | 105.9118 | -15.9118 | 55.8543 | 70.7071 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2 | 2 | 1.0805 | 0
2016-01-03 16:00 | 0 | 0 | 0 | 0 | -22.8778 | 74.7506 | 108.9111 | -18.9111 | 69.9869 | 83.2039 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2 | 2 | 1.0805 | 0
2016-01-03 17:00 | 0 | 0 | 0 | 0 | -22.8739 | 89.746 | 112.1956 | -22.1956 | 84.32 | 96.2878 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.6 | 1.6 | 1.0819 | 0
2016-01-03 18:00 | 0 | 0 | 0 | 0 | -22.8701 | 104.7414 | 115.5631 | -25.5631 | 98.9773 | 109.7345 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-01-03 19:00 | 0 | 0 | 0 | 0 | -22.8662 | 119.7369 | 118.7926 | -28.7926 | 114.0846 | 123.404 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-01-03 20:00 | 0 | 0 | 0 | 0 | -22.8624 | 134.7323 | 121.6521 | -31.6521 | 129.7377 | 137.1937 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-01-03 21:00 | 0 | 0 | 0 | 0 | -22.8585 | 149.7278 | 123.9121 | -33.9121 | 145.9626 | 150.99 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.5 | 2.5 | 1.0788 | 0
2016-01-03 22:00 | 0 | 0 | 0 | 0 | -22.8546 | 164.7232 | 125.3703 | -35.3703 | 162.6772 | 164.4892 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1 | 1 | 1.084 | 0
2016-01-03 23:00 | 0 | 0 | 0 | 0 | -22.8507 | 179.7187 | 125.8838 | -35.8838 | 179.68 | 174.11 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.1 | 1.1 | 1.0837 | 0
2016-01-04 | 0 | 0 | 0 | 0 | -22.8468 | -165.2859 | 125.3996 | -35.3996 | -163.3123 | 164.9792 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-01-04 01:00 | 0 | 0 | 0 | 0 | -22.8428 | -150.2904 | 123.967 | -33.967 | -146.5844 | 151.5071 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-01-04 02:00 | 0 | 0 | 0 | 0 | -22.8389 | -135.295 | 121.7262 | -31.7262 | -130.3414 | 137.712 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.1 | 0.1 | 1.0872 | 0
2016-01-04 03:00 | 0 | 0 | 0 | 0 | -22.8349 | -120.2995 | 118.8777 | -28.8777 | -114.6695 | 123.9168 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-01-04 04:00 | 0 | 0 | 0 | 0 | -22.831 | -105.3041 | 115.6504 | -25.6504 | -99.5457 | 110.2369 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-01-04 05:00 | 0 | 0 | 0 | 0 | -22.827 | -90.3086 | 112.2764 | -22.2764 | -84.8756 | 96.7743 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-01-04 06:00 | 0 | 0 | 0 | 0 | -22.823 | -75.3132 | 108.9773 | -18.9773 | -70.5336 | 83.666 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-01-04 07:00 | 0 | 0 | 0 | 0 | -22.819 | -60.3177 | 105.9558 | -15.9558 | -56.3953 | 71.1316 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-01-04 08:00 | 0 | 0 | 0 | 0 | -22.815 | -45.3222 | 103.3917 | -13.3917 | -42.3579 | 59.5527 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-01-04 09:00 | 0 | 0 | 0 | 0 | -22.8109 | -30.3268 | 101.4358 | -11.4358 | -28.3507 | 49.6176 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-01-04 10:00 | 0 | 0 | 0 | 0 | -22.8069 | -15.3313 | 100.2039 | -10.2039 | -14.3382 | 42.5064 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-01-04 11:00 | 0 | 0 | 0 | 0 | -22.8028 | -0.33581 | 99.7697 | -9.7697 | -0.31412 | 39.7708 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-01-04 12:00 | 0 | 0 | 0 | 0 | -22.7987 | 14.6597 | 100.1591 | -10.1591 | 13.7108 | 42.2715 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-01-04 13:00 | 0 | 0 | 0 | 0 | -22.7947 | 29.6551 | 101.3485 | -11.3485 | 27.7252 | 49.2152 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-01-04 14:00 | 0 | 0 | 0 | 0 | -22.7906 | 44.6506 | 103.2662 | -13.2662 | 41.7343 | 59.0507 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2 | -2 | 1.0945 | 0
2016-01-04 15:00 | 0 | 0 | 0 | 0 | -22.7864 | 59.6461 | 105.7983 | -15.7983 | 55.772 | 70.5732 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-01-04 16:00 | 0 | 0 | 0 | 0 | -22.7823 | 74.6416 | 108.7952 | -18.7952 | 69.9068 | 83.0753 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-01-04 17:00 | 0 | 0 | 0 | 0 | -22.7782 | 89.6371 | 112.0783 | -22.0783 | 84.24 | 96.1651 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.2 | -2.2 | 1.0952 | 0
2016-01-04 18:00 | 0 | 0 | 0 | 0 | -22.774 | 104.6326 | 115.4456 | -25.4456 | 98.8951 | 109.618 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-01-04 19:00 | 0 | 0 | 0 | 0 | -22.7699 | 119.628 | 118.6763 | -28.6763 | 113.9976 | 123.2944 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-01-04 20:00 | 0 | 0 | 0 | 0 | -22.7657 | 134.6235 | 121.5382 | -31.5382 | 129.6434 | 137.0923 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-01-04 21:00 | 0 | 0 | 0 | 0 | -22.7615 | 149.619 | 123.8022 | -33.8022 | 145.8591 | 150.9005 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-01-04 22:00 | 0 | 0 | 0 | 0 | -22.7573 | 164.6145 | 125.2659 | -35.2659 | 162.5635 | 164.4268 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-01-04 23:00 | 0 | 0 | 0 | 0 | -22.7531 | 179.61 | 125.7861 | -35.7861 | 179.5567 | 174.202 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-01-05 | 0 | 0 | 0 | 0 | -22.7488 | -165.3945 | 125.3089 | -35.3089 | -163.4431 | 165.1071 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-01-05 01:00 | 0 | 0 | 0 | 0 | -22.7446 | -150.399 | 123.8831 | -33.8831 | -146.7198 | 151.6175 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3 | -3 | 1.098 | 0
2016-01-05 02:00 | 0 | 0 | 0 | 0 | -22.7403 | -135.4035 | 121.648 | -31.648 | -130.4784 | 137.8112 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-01-05 03:00 | 0 | 0 | 0 | 0 | -22.7361 | -120.4079 | 118.8035 | -28.8035 | -114.8058 | 124.0065 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-01-05 04:00 | 0 | 0 | 0 | 0 | -22.7318 | -105.4124 | 115.5782 | -25.5782 | -99.6798 | 110.3171 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-01-05 05:00 | 0 | 0 | 0 | 0 | -22.7275 | -90.4169 | 112.2042 | -22.2042 | -85.0064 | 96.8437 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.4 | -3.4 | 1.0994 | 0
2016-01-05 06:00 | 0 | 0 | 0 | 0 | -22.7232 | -75.4214 | 108.9032 | -18.9032 | -70.6606 | 83.7225 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.3 | -4.3 | 1.1025 | 0
2016-01-05 07:00 | 0 | 0 | 0 | 0 | -22.7189 | -60.4259 | 105.8781 | -15.8781 | -56.5181 | 71.1714 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-01-05 08:00 | 0 | 0 | 0 | 0 | -22.7145 | -45.4304 | 103.3091 | -13.3091 | -42.476 | 59.5698 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-01-05 09:00 | 0 | 0 | 0 | 0 | -22.7102 | -30.4348 | 101.3474 | -11.3474 | -28.4636 | 49.6031 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.7 | -4.7 | 1.1039 | 0
2016-01-05 10:00 | 0 | 0 | 0 | 0 | -22.7058 | -15.4393 | 100.1091 | -10.1091 | -14.4455 | 42.4501 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.5 | -5.5 | 1.1067 | 0
2016-01-05 11:00 | 0 | 0 | 0 | 0 | -22.7014 | -0.4438 | 99.6685 | -9.6685 | -0.41531 | 39.6705 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.8 | -5.8 | 1.1078 | 0
2016-01-05 12:00 | 0 | 0 | 0 | 0 | -22.6971 | 14.5517 | 100.0518 | -10.0518 | 13.6158 | 42.1409 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.1 | -6.1 | 1.1088 | 0
2016-01-05 13:00 | 0 | 0 | 0 | 0 | -22.6927 | 29.5473 | 101.2358 | -11.2358 | 27.6362 | 49.0734 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.3 | -6.3 | 1.1096 | 0
2016-01-05 14:00 | 0 | 0 | 0 | 0 | -22.6882 | 44.5428 | 103.1491 | -13.1491 | 41.6506 | 58.9093 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.9 | -5.9 | 1.1081 | 0
2016-01-05 15:00 | 0 | 0 | 0 | 0 | -22.6838 | 59.5383 | 105.6777 | -15.6777 | 55.6924 | 70.4365 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.9 | -6.9 | 1.1117 | 0
2016-01-05 16:00 | 0 | 0 | 0 | 0 | -22.6794 | 74.5339 | 108.6722 | -18.6722 | 69.8296 | 82.9449 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-01-05 17:00 | 0 | 0 | 0 | 0 | -22.6749 | 89.5294 | 111.954 | -21.954 | 84.1632 | 96.0414 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.1 | -7.1 | 1.1123 | 0
2016-01-05 18:00 | 0 | 0 | 0 | 0 | -22.6705 | 104.525 | 115.3212 | -25.3212 | 98.8162 | 109.5011 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.8 | -6.8 | 1.1113 | 0
2016-01-05 19:00 | 0 | 0 | 0 | 0 | -22.666 | 119.5205 | 118.5529 | -28.5529 | 113.9139 | 123.1849 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.3 | -7.3 | 1.1131 | 0
2016-01-05 20:00 | 0 | 0 | 0 | 0 | -22.6615 | 134.5161 | 121.4172 | -31.4172 | 129.5523 | 136.9916 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.1 | -7.1 | 1.1123 | 0
2016-01-05 21:00 | 0 | 0 | 0 | 0 | -22.657 | 149.5116 | 123.6851 | -33.6851 | 145.7583 | 150.8125 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.2 | -7.2 | 1.1127 | 0
2016-01-05 22:00 | 0 | 0 | 0 | 0 | -22.6525 | 164.5072 | 125.1541 | -35.1541 | 162.452 | 164.3668 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.2 | -6.2 | 1.1092 | 0
2016-01-05 23:00 | 0 | 0 | 0 | 0 | -22.6479 | 179.5027 | 125.6807 | -35.6807 | 179.435 | 174.2995 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.9 | -5.9 | 1.1081 | 0
2016-01-06 | 0 | 0 | 0 | 0 | -22.6434 | -165.5017 | 125.2106 | -35.2106 | -163.573 | 165.2363 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6 | -6 | 1.1085 | 0
2016-01-06 01:00 | 0 | 0 | 0 | 0 | -22.6389 | -150.5062 | 123.7916 | -33.7916 | -146.8548 | 151.7273 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.5 | -6.5 | 1.1102 | 0
2016-01-06 02:00 | 0 | 0 | 0 | 0 | -22.6343 | -135.5106 | 121.5621 | -31.5621 | -130.6156 | 137.909 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-01-06 03:00 | 0 | 0 | 0 | 0 | -22.6297 | -120.515 | 118.7217 | -28.7217 | -114.9426 | 124.0943 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.5 | -6.5 | 1.1102 | 0
2016-01-06 04:00 | 0 | 0 | 0 | 0 | -22.6251 | -105.5195 | 115.4985 | -25.4985 | -99.8145 | 110.3947 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-01-06 05:00 | 0 | 0 | 0 | 0 | -22.6205 | -90.5239 | 112.1245 | -22.1245 | -85.1379 | 96.9101 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7 | -7 | 1.112 | 0
2016-01-06 06:00 | 0 | 0 | 0 | 0 | -22.6159 | -75.5283 | 108.8215 | -18.8215 | -70.7882 | 83.7754 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.6 | -7.6 | 1.1141 | 0
2016-01-06 07:00 | 0 | 0 | 0 | 0 | -22.6113 | -60.5328 | 105.7929 | -15.7929 | -56.6413 | 71.2069 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.1 | -8.1 | 1.1159 | 0
2016-01-06 08:00 | 0 | 0 | 0 | 0 | -22.6066 | -45.5372 | 103.219 | -13.219 | -42.5942 | 59.5817 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.5 | -8.5 | 1.1173 | 0
2016-01-06 09:00 | 0 | 0 | 0 | 0 | -22.602 | -30.5416 | 101.2514 | -11.2514 | -28.5763 | 49.5824 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.8 | -9.8 | 1.1218 | 0
2016-01-06 10:00 | 0 | 0 | 0 | 0 | -22.5973 | -15.546 | 100.0068 | -10.0068 | -14.552 | 42.387 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.3 | -9.3 | 1.12 | 0
2016-01-06 11:00 | 0 | 0 | 0 | 0 | -22.5926 | -0.55043 | 99.5598 | -9.5598 | -0.51534 | 39.5629 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.3 | -9.3 | 1.12 | 0
2016-01-06 12:00 | 0 | 0 | 0 | 0 | -22.5879 | 14.4452 | 99.9372 | -9.9372 | 13.5224 | 42.0038 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.2 | -8.2 | 1.1162 | 0
2016-01-06 13:00 | 0 | 0 | 0 | 0 | -22.5832 | 29.4408 | 101.116 | -11.116 | 27.5493 | 48.9265 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.6 | -7.6 | 1.1141 | 0
2016-01-06 14:00 | 0 | 0 | 0 | 0 | -22.5785 | 44.4363 | 103.0248 | -13.0248 | 41.5694 | 58.7641 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.4 | -6.4 | 1.1099 | 0
2016-01-06 15:00 | 0 | 0 | 0 | 0 | -22.5737 | 59.4319 | 105.5501 | -15.5501 | 55.6156 | 70.2973 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.1 | -7.1 | 1.1123 | 0
2016-01-06 16:00 | 0 | 0 | 0 | 0 | -22.569 | 74.4275 | 108.5422 | -18.5422 | 69.7555 | 82.8129 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.1 | -7.1 | 1.1123 | 0
2016-01-06 17:00 | 0 | 0 | 0 | 0 | -22.5642 | 89.4231 | 111.8228 | -21.8228 | 84.0896 | 95.9167 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.1 | -7.1 | 1.1123 | 0
2016-01-06 18:00 | 0 | 0 | 0 | 0 | -22.5595 | 104.4187 | 115.1898 | -25.1898 | 98.7407 | 109.384 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.4 | -6.4 | 1.1099 | 0
2016-01-06 19:00 | 0 | 0 | 0 | 0 | -22.5547 | 119.4143 | 118.4225 | -28.4225 | 113.8335 | 123.0757 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.9 | -6.9 | 1.1117 | 0
2016-01-06 20:00 | 0 | 0 | 0 | 0 | -22.5499 | 134.41 | 121.2892 | -31.2892 | 129.4643 | 136.8917 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.7 | -7.7 | 1.1144 | 0
2016-01-06 21:00 | 0 | 0 | 0 | 0 | -22.5451 | 149.4056 | 123.5608 | -33.5608 | 145.6604 | 150.7259 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-01-06 22:00 | 0 | 0 | 0 | 0 | -22.5402 | 164.4012 | 125.035 | -35.035 | 162.3429 | 164.3091 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.2 | -6.2 | 1.1092 | 0
2016-01-06 23:00 | 0 | 0 | 0 | 0 | -22.5354 | 179.3968 | 125.5679 | -35.5679 | 179.3151 | 174.4024 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.1 | -6.1 | 1.1088 | 0
2016-01-07 | 0 | 0 | 0 | 0 | -22.5306 | -165.6076 | 125.1047 | -35.1047 | -163.7017 | 165.3666 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.5 | -6.5 | 1.1102 | 0
2016-01-07 01:00 | 0 | 0 | 0 | 0 | -22.5257 | -150.612 | 123.6925 | -33.6925 | -146.9894 | 151.8365 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.8 | -6.8 | 1.1113 | 0
2016-01-07 02:00 | 0 | 0 | 0 | 0 | -22.5208 | -135.6163 | 121.4687 | -31.4687 | -130.7528 | 138.0054 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.2 | -6.2 | 1.1092 | 0
2016-01-07 03:00 | 0 | 0 | 0 | 0 | -22.5159 | -120.6207 | 118.6323 | -28.6323 | -115.0798 | 124.18 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-01-07 04:00 | 0 | 0 | 0 | 0 | -22.511 | -105.6251 | 115.4112 | -25.4112 | -99.9497 | 110.4698 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.1 | -6.1 | 1.1088 | 0
2016-01-07 05:00 | 0 | 0 | 0 | 0 | -22.5061 | -90.6294 | 112.0373 | -22.0373 | -85.2699 | 96.9734 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.6 | -5.6 | 1.1071 | 0
2016-01-07 06:00 | 0 | 0 | 0 | 0 | -22.5012 | -75.6338 | 108.7324 | -18.7324 | -70.9163 | 83.8245 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-01-07 07:00 | 0 | 0 | 0 | 0 | -22.4963 | -60.6382 | 105.7002 | -15.7002 | -56.7647 | 71.2379 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-01-07 08:00 | 0 | 0 | 0 | 0 | -22.4913 | -45.6425 | 103.1213 | -13.1213 | -42.7123 | 59.5884 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.1 | -5.1 | 1.1054 | 0
2016-01-07 09:00 | 0 | 0 | 0 | 0 | -22.4863 | -30.6469 | 101.1479 | -11.1479 | -28.6885 | 49.5558 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-01-07 10:00 | 0 | 0 | 0 | 0 | -22.4814 | -15.6512 | 99.8971 | -9.8971 | -14.6578 | 42.317 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-01-07 11:00 | 0 | 0 | 0 | 0 | -22.4764 | -0.6556 | 99.4438 | -9.4438 | -0.61412 | 39.4482 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.105 | 0
2016-01-07 12:00 | 0 | 0 | 0 | 0 | -22.4714 | 14.34 | 99.8154 | -9.8154 | 13.4308 | 41.8603 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.105 | 0
2016-01-07 13:00 | 0 | 0 | 0 | 0 | -22.4663 | 29.3357 | 100.9889 | -10.9889 | 27.4645 | 48.7746 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.105 | 0
2016-01-07 14:00 | 0 | 0 | 0 | 0 | -22.4613 | 44.3314 | 102.8935 | -12.8935 | 41.4906 | 58.6153 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.105 | 0
2016-01-07 15:00 | 0 | 0 | 0 | 0 | -22.4563 | 59.327 | 105.4155 | -15.4155 | 55.5416 | 70.1556 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.6 | -5.6 | 1.1071 | 0
2016-01-07 16:00 | 0 | 0 | 0 | 0 | -22.4512 | 74.3227 | 108.4054 | -18.4054 | 69.6845 | 82.6792 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.9 | -5.9 | 1.1081 | 0
2016-01-07 17:00 | 0 | 0 | 0 | 0 | -22.4462 | 89.3183 | 111.6847 | -21.6847 | 84.0194 | 95.7911 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6 | -6 | 1.1085 | 0
2016-01-07 18:00 | 0 | 0 | 0 | 0 | -22.4411 | 104.314 | 115.0515 | -25.0515 | 98.6685 | 109.2665 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.5 | -6.5 | 1.1102 | 0
2016-01-07 19:00 | 0 | 0 | 0 | 0 | -22.436 | 119.3097 | 118.2852 | -28.2852 | 113.7565 | 122.9668 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.3 | -6.3 | 1.1096 | 0
2016-01-07 20:00 | 0 | 0 | 0 | 0 | -22.4309 | 134.3054 | 121.1541 | -31.1541 | 129.3795 | 136.7927 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.8 | -6.8 | 1.1113 | 0
2016-01-07 21:00 | 0 | 0 | 0 | 0 | -22.4258 | 149.301 | 123.4293 | -33.4293 | 145.5654 | 150.6407 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-01-07 22:00 | 0 | 0 | 0 | 0 | -22.4206 | 164.2967 | 124.9085 | -34.9085 | 162.2362 | 164.2536 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.3 | -8.3 | 1.1165 | 0
2016-01-07 23:00 | 0 | 0 | 0 | 0 | -22.4155 | 179.2924 | 125.4477 | -35.4477 | 179.197 | 174.5106 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.7 | -8.7 | 1.1179 | 0
2016-01-08 | 0 | 0 | 0 | 0 | -22.4103 | -165.7119 | 124.9914 | -34.9914 | -163.8293 | 165.4978 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.6 | -8.6 | 1.1176 | 0
2016-01-08 01:00 | 0 | 0 | 0 | 0 | -22.4052 | -150.7162 | 123.5858 | -33.5858 | -147.1233 | 151.9449 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.2 | -8.2 | 1.1162 | 0
2016-01-08 02:00 | 0 | 0 | 0 | 0 | -22.4 | -135.7206 | 121.3677 | -31.3677 | -130.8899 | 138.1002 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.4 | -7.4 | 1.1134 | 0
2016-01-08 03:00 | 0 | 0 | 0 | 0 | -22.3948 | -120.7249 | 118.5355 | -28.5355 | -115.2172 | 124.2635 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.9 | -6.9 | 1.1117 | 0
2016-01-08 04:00 | 0 | 0 | 0 | 0 | -22.3896 | -105.7292 | 115.3164 | -25.3164 | -100.0854 | 110.5422 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-01-08 05:00 | 0 | 0 | 0 | 0 | -22.3844 | -90.7335 | 111.9426 | -21.9426 | -85.4025 | 97.0335 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.5 | -6.5 | 1.1102 | 0
2016-01-08 06:00 | 0 | 0 | 0 | 0 | -22.3791 | -75.7378 | 108.6358 | -18.6358 | -71.0447 | 83.8699 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.2 | -6.2 | 1.1092 | 0
2016-01-08 07:00 | 0 | 0 | 0 | 0 | -22.3739 | -60.7421 | 105.6 | -15.6 | -56.8883 | 71.2645 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6 | -6 | 1.1085 | 0
2016-01-08 08:00 | 0 | 0 | 0 | 0 | -22.3686 | -45.7464 | 103.0163 | -13.0163 | -42.8304 | 59.59 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.105 | 0
2016-01-08 09:00 | 0 | 0 | 0 | 0 | -22.3634 | -30.7507 | 101.0371 | -11.0371 | -28.8003 | 49.523 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.7 | -4.7 | 1.1039 | 0
2016-01-08 10:00 | 0 | 0 | 0 | 0 | -22.3581 | -15.7549 | 99.78 | -9.78 | -14.7626 | 42.24 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.3 | -4.3 | 1.1025 | 0
2016-01-08 11:00 | 0 | 0 | 0 | 0 | -22.3528 | -0.75922 | 99.3205 | -9.3205 | -0.71157 | 39.3265 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-01-08 12:00 | 0 | 0 | 0 | 0 | -22.3475 | 14.2365 | 99.6863 | -9.6863 | 13.3409 | 41.7105 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-01-08 13:00 | 0 | 0 | 0 | 0 | -22.3421 | 29.2322 | 100.8547 | -10.8547 | 27.3819 | 48.6179 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.1033 | 0
2016-01-08 14:00 | 0 | 0 | 0 | 0 | -22.3368 | 44.2279 | 102.7552 | -12.7552 | 41.4145 | 58.4629 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-01-08 15:00 | 0 | 0 | 0 | 0 | -22.3315 | 59.2237 | 105.274 | -15.274 | 55.4705 | 70.0115 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-01-08 16:00 | 0 | 0 | 0 | 0 | -22.3261 | 74.2194 | 108.2618 | -18.2618 | 69.6167 | 82.544 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-01-08 17:00 | 0 | 0 | 0 | 0 | -22.3207 | 89.2151 | 111.5399 | -21.5399 | 83.9525 | 95.6648 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-01-08 18:00 | 0 | 0 | 0 | 0 | -22.3153 | 104.2109 | 114.9065 | -24.9065 | 98.5998 | 109.1489 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-01-08 19:00 | 0 | 0 | 0 | 0 | -22.31 | 119.2066 | 118.1411 | -28.1411 | 113.683 | 122.8583 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.3 | -4.3 | 1.1025 | 0
2016-01-08 20:00 | 0 | 0 | 0 | 0 | -22.3045 | 134.2023 | 121.012 | -31.012 | 129.2981 | 136.6945 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-01-08 21:00 | 0 | 0 | 0 | 0 | -22.2991 | 149.1981 | 123.2907 | -33.2907 | 145.4734 | 150.5569 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1004 | 0
2016-01-08 22:00 | 0 | 0 | 0 | 0 | -22.2937 | 164.1938 | 124.7748 | -34.7748 | 162.1322 | 164.2002 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-01-08 23:00 | 0 | 0 | 0 | 0 | -22.2882 | 179.1896 | 125.3201 | -35.3201 | 179.081 | 174.624 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3 | -3 | 1.098 | 0
2016-01-09 | 0 | 0 | 0 | 0 | -22.2828 | -165.8147 | 124.8705 | -34.8705 | -163.9554 | 165.6297 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1004 | 0
2016-01-09 01:00 | 0 | 0 | 0 | 0 | -22.2773 | -150.8189 | 123.4716 | -33.4716 | -147.2565 | 152.0523 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.8 | -2.8 | 1.0973 | 0
2016-01-09 02:00 | 0 | 0 | 0 | 0 | -22.2718 | -135.8232 | 121.2592 | -31.2592 | -131.0267 | 138.1933 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-01-09 03:00 | 0 | 0 | 0 | 0 | -22.2663 | -120.8274 | 118.4311 | -28.4311 | -115.3547 | 124.3448 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3 | -3 | 1.098 | 0
2016-01-09 04:00 | 0 | 0 | 0 | 0 | -22.2608 | -105.8316 | 115.2142 | -25.2142 | -100.2213 | 110.6119 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-01-09 05:00 | 0 | 0 | 0 | 0 | -22.2553 | -90.8359 | 111.8404 | -21.8404 | -85.5353 | 97.0903 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.4 | -3.4 | 1.0994 | 0
2016-01-09 06:00 | 0 | 0 | 0 | 0 | -22.2498 | -75.8401 | 108.5317 | -18.5317 | -71.1734 | 83.9115 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-01-09 07:00 | 0 | 0 | 0 | 0 | -22.2442 | -60.8443 | 105.4924 | -15.4924 | -57.0119 | 71.2867 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-01-09 08:00 | 0 | 0 | 0 | 0 | -22.2386 | -45.8485 | 102.9038 | -12.9038 | -42.9482 | 59.5863 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-01-09 09:00 | 0 | 0 | 0 | 0 | -22.2331 | -30.8528 | 100.9188 | -10.9188 | -28.9115 | 49.4842 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.6 | -3.6 | 1.1001 | 0
2016-01-09 10:00 | 0 | 0 | 0 | 0 | -22.2275 | -15.857 | 99.6555 | -9.6555 | -14.8665 | 42.1563 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.4 | -3.4 | 1.0994 | 0
2016-01-09 11:00 | 0 | 0 | 0 | 0 | -22.2219 | -0.8612 | 99.1899 | -9.1899 | -0.8076 | 39.1976 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.9 | -3.9 | 1.1012 | 0
2016-01-09 12:00 | 0 | 0 | 0 | 0 | -22.2163 | 14.1346 | 99.55 | -9.55 | 13.2529 | 41.5545 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-01-09 13:00 | 0 | 0 | 0 | 0 | -22.2107 | 29.1304 | 100.7135 | -10.7135 | 27.3015 | 48.4563 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-01-09 14:00 | 0 | 0 | 0 | 0 | -22.205 | 44.1262 | 102.61 | -12.61 | 41.341 | 58.3072 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-01-09 15:00 | 0 | 0 | 0 | 0 | -22.1994 | 59.122 | 105.1257 | -15.1257 | 55.4025 | 69.8651 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-01-09 16:00 | 0 | 0 | 0 | 0 | -22.1937 | 74.1178 | 108.1114 | -18.1114 | 69.5522 | 82.4075 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-01-09 17:00 | 0 | 0 | 0 | 0 | -22.188 | 89.1136 | 111.3884 | -21.3884 | 83.8891 | 95.5378 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.7 | -4.7 | 1.1039 | 0
2016-01-09 18:00 | 0 | 0 | 0 | 0 | -22.1823 | 104.1094 | 114.7548 | -24.7548 | 98.5347 | 109.0312 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-01-09 19:00 | 0 | 0 | 0 | 0 | -22.1766 | 119.1052 | 117.9902 | -27.9902 | 113.613 | 122.7501 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-01-09 20:00 | 0 | 0 | 0 | 0 | -22.1709 | 134.101 | 120.8631 | -30.8631 | 129.2201 | 136.5973 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-01-09 21:00 | 0 | 0 | 0 | 0 | -22.1652 | 149.0968 | 123.1452 | -33.1452 | 145.3845 | 150.4745 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.3 | -5.3 | 1.106 | 0
2016-01-09 22:00 | 0 | 0 | 0 | 0 | -22.1595 | 164.0926 | 124.634 | -34.634 | 162.0308 | 164.1487 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-01-09 23:00 | 0 | 0 | 0 | 0 | -22.1537 | 179.0885 | 125.1852 | -35.1852 | 178.967 | 174.7424 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.1 | -5.1 | 1.1054 | 0
2016-01-10 | 0 | 0 | 0 | 0 | -22.148 | -165.9157 | 124.7423 | -34.7423 | -164.0801 | 165.7621 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.6 | -5.6 | 1.1071 | 0
2016-01-10 01:00 | 0 | 0 | 0 | 0 | -22.1422 | -150.9199 | 123.3499 | -33.3499 | -147.3888 | 152.1585 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-01-10 02:00 | 0 | 0 | 0 | 0 | -22.1364 | -135.9241 | 121.1433 | -31.1433 | -131.1631 | 138.2845 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.105 | 0
2016-01-10 03:00 | 0 | 0 | 0 | 0 | -22.1306 | -120.9282 | 118.3192 | -28.3192 | -115.4921 | 124.4238 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-01-10 04:00 | 0 | 0 | 0 | 0 | -22.1248 | -105.9324 | 115.1045 | -25.1045 | -100.3574 | 110.6787 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.3 | -5.3 | 1.106 | 0
2016-01-10 05:00 | 0 | 0 | 0 | 0 | -22.119 | -90.9366 | 111.7308 | -21.7308 | -85.6683 | 97.1438 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.1 | -5.1 | 1.1054 | 0
2016-01-10 06:00 | 0 | 0 | 0 | 0 | -22.1131 | -75.9407 | 108.4203 | -18.4203 | -71.3022 | 83.9491 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-01-10 07:00 | 0 | 0 | 0 | 0 | -22.1073 | -60.9449 | 105.3774 | -15.3774 | -57.1355 | 71.3044 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.105 | 0
2016-01-10 08:00 | 0 | 0 | 0 | 0 | -22.1014 | -45.949 | 102.7839 | -12.7839 | -43.0656 | 59.5774 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-01-10 09:00 | 0 | 0 | 0 | 0 | -22.0955 | -30.9532 | 100.7932 | -10.7932 | -29.022 | 49.4394 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-01-10 10:00 | 0 | 0 | 0 | 0 | -22.0897 | -15.9573 | 99.5238 | -9.5238 | -14.9693 | 42.0658 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.7 | -4.7 | 1.1039 | 0
2016-01-10 11:00 | 0 | 0 | 0 | 0 | -22.0838 | -0.96144 | 99.0521 | -9.0521 | -0.90214 | 39.0618 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.105 | 0
2016-01-10 12:00 | 0 | 0 | 0 | 0 | -22.0778 | 14.0344 | 99.4066 | -9.4066 | 13.1667 | 41.3923 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.7 | -4.7 | 1.1039 | 0
2016-01-10 13:00 | 0 | 0 | 0 | 0 | -22.0719 | 29.0303 | 100.5653 | -10.5653 | 27.2235 | 48.29 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.1 | -5.1 | 1.1054 | 0
2016-01-10 14:00 | 0 | 0 | 0 | 0 | -22.066 | 44.0262 | 102.4579 | -12.4579 | 41.2702 | 58.1481 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.105 | 0
2016-01-10 15:00 | 0 | 0 | 0 | 0 | -22.06 | 59.022 | 104.9707 | -14.9707 | 55.3374 | 69.7165 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.3 | -5.3 | 1.106 | 0
2016-01-10 16:00 | 0 | 0 | 0 | 0 | -22.0541 | 74.0179 | 107.9543 | -17.9543 | 69.4909 | 82.2696 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.1 | -5.1 | 1.1054 | 0
2016-01-10 17:00 | 0 | 0 | 0 | 0 | -22.0481 | 89.0138 | 111.2303 | -21.2303 | 83.8291 | 95.4101 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-01-10 18:00 | 0 | 0 | 0 | 0 | -22.0421 | 104.0097 | 114.5965 | -24.5965 | 98.4732 | 108.9134 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.6 | -4.6 | 1.1036 | 0
2016-01-10 19:00 | 0 | 0 | 0 | 0 | -22.0361 | 119.0055 | 117.8326 | -27.8326 | 113.5467 | 122.6424 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.1033 | 0
2016-01-10 20:00 | 0 | 0 | 0 | 0 | -22.0301 | 134.0014 | 120.7074 | -30.7074 | 129.1456 | 136.5009 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.6 | -4.6 | 1.1036 | 0
2016-01-10 21:00 | 0 | 0 | 0 | 0 | -22.0241 | 148.9973 | 122.9926 | -32.9926 | 145.2989 | 150.3935 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-01-10 22:00 | 0 | 0 | 0 | 0 | -22.018 | 163.9932 | 124.486 | -34.486 | 161.9322 | 164.0992 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-01-10 23:00 | 0 | 0 | 0 | 0 | -22.012 | 178.9891 | 125.0431 | -35.0431 | 178.8553 | 174.8655 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1004 | 0
2016-01-11 | 0 | 0 | 0 | 0 | -22.0059 | -166.015 | 124.6067 | -34.6067 | -164.2032 | 165.8947 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-01-11 01:00 | 0 | 0 | 0 | 0 | -21.9999 | -151.0191 | 123.2209 | -33.2209 | -147.5201 | 152.2634 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.8 | -3.8 | 1.1008 | 0
2016-01-11 02:00 | 0 | 0 | 0 | 0 | -21.9938 | -136.0232 | 121.0199 | -31.0199 | -131.299 | 138.3738 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-01-11 03:00 | 0 | 0 | 0 | 0 | -21.9877 | -121.0273 | 118.1999 | -28.1999 | -115.6294 | 124.5002 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-01-11 04:00 | 0 | 0 | 0 | 0 | -21.9816 | -106.0313 | 114.9873 | -24.9873 | -100.4935 | 110.7426 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.0991 | 0
2016-01-11 05:00 | 0 | 0 | 0 | 0 | -21.9755 | -91.0354 | 111.6138 | -21.6138 | -85.8015 | 97.1939 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.8 | -3.8 | 1.1008 | 0
2016-01-11 06:00 | 0 | 0 | 0 | 0 | -21.9693 | -76.0395 | 108.3015 | -18.3015 | -71.431 | 83.9829 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-01-11 07:00 | 0 | 0 | 0 | 0 | -21.9632 | -61.0436 | 105.2551 | -15.2551 | -57.2589 | 71.3176 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.9 | -3.9 | 1.1012 | 0
2016-01-11 08:00 | 0 | 0 | 0 | 0 | -21.957 | -46.0477 | 102.6567 | -12.6567 | -43.1827 | 59.5634 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.4 | -3.4 | 1.0994 | 0
2016-01-11 09:00 | 0 | 0 | 0 | 0 | -21.9508 | -31.0517 | 100.6603 | -10.6603 | -29.1318 | 49.3885 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-01-11 10:00 | 0 | 0 | 0 | 0 | -21.9447 | -16.0558 | 99.3848 | -9.3848 | -15.0709 | 41.9685 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.6 | -3.6 | 1.1001 | 0
2016-01-11 11:00 | 0 | 0 | 0 | 0 | -21.9385 | -1.0599 | 98.9072 | -8.9072 | -0.9951 | 38.919 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.6 | -3.6 | 1.1001 | 0
2016-01-11 12:00 | 0 | 0 | 0 | 0 | -21.9322 | 13.9361 | 99.2562 | -9.2562 | 13.0826 | 41.224 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1004 | 0
2016-01-11 13:00 | 0 | 0 | 0 | 0 | -21.926 | 28.932 | 100.4102 | -10.4102 | 27.1479 | 48.1191 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-01-11 14:00 | 0 | 0 | 0 | 0 | -21.9198 | 43.928 | 102.299 | -12.299 | 41.2022 | 57.9859 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.6 | -3.6 | 1.1001 | 0
2016-01-11 15:00 | 0 | 0 | 0 | 0 | -21.9135 | 58.9239 | 104.8089 | -14.8089 | 55.2755 | 69.5659 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.4 | -3.4 | 1.0994 | 0
2016-01-11 16:00 | 0 | 0 | 0 | 0 | -21.9073 | 73.9199 | 107.7907 | -17.7907 | 69.433 | 82.1305 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-01-11 17:00 | 0 | 0 | 0 | 0 | -21.901 | 88.9158 | 111.0656 | -21.0656 | 83.7728 | 95.282 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.6 | -3.6 | 1.1001 | 0
2016-01-11 18:00 | 0 | 0 | 0 | 0 | -21.8947 | 103.9118 | 114.4316 | -24.4316 | 98.4153 | 108.7957 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.9 | -3.9 | 1.1012 | 0
2016-01-11 19:00 | 0 | 0 | 0 | 0 | -21.8884 | 118.9078 | 117.6684 | -27.6684 | 113.484 | 122.5353 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.9 | -3.9 | 1.1012 | 0
2016-01-11 20:00 | 0 | 0 | 0 | 0 | -21.8821 | 133.9037 | 120.545 | -30.545 | 129.0746 | 136.4055 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-01-11 21:00 | 0 | 0 | 0 | 0 | -21.8758 | 148.8997 | 122.8333 | -32.8333 | 145.2166 | 150.3139 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-01-11 22:00 | 0 | 0 | 0 | 0 | -21.8695 | 163.8957 | 124.331 | -34.331 | 161.8364 | 164.0514 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-01-11 23:00 | 0 | 0 | 0 | 0 | -21.8631 | 178.8916 | 124.8937 | -34.8937 | 178.7459 | 174.9933 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-01-12 | 0 | 0 | 0 | 0 | -21.8568 | -166.1124 | 124.4638 | -34.4638 | -164.3246 | 166.0272 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.0991 | 0
2016-01-12 01:00 | 0 | 0 | 0 | 0 | -21.8504 | -151.1164 | 123.0845 | -33.0845 | -147.6503 | 152.3667 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1004 | 0
2016-01-12 02:00 | 0 | 0 | 0 | 0 | -21.844 | -136.1204 | 120.8891 | -30.8891 | -131.4343 | 138.4609 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.0991 | 0
2016-01-12 03:00 | 0 | 0 | 0 | 0 | -21.8376 | -121.1244 | 118.0733 | -28.0733 | -115.7664 | 124.5741 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.0991 | 0
2016-01-12 04:00 | 0 | 0 | 0 | 0 | -21.8312 | -106.1284 | 114.8629 | -24.8629 | -100.6295 | 110.8035 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.6 | -3.6 | 1.1001 | 0
2016-01-12 05:00 | 0 | 0 | 0 | 0 | -21.8248 | -91.1324 | 111.4895 | -21.4895 | -85.9346 | 97.2406 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1004 | 0
2016-01-12 06:00 | 0 | 0 | 0 | 0 | -21.8184 | -76.1364 | 108.1753 | -18.1753 | -71.5597 | 84.0128 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-01-12 07:00 | 0 | 0 | 0 | 0 | -21.8119 | -61.1404 | 105.1254 | -15.1254 | -57.3821 | 71.3263 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.3 | -4.3 | 1.1025 | 0
2016-01-12 08:00 | 0 | 0 | 0 | 0 | -21.8055 | -46.1444 | 102.5222 | -12.5222 | -43.2992 | 59.5441 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.3 | -4.3 | 1.1025 | 0
2016-01-12 09:00 | 0 | 0 | 0 | 0 | -21.799 | -31.1484 | 100.5202 | -10.5202 | -29.2407 | 49.3317 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-01-12 10:00 | 0 | 0 | 0 | 0 | -21.7925 | -16.1524 | 99.2387 | -9.2387 | -15.1713 | 41.8645 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.7 | -4.7 | 1.1039 | 0
2016-01-12 11:00 | 0 | 0 | 0 | 0 | -21.786 | -1.1564 | 98.7552 | -8.7552 | -1.0864 | 38.7693 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.3 | -5.3 | 1.106 | 0
2016-01-12 12:00 | 0 | 0 | 0 | 0 | -21.7795 | 13.8397 | 99.0988 | -9.0988 | 13.0006 | 41.0497 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.9 | -5.9 | 1.1081 | 0
2016-01-12 13:00 | 0 | 0 | 0 | 0 | -21.773 | 28.8357 | 100.2483 | -10.2483 | 27.0748 | 47.9437 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.9 | -6.9 | 1.1117 | 0
2016-01-12 14:00 | 0 | 0 | 0 | 0 | -21.7665 | 43.8317 | 102.1333 | -12.1333 | 41.137 | 57.8205 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7 | -7 | 1.112 | 0
2016-01-12 15:00 | 0 | 0 | 0 | 0 | -21.76 | 58.8278 | 104.6406 | -14.6406 | 55.2168 | 69.4133 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.9 | -8.9 | 1.1186 | 0
2016-01-12 16:00 | 0 | 0 | 0 | 0 | -21.7534 | 73.8238 | 107.6206 | -17.6206 | 69.3786 | 81.9903 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.9 | -8.9 | 1.1186 | 0
2016-01-12 17:00 | 0 | 0 | 0 | 0 | -21.7468 | 88.8198 | 110.8944 | -20.8944 | 83.72 | 95.1533 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.3 | -9.3 | 1.12 | 0
2016-01-12 18:00 | 0 | 0 | 0 | 0 | -21.7403 | 103.8159 | 114.2602 | -24.2602 | 98.3612 | 108.6781 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.7 | -8.7 | 1.1179 | 0
2016-01-12 19:00 | 0 | 0 | 0 | 0 | -21.7337 | 118.8119 | 117.4977 | -27.4977 | 113.425 | 122.4287 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.6 | -9.6 | 1.1211 | 0
2016-01-12 20:00 | 0 | 0 | 0 | 0 | -21.7271 | 133.808 | 120.376 | -30.376 | 129.0072 | 136.3111 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.7 | -9.7 | 1.1215 | 0
2016-01-12 21:00 | 0 | 0 | 0 | 0 | -21.7205 | 148.804 | 122.6671 | -32.6671 | 145.1376 | 150.2356 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.6 | -9.6 | 1.1211 | 0
2016-01-12 22:00 | 0 | 0 | 0 | 0 | -21.7138 | 163.8001 | 124.1691 | -34.1691 | 161.7437 | 164.0052 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.4 | -10.4 | 1.1239 | 0
2016-01-12 23:00 | 0 | 0 | 0 | 0 | -21.7072 | 178.7961 | 124.7373 | -34.7373 | 178.6389 | 175.1254 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.7 | -9.7 | 1.1215 | 0
2016-01-13 | 0 | 0 | 0 | 0 | -21.7005 | -166.2078 | 124.3137 | -34.3137 | -164.4441 | 166.1594 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.4 | -9.4 | 1.1204 | 0
2016-01-13 01:00 | 0 | 0 | 0 | 0 | -21.6939 | -151.2117 | 122.9407 | -32.9407 | -147.7792 | 152.4684 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.3 | -9.3 | 1.12 | 0
2016-01-13 02:00 | 0 | 0 | 0 | 0 | -21.6872 | -136.2157 | 120.751 | -30.751 | -131.5688 | 138.5458 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.4 | -9.4 | 1.1204 | 0
2016-01-13 03:00 | 0 | 0 | 0 | 0 | -21.6805 | -121.2196 | 117.9393 | -27.9393 | -115.903 | 124.6453 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.9 | -8.9 | 1.1186 | 0
2016-01-13 04:00 | 0 | 0 | 0 | 0 | -21.6738 | -106.2235 | 114.7311 | -24.7311 | -100.7654 | 110.8613 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.9 | -8.9 | 1.1186 | 0
2016-01-13 05:00 | 0 | 0 | 0 | 0 | -21.6671 | -91.2274 | 111.3578 | -21.3578 | -86.0676 | 97.2837 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.1 | -9.1 | 1.1194 | 0
2016-01-13 06:00 | 0 | 0 | 0 | 0 | -21.6604 | -76.2313 | 108.0419 | -18.0419 | -71.6883 | 84.0386 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.2 | -8.2 | 1.1162 | 0
2016-01-13 07:00 | 0 | 0 | 0 | 0 | -21.6537 | -61.2352 | 104.9885 | -14.9885 | -57.5049 | 71.3304 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9 | -9 | 1.119 | 0
2016-01-13 08:00 | 0 | 0 | 0 | 0 | -21.6469 | -46.2391 | 102.3806 | -12.3806 | -43.4152 | 59.5196 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.7 | -8.7 | 1.1179 | 0
2016-01-13 09:00 | 0 | 0 | 0 | 0 | -21.6402 | -31.2431 | 100.3729 | -10.3729 | -29.3487 | 49.2689 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.4 | -8.4 | 1.1169 | 0
2016-01-13 10:00 | 0 | 0 | 0 | 0 | -21.6334 | -16.247 | 99.0855 | -9.0855 | -15.2704 | 41.7538 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.6 | -7.6 | 1.1141 | 0
2016-01-13 11:00 | 0 | 0 | 0 | 0 | -21.6266 | -1.2508 | 98.5962 | -8.5962 | -1.176 | 38.6127 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.8 | -7.8 | 1.1148 | 0
2016-01-13 12:00 | 0 | 0 | 0 | 0 | -21.6198 | 13.7453 | 98.9345 | -8.9345 | 12.9207 | 40.8694 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.5 | -8.5 | 1.1173 | 0
2016-01-13 13:00 | 0 | 0 | 0 | 0 | -21.613 | 28.7414 | 100.0795 | -10.0795 | 27.0043 | 47.7638 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.5 | -8.5 | 1.1173 | 0
2016-01-13 14:00 | 0 | 0 | 0 | 0 | -21.6062 | 43.7375 | 101.9611 | -11.9611 | 41.0748 | 57.6522 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.7 | -7.7 | 1.1144 | 0
2016-01-13 15:00 | 0 | 0 | 0 | 0 | -21.5993 | 58.7336 | 104.4658 | -14.4658 | 55.1613 | 69.2588 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.2 | -8.2 | 1.1162 | 0
2016-01-13 16:00 | 0 | 0 | 0 | 0 | -21.5925 | 73.7297 | 107.444 | -17.444 | 69.3276 | 81.8491 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8 | -8 | 1.1155 | 0
2016-01-13 17:00 | 0 | 0 | 0 | 0 | -21.5856 | 88.7258 | 110.7169 | -20.7169 | 83.6709 | 95.0244 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.2 | -8.2 | 1.1162 | 0
2016-01-13 18:00 | 0 | 0 | 0 | 0 | -21.5788 | 103.722 | 114.0825 | -24.0825 | 98.3108 | 108.5606 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.6 | -7.6 | 1.1141 | 0
2016-01-13 19:00 | 0 | 0 | 0 | 0 | -21.5719 | 118.7181 | 117.3206 | -27.3206 | 113.3699 | 122.3227 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.3 | -7.3 | 1.1131 | 0
2016-01-13 20:00 | 0 | 0 | 0 | 0 | -21.565 | 133.7142 | 120.2004 | -30.2004 | 128.9436 | 136.2177 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.1 | -7.1 | 1.1123 | 0
2016-01-13 21:00 | 0 | 0 | 0 | 0 | -21.5581 | 148.7104 | 122.4942 | -32.4942 | 145.062 | 150.1586 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7 | -7 | 1.112 | 0
2016-01-13 22:00 | 0 | 0 | 0 | 0 | -21.5512 | 163.7065 | 124.0003 | -34.0003 | 161.6539 | 163.9605 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.3 | -7.3 | 1.1131 | 0
2016-01-13 23:00 | 0 | 0 | 0 | 0 | -21.5443 | 178.7027 | 124.5739 | -34.5739 | 178.5345 | 175.2615 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-01-14 | 0 | 0 | 0 | 0 | -21.5373 | -166.3012 | 124.1565 | -34.1565 | -164.5617 | 166.2909 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.4 | -6.4 | 1.1099 | 0
2016-01-14 01:00 | 0 | 0 | 0 | 0 | -21.5304 | -151.305 | 122.7898 | -32.7898 | -147.9067 | 152.5682 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.9 | -6.9 | 1.1117 | 0
2016-01-14 02:00 | 0 | 0 | 0 | 0 | -21.5234 | -136.3089 | 120.6056 | -30.6056 | -131.7024 | 138.6282 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.8 | -5.8 | 1.1078 | 0
2016-01-14 03:00 | 0 | 0 | 0 | 0 | -21.5164 | -121.3127 | 117.798 | -27.798 | -116.039 | 124.7137 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-01-14 04:00 | 0 | 0 | 0 | 0 | -21.5094 | -106.3165 | 114.592 | -24.592 | -100.9009 | 110.9159 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.6 | -5.6 | 1.1071 | 0
2016-01-14 05:00 | 0 | 0 | 0 | 0 | -21.5024 | -91.3204 | 111.219 | -21.219 | -86.2004 | 97.3233 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.1033 | 0
2016-01-14 06:00 | 0 | 0 | 0 | 0 | -21.4954 | -76.3242 | 107.9012 | -17.9012 | -71.8166 | 84.0604 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3 | -3 | 1.098 | 0
2016-01-14 07:00 | 0 | 0 | 0 | 0 | -21.4884 | -61.328 | 104.8444 | -14.8444 | -57.6273 | 71.33 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-01-14 08:00 | 0 | 0 | 0 | 0 | -21.4814 | -46.3318 | 102.2317 | -12.2317 | -43.5304 | 59.4899 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-01-14 09:00 | 0 | 0 | 0 | 0 | -21.4743 | -31.3356 | 100.2185 | -10.2185 | -29.4556 | 49.2002 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-01-14 10:00 | 0 | 0 | 0 | 0 | -21.4673 | -16.3395 | 98.9252 | -8.9252 | -15.3681 | 41.6365 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-01-14 11:00 | 0 | 0 | 0 | 0 | -21.4602 | -1.3433 | 98.4302 | -8.4302 | -1.2638 | 38.4494 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-01-14 12:00 | 0 | 0 | 0 | 0 | -21.4531 | 13.6529 | 98.7634 | -8.7634 | 12.8431 | 40.6833 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.6 | -4.6 | 1.1036 | 0
2016-01-14 13:00 | 0 | 0 | 0 | 0 | -21.446 | 28.6491 | 99.9041 | -9.9041 | 26.9363 | 47.5797 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.7 | -4.7 | 1.1039 | 0
2016-01-14 14:00 | 0 | 0 | 0 | 0 | -21.4389 | 43.6453 | 101.7823 | -11.7823 | 41.0155 | 57.481 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-01-14 15:00 | 0 | 0 | 0 | 0 | -21.4318 | 58.6415 | 104.2845 | -14.2845 | 55.109 | 69.1026 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-01-14 16:00 | 0 | 0 | 0 | 0 | -21.4246 | 73.6378 | 107.2611 | -17.2611 | 69.2802 | 81.707 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.6 | -4.6 | 1.1036 | 0
2016-01-14 17:00 | 0 | 0 | 0 | 0 | -21.4175 | 88.634 | 110.5332 | -20.5332 | 83.6256 | 94.8951 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-01-14 18:00 | 0 | 0 | 0 | 0 | -21.4103 | 103.6302 | 113.8985 | -23.8985 | 98.2643 | 108.4434 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.8 | -5.8 | 1.1078 | 0
2016-01-14 19:00 | 0 | 0 | 0 | 0 | -21.4032 | 118.6264 | 117.1371 | -27.1371 | 113.3185 | 122.2174 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.1 | -6.1 | 1.1088 | 0
2016-01-14 20:00 | 0 | 0 | 0 | 0 | -21.396 | 133.6226 | 120.0183 | -30.0183 | 128.8836 | 136.1253 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.8 | -5.8 | 1.1078 | 0
2016-01-14 21:00 | 0 | 0 | 0 | 0 | -21.3888 | 148.6189 | 122.3147 | -32.3147 | 144.99 | 150.0829 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.4 | -5.4 | 1.1064 | 0
2016-01-14 22:00 | 0 | 0 | 0 | 0 | -21.3816 | 163.6151 | 123.8247 | -33.8247 | 161.5673 | 163.9172 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.3 | -5.3 | 1.106 | 0
2016-01-14 23:00 | 0 | 0 | 0 | 0 | -21.3744 | 178.6113 | 124.4034 | -34.4034 | 178.4327 | 175.4014 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.5 | -5.5 | 1.1067 | 0
2016-01-15 | 0 | 0 | 0 | 0 | -21.3672 | -166.3924 | 123.9921 | -33.9921 | -164.6772 | 166.4215 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.4 | -6.4 | 1.1099 | 0
2016-01-15 01:00 | 0 | 0 | 0 | 0 | -21.3599 | -151.3962 | 122.6317 | -32.6317 | -148.0328 | 152.6658 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6 | -6 | 1.1085 | 0
2016-01-15 02:00 | 0 | 0 | 0 | 0 | -21.3527 | -136.3999 | 120.453 | -30.453 | -131.835 | 138.7081 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.3 | -6.3 | 1.1096 | 0
2016-01-15 03:00 | 0 | 0 | 0 | 0 | -21.3454 | -121.4037 | 117.6495 | -27.6495 | -116.1744 | 124.7792 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.3 | -6.3 | 1.1096 | 0
2016-01-15 04:00 | 0 | 0 | 0 | 0 | -21.3381 | -106.4074 | 114.4458 | -24.4458 | -101.036 | 110.9672 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-01-15 05:00 | 0 | 0 | 0 | 0 | -21.3308 | -91.4111 | 111.0729 | -21.0729 | -86.3328 | 97.3592 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-01-15 06:00 | 0 | 0 | 0 | 0 | -21.3235 | -76.4149 | 107.7534 | -17.7534 | -71.9445 | 84.0782 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-01-15 07:00 | 0 | 0 | 0 | 0 | -21.3162 | -61.4186 | 104.6932 | -14.6932 | -57.7492 | 71.325 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.7 | -4.7 | 1.1039 | 0
2016-01-15 08:00 | 0 | 0 | 0 | 0 | -21.3089 | -46.4223 | 102.0758 | -12.0758 | -43.6449 | 59.4551 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.105 | 0
2016-01-15 09:00 | 0 | 0 | 0 | 0 | -21.3016 | -31.4261 | 100.057 | -10.057 | -29.5615 | 49.1256 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.3 | -4.3 | 1.1025 | 0
2016-01-15 10:00 | 0 | 0 | 0 | 0 | -21.2942 | -16.4298 | 98.758 | -8.758 | -15.4644 | 41.5126 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.6 | -4.6 | 1.1036 | 0
2016-01-15 11:00 | 0 | 0 | 0 | 0 | -21.2869 | -1.4335 | 98.2573 | -8.2573 | -1.3497 | 38.2793 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-01-15 12:00 | 0 | 0 | 0 | 0 | -21.2795 | 13.5628 | 98.5856 | -8.5856 | 12.7677 | 40.4913 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4 | -4 | 1.1015 | 0
2016-01-15 13:00 | 0 | 0 | 0 | 0 | -21.2721 | 28.5591 | 99.7221 | -9.7221 | 26.8711 | 47.3913 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.3 | -4.3 | 1.1025 | 0
2016-01-15 14:00 | 0 | 0 | 0 | 0 | -21.2647 | 43.5554 | 101.597 | -11.597 | 40.9593 | 57.3071 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.9 | -3.9 | 1.1012 | 0
2016-01-15 15:00 | 0 | 0 | 0 | 0 | -21.2573 | 58.5517 | 104.097 | -14.097 | 55.0601 | 68.9447 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-01-15 16:00 | 0 | 0 | 0 | 0 | -21.2499 | 73.548 | 107.072 | -17.072 | 69.2364 | 81.5641 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-01-15 17:00 | 0 | 0 | 0 | 0 | -21.2425 | 88.5443 | 110.3432 | -20.3432 | 83.584 | 94.7657 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.4 | -3.4 | 1.0994 | 0
2016-01-15 18:00 | 0 | 0 | 0 | 0 | -21.235 | 103.5406 | 113.7083 | -23.7083 | 98.2216 | 108.3265 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.8 | -2.8 | 1.0973 | 0
2016-01-15 19:00 | 0 | 0 | 0 | 0 | -21.2276 | 118.5369 | 116.9474 | -26.9474 | 113.2711 | 122.1128 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-01-15 20:00 | 0 | 0 | 0 | 0 | -21.2201 | 133.5332 | 119.8299 | -29.8299 | 128.8275 | 136.0339 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-01-15 21:00 | 0 | 0 | 0 | 0 | -21.2126 | 148.5296 | 122.1287 | -32.1287 | 144.9215 | 150.0085 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-01-15 22:00 | 0 | 0 | 0 | 0 | -21.2052 | 163.5259 | 123.6424 | -33.6424 | 161.4839 | 163.8751 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2 | -2 | 1.0945 | 0
2016-01-15 23:00 | 0 | 0 | 0 | 0 | -21.1977 | 178.5222 | 124.2261 | -34.2261 | 178.3336 | 175.5446 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-01-16 | 0 | 0 | 0 | 0 | -21.1901 | -166.4815 | 123.8208 | -33.8208 | -164.7905 | 166.5508 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-01-16 01:00 | 0 | 0 | 0 | 0 | -21.1826 | -151.4851 | 122.4664 | -32.4664 | -148.1572 | 152.7612 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.8 | -2.8 | 1.0973 | 0
2016-01-16 02:00 | 0 | 0 | 0 | 0 | -21.1751 | -136.4888 | 120.2932 | -30.2932 | -131.9665 | 138.7853 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-01-16 03:00 | 0 | 0 | 0 | 0 | -21.1675 | -121.4924 | 117.4938 | -27.4938 | -116.3091 | 124.8416 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-01-16 04:00 | 0 | 0 | 0 | 0 | -21.16 | -106.4961 | 114.2923 | -24.2923 | -101.1706 | 111.0153 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-01-16 05:00 | 0 | 0 | 0 | 0 | -21.1524 | -91.4997 | 110.9197 | -20.9197 | -86.4647 | 97.3915 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-01-16 06:00 | 0 | 0 | 0 | 0 | -21.1448 | -76.5034 | 107.5985 | -17.5985 | -72.0718 | 84.0918 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2 | -2 | 1.0945 | 0
2016-01-16 07:00 | 0 | 0 | 0 | 0 | -21.1372 | -61.507 | 104.5348 | -14.5348 | -57.8704 | 71.3154 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-01-16 08:00 | 0 | 0 | 0 | 0 | -21.1296 | -46.5106 | 101.9128 | -11.9128 | -43.7585 | 59.4151 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-01-16 09:00 | 0 | 0 | 0 | 0 | -21.122 | -31.5143 | 99.8886 | -9.8886 | -29.6662 | 49.0451 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3 | -3 | 1.098 | 0
2016-01-16 10:00 | 0 | 0 | 0 | 0 | -21.1144 | -16.5179 | 98.5838 | -8.5838 | -15.559 | 41.3822 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-01-16 11:00 | 0 | 0 | 0 | 0 | -21.1067 | -1.5215 | 98.0777 | -8.0777 | -1.4336 | 38.1026 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-01-16 12:00 | 0 | 0 | 0 | 0 | -21.0991 | 13.4749 | 98.4011 | -8.4011 | 12.6947 | 40.2937 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-01-16 13:00 | 0 | 0 | 0 | 0 | -21.0914 | 28.4713 | 99.5335 | -9.5335 | 26.8085 | 47.1988 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-01-16 14:00 | 0 | 0 | 0 | 0 | -21.0838 | 43.4677 | 101.4054 | -11.4054 | 40.9062 | 57.1305 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-01-16 15:00 | 0 | 0 | 0 | 0 | -21.0761 | 58.4641 | 103.9031 | -13.9031 | 55.0146 | 68.7853 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-01-16 16:00 | 0 | 0 | 0 | 0 | -21.0684 | 73.4605 | 106.8767 | -16.8767 | 69.1962 | 81.4205 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-01-16 17:00 | 0 | 0 | 0 | 0 | -21.0607 | 88.4569 | 110.1471 | -20.1471 | 83.5462 | 94.6362 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-01-16 18:00 | 0 | 0 | 0 | 0 | -21.0529 | 103.4533 | 113.512 | -23.512 | 98.1829 | 108.21 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-01-16 19:00 | 0 | 0 | 0 | 0 | -21.0452 | 118.4497 | 116.7515 | -26.7515 | 113.2276 | 122.0089 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-01-16 20:00 | 0 | 0 | 0 | 0 | -21.0375 | 133.4461 | 119.6352 | -29.6352 | 128.7752 | 135.9435 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-01-16 21:00 | 0 | 0 | 0 | 0 | -21.0297 | 148.4425 | 121.9363 | -31.9363 | 144.8567 | 149.9353 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-01-16 22:00 | 0 | 0 | 0 | 0 | -21.0219 | 163.4389 | 123.4535 | -33.4535 | 161.4038 | 163.834 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-01-16 23:00 | 0 | 0 | 0 | 0 | -21.0142 | 178.4354 | 124.0421 | -34.0421 | 178.2373 | 175.6907 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2 | -2 | 1.0945 | 0
2016-01-17 | 0 | 0 | 0 | 0 | -21.0064 | -166.5682 | 123.6425 | -33.6425 | -164.9016 | 166.6783 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-01-17 01:00 | 0 | 0 | 0 | 0 | -20.9986 | -151.5718 | 122.2941 | -32.2941 | -148.2799 | 152.8541 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-01-17 02:00 | 0 | 0 | 0 | 0 | -20.9907 | -136.5753 | 120.1264 | -30.1264 | -132.0967 | 138.8597 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-01-17 03:00 | 0 | 0 | 0 | 0 | -20.9829 | -121.5789 | 117.331 | -27.331 | -116.4428 | 124.901 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-01-17 04:00 | 0 | 0 | 0 | 0 | -20.9751 | -106.5824 | 114.1318 | -24.1318 | -101.3045 | 111.0599 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-01-17 05:00 | 0 | 0 | 0 | 0 | -20.9672 | -91.586 | 110.7594 | -20.7594 | -86.5961 | 97.42 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-01-17 06:00 | 0 | 0 | 0 | 0 | -20.9594 | -76.5895 | 107.4365 | -17.4365 | -72.1986 | 84.1013 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-01-17 07:00 | 0 | 0 | 0 | 0 | -20.9515 | -61.5931 | 104.3695 | -14.3695 | -57.9909 | 71.3012 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-01-17 08:00 | 0 | 0 | 0 | 0 | -20.9436 | -46.5966 | 101.7428 | -11.7428 | -43.8711 | 59.3699 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-01-17 09:00 | 0 | 0 | 0 | 0 | -20.9357 | -31.6001 | 99.7132 | -9.7132 | -29.7696 | 48.9589 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-01-17 10:00 | 0 | 0 | 0 | 0 | -20.9278 | -16.6037 | 98.4028 | -8.4028 | -15.6521 | 41.2453 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-01-17 11:00 | 0 | 0 | 0 | 0 | -20.9199 | -1.6072 | 97.8913 | -7.8913 | -1.5156 | 37.9193 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-01-17 12:00 | 0 | 0 | 0 | 0 | -20.912 | 13.3893 | 98.21 | -8.21 | 12.6241 | 40.0905 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-01-17 13:00 | 0 | 0 | 0 | 0 | -20.904 | 28.3858 | 99.3386 | -9.3386 | 26.7488 | 47.0024 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-01-17 14:00 | 0 | 0 | 0 | 0 | -20.8961 | 43.3823 | 101.2075 | -11.2075 | 40.8561 | 56.9514 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-01-17 15:00 | 0 | 0 | 0 | 0 | -20.8881 | 58.3788 | 103.7031 | -13.7031 | 54.9725 | 68.6245 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-01-17 16:00 | 0 | 0 | 0 | 0 | -20.8801 | 73.3753 | 106.6753 | -16.6753 | 69.1596 | 81.2762 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-01-17 17:00 | 0 | 0 | 0 | 0 | -20.8721 | 88.3718 | 109.945 | -19.945 | 83.5122 | 94.5067 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-01-17 18:00 | 0 | 0 | 0 | 0 | -20.8641 | 103.3683 | 113.3097 | -23.3097 | 98.1481 | 108.0939 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-01-17 19:00 | 0 | 0 | 0 | 0 | -20.8561 | 118.3648 | 116.5495 | -26.5495 | 113.1881 | 121.9058 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-01-17 20:00 | 0 | 0 | 0 | 0 | -20.8481 | 133.3613 | 119.4343 | -29.4343 | 128.7268 | 135.8542 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-01-17 21:00 | 0 | 0 | 0 | 0 | -20.8401 | 148.3578 | 121.7375 | -31.7375 | 144.7955 | 149.8633 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-01-17 22:00 | 0 | 0 | 0 | 0 | -20.832 | 163.3544 | 123.258 | -33.258 | 161.3271 | 163.7939 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-01-17 23:00 | 0 | 0 | 0 | 0 | -20.824 | 178.3509 | 123.8513 | -33.8513 | 178.1439 | 175.8393 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-01-18 | 0 | 0 | 0 | 0 | -20.8159 | -166.6526 | 123.4573 | -33.4573 | -165.0103 | 166.8039 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-01-18 01:00 | 0 | 0 | 0 | 0 | -20.8078 | -151.656 | 122.1149 | -32.1149 | -148.4007 | 152.9442 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-01-18 02:00 | 0 | 0 | 0 | 0 | -20.7997 | -136.6595 | 119.9525 | -29.9525 | -132.2256 | 138.9311 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-01-18 03:00 | 0 | 0 | 0 | 0 | -20.7916 | -121.663 | 117.1612 | -27.1612 | -116.5756 | 124.9571 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-01-18 04:00 | 0 | 0 | 0 | 0 | -20.7835 | -106.6664 | 113.9642 | -23.9642 | -101.4376 | 111.101 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-01-18 05:00 | 0 | 0 | 0 | 0 | -20.7754 | -91.6699 | 110.5921 | -20.5921 | -86.7268 | 97.4446 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-01-18 06:00 | 0 | 0 | 0 | 0 | -20.7672 | -76.6733 | 107.2675 | -17.2675 | -72.3247 | 84.1067 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-01-18 07:00 | 0 | 0 | 0 | 0 | -20.7591 | -61.6767 | 104.1971 | -14.1971 | -58.1105 | 71.2824 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-01-18 08:00 | 0 | 0 | 0 | 0 | -20.7509 | -46.6802 | 101.5659 | -11.5659 | -43.9827 | 59.3196 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-01-18 09:00 | 0 | 0 | 0 | 0 | -20.7428 | -31.6836 | 99.531 | -9.531 | -29.8716 | 48.8668 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-01-18 10:00 | 0 | 0 | 0 | 0 | -20.7346 | -16.687 | 98.2151 | -8.2151 | -15.7434 | 41.1021 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-01-18 11:00 | 0 | 0 | 0 | 0 | -20.7264 | -1.6905 | 97.6984 | -7.6984 | -1.5954 | 37.7295 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-01-18 12:00 | 0 | 0 | 0 | 0 | -20.7182 | 13.3061 | 98.0124 | -8.0124 | 12.5559 | 39.8818 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-01-18 13:00 | 0 | 0 | 0 | 0 | -20.71 | 28.3027 | 99.1372 | -9.1372 | 26.6919 | 46.8022 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-01-18 14:00 | 0 | 0 | 0 | 0 | -20.7017 | 43.2993 | 101.0033 | -11.0033 | 40.8093 | 56.77 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-01-18 15:00 | 0 | 0 | 0 | 0 | -20.6935 | 58.2959 | 103.497 | -13.497 | 54.9339 | 68.4625 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-01-18 16:00 | 0 | 0 | 0 | 0 | -20.6852 | 73.2925 | 106.468 | -16.468 | 69.1268 | 81.1315 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-01-18 17:00 | 0 | 0 | 0 | 0 | -20.677 | 88.2891 | 109.737 | -19.737 | 83.4822 | 94.3772 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-01-18 18:00 | 0 | 0 | 0 | 0 | -20.6687 | 103.2857 | 113.1015 | -23.1015 | 98.1173 | 107.9784 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-01-18 19:00 | 0 | 0 | 0 | 0 | -20.6604 | 118.2823 | 116.3416 | -26.3416 | 113.1525 | 121.8036 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-01-18 20:00 | 0 | 0 | 0 | 0 | -20.6521 | 133.279 | 119.2273 | -29.2273 | 128.6824 | 135.766 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-01-18 21:00 | 0 | 0 | 0 | 0 | -20.6438 | 148.2756 | 121.5324 | -31.5324 | 144.7381 | 149.7924 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-01-18 22:00 | 0 | 0 | 0 | 0 | -20.6355 | 163.2722 | 123.0561 | -33.0561 | 161.2537 | 163.7546 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-01-18 23:00 | 0 | 0 | 0 | 0 | -20.6272 | 178.2688 | 123.6539 | -33.6539 | 178.0535 | 175.9895 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-01-19 | 0 | 0 | 0 | 0 | -20.6188 | -166.7345 | 123.2654 | -33.2654 | -165.1166 | 166.927 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-01-19 01:00 | 0 | 0 | 0 | 0 | -20.6105 | -151.7379 | 121.9288 | -31.9288 | -148.5197 | 153.0315 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-01-19 02:00 | 0 | 0 | 0 | 0 | -20.6021 | -136.7413 | 119.7717 | -29.7717 | -132.353 | 138.9994 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-01-19 03:00 | 0 | 0 | 0 | 0 | -20.5937 | -121.7446 | 116.9844 | -26.9844 | -116.7072 | 125.01 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-01-19 04:00 | 0 | 0 | 0 | 0 | -20.5853 | -106.748 | 113.7897 | -23.7897 | -101.5698 | 111.1385 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-01-19 05:00 | 0 | 0 | 0 | 0 | -20.5769 | -91.7513 | 110.4178 | -20.4178 | -86.8568 | 97.4655 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-01-19 06:00 | 0 | 0 | 0 | 0 | -20.5685 | -76.7546 | 107.0916 | -17.0916 | -72.45 | 84.1079 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-01-19 07:00 | 0 | 0 | 0 | 0 | -20.5601 | -61.758 | 104.0179 | -14.0179 | -58.2292 | 71.2591 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-01-19 08:00 | 0 | 0 | 0 | 0 | -20.5517 | -46.7613 | 101.3822 | -11.3822 | -44.0931 | 59.2642 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-01-19 09:00 | 0 | 0 | 0 | 0 | -20.5432 | -31.7646 | 99.342 | -9.342 | -29.9722 | 48.769 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2 | -2 | 1.0945 | 0
2016-01-19 10:00 | 0 | 0 | 0 | 0 | -20.5348 | -16.7679 | 98.0207 | -8.0207 | -15.833 | 40.9524 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-01-19 11:00 | 0 | 0 | 0 | 0 | -20.5263 | -1.7713 | 97.4988 | -7.4988 | -1.6731 | 37.5332 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-01-19 12:00 | 0 | 0 | 0 | 0 | -20.5178 | 13.2254 | 97.8083 | -7.8083 | 12.4903 | 39.6677 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-01-19 13:00 | 0 | 0 | 0 | 0 | -20.5093 | 28.2221 | 98.9296 | -8.9296 | 26.6379 | 46.5982 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-01-19 14:00 | 0 | 0 | 0 | 0 | -20.5008 | 43.2188 | 100.7931 | -10.7931 | 40.7657 | 56.5863 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.8 | -2.8 | 1.0973 | 0
2016-01-19 15:00 | 0 | 0 | 0 | 0 | -20.4923 | 58.2155 | 103.285 | -13.285 | 54.8989 | 68.2992 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-01-19 16:00 | 0 | 0 | 0 | 0 | -20.4838 | 73.2122 | 106.2549 | -16.2549 | 69.0977 | 80.9863 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4 | -4 | 1.1015 | 0
2016-01-19 17:00 | 0 | 0 | 0 | 0 | -20.4753 | 88.2089 | 109.5232 | -19.5232 | 83.4561 | 94.2479 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.7 | -4.7 | 1.1039 | 0
2016-01-19 18:00 | 0 | 0 | 0 | 0 | -20.4667 | 103.2056 | 112.8875 | -22.8875 | 98.0905 | 107.8633 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-01-19 19:00 | 0 | 0 | 0 | 0 | -20.4582 | 118.2024 | 116.1278 | -26.1278 | 113.1211 | 121.7022 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.7 | -4.7 | 1.1039 | 0
2016-01-19 20:00 | 0 | 0 | 0 | 0 | -20.4496 | 133.1991 | 119.0144 | -29.0144 | 128.6419 | 135.6788 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6 | -6 | 1.1085 | 0
2016-01-19 21:00 | 0 | 0 | 0 | 0 | -20.441 | 148.1958 | 121.3212 | -31.3212 | 144.6845 | 149.7226 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.7 | -6.7 | 1.111 | 0
2016-01-19 22:00 | 0 | 0 | 0 | 0 | -20.4324 | 163.1925 | 122.8479 | -32.8479 | 161.1838 | 163.7159 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-01-19 23:00 | 0 | 0 | 0 | 0 | -20.4238 | 178.1893 | 123.4499 | -33.4499 | 177.9662 | 176.1409 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.4 | -6.4 | 1.1099 | 0
2016-01-20 | 0 | 0 | 0 | 0 | -20.4152 | -166.814 | 123.0667 | -33.0667 | -165.2203 | 167.0473 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.5 | -6.5 | 1.1102 | 0
2016-01-20 01:00 | 0 | 0 | 0 | 0 | -20.4066 | -151.8172 | 121.7359 | -31.7359 | -148.6366 | 153.1156 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.7 | -5.7 | 1.1075 | 0
2016-01-20 02:00 | 0 | 0 | 0 | 0 | -20.398 | -136.8205 | 119.584 | -29.584 | -132.4788 | 139.0645 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.1 | -5.1 | 1.1054 | 0
2016-01-20 03:00 | 0 | 0 | 0 | 0 | -20.3893 | -121.8237 | 116.8007 | -26.8007 | -116.8376 | 125.0594 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-01-20 04:00 | 0 | 0 | 0 | 0 | -20.3807 | -106.827 | 113.6082 | -23.6082 | -101.7011 | 111.1724 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.3 | -5.3 | 1.106 | 0
2016-01-20 05:00 | 0 | 0 | 0 | 0 | -20.372 | -91.8302 | 110.2366 | -20.2366 | -86.9858 | 97.4824 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.7 | -5.7 | 1.1075 | 0
2016-01-20 06:00 | 0 | 0 | 0 | 0 | -20.3633 | -76.8334 | 106.9088 | -16.9088 | -72.5745 | 84.1048 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-01-20 07:00 | 0 | 0 | 0 | 0 | -20.3546 | -61.8367 | 103.8319 | -13.8319 | -58.3469 | 71.2311 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-01-20 08:00 | 0 | 0 | 0 | 0 | -20.3459 | -46.8399 | 101.1917 | -11.1917 | -44.2023 | 59.2038 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.9 | -3.9 | 1.1012 | 0
2016-01-20 09:00 | 0 | 0 | 0 | 0 | -20.3372 | -31.8431 | 99.1464 | -9.1464 | -30.0713 | 48.6656 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-01-20 10:00 | 0 | 0 | 0 | 0 | -20.3285 | -16.8463 | 97.8197 | -7.8197 | -15.9207 | 40.7965 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-01-20 11:00 | 0 | 0 | 0 | 0 | -20.3197 | -1.8495 | 97.2928 | -7.2928 | -1.7486 | 37.3306 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-01-20 12:00 | 0 | 0 | 0 | 0 | -20.311 | 13.1473 | 97.598 | -7.598 | 12.4273 | 39.4483 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-01-20 13:00 | 0 | 0 | 0 | 0 | -20.3022 | 28.1441 | 98.7158 | -8.7158 | 26.5869 | 46.3906 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2 | -2 | 1.0945 | 0
2016-01-20 14:00 | 0 | 0 | 0 | 0 | -20.2935 | 43.1409 | 100.5768 | -10.5768 | 40.7255 | 56.4005 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-01-20 15:00 | 0 | 0 | 0 | 0 | -20.2847 | 58.1377 | 103.067 | -13.067 | 54.8674 | 68.1349 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-01-20 16:00 | 0 | 0 | 0 | 0 | -20.2759 | 73.1345 | 106.0359 | -16.0359 | 69.0724 | 80.8409 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1004 | 0
2016-01-20 17:00 | 0 | 0 | 0 | 0 | -20.2671 | 88.1313 | 109.3037 | -19.3037 | 83.4339 | 94.1188 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.4 | -3.4 | 1.0994 | 0
2016-01-20 18:00 | 0 | 0 | 0 | 0 | -20.2583 | 103.1281 | 112.6677 | -22.6677 | 98.0678 | 107.7489 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.8 | -3.8 | 1.1008 | 0
2016-01-20 19:00 | 0 | 0 | 0 | 0 | -20.2495 | 118.1249 | 115.9082 | -25.9082 | 113.0937 | 121.6017 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-01-20 20:00 | 0 | 0 | 0 | 0 | -20.2406 | 133.1218 | 118.7955 | -28.7955 | 128.6054 | 135.5927 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.5 | -5.5 | 1.1067 | 0
2016-01-20 21:00 | 0 | 0 | 0 | 0 | -20.2318 | 148.1186 | 121.1039 | -31.1039 | 144.6347 | 149.6538 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.2 | -6.2 | 1.1092 | 0
2016-01-20 22:00 | 0 | 0 | 0 | 0 | -20.2229 | 163.1154 | 122.6334 | -32.6334 | 161.1175 | 163.6776 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.7 | -7.7 | 1.1144 | 0
2016-01-20 23:00 | 0 | 0 | 0 | 0 | -20.2141 | 178.1123 | 123.2395 | -33.2395 | 177.8819 | 176.2925 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.4 | -7.4 | 1.1134 | 0
2016-01-21 | 0 | 0 | 0 | 0 | -20.2052 | -166.8909 | 122.8615 | -32.8615 | -165.3214 | 167.1643 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.8 | -6.8 | 1.1113 | 0
2016-01-21 01:00 | 0 | 0 | 0 | 0 | -20.1963 | -151.894 | 121.5362 | -31.5362 | -148.7513 | 153.1963 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.2 | -7.2 | 1.1127 | 0
2016-01-21 02:00 | 0 | 0 | 0 | 0 | -20.1874 | -136.8971 | 119.3895 | -29.3895 | -132.603 | 139.1261 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.4 | -7.4 | 1.1134 | 0
2016-01-21 03:00 | 0 | 0 | 0 | 0 | -20.1785 | -121.9003 | 116.6102 | -26.6102 | -116.9668 | 125.1052 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.2 | -9.2 | 1.1197 | 0
2016-01-21 04:00 | 0 | 0 | 0 | 0 | -20.1696 | -106.9034 | 113.42 | -23.42 | -101.8313 | 111.2026 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.6 | -8.6 | 1.1176 | 0
2016-01-21 05:00 | 0 | 0 | 0 | 0 | -20.1606 | -91.9065 | 110.0486 | -20.0486 | -87.1139 | 97.4954 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.3 | -6.3 | 1.1096 | 0
2016-01-21 06:00 | 0 | 0 | 0 | 0 | -20.1517 | -76.9097 | 106.7192 | -16.7192 | -72.6979 | 84.0975 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-01-21 07:00 | 0 | 0 | 0 | 0 | -20.1427 | -61.9128 | 103.6391 | -13.6391 | -58.4635 | 71.1985 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.6 | -5.6 | 1.1071 | 0
2016-01-21 08:00 | 0 | 0 | 0 | 0 | -20.1338 | -46.9159 | 100.9945 | -10.9945 | -44.3102 | 59.1382 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.7 | -5.7 | 1.1075 | 0
2016-01-21 09:00 | 0 | 0 | 0 | 0 | -20.1248 | -31.919 | 98.9441 | -8.9441 | -30.1689 | 48.5565 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.3 | -5.3 | 1.106 | 0
2016-01-21 10:00 | 0 | 0 | 0 | 0 | -20.1158 | -16.9221 | 97.6122 | -7.6122 | -16.0065 | 40.6344 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.7 | -5.7 | 1.1075 | 0
2016-01-21 11:00 | 0 | 0 | 0 | 0 | -20.1068 | -1.9252 | 97.0804 | -7.0804 | -1.8217 | 37.1216 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.7 | -4.7 | 1.1039 | 0
2016-01-21 12:00 | 0 | 0 | 0 | 0 | -20.0978 | 13.0717 | 97.3814 | -7.3814 | 12.367 | 39.2237 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.1033 | 0
2016-01-21 13:00 | 0 | 0 | 0 | 0 | -20.0888 | 28.0686 | 98.496 | -8.496 | 26.5389 | 46.1795 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-01-21 14:00 | 0 | 0 | 0 | 0 | -20.0797 | 43.0655 | 100.3546 | -10.3546 | 40.6885 | 56.2126 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-01-21 15:00 | 0 | 0 | 0 | 0 | -20.0707 | 58.0624 | 102.8433 | -12.8433 | 54.8394 | 67.9696 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.9 | -3.9 | 1.1012 | 0
2016-01-21 16:00 | 0 | 0 | 0 | 0 | -20.0616 | 73.0593 | 105.8113 | -15.8113 | 69.0509 | 80.6952 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-01-21 17:00 | 0 | 0 | 0 | 0 | -20.0526 | 88.0563 | 109.0785 | -19.0785 | 83.4157 | 93.9901 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-01-21 18:00 | 0 | 0 | 0 | 0 | -20.0435 | 103.0532 | 112.4424 | -22.4424 | 98.0492 | 107.6352 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-01-21 19:00 | 0 | 0 | 0 | 0 | -20.0344 | 118.0501 | 115.6829 | -25.6829 | 113.0704 | 121.5022 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-01-21 20:00 | 0 | 0 | 0 | 0 | -20.0253 | 133.0471 | 118.5709 | -28.5709 | 128.573 | 135.5076 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-01-21 21:00 | 0 | 0 | 0 | 0 | -20.0162 | 148.044 | 120.8807 | -30.8807 | 144.5888 | 149.5861 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-01-21 22:00 | 0 | 0 | 0 | 0 | -20.0071 | 163.041 | 122.4128 | -32.4128 | 161.0548 | 163.6396 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-01-21 23:00 | 0 | 0 | 0 | 0 | -19.998 | 178.0379 | 123.0228 | -33.0228 | 177.8009 | 176.4433 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.2 | -2.2 | 1.0952 | 0
2016-01-22 | 0 | 0 | 0 | 0 | -19.9888 | -166.9651 | 122.6498 | -32.6498 | -165.4197 | 167.2775 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-01-22 01:00 | 0 | 0 | 0 | 0 | -19.9797 | -151.9681 | 121.3299 | -31.3299 | -148.8639 | 153.2735 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-01-22 02:00 | 0 | 0 | 0 | 0 | -19.9705 | -136.9712 | 119.1883 | -29.1883 | -132.7253 | 139.1842 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-01-22 03:00 | 0 | 0 | 0 | 0 | -19.9613 | -121.9742 | 116.4129 | -26.4129 | -117.0944 | 125.1474 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-01-22 04:00 | 0 | 0 | 0 | 0 | -19.9522 | -106.9772 | 113.2249 | -23.2249 | -101.9603 | 111.229 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-01-22 05:00 | 0 | 0 | 0 | 0 | -19.943 | -91.9802 | 109.8539 | -19.8539 | -87.2409 | 97.5044 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-01-22 06:00 | 0 | 0 | 0 | 0 | -19.9338 | -76.9832 | 106.5229 | -16.5229 | -72.8202 | 84.086 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-01-22 07:00 | 0 | 0 | 0 | 0 | -19.9245 | -61.9863 | 103.4397 | -13.4397 | -58.579 | 71.1613 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.1 | 0.1 | 1.0872 | 0
2016-01-22 08:00 | 0 | 0 | 0 | 0 | -19.9153 | -46.9893 | 100.7907 | -10.7907 | -44.4167 | 59.0676 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-01-22 09:00 | 0 | 0 | 0 | 0 | -19.9061 | -31.9923 | 98.7353 | -8.7353 | -30.2647 | 48.4418 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-01-22 10:00 | 0 | 0 | 0 | 0 | -19.8968 | -16.9952 | 97.3982 | -7.3982 | -16.0903 | 40.4661 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-01-22 11:00 | 0 | 0 | 0 | 0 | -19.8876 | -1.9982 | 96.8617 | -6.8617 | -1.8926 | 36.9064 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1 | 1 | 1.084 | 0
2016-01-22 12:00 | 0 | 0 | 0 | 0 | -19.8783 | 12.9988 | 97.1587 | -7.1587 | 12.3094 | 38.994 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-01-22 13:00 | 0 | 0 | 0 | 0 | -19.869 | 27.9958 | 98.2702 | -8.2702 | 26.4939 | 45.9651 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-01-22 14:00 | 0 | 0 | 0 | 0 | -19.8597 | 42.9928 | 100.1266 | -10.1266 | 40.6549 | 56.023 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-01-22 15:00 | 0 | 0 | 0 | 0 | -19.8504 | 57.9899 | 102.6139 | -12.6139 | 54.8152 | 67.8036 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-01-22 16:00 | 0 | 0 | 0 | 0 | -19.8411 | 72.9869 | 105.5811 | -15.5811 | 69.0333 | 80.5494 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-01-22 17:00 | 0 | 0 | 0 | 0 | -19.8318 | 87.9839 | 108.8479 | -18.8479 | 83.4015 | 93.8617 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-01-22 18:00 | 0 | 0 | 0 | 0 | -19.8224 | 102.981 | 112.2115 | -22.2115 | 98.0346 | 107.5223 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-01-22 19:00 | 0 | 0 | 0 | 0 | -19.8131 | 117.978 | 115.4521 | -25.4521 | 113.0512 | 121.4036 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-01-22 20:00 | 0 | 0 | 0 | 0 | -19.8037 | 132.9751 | 118.3405 | -28.3405 | 128.5446 | 135.4237 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-01-22 21:00 | 0 | 0 | 0 | 0 | -19.7944 | 147.9721 | 120.6516 | -30.6516 | 144.5468 | 149.5193 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-01-22 22:00 | 0 | 0 | 0 | 0 | -19.785 | 162.9692 | 122.1861 | -32.1861 | 160.9956 | 163.6018 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-01-22 23:00 | 0 | 0 | 0 | 0 | -19.7756 | 177.9663 | 122.7998 | -32.7998 | 177.7231 | 176.592 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-01-23 | 0 | 0 | 0 | 0 | -19.7662 | -167.0367 | 122.4316 | -32.4316 | -165.5153 | 167.3866 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-01-23 01:00 | 0 | 0 | 0 | 0 | -19.7568 | -152.0396 | 121.1171 | -31.1171 | -148.9741 | 153.3469 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-01-23 02:00 | 0 | 0 | 0 | 0 | -19.7474 | -137.0425 | 118.9804 | -28.9804 | -132.8458 | 139.2386 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-01-23 03:00 | 0 | 0 | 0 | 0 | -19.738 | -122.0454 | 116.209 | -26.209 | -117.2206 | 125.1859 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-01-23 04:00 | 0 | 0 | 0 | 0 | -19.7285 | -107.0483 | 113.0232 | -23.0232 | -102.088 | 111.2516 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-01-23 05:00 | 0 | 0 | 0 | 0 | -19.7191 | -92.0512 | 109.6525 | -19.6525 | -87.3668 | 97.5094 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-01-23 06:00 | 0 | 0 | 0 | 0 | -19.7096 | -77.0541 | 106.32 | -16.32 | -72.9414 | 84.0702 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-01-23 07:00 | 0 | 0 | 0 | 0 | -19.7001 | -62.057 | 103.2336 | -13.2336 | -58.6931 | 71.1196 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-01-23 08:00 | 0 | 0 | 0 | 0 | -19.6906 | -47.0599 | 100.5804 | -10.5804 | -44.5218 | 58.992 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-01-23 09:00 | 0 | 0 | 0 | 0 | -19.6811 | -32.0628 | 98.52 | -8.52 | -30.3589 | 48.3216 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-01-23 10:00 | 0 | 0 | 0 | 0 | -19.6716 | -17.0657 | 97.178 | -7.178 | -16.172 | 40.2917 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-01-23 11:00 | 0 | 0 | 0 | 0 | -19.6621 | -2.0685 | 96.6368 | -6.6368 | -1.961 | 36.6851 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-01-23 12:00 | 0 | 0 | 0 | 0 | -19.6526 | 12.9286 | 96.9299 | -6.9299 | 12.2545 | 38.7593 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-01-23 13:00 | 0 | 0 | 0 | 0 | -19.6431 | 27.9257 | 98.0385 | -8.0385 | 26.4521 | 45.7475 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-01-23 14:00 | 0 | 0 | 0 | 0 | -19.6335 | 42.9229 | 99.8929 | -9.8929 | 40.6247 | 55.8316 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-01-23 15:00 | 0 | 0 | 0 | 0 | -19.624 | 57.92 | 102.379 | -12.379 | 54.7946 | 67.6368 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-01-23 16:00 | 0 | 0 | 0 | 0 | -19.6144 | 72.9172 | 105.3454 | -15.3454 | 69.0196 | 80.4037 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-01-23 17:00 | 0 | 0 | 0 | 0 | -19.6048 | 87.9143 | 108.6118 | -18.6118 | 83.3913 | 93.7338 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-01-23 18:00 | 0 | 0 | 0 | 0 | -19.5952 | 102.9115 | 111.9752 | -21.9752 | 98.0242 | 107.4101 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-01-23 19:00 | 0 | 0 | 0 | 0 | -19.5856 | 117.9087 | 115.2158 | -25.2158 | 113.0362 | 121.306 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-01-23 20:00 | 0 | 0 | 0 | 0 | -19.576 | 132.9058 | 118.1046 | -28.1046 | 128.5203 | 135.3408 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-01-23 21:00 | 0 | 0 | 0 | 0 | -19.5664 | 147.903 | 120.4168 | -30.4168 | 144.5088 | 149.4534 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-01-23 22:00 | 0 | 0 | 0 | 0 | -19.5567 | 162.9002 | 121.9535 | -31.9535 | 160.9402 | 163.5639 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.8 | 0.8 | 1.0847 | 0
2016-01-23 23:00 | 0 | 0 | 0 | 0 | -19.5471 | 177.8974 | 122.5707 | -32.5707 | 177.6486 | 176.7373 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.1 | 1.1 | 1.0837 | 0
2016-01-24 | 0 | 0 | 0 | 0 | -19.5375 | -167.1054 | 122.2071 | -32.2071 | -165.608 | 167.4911 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.5 | 1.5 | 1.0822 | 0
2016-01-24 01:00 | 0 | 0 | 0 | 0 | -19.5278 | -152.1083 | 120.8978 | -30.8978 | -149.0819 | 153.4163 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.3 | 1.3 | 1.083 | 0
2016-01-24 02:00 | 0 | 0 | 0 | 0 | -19.5181 | -137.1111 | 118.766 | -28.766 | -132.9644 | 139.2892 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-01-24 03:00 | 0 | 0 | 0 | 0 | -19.5084 | -122.1138 | 115.9984 | -25.9984 | -117.3451 | 125.2206 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-01-24 04:00 | 0 | 0 | 0 | 0 | -19.4987 | -107.1166 | 112.8149 | -22.8149 | -102.2143 | 111.2702 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-01-24 05:00 | 0 | 0 | 0 | 0 | -19.489 | -92.1194 | 109.4445 | -19.4445 | -87.4914 | 97.5102 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2 | 2 | 1.0805 | 0
2016-01-24 06:00 | 0 | 0 | 0 | 0 | -19.4793 | -77.1222 | 106.1105 | -16.1105 | -73.0614 | 84.0501 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-01-24 07:00 | 0 | 0 | 0 | 0 | -19.4696 | -62.125 | 103.0211 | -13.0211 | -58.806 | 71.0732 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-01-24 08:00 | 0 | 0 | 0 | 0 | -19.4599 | -47.1278 | 100.3636 | -10.3636 | -44.6253 | 58.9115 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-01-24 09:00 | 0 | 0 | 0 | 0 | -19.4501 | -32.1305 | 98.2984 | -8.2984 | -30.4512 | 48.1959 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-01-24 10:00 | 0 | 0 | 0 | 0 | -19.4403 | -17.1333 | 96.9514 | -6.9514 | -16.2517 | 40.1113 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-01-24 11:00 | 0 | 0 | 0 | 0 | -19.4306 | -2.136 | 96.4058 | -6.4058 | -2.027 | 36.4577 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-01-24 12:00 | 0 | 0 | 0 | 0 | -19.4208 | 12.8612 | 96.6952 | -6.6952 | 12.2024 | 38.5198 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-01-24 13:00 | 0 | 0 | 0 | 0 | -19.411 | 27.8585 | 97.801 | -7.801 | 26.4134 | 45.5269 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-01-24 14:00 | 0 | 0 | 0 | 0 | -19.4012 | 42.8557 | 99.6536 | -9.6536 | 40.598 | 55.6386 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.1 | 2.1 | 1.0801 | 0
2016-01-24 15:00 | 0 | 0 | 0 | 0 | -19.3914 | 57.853 | 102.1386 | -12.1386 | 54.7777 | 67.4695 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2 | 2 | 1.0805 | 0
2016-01-24 16:00 | 0 | 0 | 0 | 0 | -19.3816 | 72.8502 | 105.1044 | -15.1044 | 69.0097 | 80.258 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.7 | 1.7 | 1.0816 | 0
2016-01-24 17:00 | 0 | 0 | 0 | 0 | -19.3718 | 87.8475 | 108.3705 | -18.3705 | 83.3852 | 93.6065 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.6 | 1.6 | 1.0819 | 0
2016-01-24 18:00 | 0 | 0 | 0 | 0 | -19.3619 | 102.8448 | 111.7337 | -21.7337 | 98.0179 | 107.2988 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.2 | 1.2 | 1.0833 | 0
2016-01-24 19:00 | 0 | 0 | 0 | 0 | -19.3521 | 117.8421 | 114.9742 | -24.9742 | 113.0254 | 121.2095 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.3 | 1.3 | 1.083 | 0
2016-01-24 20:00 | 0 | 0 | 0 | 0 | -19.3422 | 132.8394 | 117.8632 | -27.8632 | 128.5002 | 135.2589 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.2 | 1.2 | 1.0833 | 0
2016-01-24 21:00 | 0 | 0 | 0 | 0 | -19.3323 | 147.8367 | 120.1763 | -30.1763 | 144.4747 | 149.3883 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.4 | 1.4 | 1.0826 | 0
2016-01-24 22:00 | 0 | 0 | 0 | 0 | -19.3224 | 162.834 | 121.715 | -31.715 | 160.8885 | 163.5257 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.2 | 1.2 | 1.0833 | 0
2016-01-24 23:00 | 0 | 0 | 0 | 0 | -19.3125 | 177.8313 | 122.3355 | -32.3355 | 177.5775 | 176.8775 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-01-25 | 0 | 0 | 0 | 0 | -19.3026 | -167.1714 | 121.9764 | -31.9764 | -165.6978 | 167.5904 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-01-25 01:00 | 0 | 0 | 0 | 0 | -19.2927 | -152.1741 | 120.6721 | -30.6721 | -149.1872 | 153.4815 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-01-25 02:00 | 0 | 0 | 0 | 0 | -19.2828 | -137.1768 | 118.5452 | -28.5452 | -133.0808 | 139.3358 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-01-25 03:00 | 0 | 0 | 0 | 0 | -19.2729 | -122.1795 | 115.7814 | -25.7814 | -117.468 | 125.2513 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-01-25 04:00 | 0 | 0 | 0 | 0 | -19.2629 | -107.1822 | 112.6 | -22.6 | -102.3392 | 111.2848 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-01-25 05:00 | 0 | 0 | 0 | 0 | -19.253 | -92.1848 | 109.23 | -19.23 | -87.6146 | 97.507 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-01-25 06:00 | 0 | 0 | 0 | 0 | -19.243 | -77.1875 | 105.8946 | -15.8946 | -73.18 | 84.0256 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.4 | 0.4 | 1.0861 | 0
2016-01-25 07:00 | 0 | 0 | 0 | 0 | -19.233 | -62.1901 | 102.8021 | -12.8021 | -58.9173 | 71.0223 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.4 | 0.4 | 1.0861 | 0
2016-01-25 08:00 | 0 | 0 | 0 | 0 | -19.223 | -47.1928 | 100.1405 | -10.1405 | -44.7272 | 58.826 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-01-25 09:00 | 0 | 0 | 0 | 0 | -19.2131 | -32.1954 | 98.0706 | -8.0706 | -30.5417 | 48.0648 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-01-25 10:00 | 0 | 0 | 0 | 0 | -19.203 | -17.1981 | 96.7188 | -6.7188 | -16.3292 | 39.9249 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-01-25 11:00 | 0 | 0 | 0 | 0 | -19.193 | -2.2007 | 96.1687 | -6.1687 | -2.0905 | 36.2243 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.1 | 0.1 | 1.0872 | 0
2016-01-25 12:00 | 0 | 0 | 0 | 0 | -19.183 | 12.7966 | 96.4546 | -6.4546 | 12.1533 | 38.2755 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-01-25 13:00 | 0 | 0 | 0 | 0 | -19.173 | 27.794 | 97.5578 | -7.5578 | 26.3779 | 45.3033 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.1 | 0.1 | 1.0872 | 0
2016-01-25 14:00 | 0 | 0 | 0 | 0 | -19.1629 | 42.7914 | 99.4088 | -9.4088 | 40.5747 | 55.4442 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-01-25 15:00 | 0 | 0 | 0 | 0 | -19.1529 | 57.7888 | 101.8928 | -11.8928 | 54.7645 | 67.3017 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-01-25 16:00 | 0 | 0 | 0 | 0 | -19.1428 | 72.7862 | 104.8582 | -14.8582 | 69.0038 | 80.1126 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-01-25 17:00 | 0 | 0 | 0 | 0 | -19.1327 | 87.7836 | 108.124 | -18.124 | 83.3831 | 93.4798 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-01-25 18:00 | 0 | 0 | 0 | 0 | -19.1226 | 102.7809 | 111.4869 | -21.4869 | 98.0158 | 107.1885 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-01-25 19:00 | 0 | 0 | 0 | 0 | -19.1125 | 117.7784 | 114.7273 | -24.7273 | 113.0187 | 121.114 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-01-25 20:00 | 0 | 0 | 0 | 0 | -19.1024 | 132.7758 | 117.6164 | -27.6164 | 128.4842 | 135.1781 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-01-25 21:00 | 0 | 0 | 0 | 0 | -19.0923 | 147.7732 | 119.9303 | -29.9303 | 144.4446 | 149.324 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-01-25 22:00 | 0 | 0 | 0 | 0 | -19.0822 | 162.7706 | 121.4708 | -31.4708 | 160.8405 | 163.4872 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-01-25 23:00 | 0 | 0 | 0 | 0 | -19.072 | 177.768 | 122.0944 | -32.0944 | 177.5098 | 177.0105 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-01-26 | 0 | 0 | 0 | 0 | -19.0619 | -167.2346 | 121.7396 | -31.7396 | -165.7845 | 167.6841 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-01-26 01:00 | 0 | 0 | 0 | 0 | -19.0517 | -152.2371 | 120.4402 | -30.4402 | -149.29 | 153.5422 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-01-26 02:00 | 0 | 0 | 0 | 0 | -19.0416 | -137.2397 | 118.318 | -28.318 | -133.1951 | 139.3783 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-01-26 03:00 | 0 | 0 | 0 | 0 | -19.0314 | -122.2423 | 115.5579 | -25.5579 | -117.589 | 125.278 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-01-26 04:00 | 0 | 0 | 0 | 0 | -19.0212 | -107.2448 | 112.3787 | -22.3787 | -102.4625 | 111.2954 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-01-26 05:00 | 0 | 0 | 0 | 0 | -19.011 | -92.2474 | 109.0091 | -19.0091 | -87.7364 | 97.4996 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2 | -2 | 1.0945 | 0
2016-01-26 06:00 | 0 | 0 | 0 | 0 | -19.0008 | -77.2499 | 105.6722 | -15.6722 | -73.2972 | 83.9969 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-01-26 07:00 | 0 | 0 | 0 | 0 | -18.9906 | -62.2524 | 102.5768 | -12.5768 | -59.0272 | 70.9669 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-01-26 08:00 | 0 | 0 | 0 | 0 | -18.9803 | -47.255 | 99.9111 | -9.9111 | -44.8275 | 58.7357 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-01-26 09:00 | 0 | 0 | 0 | 0 | -18.9701 | -32.2575 | 97.8365 | -7.8365 | -30.6302 | 47.9284 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-01-26 10:00 | 0 | 0 | 0 | 0 | -18.9598 | -17.26 | 96.48 | -6.48 | -16.4044 | 39.7327 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3 | -3 | 1.098 | 0
2016-01-26 11:00 | 0 | 0 | 0 | 0 | -18.9496 | -2.2625 | 95.9258 | -5.9258 | -2.1514 | 35.9851 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.0991 | 0
2016-01-26 12:00 | 0 | 0 | 0 | 0 | -18.9393 | 12.735 | 96.2083 | -6.2083 | 12.107 | 38.0266 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-01-26 13:00 | 0 | 0 | 0 | 0 | -18.929 | 27.7325 | 97.3091 | -7.3091 | 26.3456 | 45.0769 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-01-26 14:00 | 0 | 0 | 0 | 0 | -18.9187 | 42.73 | 99.1585 | -9.1585 | 40.555 | 55.2484 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-01-26 15:00 | 0 | 0 | 0 | 0 | -18.9084 | 57.7275 | 101.6418 | -11.6418 | 54.755 | 67.1336 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-01-26 16:00 | 0 | 0 | 0 | 0 | -18.8981 | 72.725 | 104.6067 | -14.6067 | 69.0018 | 79.9674 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-01-26 17:00 | 0 | 0 | 0 | 0 | -18.8878 | 87.7225 | 107.8723 | -17.8723 | 83.3852 | 93.3538 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2 | -2 | 1.0945 | 0
2016-01-26 18:00 | 0 | 0 | 0 | 0 | -18.8775 | 102.72 | 111.2351 | -21.2351 | 98.0178 | 107.079 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2 | -2 | 1.0945 | 0
2016-01-26 19:00 | 0 | 0 | 0 | 0 | -18.8671 | 117.7175 | 114.4752 | -24.4752 | 113.0163 | 121.0196 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-01-26 20:00 | 0 | 0 | 0 | 0 | -18.8568 | 132.715 | 117.3644 | -27.3644 | 128.4723 | 135.0984 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-01-26 21:00 | 0 | 0 | 0 | 0 | -18.8464 | 147.7126 | 119.6789 | -29.6789 | 144.4185 | 149.2605 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-01-26 22:00 | 0 | 0 | 0 | 0 | -18.836 | 162.7101 | 121.221 | -31.221 | 160.7964 | 163.4482 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.8 | -3.8 | 1.1008 | 0
2016-01-26 23:00 | 0 | 0 | 0 | 0 | -18.8257 | 177.7077 | 121.8475 | -31.8475 | 177.4456 | 177.134 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3 | -3 | 1.098 | 0
2016-01-27 | 0 | 0 | 0 | 0 | -18.8153 | -167.2948 | 121.4967 | -31.4967 | -165.8682 | 167.7717 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3 | -3 | 1.098 | 0
2016-01-27 01:00 | 0 | 0 | 0 | 0 | -18.8049 | -152.2972 | 120.2021 | -30.2021 | -149.3902 | 153.5982 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-01-27 02:00 | 0 | 0 | 0 | 0 | -18.7945 | -137.2997 | 118.0845 | -28.0845 | -133.3072 | 139.4166 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-01-27 03:00 | 0 | 0 | 0 | 0 | -18.784 | -122.3021 | 115.3281 | -25.3281 | -117.7081 | 125.3006 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-01-27 04:00 | 0 | 0 | 0 | 0 | -18.7736 | -107.3045 | 112.1511 | -22.1511 | -102.5841 | 111.3019 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.8 | -2.8 | 1.0973 | 0
2016-01-27 05:00 | 0 | 0 | 0 | 0 | -18.7632 | -92.307 | 108.7819 | -18.7819 | -87.8567 | 97.4881 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-01-27 06:00 | 0 | 0 | 0 | 0 | -18.7527 | -77.3094 | 105.4436 | -15.4436 | -73.4128 | 83.9638 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.4 | -3.4 | 1.0994 | 0
2016-01-27 07:00 | 0 | 0 | 0 | 0 | -18.7423 | -62.3118 | 102.3452 | -12.3452 | -59.1355 | 70.9069 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-01-27 08:00 | 0 | 0 | 0 | 0 | -18.7318 | -47.3142 | 99.6755 | -9.6755 | -44.926 | 58.6404 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.8 | -2.8 | 1.0973 | 0
2016-01-27 09:00 | 0 | 0 | 0 | 0 | -18.7213 | -32.3166 | 97.5964 | -7.5964 | -30.7168 | 47.7867 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-01-27 10:00 | 0 | 0 | 0 | 0 | -18.7108 | -17.319 | 96.2354 | -6.2354 | -16.4774 | 39.5346 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-01-27 11:00 | 0 | 0 | 0 | 0 | -18.7003 | -2.3214 | 95.6771 | -5.6771 | -2.2096 | 35.74 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4 | -4 | 1.1015 | 0
2016-01-27 12:00 | 0 | 0 | 0 | 0 | -18.6898 | 12.6762 | 95.9564 | -5.9564 | 12.0636 | 37.7731 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-01-27 13:00 | 0 | 0 | 0 | 0 | -18.6793 | 27.6738 | 97.0549 | -7.0549 | 26.3166 | 44.8479 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-01-27 14:00 | 0 | 0 | 0 | 0 | -18.6688 | 42.6714 | 98.903 | -8.903 | 40.5387 | 55.0515 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-01-27 15:00 | 0 | 0 | 0 | 0 | -18.6582 | 57.6691 | 101.3856 | -11.3856 | 54.7494 | 66.9653 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-01-27 16:00 | 0 | 0 | 0 | 0 | -18.6477 | 72.6667 | 104.3503 | -14.3503 | 69.0038 | 79.8227 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-01-27 17:00 | 0 | 0 | 0 | 0 | -18.6371 | 87.6643 | 107.6158 | -17.6158 | 83.3913 | 93.2286 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-01-27 18:00 | 0 | 0 | 0 | 0 | -18.6265 | 102.662 | 110.9783 | -20.9783 | 98.0241 | 106.9706 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.6 | -3.6 | 1.1001 | 0
2016-01-27 19:00 | 0 | 0 | 0 | 0 | -18.616 | 117.6596 | 114.2182 | -24.2182 | 113.018 | 120.9264 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1004 | 0
2016-01-27 20:00 | 0 | 0 | 0 | 0 | -18.6054 | 132.6573 | 117.1072 | -27.1072 | 128.4645 | 135.0197 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.4 | -3.4 | 1.0994 | 0
2016-01-27 21:00 | 0 | 0 | 0 | 0 | -18.5948 | 147.6549 | 119.4221 | -29.4221 | 144.3964 | 149.1976 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.8 | -3.8 | 1.1008 | 0
2016-01-27 22:00 | 0 | 0 | 0 | 0 | -18.5842 | 162.6526 | 120.9656 | -30.9656 | 160.756 | 163.4084 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.8 | -3.8 | 1.1008 | 0
2016-01-27 23:00 | 0 | 0 | 0 | 0 | -18.5736 | 177.6503 | 121.5948 | -31.5948 | 177.3849 | 177.2453 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-01-28 | 0 | 0 | 0 | 0 | -18.5629 | -167.3521 | 121.2479 | -31.2479 | -165.9488 | 167.8526 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-01-28 01:00 | 0 | 0 | 0 | 0 | -18.5523 | -152.3544 | 119.9579 | -29.9579 | -149.4876 | 153.6494 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.105 | 0
2016-01-28 02:00 | 0 | 0 | 0 | 0 | -18.5416 | -137.3567 | 117.8448 | -27.8448 | -133.417 | 139.4504 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.6 | -4.6 | 1.1036 | 0
2016-01-28 03:00 | 0 | 0 | 0 | 0 | -18.531 | -122.359 | 115.0921 | -25.0921 | -117.8253 | 125.319 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-01-28 04:00 | 0 | 0 | 0 | 0 | -18.5203 | -107.3613 | 111.9172 | -21.9172 | -102.704 | 111.3042 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-01-28 05:00 | 0 | 0 | 0 | 0 | -18.5096 | -92.3636 | 108.5484 | -18.5484 | -87.9754 | 97.4723 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-01-28 06:00 | 0 | 0 | 0 | 0 | -18.499 | -77.3659 | 105.2087 | -15.2087 | -73.527 | 83.9265 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.1033 | 0
2016-01-28 07:00 | 0 | 0 | 0 | 0 | -18.4883 | -62.3682 | 102.1075 | -12.1075 | -59.2422 | 70.8423 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-01-28 08:00 | 0 | 0 | 0 | 0 | -18.4775 | -47.3705 | 99.4339 | -9.4339 | -45.0226 | 58.5404 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-01-28 09:00 | 0 | 0 | 0 | 0 | -18.4668 | -32.3728 | 97.3503 | -7.3503 | -30.8013 | 47.6397 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.105 | 0
2016-01-28 10:00 | 0 | 0 | 0 | 0 | -18.4561 | -17.375 | 95.9848 | -5.9848 | -16.548 | 39.3309 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-01-28 11:00 | 0 | 0 | 0 | 0 | -18.4454 | -2.3773 | 95.4226 | -5.4226 | -2.2653 | 35.4892 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-01-28 12:00 | 0 | 0 | 0 | 0 | -18.4346 | 12.6204 | 95.6989 | -5.6989 | 12.0233 | 37.5153 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-01-28 13:00 | 0 | 0 | 0 | 0 | -18.4239 | 27.6182 | 96.7953 | -6.7953 | 26.2908 | 44.6164 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4 | -4 | 1.1015 | 0
2016-01-28 14:00 | 0 | 0 | 0 | 0 | -18.4131 | 42.6159 | 98.6423 | -8.6423 | 40.5261 | 54.8536 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4 | -4 | 1.1015 | 0
2016-01-28 15:00 | 0 | 0 | 0 | 0 | -18.4023 | 57.6137 | 101.1244 | -11.1244 | 54.7475 | 66.7969 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.9 | -3.9 | 1.1012 | 0
2016-01-28 16:00 | 0 | 0 | 0 | 0 | -18.3916 | 72.6114 | 104.0889 | -14.0889 | 69.0098 | 79.6784 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.9 | -3.9 | 1.1012 | 0
2016-01-28 17:00 | 0 | 0 | 0 | 0 | -18.3808 | 87.6092 | 107.3543 | -17.3543 | 83.4015 | 93.1043 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4 | -4 | 1.1015 | 0
2016-01-28 18:00 | 0 | 0 | 0 | 0 | -18.37 | 102.607 | 110.7166 | -20.7166 | 98.0344 | 106.8633 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-01-28 19:00 | 0 | 0 | 0 | 0 | -18.3591 | 117.6047 | 113.9562 | -23.9562 | 113.0239 | 120.8342 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-01-28 20:00 | 0 | 0 | 0 | 0 | -18.3483 | 132.6025 | 116.8449 | -26.8449 | 128.461 | 134.942 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-01-28 21:00 | 0 | 0 | 0 | 0 | -18.3375 | 147.6003 | 119.1601 | -29.1601 | 144.3784 | 149.1353 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-01-28 22:00 | 0 | 0 | 0 | 0 | -18.3266 | 162.5981 | 120.7048 | -30.7048 | 160.7195 | 163.3677 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-01-28 23:00 | 0 | 0 | 0 | 0 | -18.3158 | 177.5959 | 121.3365 | -31.3365 | 177.3277 | 177.3413 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-01-29 | 0 | 0 | 0 | 0 | -18.3049 | -167.4063 | 120.9933 | -30.9933 | -166.0261 | 167.9264 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.1 | -5.1 | 1.1054 | 0
2016-01-29 01:00 | 0 | 0 | 0 | 0 | -18.2941 | -152.4085 | 119.7078 | -29.7078 | -149.5823 | 153.6956 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.105 | 0
2016-01-29 02:00 | 0 | 0 | 0 | 0 | -18.2832 | -137.4107 | 117.5991 | -27.5991 | -133.5244 | 139.4798 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.7 | -5.7 | 1.1075 | 0
2016-01-29 03:00 | 0 | 0 | 0 | 0 | -18.2723 | -122.4129 | 114.8499 | -24.8499 | -117.9404 | 125.3331 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-01-29 04:00 | 0 | 0 | 0 | 0 | -18.2614 | -107.4151 | 111.6772 | -21.6772 | -102.8221 | 111.3023 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-01-29 05:00 | 0 | 0 | 0 | 0 | -18.2505 | -92.4173 | 108.3087 | -18.3087 | -88.0924 | 97.4523 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-01-29 06:00 | 0 | 0 | 0 | 0 | -18.2396 | -77.4194 | 104.9678 | -14.9678 | -73.6394 | 83.8847 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.1 | -5.1 | 1.1054 | 0
2016-01-29 07:00 | 0 | 0 | 0 | 0 | -18.2286 | -62.4216 | 101.8637 | -11.8637 | -59.3471 | 70.7733 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.105 | 0
2016-01-29 08:00 | 0 | 0 | 0 | 0 | -18.2177 | -47.4238 | 99.1862 | -9.1862 | -45.1174 | 58.4356 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.1 | -6.1 | 1.1088 | 0
2016-01-29 09:00 | 0 | 0 | 0 | 0 | -18.2068 | -32.4259 | 97.0983 | -7.0983 | -30.8837 | 47.4876 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.6 | -5.6 | 1.1071 | 0
2016-01-29 10:00 | 0 | 0 | 0 | 0 | -18.1958 | -17.4281 | 95.7285 | -5.7285 | -16.6162 | 39.1215 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-01-29 11:00 | 0 | 0 | 0 | 0 | -18.1848 | -2.4302 | 95.1626 | -5.1626 | -2.3182 | 35.2327 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.7 | -5.7 | 1.1075 | 0
2016-01-29 12:00 | 0 | 0 | 0 | 0 | -18.1739 | 12.5677 | 95.4359 | -5.4359 | 11.9859 | 37.2532 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.4 | -5.4 | 1.1064 | 0
2016-01-29 13:00 | 0 | 0 | 0 | 0 | -18.1629 | 27.5655 | 96.5305 | -6.5305 | 26.2684 | 44.3825 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-01-29 14:00 | 0 | 0 | 0 | 0 | -18.1519 | 42.5634 | 98.3765 | -8.3765 | 40.517 | 54.6548 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.1 | -5.1 | 1.1054 | 0
2016-01-29 15:00 | 0 | 0 | 0 | 0 | -18.1409 | 57.5613 | 100.8582 | -10.8582 | 54.7495 | 66.6285 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.3 | -4.3 | 1.1025 | 0
2016-01-29 16:00 | 0 | 0 | 0 | 0 | -18.1299 | 72.5592 | 103.8227 | -13.8227 | 69.0197 | 79.5348 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1004 | 0
2016-01-29 17:00 | 0 | 0 | 0 | 0 | -18.1188 | 87.5571 | 107.0881 | -17.0881 | 83.4158 | 92.9809 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-01-29 18:00 | 0 | 0 | 0 | 0 | -18.1078 | 102.5549 | 110.4502 | -20.4502 | 98.049 | 106.7571 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-01-29 19:00 | 0 | 0 | 0 | 0 | -18.0968 | 117.5528 | 113.6893 | -23.6893 | 113.034 | 120.7433 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-01-29 20:00 | 0 | 0 | 0 | 0 | -18.0857 | 132.5507 | 116.5778 | -26.5778 | 128.4616 | 134.8654 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-01-29 21:00 | 0 | 0 | 0 | 0 | -18.0746 | 147.5487 | 118.893 | -28.893 | 144.3644 | 149.0735 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-01-29 22:00 | 0 | 0 | 0 | 0 | -18.0636 | 162.5466 | 120.4387 | -30.4387 | 160.6868 | 163.3258 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-01-29 23:00 | 0 | 0 | 0 | 0 | -18.0525 | 177.5445 | 121.0727 | -31.0727 | 177.2741 | 177.4188 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-01-30 | 0 | 0 | 0 | 0 | -18.0414 | -167.4576 | 120.733 | -30.733 | -166.1003 | 167.9926 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-01-30 01:00 | 0 | 0 | 0 | 0 | -18.0303 | -152.4596 | 119.4517 | -29.4517 | -149.6741 | 153.7364 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-01-30 02:00 | 0 | 0 | 0 | 0 | -18.0192 | -137.4617 | 117.3474 | -27.3474 | -133.6294 | 139.5046 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.9 | 0.9 | 1.0843 | 0
2016-01-30 03:00 | 0 | 0 | 0 | 0 | -18.0081 | -122.4638 | 114.6017 | -24.6017 | -118.0534 | 125.3429 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-01-30 04:00 | 0 | 0 | 0 | 0 | -17.997 | -107.4658 | 111.4311 | -21.4311 | -102.9383 | 111.2962 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-01-30 05:00 | 0 | 0 | 0 | 0 | -17.9858 | -92.4679 | 108.063 | -18.063 | -88.2077 | 97.428 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.4 | 1.4 | 1.0826 | 0
2016-01-30 06:00 | 0 | 0 | 0 | 0 | -17.9747 | -77.4699 | 104.7207 | -14.7207 | -73.7502 | 83.8387 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.5 | 1.5 | 1.0822 | 0
2016-01-30 07:00 | 0 | 0 | 0 | 0 | -17.9635 | -62.472 | 101.614 | -11.614 | -59.4503 | 70.6998 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.4 | 1.4 | 1.0826 | 0
2016-01-30 08:00 | 0 | 0 | 0 | 0 | -17.9524 | -47.474 | 98.9327 | -8.9327 | -45.2103 | 58.3261 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.2 | 1.2 | 1.0833 | 0
2016-01-30 09:00 | 0 | 0 | 0 | 0 | -17.9412 | -32.476 | 96.8405 | -6.8405 | -30.964 | 47.3304 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.9 | 0.9 | 1.0843 | 0
2016-01-30 10:00 | 0 | 0 | 0 | 0 | -17.93 | -17.478 | 95.4666 | -5.4666 | -16.682 | 38.9065 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1 | 1 | 1.084 | 0
2016-01-30 11:00 | 0 | 0 | 0 | 0 | -17.9188 | -2.48 | 94.897 | -4.897 | -2.3683 | 34.9708 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-01-30 12:00 | 0 | 0 | 0 | 0 | -17.9076 | 12.5179 | 95.1677 | -5.1677 | 11.9517 | 36.9869 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-01-30 13:00 | 0 | 0 | 0 | 0 | -17.8964 | 27.5159 | 96.2606 | -6.2606 | 26.2494 | 44.1465 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.4 | 0.4 | 1.0861 | 0
2016-01-30 14:00 | 0 | 0 | 0 | 0 | -17.8852 | 42.5139 | 98.1057 | -8.1057 | 40.5116 | 54.4552 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-01-30 15:00 | 0 | 0 | 0 | 0 | -17.8739 | 57.5119 | 100.5872 | -10.5872 | 54.7552 | 66.4603 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-01-30 16:00 | 0 | 0 | 0 | 0 | -17.8627 | 72.51 | 103.5519 | -13.5519 | 69.0336 | 79.3918 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-01-30 17:00 | 0 | 0 | 0 | 0 | -17.8515 | 87.508 | 106.8172 | -16.8172 | 83.4342 | 92.8586 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-01-30 18:00 | 0 | 0 | 0 | 0 | -17.8402 | 102.506 | 110.1792 | -20.1792 | 98.0677 | 106.6521 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-01-30 19:00 | 0 | 0 | 0 | 0 | -17.8289 | 117.504 | 113.4178 | -23.4178 | 113.0483 | 120.6534 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-01-30 20:00 | 0 | 0 | 0 | 0 | -17.8177 | 132.5021 | 116.3058 | -26.3058 | 128.4663 | 134.7897 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-01-30 21:00 | 0 | 0 | 0 | 0 | -17.8064 | 147.5001 | 118.6209 | -28.6209 | 144.3545 | 149.0122 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-01-30 22:00 | 0 | 0 | 0 | 0 | -17.7951 | 162.4981 | 120.1674 | -30.1674 | 160.658 | 163.2828 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-01-30 23:00 | 0 | 0 | 0 | 0 | -17.7838 | 177.4962 | 120.8034 | -30.8034 | 177.224 | 177.4746 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-01-31 | 0 | 0 | 0 | 0 | -17.7725 | -167.5058 | 120.4671 | -30.4671 | -166.1712 | 168.0506 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-01-31 01:00 | 0 | 0 | 0 | 0 | -17.7611 | -152.5077 | 119.19 | -29.19 | -149.7631 | 153.7717 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-01-31 02:00 | 0 | 0 | 0 | 0 | -17.7498 | -137.5096 | 117.0898 | -27.0898 | -133.7318 | 139.5246 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-01-31 03:00 | 0 | 0 | 0 | 0 | -17.7385 | -122.5116 | 114.3475 | -24.3475 | -118.1642 | 125.3482 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-01-31 04:00 | 0 | 0 | 0 | 0 | -17.7271 | -107.5135 | 111.179 | -21.179 | -103.0526 | 111.2857 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-01-31 05:00 | 0 | 0 | 0 | 0 | -17.7157 | -92.5154 | 107.8114 | -17.8114 | -88.3211 | 97.3994 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.8 | -2.8 | 1.0973 | 0
2016-01-31 06:00 | 0 | 0 | 0 | 0 | -17.7044 | -77.5173 | 104.4678 | -14.4678 | -73.8591 | 83.7883 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-01-31 07:00 | 0 | 0 | 0 | 0 | -17.693 | -62.5192 | 101.3583 | -11.3583 | -59.5516 | 70.6219 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.0991 | 0
2016-01-31 08:00 | 0 | 0 | 0 | 0 | -17.6816 | -47.5211 | 98.6734 | -8.6734 | -45.3012 | 58.212 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.0991 | 0
2016-01-31 09:00 | 0 | 0 | 0 | 0 | -17.6702 | -32.523 | 96.577 | -6.577 | -31.042 | 47.1682 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-01-31 10:00 | 0 | 0 | 0 | 0 | -17.6588 | -17.5249 | 95.1991 | -5.1991 | -16.7453 | 38.6861 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-01-31 11:00 | 0 | 0 | 0 | 0 | -17.6474 | -2.5268 | 94.6261 | -4.6261 | -2.4157 | 34.7034 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-01-31 12:00 | 0 | 0 | 0 | 0 | -17.636 | 12.4713 | 94.8942 | -4.8942 | 11.9205 | 36.7166 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-01-31 13:00 | 0 | 0 | 0 | 0 | -17.6245 | 27.4694 | 95.9856 | -5.9856 | 26.2337 | 43.9084 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.2 | -2.2 | 1.0952 | 0
2016-01-31 14:00 | 0 | 0 | 0 | 0 | -17.6131 | 42.4676 | 97.8301 | -7.8301 | 40.5098 | 54.2551 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-01-31 15:00 | 0 | 0 | 0 | 0 | -17.6017 | 57.4657 | 100.3116 | -10.3116 | 54.7648 | 66.2924 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-01-31 16:00 | 0 | 0 | 0 | 0 | -17.5902 | 72.4638 | 103.2764 | -13.2764 | 69.0515 | 79.2497 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-01-31 17:00 | 0 | 0 | 0 | 0 | -17.5787 | 87.462 | 106.5418 | -16.5418 | 83.4568 | 92.7373 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-01-31 18:00 | 0 | 0 | 0 | 0 | -17.5672 | 102.4601 | 109.9036 | -19.9036 | 98.0906 | 106.5482 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-01-31 19:00 | 0 | 0 | 0 | 0 | -17.5558 | 117.4583 | 113.1417 | -23.1417 | 113.0668 | 120.5648 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-01-31 20:00 | 0 | 0 | 0 | 0 | -17.5443 | 132.4565 | 116.0291 | -26.0291 | 128.4752 | 134.7151 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-01-31 21:00 | 0 | 0 | 0 | 0 | -17.5328 | 147.4546 | 118.3439 | -28.3439 | 144.3486 | 148.9513 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-01-31 22:00 | 0 | 0 | 0 | 0 | -17.5212 | 162.4528 | 119.891 | -29.891 | 160.633 | 163.2382 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-01-31 23:00 | 0 | 0 | 0 | 0 | -17.5097 | 177.451 | 120.5289 | -30.5289 | 177.1776 | 177.5057 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-02-01 | 0 | 0 | 0 | 0 | -17.4982 | -167.5508 | 120.1957 | -30.1957 | -166.2389 | 168.0999 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-02-01 01:00 | 0 | 0 | 0 | 0 | -17.4866 | -152.5527 | 118.9225 | -28.9225 | -149.8491 | 153.8013 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-02-01 02:00 | 0 | 0 | 0 | 0 | -17.4751 | -137.5545 | 116.8264 | -26.8264 | -133.8317 | 139.5397 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-02-01 03:00 | 0 | 0 | 0 | 0 | -17.4635 | -122.5563 | 114.0875 | -24.0875 | -118.2727 | 125.349 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-02-01 04:00 | 0 | 0 | 0 | 0 | -17.452 | -107.5581 | 110.921 | -20.921 | -103.1648 | 111.2708 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-02-01 05:00 | 0 | 0 | 0 | 0 | -17.4404 | -92.5598 | 107.5538 | -17.5538 | -88.4326 | 97.3665 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-02-01 06:00 | 0 | 0 | 0 | 0 | -17.4288 | -77.5616 | 104.209 | -14.209 | -73.9662 | 83.7336 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-02-01 07:00 | 0 | 0 | 0 | 0 | -17.4172 | -62.5634 | 101.0969 | -11.0969 | -59.651 | 70.5395 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.2 | -2.2 | 1.0952 | 0
2016-02-01 08:00 | 0 | 0 | 0 | 0 | -17.4056 | -47.5652 | 98.4084 | -8.4084 | -45.39 | 58.0932 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-02-01 09:00 | 0 | 0 | 0 | 0 | -17.394 | -32.5669 | 96.308 | -6.308 | -31.1178 | 47.001 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-02-01 10:00 | 0 | 0 | 0 | 0 | -17.3824 | -17.5687 | 94.9261 | -4.9261 | -16.806 | 38.4603 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-02-01 11:00 | 0 | 0 | 0 | 0 | -17.3707 | -2.5705 | 94.3498 | -4.3498 | -2.4602 | 34.4306 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-02-01 12:00 | 0 | 0 | 0 | 0 | -17.3591 | 12.4278 | 94.6156 | -4.6156 | 11.8925 | 36.4425 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-02-01 13:00 | 0 | 0 | 0 | 0 | -17.3474 | 27.426 | 95.7057 | -5.7057 | 26.2214 | 43.6685 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-02-01 14:00 | 0 | 0 | 0 | 0 | -17.3358 | 42.4243 | 97.5497 | -7.5497 | 40.5116 | 54.0545 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-02-01 15:00 | 0 | 0 | 0 | 0 | -17.3241 | 57.4226 | 100.0313 | -10.0313 | 54.7783 | 66.1249 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-02-01 16:00 | 0 | 0 | 0 | 0 | -17.3124 | 72.4208 | 102.9964 | -12.9964 | 69.0734 | 79.1084 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-02-01 17:00 | 0 | 0 | 0 | 0 | -17.3008 | 87.4191 | 106.2621 | -16.2621 | 83.4834 | 92.6171 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-02-01 18:00 | 0 | 0 | 0 | 0 | -17.2891 | 102.4174 | 109.6236 | -19.6236 | 98.1176 | 106.4456 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-02-01 19:00 | 0 | 0 | 0 | 0 | -17.2774 | 117.4157 | 112.8612 | -22.8612 | 113.0894 | 120.4774 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-02-01 20:00 | 0 | 0 | 0 | 0 | -17.2656 | 132.414 | 115.7478 | -25.7478 | 128.4882 | 134.6414 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-02-01 21:00 | 0 | 0 | 0 | 0 | -17.2539 | 147.4123 | 118.0622 | -28.0622 | 144.3468 | 148.8908 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-02-01 22:00 | 0 | 0 | 0 | 0 | -17.2422 | 162.4106 | 119.6097 | -29.6097 | 160.612 | 163.1921 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-02-01 23:00 | 0 | 0 | 0 | 0 | -17.2305 | 177.4089 | 120.2492 | -30.2492 | 177.1349 | 177.5094 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-02-02 | 0 | 0 | 0 | 0 | -17.2187 | -167.5928 | 119.9189 | -29.9189 | -166.3032 | 168.1402 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2 | -2 | 1.0945 | 0
2016-02-02 01:00 | 0 | 0 | 0 | 0 | -17.207 | -152.5945 | 118.6495 | -28.6495 | -149.9321 | 153.8251 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-02-02 02:00 | 0 | 0 | 0 | 0 | -17.1952 | -137.5962 | 116.5574 | -26.5574 | -133.9289 | 139.5499 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2 | -2 | 1.0945 | 0
2016-02-02 03:00 | 0 | 0 | 0 | 0 | -17.1834 | -122.5978 | 113.8218 | -23.8218 | -118.3789 | 125.3452 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-02-02 04:00 | 0 | 0 | 0 | 0 | -17.1716 | -107.5995 | 110.6573 | -20.6573 | -103.2749 | 111.2516 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-02-02 05:00 | 0 | 0 | 0 | 0 | -17.1598 | -92.6011 | 107.2905 | -17.2905 | -88.5422 | 97.3293 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-02-02 06:00 | 0 | 0 | 0 | 0 | -17.148 | -77.6028 | 103.9445 | -13.9445 | -74.0714 | 83.6746 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-02-02 07:00 | 0 | 0 | 0 | 0 | -17.1362 | -62.6044 | 100.8299 | -10.8299 | -59.7484 | 70.4527 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-02-02 08:00 | 0 | 0 | 0 | 0 | -17.1244 | -47.6061 | 98.1378 | -8.1378 | -45.4767 | 57.9699 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-02-02 09:00 | 0 | 0 | 0 | 0 | -17.1126 | -32.6077 | 96.0334 | -6.0334 | -31.1912 | 46.829 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-02-02 10:00 | 0 | 0 | 0 | 0 | -17.1008 | -17.6093 | 94.6478 | -4.6478 | -16.8642 | 38.2292 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-02-02 11:00 | 0 | 0 | 0 | 0 | -17.0889 | -2.611 | 94.0684 | -4.0684 | -2.5019 | 34.1526 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-02-02 12:00 | 0 | 0 | 0 | 0 | -17.0771 | 12.3874 | 94.332 | -4.332 | 11.8676 | 36.1646 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-02-02 13:00 | 0 | 0 | 0 | 0 | -17.0652 | 27.3858 | 95.421 | -5.421 | 26.2126 | 43.4268 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1004 | 0
2016-02-02 14:00 | 0 | 0 | 0 | 0 | -17.0533 | 42.3842 | 97.2647 | -7.2647 | 40.5171 | 53.8536 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-02-02 15:00 | 0 | 0 | 0 | 0 | -17.0414 | 57.3826 | 99.7466 | -9.7466 | 54.7955 | 65.9579 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-02-02 16:00 | 0 | 0 | 0 | 0 | -17.0296 | 72.381 | 102.7121 | -12.7121 | 69.0993 | 78.9681 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.3 | -4.3 | 1.1025 | 0
2016-02-02 17:00 | 0 | 0 | 0 | 0 | -17.0177 | 87.3794 | 105.978 | -15.978 | 83.5141 | 92.4982 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-02-02 18:00 | 0 | 0 | 0 | 0 | -17.0058 | 102.3778 | 109.3393 | -19.3393 | 98.1488 | 106.3443 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-02-02 19:00 | 0 | 0 | 0 | 0 | -16.9938 | 117.3762 | 112.5762 | -22.5762 | 113.1162 | 120.3912 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.6 | -4.6 | 1.1036 | 0
2016-02-02 20:00 | 0 | 0 | 0 | 0 | -16.9819 | 132.3746 | 115.462 | -25.462 | 128.5053 | 134.5686 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.4 | -5.4 | 1.1064 | 0
2016-02-02 21:00 | 0 | 0 | 0 | 0 | -16.97 | 147.3731 | 117.7758 | -27.7758 | 144.349 | 148.8304 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.3 | -5.3 | 1.106 | 0
2016-02-02 22:00 | 0 | 0 | 0 | 0 | -16.9581 | 162.3715 | 119.3235 | -29.3235 | 160.5948 | 163.1441 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-02-02 23:00 | 0 | 0 | 0 | 0 | -16.9461 | 177.37 | 119.9644 | -29.9644 | 177.0958 | 177.4842 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-02-03 | 0 | 0 | 0 | 0 | -16.9341 | -167.6316 | 119.6369 | -29.6369 | -166.3641 | 168.1708 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.105 | 0
2016-02-03 01:00 | 0 | 0 | 0 | 0 | -16.9222 | -152.6331 | 118.3711 | -28.3711 | -150.0122 | 153.8427 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-02-03 02:00 | 0 | 0 | 0 | 0 | -16.9102 | -137.6347 | 116.2828 | -26.2828 | -134.0235 | 139.555 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-02-03 03:00 | 0 | 0 | 0 | 0 | -16.8982 | -122.6362 | 113.5504 | -23.5504 | -118.4827 | 125.3367 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-02-03 04:00 | 0 | 0 | 0 | 0 | -16.8862 | -107.6378 | 110.3879 | -20.3879 | -103.3829 | 111.2279 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.3 | -5.3 | 1.106 | 0
2016-02-03 05:00 | 0 | 0 | 0 | 0 | -16.8742 | -92.6393 | 107.0216 | -17.0216 | -88.6498 | 97.2878 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.3 | -6.3 | 1.1096 | 0
2016-02-03 06:00 | 0 | 0 | 0 | 0 | -16.8622 | -77.6408 | 103.6744 | -13.6744 | -74.1746 | 83.6112 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.8 | -6.8 | 1.1113 | 0
2016-02-03 07:00 | 0 | 0 | 0 | 0 | -16.8502 | -62.6423 | 100.5572 | -10.5572 | -59.8438 | 70.3616 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.9 | -6.9 | 1.1117 | 0
2016-02-03 08:00 | 0 | 0 | 0 | 0 | -16.8382 | -47.6438 | 97.8617 | -7.8617 | -45.5613 | 57.8421 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.3 | -7.3 | 1.1131 | 0
2016-02-03 09:00 | 0 | 0 | 0 | 0 | -16.8261 | -32.6453 | 95.7535 | -5.7535 | -31.2623 | 46.6522 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.6 | -7.6 | 1.1141 | 0
2016-02-03 10:00 | 0 | 0 | 0 | 0 | -16.8141 | -17.6468 | 94.3643 | -4.3643 | -16.9198 | 37.9929 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-02-03 11:00 | 0 | 0 | 0 | 0 | -16.8021 | -2.6483 | 93.782 | -3.782 | -2.5407 | 33.8694 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.1 | -8.1 | 1.1159 | 0
2016-02-03 12:00 | 0 | 0 | 0 | 0 | -16.79 | 12.3502 | 94.0436 | -4.0436 | 11.8458 | 35.8831 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.2 | -8.2 | 1.1162 | 0
2016-02-03 13:00 | 0 | 0 | 0 | 0 | -16.7779 | 27.3487 | 95.1315 | -5.1315 | 26.2072 | 43.1836 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.8 | -7.8 | 1.1148 | 0
2016-02-03 14:00 | 0 | 0 | 0 | 0 | -16.7658 | 42.3472 | 96.9752 | -6.9752 | 40.5263 | 53.6525 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.2 | -7.2 | 1.1127 | 0
2016-02-03 15:00 | 0 | 0 | 0 | 0 | -16.7538 | 57.3458 | 99.4575 | -9.4575 | 54.8167 | 65.7915 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.2 | -6.2 | 1.1092 | 0
2016-02-03 16:00 | 0 | 0 | 0 | 0 | -16.7417 | 72.3443 | 102.4235 | -12.4235 | 69.1291 | 78.8289 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.1 | -5.1 | 1.1054 | 0
2016-02-03 17:00 | 0 | 0 | 0 | 0 | -16.7296 | 87.3428 | 105.6897 | -15.6897 | 83.5488 | 92.3805 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.1033 | 0
2016-02-03 18:00 | 0 | 0 | 0 | 0 | -16.7174 | 102.3414 | 109.0508 | -19.0508 | 98.1842 | 106.2443 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1004 | 0
2016-02-03 19:00 | 0 | 0 | 0 | 0 | -16.7053 | 117.3399 | 112.287 | -22.287 | 113.1472 | 120.3062 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-02-03 20:00 | 0 | 0 | 0 | 0 | -16.6932 | 132.3385 | 115.1718 | -25.1718 | 128.5266 | 134.4968 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-02-03 21:00 | 0 | 0 | 0 | 0 | -16.6811 | 147.337 | 117.4849 | -27.4849 | 144.3552 | 148.7703 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-02-03 22:00 | 0 | 0 | 0 | 0 | -16.6689 | 162.3356 | 119.0326 | -29.0326 | 160.5815 | 163.0942 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-02-03 23:00 | 0 | 0 | 0 | 0 | -16.6568 | 177.3342 | 119.6747 | -29.6747 | 177.0603 | 177.4294 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-02-04 | 0 | 0 | 0 | 0 | -16.6446 | -167.6672 | 119.3497 | -29.3497 | -166.4217 | 168.1915 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.2 | -2.2 | 1.0952 | 0
2016-02-04 01:00 | 0 | 0 | 0 | 0 | -16.6324 | -152.6686 | 118.0874 | -28.0874 | -150.0892 | 153.8542 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-02-04 02:00 | 0 | 0 | 0 | 0 | -16.6203 | -137.6701 | 116.0027 | -26.0027 | -134.1153 | 139.5549 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-02-04 03:00 | 0 | 0 | 0 | 0 | -16.6081 | -122.6715 | 113.2735 | -23.2735 | -118.5841 | 125.3235 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2 | -2 | 1.0945 | 0
2016-02-04 04:00 | 0 | 0 | 0 | 0 | -16.5959 | -107.6729 | 110.113 | -20.113 | -103.4887 | 111.1998 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-02-04 05:00 | 0 | 0 | 0 | 0 | -16.5837 | -92.6743 | 106.7471 | -16.7471 | -88.7553 | 97.2419 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.8 | -2.8 | 1.0973 | 0
2016-02-04 06:00 | 0 | 0 | 0 | 0 | -16.5715 | -77.6756 | 103.3988 | -13.3988 | -74.2758 | 83.5436 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-02-04 07:00 | 0 | 0 | 0 | 0 | -16.5592 | -62.677 | 100.2791 | -10.2791 | -59.9372 | 70.2662 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-02-04 08:00 | 0 | 0 | 0 | 0 | -16.547 | -47.6784 | 97.5802 | -7.5802 | -45.6436 | 57.7099 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-02-04 09:00 | 0 | 0 | 0 | 0 | -16.5348 | -32.6798 | 95.4684 | -5.4684 | -31.331 | 46.4708 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-02-04 10:00 | 0 | 0 | 0 | 0 | -16.5225 | -17.6811 | 94.0756 | -4.0756 | -16.9727 | 37.7515 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.6 | -3.6 | 1.1001 | 0
2016-02-04 11:00 | 0 | 0 | 0 | 0 | -16.5103 | -2.6825 | 93.4905 | -3.4905 | -2.5766 | 33.5812 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.6 | -3.6 | 1.1001 | 0
2016-02-04 12:00 | 0 | 0 | 0 | 0 | -16.498 | 12.3161 | 93.7504 | -3.7504 | 11.8273 | 35.5981 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1004 | 0
2016-02-04 13:00 | 0 | 0 | 0 | 0 | -16.4857 | 27.3148 | 94.8376 | -4.8376 | 26.2052 | 42.9389 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-02-04 14:00 | 0 | 0 | 0 | 0 | -16.4734 | 42.3135 | 96.6813 | -6.6813 | 40.5391 | 53.4515 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-02-04 15:00 | 0 | 0 | 0 | 0 | -16.4612 | 57.3121 | 99.1642 | -9.1642 | 54.8417 | 65.6259 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-02-04 16:00 | 0 | 0 | 0 | 0 | -16.4489 | 72.3108 | 102.1309 | -12.1309 | 69.163 | 78.6908 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-02-04 17:00 | 0 | 0 | 0 | 0 | -16.4366 | 87.3095 | 105.3973 | -15.3973 | 83.5877 | 92.2641 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-02-04 18:00 | 0 | 0 | 0 | 0 | -16.4242 | 102.3081 | 108.7582 | -18.7582 | 98.2236 | 106.1457 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.3 | -5.3 | 1.106 | 0
2016-02-04 19:00 | 0 | 0 | 0 | 0 | -16.4119 | 117.3068 | 111.9937 | -21.9937 | 113.1823 | 120.2225 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.6 | -5.6 | 1.1071 | 0
2016-02-04 20:00 | 0 | 0 | 0 | 0 | -16.3996 | 132.3055 | 114.8774 | -24.8774 | 128.5519 | 134.4258 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6 | -6 | 1.1085 | 0
2016-02-04 21:00 | 0 | 0 | 0 | 0 | -16.3873 | 147.3042 | 117.1895 | -27.1895 | 144.3654 | 148.7103 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.9 | -5.9 | 1.1081 | 0
2016-02-04 22:00 | 0 | 0 | 0 | 0 | -16.3749 | 162.3029 | 118.737 | -28.737 | 160.572 | 163.0421 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.8 | -6.8 | 1.1113 | 0
2016-02-04 23:00 | 0 | 0 | 0 | 0 | -16.3626 | 177.3016 | 119.3801 | -29.3801 | 177.0285 | 177.3453 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.6 | -7.6 | 1.1141 | 0
2016-02-05 | 0 | 0 | 0 | 0 | -16.3502 | -167.6997 | 119.0574 | -29.0574 | -166.4759 | 168.2017 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.3 | -8.3 | 1.1165 | 0
2016-02-05 01:00 | 0 | 0 | 0 | 0 | -16.3378 | -152.701 | 117.7984 | -27.7984 | -150.1631 | 153.8592 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.3 | -9.3 | 1.12 | 0
2016-02-05 02:00 | 0 | 0 | 0 | 0 | -16.3254 | -137.7022 | 115.7174 | -25.7174 | -134.2044 | 139.5495 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.1 | -9.1 | 1.1194 | 0
2016-02-05 03:00 | 0 | 0 | 0 | 0 | -16.3131 | -122.7035 | 112.9912 | -22.9912 | -118.683 | 125.3056 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.3 | -9.3 | 1.12 | 0
2016-02-05 04:00 | 0 | 0 | 0 | 0 | -16.3007 | -107.7048 | 109.8326 | -19.8326 | -103.5922 | 111.1671 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.1 | -10.1 | 1.1228 | 0
2016-02-05 05:00 | 0 | 0 | 0 | 0 | -16.2883 | -92.706 | 106.4671 | -16.4671 | -88.8587 | 97.1917 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10 | -10 | 1.1225 | 0
2016-02-05 06:00 | 0 | 0 | 0 | 0 | -16.2758 | -77.7073 | 103.1177 | -13.1177 | -74.3749 | 83.4717 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.5 | -10.5 | 1.1242 | 0
2016-02-05 07:00 | 0 | 0 | 0 | 0 | -16.2634 | -62.7085 | 99.9956 | -9.9956 | -60.0284 | 70.1666 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10 | -10 | 1.1225 | 0
2016-02-05 08:00 | 0 | 0 | 0 | 0 | -16.251 | -47.7098 | 97.2935 | -7.2935 | -45.7238 | 57.5733 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.2 | -9.2 | 1.1197 | 0
2016-02-05 09:00 | 0 | 0 | 0 | 0 | -16.2386 | -32.711 | 95.1781 | -5.1781 | -31.3973 | 46.2847 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.6 | -8.6 | 1.1176 | 0
2016-02-05 10:00 | 0 | 0 | 0 | 0 | -16.2261 | -17.7122 | 93.782 | -3.782 | -17.023 | 37.5051 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.2 | -8.2 | 1.1162 | 0
2016-02-05 11:00 | 0 | 0 | 0 | 0 | -16.2137 | -2.7135 | 93.1943 | -3.1943 | -2.6095 | 33.288 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.2 | -8.2 | 1.1162 | 0
2016-02-05 12:00 | 0 | 0 | 0 | 0 | -16.2012 | 12.2853 | 93.4525 | -3.4525 | 11.812 | 35.3099 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.9 | -8.9 | 1.1186 | 0
2016-02-05 13:00 | 0 | 0 | 0 | 0 | -16.1887 | 27.2841 | 94.5391 | -4.5391 | 26.2067 | 42.6931 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.5 | -8.5 | 1.1173 | 0
2016-02-05 14:00 | 0 | 0 | 0 | 0 | -16.1762 | 42.2829 | 96.3831 | -6.3831 | 40.5556 | 53.2505 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.1 | -8.1 | 1.1159 | 0
2016-02-05 15:00 | 0 | 0 | 0 | 0 | -16.1638 | 57.2817 | 98.8667 | -8.8667 | 54.8705 | 65.4611 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.5 | -8.5 | 1.1173 | 0
2016-02-05 16:00 | 0 | 0 | 0 | 0 | -16.1513 | 72.2805 | 101.8341 | -11.8341 | 69.2008 | 78.554 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.5 | -9.5 | 1.1207 | 0
2016-02-05 17:00 | 0 | 0 | 0 | 0 | -16.1388 | 87.2793 | 105.101 | -15.101 | 83.6305 | 92.1492 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.2 | -9.2 | 1.1197 | 0
2016-02-05 18:00 | 0 | 0 | 0 | 0 | -16.1263 | 102.2781 | 108.4617 | -18.4617 | 98.2671 | 106.0485 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.2 | -8.2 | 1.1162 | 0
2016-02-05 19:00 | 0 | 0 | 0 | 0 | -16.1137 | 117.2769 | 111.6964 | -21.6964 | 113.2214 | 120.14 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.1 | -8.1 | 1.1159 | 0
2016-02-05 20:00 | 0 | 0 | 0 | 0 | -16.1012 | 132.2757 | 114.5789 | -24.5789 | 128.5813 | 134.3557 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.8 | -7.8 | 1.1148 | 0
2016-02-05 21:00 | 0 | 0 | 0 | 0 | -16.0887 | 147.2746 | 116.8899 | -26.8899 | 144.3796 | 148.6504 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.6 | -7.6 | 1.1141 | 0
2016-02-05 22:00 | 0 | 0 | 0 | 0 | -16.0761 | 162.2734 | 118.4369 | -28.4369 | 160.5665 | 162.9877 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.8 | -7.8 | 1.1148 | 0
2016-02-05 23:00 | 0 | 0 | 0 | 0 | -16.0636 | 177.2722 | 119.0808 | -29.0808 | 177.0004 | 177.2333 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-02-06 | 0 | 0 | 0 | 0 | -16.051 | -167.7289 | 118.7602 | -28.7602 | -166.5266 | 168.2012 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.1 | -7.1 | 1.1123 | 0
2016-02-06 01:00 | 0 | 0 | 0 | 0 | -16.0385 | -152.7301 | 117.5044 | -27.5044 | -150.2338 | 153.8576 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.7 | -7.7 | 1.1144 | 0
2016-02-06 02:00 | 0 | 0 | 0 | 0 | -16.0259 | -137.7312 | 115.4268 | -25.4268 | -134.2907 | 139.5387 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.4 | -7.4 | 1.1134 | 0
2016-02-06 03:00 | 0 | 0 | 0 | 0 | -16.0133 | -122.7323 | 112.7036 | -22.7036 | -118.7794 | 125.2828 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.1 | -8.1 | 1.1159 | 0
2016-02-06 04:00 | 0 | 0 | 0 | 0 | -16.0007 | -107.7335 | 109.5468 | -19.5468 | -103.6934 | 111.1299 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-02-06 05:00 | 0 | 0 | 0 | 0 | -15.9881 | -92.7346 | 106.1818 | -16.1818 | -88.9599 | 97.1372 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.3 | -7.3 | 1.1131 | 0
2016-02-06 06:00 | 0 | 0 | 0 | 0 | -15.9755 | -77.7357 | 102.8313 | -12.8313 | -74.4719 | 83.3956 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.4 | -7.4 | 1.1134 | 0
2016-02-06 07:00 | 0 | 0 | 0 | 0 | -15.9629 | -62.7368 | 99.7069 | -9.7069 | -60.1175 | 70.0627 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.7 | -7.7 | 1.1144 | 0
2016-02-06 08:00 | 0 | 0 | 0 | 0 | -15.9503 | -47.7379 | 97.0016 | -7.0016 | -45.8016 | 57.4324 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.3 | -7.3 | 1.1131 | 0
2016-02-06 09:00 | 0 | 0 | 0 | 0 | -15.9376 | -32.7391 | 94.8827 | -4.8827 | -31.4611 | 46.0941 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-02-06 10:00 | 0 | 0 | 0 | 0 | -15.925 | -17.7402 | 93.4834 | -3.4834 | -17.0706 | 37.2538 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-02-06 11:00 | 0 | 0 | 0 | 0 | -15.9124 | -2.7412 | 92.8933 | -2.8933 | -2.6395 | 32.9899 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.5 | -8.5 | 1.1173 | 0
2016-02-06 12:00 | 0 | 0 | 0 | 0 | -15.8997 | 12.2577 | 93.1501 | -3.1501 | 11.7999 | 35.0184 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.6 | -8.6 | 1.1176 | 0
2016-02-06 13:00 | 0 | 0 | 0 | 0 | -15.887 | 27.2566 | 94.2363 | -4.2363 | 26.2117 | 42.4461 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.6 | -8.6 | 1.1176 | 0
2016-02-06 14:00 | 0 | 0 | 0 | 0 | -15.8744 | 42.2555 | 96.0808 | -6.0808 | 40.5758 | 53.0498 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.9 | -8.9 | 1.1186 | 0
2016-02-06 15:00 | 0 | 0 | 0 | 0 | -15.8617 | 57.2544 | 98.5652 | -8.5652 | 54.9032 | 65.2973 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.9 | -8.9 | 1.1186 | 0
2016-02-06 16:00 | 0 | 0 | 0 | 0 | -15.849 | 72.2534 | 101.5335 | -11.5335 | 69.2425 | 78.4184 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.7 | -8.7 | 1.1179 | 0
2016-02-06 17:00 | 0 | 0 | 0 | 0 | -15.8363 | 87.2523 | 104.8008 | -14.8008 | 83.6774 | 92.0357 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.9 | -8.9 | 1.1186 | 0
2016-02-06 18:00 | 0 | 0 | 0 | 0 | -15.8236 | 102.2513 | 108.1613 | -18.1613 | 98.3147 | 105.9527 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.1 | -8.1 | 1.1159 | 0
2016-02-06 19:00 | 0 | 0 | 0 | 0 | -15.8109 | 117.2502 | 111.3951 | -21.3951 | 113.2646 | 120.0587 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-02-06 20:00 | 0 | 0 | 0 | 0 | -15.7982 | 132.2492 | 114.2763 | -24.2763 | 128.6148 | 134.2865 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8 | -8 | 1.1155 | 0
2016-02-06 21:00 | 0 | 0 | 0 | 0 | -15.7854 | 147.2481 | 116.586 | -26.586 | 144.3978 | 148.5904 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.2 | -8.2 | 1.1162 | 0
2016-02-06 22:00 | 0 | 0 | 0 | 0 | -15.7727 | 162.2471 | 118.1325 | -28.1325 | 160.5647 | 162.9308 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.5 | -8.5 | 1.1173 | 0
2016-02-06 23:00 | 0 | 0 | 0 | 0 | -15.76 | 177.2461 | 118.7769 | -28.7769 | 176.9759 | 177.0952 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.3 | -8.3 | 1.1165 | 0
2016-02-07 | 0 | 0 | 0 | 0 | -15.7472 | -167.7549 | 118.4582 | -28.4582 | -166.574 | 168.1895 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.3 | -8.3 | 1.1165 | 0
2016-02-07 01:00 | 0 | 0 | 0 | 0 | -15.7345 | -152.756 | 117.2053 | -27.2053 | -150.3015 | 153.8493 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-02-07 02:00 | 0 | 0 | 0 | 0 | -15.7217 | -137.757 | 115.131 | -25.131 | -134.3741 | 139.5224 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.7 | -7.7 | 1.1144 | 0
2016-02-07 03:00 | 0 | 0 | 0 | 0 | -15.7089 | -122.758 | 112.4107 | -22.4107 | -118.8732 | 125.2552 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.8 | -7.8 | 1.1148 | 0
2016-02-07 04:00 | 0 | 0 | 0 | 0 | -15.6961 | -107.759 | 109.2559 | -19.2559 | -103.7922 | 111.0882 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.7 | -7.7 | 1.1144 | 0
2016-02-07 05:00 | 0 | 0 | 0 | 0 | -15.6834 | -92.76 | 105.8912 | -15.8912 | -89.0589 | 97.0783 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.6 | -7.6 | 1.1141 | 0
2016-02-07 06:00 | 0 | 0 | 0 | 0 | -15.6706 | -77.7609 | 102.5397 | -12.5397 | -74.5668 | 83.3152 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.4 | -7.4 | 1.1134 | 0
2016-02-07 07:00 | 0 | 0 | 0 | 0 | -15.6578 | -62.7619 | 99.4131 | -9.4131 | -60.2044 | 69.9546 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.3 | -7.3 | 1.1131 | 0
2016-02-07 08:00 | 0 | 0 | 0 | 0 | -15.6449 | -47.7629 | 96.7047 | -6.7047 | -45.8772 | 57.2873 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.9 | -6.9 | 1.1117 | 0
2016-02-07 09:00 | 0 | 0 | 0 | 0 | -15.6321 | -32.7639 | 94.5824 | -4.5824 | -31.5224 | 45.899 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.8 | -6.8 | 1.1113 | 0
2016-02-07 10:00 | 0 | 0 | 0 | 0 | -15.6193 | -17.7648 | 93.1801 | -3.1801 | -17.1154 | 36.9976 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.1 | -7.1 | 1.1123 | 0
2016-02-07 11:00 | 0 | 0 | 0 | 0 | -15.6065 | -2.7658 | 92.5876 | -2.5876 | -2.6665 | 32.6872 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7 | -7 | 1.112 | 0
2016-02-07 12:00 | 0 | 0 | 0 | 0 | -15.5936 | 12.2333 | 92.8432 | -2.8432 | 11.7911 | 34.7239 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.1 | -7.1 | 1.1123 | 0
2016-02-07 13:00 | 0 | 0 | 0 | 0 | -15.5808 | 27.2323 | 93.9293 | -3.9293 | 26.2202 | 42.1983 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.9 | -6.9 | 1.1117 | 0
2016-02-07 14:00 | 0 | 0 | 0 | 0 | -15.5679 | 42.2314 | 95.7744 | -5.7744 | 40.5997 | 52.8496 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.9 | -6.9 | 1.1117 | 0
2016-02-07 15:00 | 0 | 0 | 0 | 0 | -15.555 | 57.2304 | 98.2598 | -8.2598 | 54.9396 | 65.1347 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7 | -7 | 1.112 | 0
2016-02-07 16:00 | 0 | 0 | 0 | 0 | -15.5422 | 72.2295 | 101.2291 | -11.2291 | 69.2882 | 78.2843 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.3 | -7.3 | 1.1131 | 0
2016-02-07 17:00 | 0 | 0 | 0 | 0 | -15.5293 | 87.2286 | 104.4969 | -14.4969 | 83.7283 | 91.9237 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.1 | -7.1 | 1.1123 | 0
2016-02-07 18:00 | 0 | 0 | 0 | 0 | -15.5164 | 102.2277 | 107.8572 | -17.8572 | 98.3663 | 105.8583 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.7 | -6.7 | 1.111 | 0
2016-02-07 19:00 | 0 | 0 | 0 | 0 | -15.5035 | 117.2267 | 111.09 | -21.09 | 113.3119 | 119.9787 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.5 | -6.5 | 1.1102 | 0
2016-02-07 20:00 | 0 | 0 | 0 | 0 | -15.4906 | 132.2258 | 113.9698 | -23.9698 | 128.6522 | 134.2181 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.1 | -6.1 | 1.1088 | 0
2016-02-07 21:00 | 0 | 0 | 0 | 0 | -15.4777 | 147.2249 | 116.2781 | -26.2781 | 144.4199 | 148.5302 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.9 | -5.9 | 1.1081 | 0
2016-02-07 22:00 | 0 | 0 | 0 | 0 | -15.4648 | 162.224 | 117.8237 | -27.8237 | 160.5668 | 162.8712 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-02-07 23:00 | 0 | 0 | 0 | 0 | -15.4518 | 177.2231 | 118.4685 | -28.4685 | 176.9551 | 176.9334 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-02-08 | 0 | 0 | 0 | 0 | -15.4389 | -167.7777 | 118.1516 | -28.1516 | -166.6179 | 168.1664 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-02-08 01:00 | 0 | 0 | 0 | 0 | -15.426 | -152.7786 | 116.9014 | -26.9014 | -150.366 | 153.8341 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-02-08 02:00 | 0 | 0 | 0 | 0 | -15.413 | -137.7795 | 114.8303 | -24.8303 | -134.4546 | 139.5006 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.7 | -4.7 | 1.1039 | 0
2016-02-08 03:00 | 0 | 0 | 0 | 0 | -15.4001 | -122.7804 | 112.1128 | -22.1128 | -118.9644 | 125.2226 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.7 | -4.7 | 1.1039 | 0
2016-02-08 04:00 | 0 | 0 | 0 | 0 | -15.3871 | -107.7812 | 108.9598 | -18.9598 | -103.8887 | 111.042 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.7 | -4.7 | 1.1039 | 0
2016-02-08 05:00 | 0 | 0 | 0 | 0 | -15.3741 | -92.7821 | 105.5956 | -15.5956 | -89.1556 | 97.015 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.1 | -5.1 | 1.1054 | 0
2016-02-08 06:00 | 0 | 0 | 0 | 0 | -15.3611 | -77.7829 | 102.2431 | -12.2431 | -74.6594 | 83.2307 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.1 | -5.1 | 1.1054 | 0
2016-02-08 07:00 | 0 | 0 | 0 | 0 | -15.3481 | -62.7838 | 99.1142 | -9.1142 | -60.289 | 69.8424 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.6 | -5.6 | 1.1071 | 0
2016-02-08 08:00 | 0 | 0 | 0 | 0 | -15.3351 | -47.7846 | 96.4028 | -6.4028 | -45.9504 | 57.138 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.9 | -5.9 | 1.1081 | 0
2016-02-08 09:00 | 0 | 0 | 0 | 0 | -15.3221 | -32.7855 | 94.2773 | -4.2773 | -31.5812 | 45.6997 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.4 | -6.4 | 1.1099 | 0
2016-02-08 10:00 | 0 | 0 | 0 | 0 | -15.3091 | -17.7863 | 92.8721 | -2.8721 | -17.1575 | 36.7367 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7 | -7 | 1.112 | 0
2016-02-08 11:00 | 0 | 0 | 0 | 0 | -15.2961 | -2.7871 | 92.2775 | -2.2775 | -2.6904 | 32.3797 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-02-08 12:00 | 0 | 0 | 0 | 0 | -15.2831 | 12.2121 | 92.532 | -2.532 | 11.7856 | 34.4265 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.3 | -8.3 | 1.1165 | 0
2016-02-08 13:00 | 0 | 0 | 0 | 0 | -15.2701 | 27.2112 | 93.6181 | -3.6181 | 26.2322 | 41.9497 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.5 | -8.5 | 1.1173 | 0
2016-02-08 14:00 | 0 | 0 | 0 | 0 | -15.257 | 42.2104 | 95.464 | -5.464 | 40.6272 | 52.6499 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.9 | -8.9 | 1.1186 | 0
2016-02-08 15:00 | 0 | 0 | 0 | 0 | -15.244 | 57.2096 | 97.9507 | -7.9507 | 54.98 | 64.9732 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.1 | -9.1 | 1.1194 | 0
2016-02-08 16:00 | 0 | 0 | 0 | 0 | -15.2309 | 72.2088 | 100.921 | -10.921 | 69.3378 | 78.1517 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.5 | -9.5 | 1.1207 | 0
2016-02-08 17:00 | 0 | 0 | 0 | 0 | -15.2178 | 87.2081 | 104.1894 | -14.1894 | 83.7832 | 91.8133 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.2 | -9.2 | 1.1197 | 0
2016-02-08 18:00 | 0 | 0 | 0 | 0 | -15.2048 | 102.2073 | 107.5495 | -17.5495 | 98.4219 | 105.7655 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9 | -9 | 1.119 | 0
2016-02-08 19:00 | 0 | 0 | 0 | 0 | -15.1917 | 117.2065 | 110.7813 | -20.7813 | 113.3632 | 119.9 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.1 | -9.1 | 1.1194 | 0
2016-02-08 20:00 | 0 | 0 | 0 | 0 | -15.1786 | 132.2057 | 113.6595 | -23.6595 | 128.6936 | 134.1504 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.1 | -9.1 | 1.1194 | 0
2016-02-08 21:00 | 0 | 0 | 0 | 0 | -15.1655 | 147.2049 | 115.9662 | -25.9662 | 144.446 | 148.4699 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.3 | -9.3 | 1.12 | 0
2016-02-08 22:00 | 0 | 0 | 0 | 0 | -15.1524 | 162.2042 | 117.5108 | -27.5108 | 160.5727 | 162.8089 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.4 | -9.4 | 1.1204 | 0
2016-02-08 23:00 | 0 | 0 | 0 | 0 | -15.1393 | 177.2034 | 118.1558 | -28.1558 | 176.9379 | 176.7502 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.8 | -8.8 | 1.1183 | 0
2016-02-09 | 0 | 0 | 0 | 0 | -15.1262 | -167.7973 | 117.8403 | -27.8403 | -166.6584 | 168.1315 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.6 | -8.6 | 1.1176 | 0
2016-02-09 01:00 | 0 | 0 | 0 | 0 | -15.1131 | -152.7981 | 116.5928 | -26.5928 | -150.4273 | 153.8119 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-02-09 02:00 | 0 | 0 | 0 | 0 | -15.0999 | -137.7988 | 114.5247 | -24.5247 | -134.5323 | 139.4732 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.4 | -7.4 | 1.1134 | 0
2016-02-09 03:00 | 0 | 0 | 0 | 0 | -15.0868 | -122.7995 | 111.81 | -21.81 | -119.053 | 125.1851 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.2 | -7.2 | 1.1127 | 0
2016-02-09 04:00 | 0 | 0 | 0 | 0 | -15.0736 | -107.8003 | 108.6587 | -18.6587 | -103.9827 | 110.9911 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.7 | -6.7 | 1.111 | 0
2016-02-09 05:00 | 0 | 0 | 0 | 0 | -15.0605 | -92.801 | 105.2949 | -15.2949 | -89.25 | 96.9475 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.5 | -6.5 | 1.1102 | 0
2016-02-09 06:00 | 0 | 0 | 0 | 0 | -15.0473 | -77.8017 | 101.9414 | -11.9414 | -74.7498 | 83.142 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.4 | -6.4 | 1.1099 | 0
2016-02-09 07:00 | 0 | 0 | 0 | 0 | -15.0342 | -62.8024 | 98.8104 | -8.8104 | -60.3714 | 69.7262 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.7 | -5.7 | 1.1075 | 0
2016-02-09 08:00 | 0 | 0 | 0 | 0 | -15.021 | -47.8031 | 96.0961 | -6.0961 | -46.0212 | 56.9847 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-02-09 09:00 | 0 | 0 | 0 | 0 | -15.0078 | -32.8038 | 93.9675 | -3.9675 | -31.6374 | 45.4961 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-02-09 10:00 | 0 | 0 | 0 | 0 | -14.9946 | -17.8045 | 92.5595 | -2.5595 | -17.1968 | 36.4712 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.7 | -5.7 | 1.1075 | 0
2016-02-09 11:00 | 0 | 0 | 0 | 0 | -14.9814 | -2.8052 | 91.963 | -1.963 | -2.7114 | 32.0678 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.8 | -5.8 | 1.1078 | 0
2016-02-09 12:00 | 0 | 0 | 0 | 0 | -14.9682 | 12.1941 | 92.2167 | -2.2167 | 11.7832 | 34.1264 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.5 | -6.5 | 1.1102 | 0
2016-02-09 13:00 | 0 | 0 | 0 | 0 | -14.955 | 27.1934 | 93.303 | -3.303 | 26.2476 | 41.7005 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.1 | -6.1 | 1.1088 | 0
2016-02-09 14:00 | 0 | 0 | 0 | 0 | -14.9418 | 42.1927 | 95.1498 | -5.1498 | 40.6584 | 52.4509 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6 | -6 | 1.1085 | 0
2016-02-09 15:00 | 0 | 0 | 0 | 0 | -14.9285 | 57.1921 | 97.6378 | -7.6378 | 55.0241 | 64.813 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.5 | -5.5 | 1.1067 | 0
2016-02-09 16:00 | 0 | 0 | 0 | 0 | -14.9153 | 72.1914 | 100.6094 | -10.6094 | 69.3913 | 78.0206 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.7 | -6.7 | 1.111 | 0
2016-02-09 17:00 | 0 | 0 | 0 | 0 | -14.9021 | 87.1908 | 103.8784 | -13.8784 | 83.842 | 91.7045 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.8 | -5.8 | 1.1078 | 0
2016-02-09 18:00 | 0 | 0 | 0 | 0 | -14.8888 | 102.1901 | 107.2383 | -17.2383 | 98.4815 | 105.6741 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7 | -7 | 1.112 | 0
2016-02-09 19:00 | 0 | 0 | 0 | 0 | -14.8756 | 117.1895 | 110.469 | -20.469 | 113.4184 | 119.8224 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.9 | -6.9 | 1.1117 | 0
2016-02-09 20:00 | 0 | 0 | 0 | 0 | -14.8623 | 132.1888 | 113.3455 | -23.3455 | 128.7389 | 134.0835 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.1 | -7.1 | 1.1123 | 0
2016-02-09 21:00 | 0 | 0 | 0 | 0 | -14.849 | 147.1882 | 115.6504 | -25.6504 | 144.4759 | 148.4093 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.4 | -8.4 | 1.1169 | 0
2016-02-09 22:00 | 0 | 0 | 0 | 0 | -14.8358 | 162.1876 | 117.1939 | -27.1939 | 160.5823 | 162.7435 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.5 | -7.5 | 1.1138 | 0
2016-02-09 23:00 | 0 | 0 | 0 | 0 | -14.8225 | 177.1869 | 117.8388 | -27.8388 | 176.9244 | 176.548 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.2 | -7.2 | 1.1127 | 0
2016-02-10 | 0 | 0 | 0 | 0 | -14.8092 | -167.8137 | 117.5246 | -27.5246 | -166.6954 | 168.0848 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.2 | -8.2 | 1.1162 | 0
2016-02-10 01:00 | 0 | 0 | 0 | 0 | -14.7959 | -152.8143 | 116.2795 | -26.2795 | -150.4855 | 153.7826 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.6 | -7.6 | 1.1141 | 0
2016-02-10 02:00 | 0 | 0 | 0 | 0 | -14.7826 | -137.8149 | 114.2144 | -24.2144 | -134.6071 | 139.4401 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.1 | -6.1 | 1.1088 | 0
2016-02-10 03:00 | 0 | 0 | 0 | 0 | -14.7693 | -122.8155 | 111.5023 | -21.5023 | -119.1389 | 125.1426 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.5 | -8.5 | 1.1173 | 0
2016-02-10 04:00 | 0 | 0 | 0 | 0 | -14.7559 | -107.8161 | 108.3527 | -18.3527 | -104.0742 | 110.9357 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7 | -7 | 1.112 | 0
2016-02-10 05:00 | 0 | 0 | 0 | 0 | -14.7426 | -92.8167 | 104.9893 | -14.9893 | -89.3422 | 96.8756 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.7 | -6.7 | 1.111 | 0
2016-02-10 06:00 | 0 | 0 | 0 | 0 | -14.7293 | -77.8173 | 101.6349 | -11.6349 | -74.8379 | 83.0492 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.8 | -6.8 | 1.1113 | 0
2016-02-10 07:00 | 0 | 0 | 0 | 0 | -14.7159 | -62.8178 | 98.5018 | -8.5018 | -60.4515 | 69.6059 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.8 | -6.8 | 1.1113 | 0
2016-02-10 08:00 | 0 | 0 | 0 | 0 | -14.7026 | -47.8184 | 95.7847 | -5.7847 | -46.0896 | 56.8274 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.9 | -6.9 | 1.1117 | 0
2016-02-10 09:00 | 0 | 0 | 0 | 0 | -14.6892 | -32.819 | 93.6531 | -3.6531 | -31.6911 | 45.2883 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.4 | -7.4 | 1.1134 | 0
2016-02-10 10:00 | 0 | 0 | 0 | 0 | -14.6759 | -17.8195 | 92.2425 | -2.2425 | -17.2333 | 36.2012 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.6 | -7.6 | 1.1141 | 0
2016-02-10 11:00 | 0 | 0 | 0 | 0 | -14.6625 | -2.8201 | 91.6443 | -1.6443 | -2.7293 | 31.7514 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-02-10 12:00 | 0 | 0 | 0 | 0 | -14.6491 | 12.1793 | 91.8973 | -1.8973 | 11.7842 | 33.8237 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.6 | -8.6 | 1.1176 | 0
2016-02-10 13:00 | 0 | 0 | 0 | 0 | -14.6357 | 27.1788 | 92.9839 | -2.9839 | 26.2665 | 41.4509 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8 | -8 | 1.1155 | 0
2016-02-10 14:00 | 0 | 0 | 0 | 0 | -14.6223 | 42.1783 | 94.832 | -4.832 | 40.6933 | 52.2528 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.7 | -7.7 | 1.1144 | 0
2016-02-10 15:00 | 0 | 0 | 0 | 0 | -14.6089 | 57.1777 | 97.3215 | -7.3215 | 55.072 | 64.6542 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-02-10 16:00 | 0 | 0 | 0 | 0 | -14.5955 | 72.1772 | 100.2943 | -10.2943 | 69.4487 | 77.8912 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-02-10 17:00 | 0 | 0 | 0 | 0 | -14.5821 | 87.1767 | 103.564 | -13.564 | 83.9048 | 91.5973 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-02-10 18:00 | 0 | 0 | 0 | 0 | -14.5687 | 102.1762 | 106.9236 | -16.9236 | 98.545 | 105.5842 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-02-10 19:00 | 0 | 0 | 0 | 0 | -14.5552 | 117.1757 | 110.1532 | -20.1532 | 113.4776 | 119.7461 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.7 | -7.7 | 1.1144 | 0
2016-02-10 20:00 | 0 | 0 | 0 | 0 | -14.5418 | 132.1752 | 113.028 | -23.028 | 128.7882 | 134.0172 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.8 | -7.8 | 1.1148 | 0
2016-02-10 21:00 | 0 | 0 | 0 | 0 | -14.5284 | 147.1747 | 115.3309 | -25.3309 | 144.5096 | 148.3484 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8 | -8 | 1.1155 | 0
2016-02-10 22:00 | 0 | 0 | 0 | 0 | -14.5149 | 162.1742 | 116.873 | -26.873 | 160.5957 | 162.6751 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.1 | -7.1 | 1.1123 | 0
2016-02-10 23:00 | 0 | 0 | 0 | 0 | -14.5015 | 177.1737 | 117.5176 | -27.5176 | 176.9144 | 176.329 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.7 | -6.7 | 1.111 | 0
2016-02-11 | 0 | 0 | 0 | 0 | -14.488 | -167.8268 | 117.2046 | -27.2046 | -166.7291 | 168.026 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-02-11 01:00 | 0 | 0 | 0 | 0 | -14.4745 | -152.8273 | 115.9617 | -25.9617 | -150.5405 | 153.7461 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-02-11 02:00 | 0 | 0 | 0 | 0 | -14.4611 | -137.8278 | 113.8994 | -23.8994 | -134.6789 | 139.4013 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.7 | -6.7 | 1.111 | 0
2016-02-11 03:00 | 0 | 0 | 0 | 0 | -14.4476 | -122.8282 | 111.1898 | -21.1898 | -119.2221 | 125.0951 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-02-11 04:00 | 0 | 0 | 0 | 0 | -14.4341 | -107.8287 | 108.0419 | -18.0419 | -104.1633 | 110.8757 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.7 | -6.7 | 1.111 | 0
2016-02-11 05:00 | 0 | 0 | 0 | 0 | -14.4206 | -92.8291 | 104.679 | -14.679 | -89.4319 | 96.7995 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.1 | -7.1 | 1.1123 | 0
2016-02-11 06:00 | 0 | 0 | 0 | 0 | -14.4071 | -77.8296 | 101.3237 | -11.3237 | -74.9238 | 82.9523 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.1 | -7.1 | 1.1123 | 0
2016-02-11 07:00 | 0 | 0 | 0 | 0 | -14.3936 | -62.83 | 98.1885 | -8.1885 | -60.5292 | 69.4816 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.7 | -6.7 | 1.111 | 0
2016-02-11 08:00 | 0 | 0 | 0 | 0 | -14.38 | -47.8305 | 95.4687 | -5.4687 | -46.1556 | 56.6662 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.8 | -6.8 | 1.1113 | 0
2016-02-11 09:00 | 0 | 0 | 0 | 0 | -14.3665 | -32.8309 | 93.3342 | -3.3342 | -31.7422 | 45.0765 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.5 | -6.5 | 1.1102 | 0
2016-02-11 10:00 | 0.01 | 0.01 | 0 | 0 | -14.353 | -17.8313 | 91.9212 | -1.9212 | -17.267 | 35.9268 | 0 | 0.0075 | 0.8 | 1 | 0.002 | 0.0095 | -7.3 | -7.2997 | 1.113 | 8.6707e-06
2016-02-11 11:00 | 0.02 | 0.02 | 0 | 0 | -14.3394 | -2.8318 | 91.3214 | -1.3214 | -2.7442 | 31.4307 | 0 | 0.015 | 0.8 | 1 | 0.004 | 0.019 | -7.3 | -7.2994 | 1.113 | 1.7341e-05
2016-02-11 12:00 | 0.03 | 0.03 | 0 | 0 | -14.3259 | 12.1678 | 91.5739 | -1.5739 | 11.7884 | 33.5186 | 0 | 0.0225 | 0.8 | 1 | 0.006 | 0.0285 | -6.9 | -6.8991 | 1.1116 | 2.5979e-05
2016-02-11 13:00 | 0.02 | 0.02 | 0 | 0 | -14.3123 | 27.1674 | 92.6611 | -2.6611 | 26.2889 | 41.2011 | 0 | 0.015 | 0.8 | 1 | 0.004 | 0.019 | -6.2 | -6.1994 | 1.1092 | 1.7281e-05
2016-02-11 14:00 | 0.01 | 0.01 | 0 | 0 | -14.2988 | 42.167 | 94.5105 | -4.5105 | 40.7318 | 52.0556 | 0 | 0.0075 | 0.8 | 1 | 0.002 | 0.0095 | -6.3 | -6.2997 | 1.1095 | 8.6434e-06
2016-02-11 15:00 | 0 | 0 | 0 | 0 | -14.2852 | 57.1666 | 97.0016 | -7.0016 | 55.1236 | 64.497 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.2 | -6.2 | 1.1092 | 0
2016-02-11 16:00 | 0 | 0 | 0 | 0 | -14.2716 | 72.1662 | 99.9759 | -9.9759 | 69.5099 | 77.7634 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.8 | -5.8 | 1.1078 | 0
2016-02-11 17:00 | 0 | 0 | 0 | 0 | -14.258 | 87.1658 | 103.2463 | -13.2463 | 83.9714 | 91.4918 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.5 | -6.5 | 1.1102 | 0
2016-02-11 18:00 | 0 | 0 | 0 | 0 | -14.2445 | 102.1654 | 106.6057 | -16.6057 | 98.6124 | 105.4959 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7 | -7 | 1.112 | 0
2016-02-11 19:00 | 0 | 0 | 0 | 0 | -14.2309 | 117.1651 | 109.8341 | -19.8341 | 113.5406 | 119.6711 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.8 | -5.8 | 1.1078 | 0
2016-02-11 20:00 | 0 | 0 | 0 | 0 | -14.2173 | 132.1647 | 112.7069 | -22.7069 | 128.8413 | 133.9517 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.1 | -6.1 | 1.1088 | 0
2016-02-11 21:00 | 0 | 0 | 0 | 0 | -14.2036 | 147.1643 | 115.0078 | -25.0078 | 144.5471 | 148.2871 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.1 | -6.1 | 1.1088 | 0
2016-02-11 22:00 | 0 | 0 | 0 | 0 | -14.19 | 162.164 | 116.5483 | -26.5483 | 160.6128 | 162.6033 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.4 | -5.4 | 1.1064 | 0
2016-02-11 23:00 | 0 | 0 | 0 | 0 | -14.1764 | 177.1636 | 117.1925 | -27.1925 | 176.908 | 176.095 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.5 | -6.5 | 1.1102 | 0
2016-02-12 | 0 | 0 | 0 | 0 | -14.1628 | -167.8367 | 116.8803 | -26.8803 | -166.7594 | 167.9549 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9 | -9 | 1.119 | 0
2016-02-12 01:00 | 0 | 0 | 0 | 0 | -14.1491 | -152.8371 | 115.6396 | -25.6396 | -150.5923 | 153.7022 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-02-12 02:00 | 0 | 0 | 0 | 0 | -14.1355 | -137.8374 | 113.5798 | -23.5798 | -134.7478 | 139.3567 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.1 | -7.1 | 1.1123 | 0
2016-02-12 03:00 | 0 | 0 | 0 | 0 | -14.1218 | -122.8378 | 110.8727 | -20.8727 | -119.3027 | 125.0425 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.9 | -6.9 | 1.1117 | 0
2016-02-12 04:00 | 0 | 0 | 0 | 0 | -14.1082 | -107.8381 | 107.7265 | -17.7265 | -104.2499 | 110.8111 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-02-12 05:00 | 0 | 0 | 0 | 0 | -14.0945 | -92.8384 | 104.3639 | -14.3639 | -89.5193 | 96.7191 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.8 | -8.8 | 1.1183 | 0
2016-02-12 06:00 | 0 | 0 | 0 | 0 | -14.0809 | -77.8387 | 101.0078 | -11.0078 | -75.0072 | 82.8513 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.8 | -8.8 | 1.1183 | 0
2016-02-12 07:00 | 0.0033333 | 0.0033333 | 0 | 0 | -14.0672 | -62.839 | 97.8707 | -7.8707 | -60.6046 | 69.3535 | 0 | 0.0025 | 0.8 | 1 | 0.00066667 | 0.0031667 | -9.1 | -9.0999 | 1.1193 | 2.9066e-06
2016-02-12 08:00 | 0.0066667 | 0.0066667 | 0 | 0 | -14.0535 | -47.8393 | 95.1482 | -5.1482 | -46.2192 | 56.5011 | 0 | 0.005 | 0.8 | 1 | 0.0013333 | 0.0063333 | -9 | -8.9998 | 1.119 | 5.8113e-06
2016-02-12 09:00 | 0.01 | 0.01 | 0 | 0 | -14.0398 | -32.8396 | 93.011 | -3.011 | -31.7907 | 44.8608 | 0 | 0.0075 | 0.8 | 1 | 0.002 | 0.0095 | -9.1 | -9.0997 | 1.1193 | 8.7197e-06
2016-02-12 10:00 | 0.03 | 0.026667 | 0.0033333 | 0 | -14.0261 | -17.8399 | 91.5957 | -1.5957 | -17.2979 | 35.648 | 0 | 0.02 | 0.8 | 1 | 0.006 | 0.026 | -9 | -8.9992 | 1.119 | 2.3857e-05
2016-02-12 11:00 | 0.05 | 0.043333 | 0.0066667 | 0 | -14.0124 | -2.8402 | 90.9945 | -0.99446 | -2.756 | 31.1057 | 0 | 0.0325 | 0.8 | 1 | 0.01 | 0.0425 | -8.6 | -8.5987 | 1.1176 | 3.8948e-05
2016-02-12 12:00 | 0.07 | 0.06 | 0.01 | 0 | -13.9987 | 12.1595 | 91.2467 | -1.2467 | 11.7959 | 33.2112 | 0 | 0.045 | 0.8 | 1 | 0.014 | 0.059 | -8.5 | -8.4982 | 1.1172 | 5.4052e-05
2016-02-12 13:00 | 0.046667 | 0.04 | 0.0066667 | 0 | -13.985 | 27.1592 | 92.3347 | -2.3347 | 26.3148 | 40.9512 | 0 | 0.03 | 0.8 | 1 | 0.0093333 | 0.039333 | -7.9 | -7.8988 | 1.1151 | 3.5967e-05
2016-02-12 14:00 | 0.023333 | 0.02 | 0.0033333 | 0 | -13.9712 | 42.159 | 94.1856 | -4.1856 | 40.7739 | 51.8595 | 0 | 0.015 | 0.8 | 1 | 0.0046667 | 0.019667 | -7.7 | -7.6994 | 1.1144 | 1.7972e-05
2016-02-12 15:00 | 0 | 0 | 0 | 0 | -13.9575 | 57.1587 | 96.6785 | -6.6785 | 55.179 | 64.3414 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.4 | -7.4 | 1.1134 | 0
2016-02-12 16:00 | 0 | 0 | 0 | 0 | -13.9438 | 72.1584 | 99.6543 | -9.6543 | 69.5749 | 77.6375 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.2 | -7.2 | 1.1127 | 0
2016-02-12 17:00 | 0 | 0 | 0 | 0 | -13.93 | 87.1582 | 102.9254 | -12.9254 | 84.0419 | 91.3881 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.8 | -6.8 | 1.1113 | 0
2016-02-12 18:00 | 0 | 0 | 0 | 0 | -13.9163 | 102.1579 | 106.2847 | -16.2847 | 98.6836 | 105.4092 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.8 | -6.8 | 1.1113 | 0
2016-02-12 19:00 | 0 | 0 | 0 | 0 | -13.9025 | 117.1577 | 109.5118 | -19.5118 | 113.6075 | 119.5972 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-02-12 20:00 | 0 | 0 | 0 | 0 | -13.8887 | 132.1574 | 112.3826 | -22.3826 | 128.8982 | 133.8868 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-02-12 21:00 | 0 | 0 | 0 | 0 | -13.875 | 147.1572 | 114.6812 | -24.6812 | 144.5884 | 148.2252 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.8 | -6.8 | 1.1113 | 0
2016-02-12 22:00 | 0 | 0 | 0 | 0 | -13.8612 | 162.157 | 116.2199 | -26.2199 | 160.6336 | 162.5281 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-02-12 23:00 | 0 | 0 | 0 | 0 | -13.8474 | 177.1568 | 116.8634 | -26.8634 | 176.9052 | 175.8478 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.5 | -6.5 | 1.1102 | 0
2016-02-13 | 0 | 0 | 0 | 0 | -13.8336 | -167.8435 | 116.552 | -26.552 | -166.7863 | 167.8716 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.5 | -6.5 | 1.1102 | 0
2016-02-13 01:00 | 0 | 0 | 0 | 0 | -13.8198 | -152.8437 | 115.3131 | -25.3131 | -150.6409 | 153.651 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.4 | -6.4 | 1.1099 | 0
2016-02-13 02:00 | 0 | 0 | 0 | 0 | -13.806 | -137.8439 | 113.2559 | -23.2559 | -134.8138 | 139.3062 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.3 | -6.3 | 1.1096 | 0
2016-02-13 03:00 | 0 | 0 | 0 | 0 | -13.7922 | -122.8441 | 110.5512 | -20.5512 | -119.3805 | 124.9849 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.4 | -6.4 | 1.1099 | 0
2016-02-13 04:00 | 0 | 0 | 0 | 0 | -13.7784 | -107.8443 | 107.4065 | -17.4065 | -104.3339 | 110.742 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.2 | -6.2 | 1.1092 | 0
2016-02-13 05:00 | 0 | 0 | 0 | 0 | -13.7646 | -92.8445 | 104.0444 | -14.0444 | -89.6043 | 96.6344 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.3 | -6.3 | 1.1096 | 0
2016-02-13 06:00 | 0 | 0 | 0 | 0 | -13.7507 | -77.8446 | 100.6874 | -10.6874 | -75.0884 | 82.7463 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.1 | -6.1 | 1.1088 | 0
2016-02-13 07:00 | 0.01 | 0.01 | 0 | 0 | -13.7369 | -62.8448 | 97.5484 | -7.5484 | -60.6777 | 69.2216 | 0 | 0.0075 | 0.8 | 1 | 0.002 | 0.0095 | -6 | -5.9997 | 1.1085 | 8.6352e-06
2016-02-13 08:00 | 0.02 | 0.02 | 0 | 0 | -13.723 | -47.845 | 94.8234 | -4.8234 | -46.2803 | 56.3323 | 0 | 0.015 | 0.8 | 1 | 0.004 | 0.019 | -5.9 | -5.8994 | 1.1081 | 1.7265e-05
2016-02-13 09:00 | 0.03 | 0.03 | 0 | 0 | -13.7092 | -32.8451 | 92.6836 | -2.6836 | -31.8365 | 44.6412 | 0 | 0.0225 | 0.8 | 1 | 0.006 | 0.0285 | -5.8 | -5.7991 | 1.1078 | 2.5889e-05
2016-02-13 10:00 | 0.056667 | 0.056667 | 0 | 0 | -13.6953 | -17.8453 | 91.2661 | -1.2661 | -17.326 | 35.3651 | 0 | 0.0425 | 0.8 | 1 | 0.011333 | 0.053833 | -6.4 | -6.3983 | 1.1099 | 4.8994e-05
2016-02-13 11:00 | 0.083333 | 0.083333 | 0 | 0 | -13.6815 | -2.8455 | 90.6636 | -0.66362 | -2.7648 | 30.7767 | 0 | 0.0625 | 0.8 | 1 | 0.016667 | 0.079167 | -5.9 | -5.8975 | 1.1081 | 7.1937e-05
2016-02-13 12:00 | 0.11 | 0.11 | 0 | 0 | -13.6676 | 12.1544 | 90.9157 | -0.91574 | 11.8067 | 32.9017 | 0 | 0.0825 | 0.8 | 1 | 0.022 | 0.1045 | -5.8 | -5.7967 | 1.1078 | 9.4926e-05
2016-02-13 13:00 | 0.073333 | 0.073333 | 0 | 0 | -13.6537 | 27.1542 | 92.0047 | -2.0047 | 26.3441 | 40.7014 | 0 | 0.055 | 0.8 | 1 | 0.014667 | 0.069667 | -5.8 | -5.7978 | 1.1078 | 6.3284e-05
2016-02-13 14:00 | 0.036667 | 0.036667 | 0 | 0 | -13.6398 | 42.1541 | 93.8573 | -3.8573 | 40.8196 | 51.6647 | 0 | 0.0275 | 0.8 | 1 | 0.0073333 | 0.034833 | -4.8 | -4.7989 | 1.1043 | 3.1542e-05
2016-02-13 15:00 | 0 | 0 | 0 | 0 | -13.626 | 57.154 | 96.3522 | -6.3522 | 55.2381 | 64.1875 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-02-13 16:00 | 0 | 0 | 0 | 0 | -13.6121 | 72.1538 | 99.3295 | -9.3295 | 69.6437 | 77.5133 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-02-13 17:00 | 0 | 0 | 0 | 0 | -13.5982 | 87.1537 | 102.6015 | -12.6015 | 84.1161 | 91.2861 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-02-13 18:00 | 0 | 0 | 0 | 0 | -13.5842 | 102.1536 | 105.9605 | -15.9605 | 98.7587 | 105.324 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.0991 | 0
2016-02-13 19:00 | 0 | 0 | 0 | 0 | -13.5703 | 117.1535 | 109.1864 | -19.1864 | 113.6781 | 119.5246 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2 | -2 | 1.0945 | 0
2016-02-13 20:00 | 0 | 0 | 0 | 0 | -13.5564 | 132.1534 | 112.055 | -22.055 | 128.9588 | 133.8224 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-02-13 21:00 | 0 | 0 | 0 | 0 | -13.5425 | 147.1533 | 114.3512 | -24.3512 | 144.6334 | 148.1627 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-02-13 22:00 | 0 | 0 | 0 | 0 | -13.5285 | 162.1532 | 115.888 | -25.888 | 160.658 | 162.4494 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-02-13 23:00 | 0 | 0 | 0 | 0 | -13.5146 | 177.1531 | 116.5306 | -26.5306 | 176.9059 | 175.5888 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-02-14 | 0 | 0 | 0 | 0 | -13.5007 | -167.847 | 116.2197 | -26.2197 | -166.8098 | 167.776 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-02-14 01:00 | 0 | 0 | 0 | 0 | -13.4867 | -152.8471 | 114.9825 | -24.9825 | -150.6863 | 153.5922 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-02-14 02:00 | 0 | 0 | 0 | 0 | -13.4727 | -137.8471 | 112.9277 | -22.9277 | -134.8768 | 139.2499 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-02-14 03:00 | 0 | 0 | 0 | 0 | -13.4588 | -122.8472 | 110.2252 | -20.2252 | -119.4556 | 124.9222 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-02-14 04:00 | 0 | 0 | 0 | 0 | -13.4448 | -107.8473 | 107.0821 | -17.0821 | -104.4154 | 110.6683 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-02-14 05:00 | 0 | 0 | 0 | 0 | -13.4308 | -92.8473 | 103.7204 | -13.7204 | -89.6868 | 96.5456 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-02-14 06:00 | 0 | 0 | 0 | 0 | -13.4168 | -77.8474 | 100.3626 | -10.3626 | -75.1672 | 82.6374 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-02-14 07:00 | 0.04 | 0.04 | 0 | 0 | -13.4028 | -62.8474 | 97.2218 | -7.2218 | -60.7483 | 69.0859 | 0 | 0.03 | 0.8 | 1 | 0.008 | 0.038 | -0.8 | -0.79881 | 1.0903 | 3.3974e-05
2016-02-14 08:00 | 0.08 | 0.08 | 0 | 0 | -13.3888 | -47.8475 | 94.4943 | -4.4943 | -46.3389 | 56.1598 | 0 | 0.06 | 0.8 | 1 | 0.016 | 0.076 | -1.2 | -1.1976 | 1.0917 | 6.8034e-05
2016-02-14 09:00 | 0.12 | 0.12 | 0 | 0 | -13.3748 | -32.8475 | 92.352 | -2.352 | -31.8798 | 44.4179 | 0 | 0.09 | 0.8 | 1 | 0.024 | 0.114 | -1 | -0.99644 | 1.091 | 0.00010199
2016-02-14 10:00 | 0.42667 | 0.40333 | 0.023333 | 0 | -13.3608 | -17.8475 | 90.9325 | -0.93252 | -17.3513 | 35.0781 | 0 | 0.3025 | 0.8 | 1 | 0.085333 | 0.38783 | -1.2 | -1.1879 | 1.0917 | 0.00034717
2016-02-14 11:00 | 0.73333 | 0.68667 | 0.046667 | 0 | -13.3468 | -2.8475 | 90.329 | -0.32899 | -2.7706 | 30.4437 | 0 | 0.515 | 0.8 | 1 | 0.14667 | 0.66167 | -0.9 | -0.87932 | 1.0906 | 0.00059171
2016-02-14 12:00 | 1.04 | 0.97 | 0.07 | 0 | -13.3328 | 12.1524 | 90.5812 | -0.5812 | 11.8207 | 32.5902 | 0 | 0.7275 | 0.8 | 1 | 0.208 | 0.9355 | -1 | -0.97077 | 1.0909 | 0.00083684
2016-02-14 13:00 | 0.69333 | 0.64667 | 0.046667 | 0 | -13.3187 | 27.1524 | 91.6713 | -1.6713 | 26.3769 | 40.4519 | 0 | 0.485 | 0.8 | 1 | 0.13867 | 0.62367 | -0.5 | -0.48051 | 1.0892 | 0.00055701
2016-02-14 14:00 | 0.34667 | 0.32333 | 0.023333 | 0 | -13.3047 | 42.1524 | 93.5258 | -3.5258 | 40.869 | 51.4713 | 0 | 0.2425 | 0.8 | 1 | 0.069333 | 0.31183 | -0.4 | -0.39026 | 1.0889 | 0.00027843
2016-02-14 15:00 | 0 | 0 | 0 | 0 | -13.2907 | 57.1524 | 96.0227 | -6.0227 | 55.3009 | 64.0353 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-02-14 16:00 | 0 | 0 | 0 | 0 | -13.2766 | 72.1524 | 99.0018 | -9.0018 | 69.7162 | 77.3911 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-02-14 17:00 | 0 | 0 | 0 | 0 | -13.2626 | 87.1524 | 102.2747 | -12.2747 | 84.1942 | 91.1859 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-02-14 18:00 | 0 | 0 | 0 | 0 | -13.2485 | 102.1525 | 105.6335 | -15.6335 | 98.8375 | 105.2404 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-02-14 19:00 | 0 | 0 | 0 | 0 | -13.2344 | 117.1525 | 108.8579 | -18.8579 | 113.7525 | 119.4531 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-02-14 20:00 | 0 | 0 | 0 | 0 | -13.2204 | 132.1525 | 111.7243 | -21.7243 | 129.0232 | 133.7586 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-02-14 21:00 | 0 | 0 | 0 | 0 | -13.2063 | 147.1525 | 114.018 | -24.018 | 144.682 | 148.0996 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-02-14 22:00 | 0 | 0 | 0 | 0 | -13.1922 | 162.1526 | 115.5526 | -25.5526 | 160.686 | 162.367 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-02-14 23:00 | 0 | 0 | 0 | 0 | -13.1781 | 177.1526 | 116.1941 | -26.1941 | 176.9101 | 175.3193 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-02-15 | 0 | 0 | 0 | 0 | -13.164 | -167.8473 | 115.8835 | -25.8835 | -166.83 | 167.6682 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.1 | 0.1 | 1.0872 | 0
2016-02-15 01:00 | 0 | 0 | 0 | 0 | -13.1499 | -152.8473 | 114.6479 | -24.6479 | -150.7287 | 153.5259 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-02-15 02:00 | 0 | 0 | 0 | 0 | -13.1358 | -137.8472 | 112.5953 | -22.5953 | -134.9368 | 139.1876 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-02-15 03:00 | 0 | 0 | 0 | 0 | -13.1217 | -122.8472 | 109.895 | -19.895 | -119.5279 | 124.8545 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-02-15 04:00 | 0 | 0 | 0 | 0 | -13.1075 | -107.8471 | 106.7534 | -16.7534 | -104.4943 | 110.59 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-02-15 05:00 | 0 | 0 | 0 | 0 | -13.0934 | -92.847 | 103.3921 | -13.3921 | -89.767 | 96.4525 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-02-15 06:00 | 0 | 0 | 0 | 0 | -13.0793 | -77.8469 | 100.0335 | -10.0335 | -75.2436 | 82.5246 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-02-15 07:00 | 0.17333 | 0.15667 | 0.016667 | 0 | -13.0651 | -62.8468 | 96.8909 | -6.8909 | -60.8166 | 68.9465 | 0 | 0.1175 | 0.8 | 1 | 0.034667 | 0.15217 | -0.8 | -0.79524 | 1.0903 | 0.00013604
2016-02-15 08:00 | 0.34667 | 0.31333 | 0.033333 | 0 | -13.051 | -47.8468 | 94.1611 | -4.1611 | -46.395 | 55.9838 | 0 | 0.235 | 0.8 | 1 | 0.069333 | 0.30433 | -0.4 | -0.39049 | 1.0889 | 0.00027173
2016-02-15 09:00 | 0.52 | 0.47 | 0.05 | 0 | -13.0368 | -32.8467 | 92.0164 | -2.0164 | -31.9204 | 44.191 | 0 | 0.3525 | 0.8 | 1 | 0.104 | 0.4565 | -0.2 | -0.18573 | 1.0882 | 0.00040733
2016-02-15 10:00 | 1.1267 | 0.94333 | 0.18333 | 0 | -13.0227 | -17.8466 | 90.5951 | -0.5951 | -17.3737 | 34.7871 | 0 | 0.7075 | 0.8 | 1 | 0.22533 | 0.93283 | -0.1 | -0.070849 | 1.0877 | 0.00083204
2016-02-15 11:00 | 1.7333 | 1.4167 | 0.31667 | 0 | -13.0085 | -2.8464 | 89.9907 | 0.0093144 | -2.7733 | 30.1067 | 0 | 1.0625 | 0.8 | 1 | 0.34667 | 1.4092 | -0.1 | -0.055964 | 1.0877 | 0.0012569
2016-02-15 12:00 | 2.34 | 1.89 | 0.45 | 0 | -12.9943 | 12.1537 | 90.2432 | -0.24317 | 11.838 | 32.277 | 0 | 1.4175 | 0.8 | 1 | 0.468 | 1.8855 | -0.1 | -0.041078 | 1.0876 | 0.0016816
2016-02-15 13:00 | 1.56 | 1.26 | 0.3 | 0 | -12.9801 | 27.1538 | 91.3346 | -1.3346 | 26.4131 | 40.2028 | 0 | 0.945 | 0.8 | 1 | 0.312 | 1.257 | -0.3 | -0.26072 | 1.0884 | 0.0011219
2016-02-15 14:00 | 0.78 | 0.63 | 0.15 | 0 | -12.9659 | 42.1539 | 93.1912 | -3.1912 | 40.9218 | 51.2794 | 0 | 0.4725 | 0.8 | 1 | 0.156 | 0.6285 | 0.1 | 0.11964 | 1.0871 | 0.00056025
2016-02-15 15:00 | 0 | 0 | 0 | 0 | -12.9518 | 57.154 | 95.6903 | -5.6903 | 55.3674 | 63.8851 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.1 | 0.1 | 1.0872 | 0
2016-02-15 16:00 | 0 | 0 | 0 | 0 | -12.9376 | 72.1542 | 98.6712 | -8.6712 | 69.7924 | 77.2708 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-02-15 17:00 | 0 | 0 | 0 | 0 | -12.9234 | 87.1543 | 101.9451 | -11.9451 | 84.2759 | 91.0876 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.1 | 0.1 | 1.0872 | 0
2016-02-15 18:00 | 0 | 0 | 0 | 0 | -12.9091 | 102.1545 | 105.3035 | -15.3035 | 98.92 | 105.1583 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-02-15 19:00 | 0 | 0 | 0 | 0 | -12.8949 | 117.1546 | 108.5266 | -18.5266 | 113.8306 | 119.3828 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-02-15 20:00 | 0 | 0 | 0 | 0 | -12.8807 | 132.1548 | 111.3906 | -21.3906 | 129.0911 | 133.6953 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-02-15 21:00 | 0 | 0 | 0 | 0 | -12.8665 | 147.1549 | 113.6815 | -23.6815 | 144.7342 | 148.0357 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-02-15 22:00 | 0 | 0 | 0 | 0 | -12.8522 | 162.1551 | 115.2138 | -25.2138 | 160.7175 | 162.2807 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-02-15 23:00 | 0 | 0 | 0 | 0 | -12.838 | 177.1553 | 115.8541 | -25.8541 | 176.9177 | 175.0403 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-02-16 | 0 | 0 | 0 | 0 | -12.8238 | -167.8445 | 115.5436 | -25.5436 | -166.8469 | 167.5482 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-02-16 01:00 | 0 | 0 | 0 | 0 | -12.8095 | -152.8444 | 114.3094 | -24.3094 | -150.7678 | 153.4521 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-02-16 02:00 | 0 | 0 | 0 | 0 | -12.7952 | -137.8442 | 112.2589 | -22.2589 | -134.994 | 139.1195 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-02-16 03:00 | 0 | 0 | 0 | 0 | -12.781 | -122.844 | 109.5607 | -19.5607 | -119.5975 | 124.7817 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-02-16 04:00 | 0 | 0 | 0 | 0 | -12.7667 | -107.8438 | 106.4205 | -16.4205 | -104.5707 | 110.5072 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-02-16 05:00 | 0 | 0 | 0 | 0 | -12.7524 | -92.8436 | 103.0596 | -13.0596 | -89.8446 | 96.3554 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.9 | -3.9 | 1.1012 | 0
2016-02-16 06:00 | 0 | 0 | 0 | 0 | -12.7382 | -77.8434 | 99.7003 | -9.7003 | -75.3176 | 82.408 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-02-16 07:00 | 0.39667 | 0.33 | 0.066667 | 0 | -12.7239 | -62.8431 | 96.556 | -6.556 | -60.8824 | 68.8035 | 0 | 0.2475 | 0.8 | 1 | 0.079333 | 0.32683 | -5.6 | -5.5898 | 1.1071 | 0.0002967
2016-02-16 08:00 | 0.79333 | 0.66 | 0.13333 | 0 | -12.7096 | -47.8429 | 93.8239 | -3.8239 | -46.4487 | 55.8043 | 0 | 0.495 | 0.8 | 1 | 0.15867 | 0.65367 | -4 | -3.9796 | 1.1014 | 0.00059037
2016-02-16 09:00 | 1.19 | 0.99 | 0.2 | 0 | -12.6953 | -32.8427 | 91.677 | -1.677 | -31.9583 | 43.9606 | 0 | 0.7425 | 0.8 | 1 | 0.238 | 0.9805 | -5 | -4.9694 | 1.1049 | 0.00088834
2016-02-16 10:00 | 2.0967 | 1.7433 | 0.35333 | 0 | -12.681 | -17.8425 | 90.254 | -0.25395 | -17.3933 | 34.4923 | 0 | 1.3075 | 0.8 | 1 | 0.41933 | 1.7268 | -5.3 | -5.246 | 1.1059 | 0.0015659
2016-02-16 11:00 | 3.0033 | 2.4967 | 0.50667 | 0 | -12.6667 | -2.8422 | 89.6488 | 0.35117 | -2.773 | 29.7661 | 0 | 1.8725 | 0.8 | 1 | 0.60067 | 2.4732 | -5.8 | -5.7227 | 1.1075 | 0.0022461
2016-02-16 12:00 | 3.91 | 3.25 | 0.66 | 0 | -12.6523 | 12.158 | 89.9018 | 0.098217 | 11.8585 | 31.9621 | 0 | 2.4375 | 0.8 | 1 | 0.782 | 3.2195 | -4.8 | -4.6994 | 1.1039 | 0.0029144
2016-02-16 13:00 | 2.6067 | 2.1667 | 0.44 | 0 | -12.638 | 27.1583 | 90.9948 | -0.99479 | 26.4527 | 39.9543 | 0 | 1.625 | 0.8 | 1 | 0.52133 | 2.1463 | -5 | -4.9329 | 1.1048 | 0.0019444
2016-02-16 14:00 | 1.3033 | 1.0833 | 0.22 | 0 | -12.6237 | 42.1585 | 92.8536 | -2.8536 | 40.9783 | 51.0891 | 0 | 0.8125 | 0.8 | 1 | 0.26067 | 1.0732 | -5.9 | -5.8665 | 1.108 | 0.00097507
2016-02-16 15:00 | 0 | 0 | 0 | 0 | -12.6093 | 57.1588 | 95.3551 | -5.3551 | 55.4374 | 63.7369 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-02-16 16:00 | 0 | 0 | 0 | 0 | -12.595 | 72.1591 | 98.3379 | -8.3379 | 69.8723 | 77.1525 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.8 | -5.8 | 1.1078 | 0
2016-02-16 17:00 | 0 | 0 | 0 | 0 | -12.5807 | 87.1593 | 101.6127 | -11.6127 | 84.3613 | 90.9911 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.3 | -5.3 | 1.106 | 0
2016-02-16 18:00 | 0 | 0 | 0 | 0 | -12.5663 | 102.1596 | 104.9709 | -14.9709 | 99.0062 | 105.0779 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-02-16 19:00 | 0 | 0 | 0 | 0 | -12.5519 | 117.1599 | 108.1924 | -18.1924 | 113.9123 | 119.3137 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-02-16 20:00 | 0 | 0 | 0 | 0 | -12.5376 | 132.1602 | 111.054 | -21.054 | 129.1627 | 133.6324 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3 | -3 | 1.098 | 0
2016-02-16 21:00 | 0 | 0 | 0 | 0 | -12.5232 | 147.1605 | 113.3421 | -23.3421 | 144.79 | 147.9709 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.0991 | 0
2016-02-16 22:00 | 0 | 0 | 0 | 0 | -12.5088 | 162.1608 | 114.8718 | -24.8718 | 160.7525 | 162.1905 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-02-16 23:00 | 0 | 0 | 0 | 0 | -12.4945 | 177.1611 | 115.5106 | -25.5106 | 176.9287 | 174.7527 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-02-17 | 0 | 0 | 0 | 0 | -12.4801 | -167.8386 | 115.2001 | -25.2001 | -166.8605 | 167.416 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-02-17 01:00 | 0 | 0 | 0 | 0 | -12.4657 | -152.8383 | 113.9671 | -23.9671 | -150.8039 | 153.3706 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.6 | -3.6 | 1.1001 | 0
2016-02-17 02:00 | 0 | 0 | 0 | 0 | -12.4513 | -137.838 | 111.9186 | -21.9186 | -135.0482 | 139.0454 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-02-17 03:00 | 0 | 0 | 0 | 0 | -12.4369 | -122.8377 | 109.2224 | -19.2224 | -119.6644 | 124.7038 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.1033 | 0
2016-02-17 04:00 | 0 | 0 | 0 | 0 | -12.4225 | -107.8373 | 106.0836 | -16.0836 | -104.6445 | 110.42 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.7 | -5.7 | 1.1075 | 0
2016-02-17 05:00 | 0 | 0 | 0 | 0 | -12.408 | -92.837 | 102.723 | -12.723 | -89.9199 | 96.2541 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.1033 | 0
2016-02-17 06:00 | 0 | 0 | 0 | 0 | -12.3936 | -77.8367 | 99.363 | -9.363 | -75.3893 | 82.2876 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.0991 | 0
2016-02-17 07:00 | 0.46333 | 0.46333 | 0 | 0 | -12.3792 | -62.8363 | 96.217 | -6.217 | -60.9459 | 68.6569 | 0 | 0.3475 | 0.8 | 1 | 0.092667 | 0.44017 | -2.6 | -2.5862 | 1.0966 | 0.00039579
2016-02-17 08:00 | 0.92667 | 0.92667 | 0 | 0 | -12.3648 | -47.836 | 93.4828 | -3.4828 | -46.4998 | 55.6214 | 0 | 0.695 | 0.8 | 1 | 0.18533 | 0.88033 | -2 | -1.9725 | 1.0944 | 0.00079002
2016-02-17 09:00 | 1.39 | 1.39 | 0 | 0 | -12.3503 | -32.8356 | 91.3338 | -1.3338 | -31.9937 | 43.7268 | 0 | 1.0425 | 0.8 | 1 | 0.278 | 1.3205 | -2.1 | -2.0587 | 1.0947 | 0.0011854
2016-02-17 10:00 | 2.32 | 2.32 | 0 | 0 | -12.3359 | -17.8352 | 89.9092 | 0.090807 | -17.4102 | 34.1938 | 0 | 1.74 | 0.8 | 1 | 0.464 | 2.204 | -2 | -1.9311 | 1.0943 | 0.0019776
2016-02-17 11:00 | 3.25 | 3.25 | 0 | 0 | -12.3214 | -2.8349 | 89.3035 | 0.69647 | -2.7697 | 29.4217 | 0 | 2.4375 | 0.8 | 1 | 0.65 | 3.0875 | -2 | -1.9035 | 1.0942 | 0.0027701
2016-02-17 12:00 | 4.18 | 4.18 | 0 | 0 | -12.307 | 12.1655 | 89.5571 | 0.44285 | 11.8822 | 31.6457 | 0 | 3.135 | 0.8 | 1 | 0.836 | 3.971 | -1.7 | -1.5759 | 1.093 | 0.0035591
2016-02-17 13:00 | 2.7867 | 2.7867 | 0 | 0 | -12.2925 | 27.1659 | 90.6519 | -0.65188 | 26.4956 | 39.7065 | 0 | 2.09 | 0.8 | 1 | 0.55733 | 2.6473 | -1.5 | -1.4173 | 1.0925 | 0.0023715
2016-02-17 14:00 | 1.3933 | 1.3933 | 0 | 0 | -12.278 | 42.1663 | 92.513 | -2.513 | 41.0382 | 50.9006 | 0 | 1.045 | 0.8 | 1 | 0.27867 | 1.3237 | -1.6 | -1.5586 | 1.093 | 0.0011863
2016-02-17 15:00 | 0 | 0 | 0 | 0 | -12.2636 | 57.1666 | 95.017 | -5.017 | 55.511 | 63.5907 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-02-17 16:00 | 0 | 0 | 0 | 0 | -12.2491 | 72.167 | 98.0019 | -8.0019 | 69.9558 | 77.0363 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.2 | -2.2 | 1.0952 | 0
2016-02-17 17:00 | 0 | 0 | 0 | 0 | -12.2346 | 87.1674 | 101.2777 | -11.2777 | 84.4503 | 90.8965 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-02-17 18:00 | 0 | 0 | 0 | 0 | -12.2201 | 102.1678 | 104.6357 | -14.6357 | 99.096 | 104.999 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-02-17 19:00 | 0 | 0 | 0 | 0 | -12.2056 | 117.1683 | 107.8556 | -17.8556 | 113.9975 | 119.2456 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-02-17 20:00 | 0 | 0 | 0 | 0 | -12.1911 | 132.1687 | 110.7146 | -20.7146 | 129.2378 | 133.57 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-02-17 21:00 | 0 | 0 | 0 | 0 | -12.1766 | 147.1691 | 112.9996 | -22.9996 | 144.8492 | 147.9053 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-02-17 22:00 | 0 | 0 | 0 | 0 | -12.1621 | 162.1695 | 114.5267 | -24.5267 | 160.7909 | 162.0963 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-02-17 23:00 | 0 | 0 | 0 | 0 | -12.1476 | 177.17 | 115.1639 | -25.1639 | 176.943 | 174.4573 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-02-18 | 0 | 0 | 0 | 0 | -12.133 | -167.8296 | 114.8531 | -24.8531 | -166.8708 | 167.272 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-02-18 01:00 | 0 | 0 | 0 | 0 | -12.1185 | -152.8292 | 113.6211 | -23.6211 | -150.8369 | 153.2815 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-02-18 02:00 | 0 | 0 | 0 | 0 | -12.104 | -137.8287 | 111.5744 | -21.5744 | -135.0995 | 138.9654 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-02-18 03:00 | 0 | 0 | 0 | 0 | -12.0894 | -122.8283 | 108.8802 | -18.8802 | -119.7286 | 124.6209 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-02-18 04:00 | 0 | 0 | 0 | 0 | -12.0749 | -107.8278 | 105.7427 | -15.7427 | -104.7157 | 110.3282 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-02-18 05:00 | 0 | 0 | 0 | 0 | -12.0603 | -92.8273 | 102.3825 | -12.3825 | -89.9927 | 96.1488 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-02-18 06:00 | 0 | 0 | 0 | 0 | -12.0458 | -77.8269 | 99.0218 | -9.0218 | -75.4585 | 82.1635 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-02-18 07:00 | 0.96667 | 0.78 | 0.18667 | 0 | -12.0312 | -62.8264 | 95.8743 | -5.8743 | -61.007 | 68.5069 | 0 | 0.585 | 0.8 | 1 | 0.19333 | 0.77833 | -1.5 | -1.4757 | 1.0927 | 0.00069738
2016-02-18 08:00 | 1.9333 | 1.56 | 0.37333 | 0 | -12.0166 | -47.8259 | 93.138 | -3.138 | -46.5485 | 55.4353 | 0 | 1.17 | 0.8 | 1 | 0.38667 | 1.5567 | -1.6 | -1.5514 | 1.0929 | 0.0013951
2016-02-18 09:00 | 2.9 | 2.34 | 0.56 | 0 | -12.0021 | -32.8254 | 90.9869 | -0.98692 | -32.0264 | 43.4897 | 0 | 1.755 | 0.8 | 1 | 0.58 | 2.335 | -0.6 | -0.52703 | 1.0893 | 0.0020858
2016-02-18 10:00 | 4.3133 | 3.7067 | 0.60667 | 0 | -11.9875 | -17.8249 | 89.5609 | 0.43905 | -17.4242 | 33.8916 | 0 | 2.78 | 0.8 | 1 | 0.86267 | 3.6427 | -0.6 | -0.48617 | 1.0892 | 0.0032534
2016-02-18 11:00 | 5.7267 | 5.0733 | 0.65333 | 0 | -11.9729 | -2.8244 | 88.9549 | 1.0451 | -2.7634 | 29.0739 | 0 | 3.805 | 0.8 | 1 | 1.1453 | 4.9503 | 0.1 | 0.2547 | 1.0866 | 0.0044108
2016-02-18 12:00 | 7.14 | 6.44 | 0.7 | 0 | -11.9583 | 12.1761 | 89.2094 | 0.79062 | 11.909 | 31.3281 | 0 | 4.83 | 0.8 | 1 | 1.428 | 6.258 | -0.3 | -0.10444 | 1.0879 | 0.0055824
2016-02-18 13:00 | 4.76 | 4.2933 | 0.46667 | 0 | -11.9437 | 27.1766 | 90.306 | -0.30602 | 26.5419 | 39.4597 | 0 | 3.22 | 0.8 | 1 | 0.952 | 4.172 | 0 | 0.13037 | 1.087 | 0.0037188
2016-02-18 14:00 | 2.38 | 2.1467 | 0.23333 | 0 | -11.9291 | 42.1771 | 92.1698 | -2.1698 | 41.1015 | 50.714 | 0 | 1.61 | 0.8 | 1 | 0.476 | 2.086 | 0.1 | 0.16519 | 1.0869 | 0.0018592
2016-02-18 15:00 | 0 | 0 | 0 | 0 | -11.9145 | 57.1776 | 94.6764 | -4.6764 | 55.5882 | 63.4467 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-02-18 16:00 | 0 | 0 | 0 | 0 | -11.8999 | 72.1781 | 97.6633 | -7.6633 | 70.0428 | 76.9222 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.4 | 0.4 | 1.0861 | 0
2016-02-18 17:00 | 0 | 0 | 0 | 0 | -11.8853 | 87.1786 | 100.9402 | -10.9402 | 84.5429 | 90.8039 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-02-18 18:00 | 0 | 0 | 0 | 0 | -11.8706 | 102.1792 | 104.2979 | -14.2979 | 99.1893 | 104.9217 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-02-18 19:00 | 0 | 0 | 0 | 0 | -11.856 | 117.1797 | 107.5162 | -17.5162 | 114.0863 | 119.1787 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-02-18 20:00 | 0 | 0 | 0 | 0 | -11.8414 | 132.1803 | 110.3725 | -20.3725 | 129.3164 | 133.5078 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-02-18 21:00 | 0 | 0 | 0 | 0 | -11.8267 | 147.1808 | 112.6544 | -22.6544 | 144.9119 | 147.8386 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.4 | 1.4 | 1.0826 | 0
2016-02-18 22:00 | 0 | 0 | 0 | 0 | -11.8121 | 162.1814 | 114.1786 | -24.1786 | 160.8326 | 161.9979 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.5 | 1.5 | 1.0822 | 0
2016-02-18 23:00 | 0 | 0 | 0 | 0 | -11.7974 | 177.1819 | 114.8139 | -24.8139 | 176.9607 | 174.1548 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-02-19 | 0 | 0 | 0 | 0 | -11.7828 | -167.8175 | 114.5027 | -24.5027 | -166.878 | 167.1162 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-02-19 01:00 | 0 | 0 | 0 | 0 | -11.7681 | -152.817 | 113.2716 | -23.2716 | -150.8668 | 153.1848 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-02-19 02:00 | 0 | 0 | 0 | 0 | -11.7535 | -137.8164 | 111.2266 | -21.2266 | -135.148 | 138.8794 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-02-19 03:00 | 0 | 0 | 0 | 0 | -11.7388 | -122.8158 | 108.5342 | -18.5342 | -119.79 | 124.533 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3 | -3 | 1.098 | 0
2016-02-19 04:00 | 0 | 0 | 0 | 0 | -11.7241 | -107.8152 | 105.398 | -15.398 | -104.7844 | 110.2321 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-02-19 05:00 | 0 | 0 | 0 | 0 | -11.7094 | -92.8146 | 102.0382 | -12.0382 | -90.063 | 96.0395 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-02-19 06:00 | 0 | 0 | 0 | 0 | -11.6947 | -77.814 | 98.6768 | -8.6768 | -75.5254 | 82.0357 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.9 | -3.9 | 1.1012 | 0
2016-02-19 07:00 | 1.03 | 1.02 | 0.01 | 0 | -11.68 | -62.8134 | 95.5277 | -5.5277 | -61.0656 | 68.3536 | 0 | 0.765 | 0.8 | 1 | 0.206 | 0.971 | -4.7 | -4.6697 | 1.1038 | 0.0008789
2016-02-19 08:00 | 2.06 | 2.04 | 0.02 | 0 | -11.6653 | -47.8128 | 92.7895 | -2.7895 | -46.5947 | 55.246 | 0 | 1.53 | 0.8 | 1 | 0.412 | 1.942 | -2.3 | -2.2393 | 1.0953 | 0.0017443
2016-02-19 09:00 | 3.09 | 3.06 | 0.03 | 0 | -11.6506 | -32.8122 | 90.6365 | -0.63655 | -32.0565 | 43.2494 | 0 | 2.295 | 0.8 | 1 | 0.618 | 2.913 | -1.6 | -1.509 | 1.0928 | 0.0026103
2016-02-19 10:00 | 4.5533 | 4.4933 | 0.06 | 0 | -11.6359 | -17.8116 | 89.2093 | 0.79067 | -17.4354 | 33.5859 | 0 | 3.37 | 0.8 | 1 | 0.91067 | 4.2807 | -1.5 | -1.3662 | 1.0923 | 0.0038341
2016-02-19 11:00 | 6.0167 | 5.9267 | 0.09 | 0 | -11.6212 | -2.811 | 88.6031 | 1.3969 | -2.7541 | 28.7226 | 0 | 4.445 | 0.8 | 1 | 1.2033 | 5.6483 | -0.5 | -0.32349 | 1.0886 | 0.0050421
2016-02-19 12:00 | 7.48 | 7.36 | 0.12 | 0 | -11.6065 | 12.1897 | 88.8586 | 1.1414 | 11.9391 | 31.0093 | 0 | 5.52 | 0.8 | 1 | 1.496 | 7.016 | -1.3 | -1.0808 | 1.0913 | 0.0062783
2016-02-19 13:00 | 4.9867 | 4.9067 | 0.08 | 0 | -11.5918 | 27.1903 | 89.9573 | 0.042658 | 26.5916 | 39.2141 | 0 | 3.68 | 0.8 | 1 | 0.99733 | 4.6773 | -1.5 | -1.3538 | 1.0922 | 0.0041892
2016-02-19 14:00 | 2.4933 | 2.4533 | 0.04 | 0 | -11.577 | 42.1909 | 91.8238 | -1.8238 | 41.1683 | 50.5294 | 0 | 1.84 | 0.8 | 1 | 0.49867 | 2.3387 | -1.4 | -1.3269 | 1.0921 | 0.0020944
2016-02-19 15:00 | 0 | 0 | 0 | 0 | -11.5623 | 57.1916 | 94.3332 | -4.3332 | 55.6688 | 63.3049 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-02-19 16:00 | 0 | 0 | 0 | 0 | -11.5476 | 72.1922 | 97.3224 | -7.3224 | 70.1334 | 76.8102 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-02-19 17:00 | 0 | 0 | 0 | 0 | -11.5328 | 87.1929 | 100.6003 | -10.6003 | 84.639 | 90.7131 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-02-19 18:00 | 0 | 0 | 0 | 0 | -11.5181 | 102.1935 | 103.9578 | -13.9578 | 99.286 | 104.846 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-02-19 19:00 | 0 | 0 | 0 | 0 | -11.5033 | 117.1942 | 107.1743 | -17.1743 | 114.1785 | 119.1128 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-02-19 20:00 | 0 | 0 | 0 | 0 | -11.4885 | 132.1949 | 110.0278 | -20.0278 | 129.3983 | 133.446 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-02-19 21:00 | 0 | 0 | 0 | 0 | -11.4738 | 147.1955 | 112.3065 | -22.3065 | 144.9779 | 147.7709 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-02-19 22:00 | 0 | 0 | 0 | 0 | -11.459 | 162.1962 | 113.8276 | -23.8276 | 160.8777 | 161.8953 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-02-19 23:00 | 0 | 0 | 0 | 0 | -11.4442 | 177.1969 | 114.4609 | -24.4609 | 176.9815 | 173.8458 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-02-20 | 0 | 0 | 0 | 0 | -11.4294 | -167.8024 | 114.1491 | -24.1491 | -166.8821 | 166.949 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-02-20 01:00 | 0 | 0 | 0 | 0 | -11.4147 | -152.8017 | 112.9187 | -22.9187 | -150.8938 | 153.0805 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-02-20 02:00 | 0 | 0 | 0 | 0 | -11.3999 | -137.801 | 110.8753 | -20.8753 | -135.1935 | 138.7876 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-02-20 03:00 | 0 | 0 | 0 | 0 | -11.3851 | -122.8003 | 108.1845 | -18.1845 | -119.8488 | 124.4401 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-02-20 04:00 | 0 | 0 | 0 | 0 | -11.3703 | -107.7996 | 105.0496 | -15.0496 | -104.8506 | 110.1315 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-02-20 05:00 | 0 | 0 | 0 | 0 | -11.3555 | -92.7989 | 101.6902 | -11.6902 | -90.1309 | 95.9262 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-02-20 06:00 | 0 | 0 | 0 | 0 | -11.3406 | -77.7982 | 98.3281 | -8.3281 | -75.5898 | 81.9043 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-02-20 07:00 | 1.91 | 1.3767 | 0.53333 | 0 | -11.3258 | -62.7974 | 95.1776 | -5.1776 | -61.1219 | 68.197 | 0 | 1.0325 | 0.8 | 1 | 0.382 | 1.4145 | -1.4 | -1.3558 | 1.0922 | 0.0012669
2016-02-20 08:00 | 3.82 | 2.7533 | 1.0667 | 0 | -11.311 | -47.7967 | 92.4375 | -2.4375 | -46.6385 | 55.0536 | 0 | 2.065 | 0.8 | 1 | 0.764 | 2.829 | -1.4 | -1.3116 | 1.0921 | 0.0025334
2016-02-20 09:00 | 5.73 | 4.13 | 1.6 | 0 | -11.2962 | -32.796 | 90.2828 | -0.28278 | -32.084 | 43.0061 | 0 | 3.0975 | 0.8 | 1 | 1.146 | 4.2435 | -1.2 | -1.0674 | 1.0912 | 0.0037971
2016-02-20 10:00 | 8.2233 | 5.9267 | 2.2967 | 0 | -11.2813 | -17.7952 | 88.8545 | 1.1455 | -17.4438 | 33.2769 | 0 | 4.445 | 0.8 | 1 | 1.6447 | 6.0897 | -1.4 | -1.2097 | 1.0917 | 0.0054516
2016-02-20 11:00 | 10.7167 | 7.7233 | 2.9933 | 0 | -11.2665 | -2.7945 | 88.2482 | 1.7518 | -2.7419 | 28.368 | 0 | 5.7925 | 0.8 | 1 | 2.1433 | 7.9358 | -0.8 | -0.55201 | 1.0894 | 0.0070894
2016-02-20 12:00 | 13.21 | 9.52 | 3.69 | 0 | -11.2516 | 12.2063 | 88.5049 | 1.4951 | 11.9723 | 30.6896 | 0 | 7.14 | 0.8 | 1 | 2.642 | 9.782 | -1.2 | -0.89431 | 1.0906 | 0.0087482
2016-02-20 13:00 | 8.82 | 6.36 | 2.46 | 0 | -11.2368 | 27.207 | 89.6059 | 0.39405 | 26.6445 | 38.9696 | 0 | 4.77 | 0.8 | 1 | 1.764 | 6.534 | -1.7 | -1.4958 | 1.0927 | 0.0058547
2016-02-20 14:00 | 4.43 | 3.2 | 1.23 | 0 | -11.2219 | 42.2078 | 91.4753 | -1.4753 | 41.2385 | 50.3469 | 0 | 2.4 | 0.8 | 1 | 0.886 | 3.286 | -1.8 | -1.6973 | 1.0934 | 0.0029463
2016-02-20 15:00 | 0.04 | 0.04 | 0 | 0 | -11.2071 | 57.2086 | 93.9876 | -3.9876 | 55.7529 | 63.1654 | 0 | 0.03 | 0.8 | 1 | 0.008 | 0.038 | -1.5 | -1.4988 | 1.0927 | 3.405e-05
2016-02-20 16:00 | 0.026667 | 0.026667 | 0 | 0 | -11.1922 | 72.2093 | 96.9791 | -6.9791 | 70.2274 | 76.7005 | 0 | 0.02 | 0.8 | 1 | 0.0053333 | 0.025333 | -1.7 | -1.6992 | 1.0934 | 2.2715e-05
2016-02-20 17:00 | 0.013333 | 0.013333 | 0 | 0 | -11.1773 | 87.2101 | 100.2582 | -10.2582 | 84.7385 | 90.6243 | 0 | 0.01 | 0.8 | 1 | 0.0026667 | 0.012667 | -2 | -1.9996 | 1.0945 | 1.1368e-05
2016-02-20 18:00 | 0 | 0 | 0 | 0 | -11.1625 | 102.2109 | 103.6153 | -13.6153 | 99.3862 | 104.7718 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-02-20 19:00 | 0 | 0 | 0 | 0 | -11.1476 | 117.2117 | 106.8301 | -16.8301 | 114.2741 | 119.048 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-02-20 20:00 | 0 | 0 | 0 | 0 | -11.1327 | 132.2125 | 109.6807 | -19.6807 | 129.4836 | 133.3844 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-02-20 21:00 | 0 | 0 | 0 | 0 | -11.1178 | 147.2133 | 111.9559 | -21.9559 | 145.0472 | 147.7019 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.8 | -3.8 | 1.1008 | 0
2016-02-20 22:00 | 0 | 0 | 0 | 0 | -11.1029 | 162.2141 | 113.4739 | -23.4739 | 160.926 | 161.7883 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.0991 | 0
2016-02-20 23:00 | 0 | 0 | 0 | 0 | -11.088 | 177.2149 | 114.1049 | -24.1049 | 177.0056 | 173.5307 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.6 | -3.6 | 1.1001 | 0
2016-02-21 | 0 | 0 | 0 | 0 | -11.0731 | -167.7843 | 113.7923 | -23.7923 | -166.883 | 166.7704 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-02-21 01:00 | 0 | 0 | 0 | 0 | -11.0582 | -152.7835 | 112.5625 | -22.5625 | -150.9177 | 152.9686 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.2 | -2.2 | 1.0952 | 0
2016-02-21 02:00 | 0 | 0 | 0 | 0 | -11.0433 | -137.7826 | 110.5205 | -20.5205 | -135.2363 | 138.6898 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.2 | -2.2 | 1.0952 | 0
2016-02-21 03:00 | 0 | 0 | 0 | 0 | -11.0284 | -122.7818 | 107.8314 | -17.8314 | -119.9049 | 124.3422 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-02-21 04:00 | 0 | 0 | 0 | 0 | -11.0134 | -107.781 | 104.6976 | -14.6976 | -104.9142 | 110.0266 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-02-21 05:00 | 0 | 0 | 0 | 0 | -10.9985 | -92.7801 | 101.3386 | -11.3386 | -90.1964 | 95.8091 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-02-21 06:00 | 0 | 0 | 0 | 0 | -10.9836 | -77.7793 | 97.9759 | -7.9759 | -75.6519 | 81.7694 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-02-21 07:00 | 1.6967 | 1.6967 | 0 | 0 | -10.9686 | -62.7785 | 94.824 | -4.824 | -61.1757 | 68.0371 | 0 | 1.2725 | 0.8 | 1 | 0.33933 | 1.6118 | 0.8 | 0.85037 | 1.0845 | 0.0014334
2016-02-21 08:00 | 3.3933 | 3.3933 | 0 | 0 | -10.9537 | -47.7776 | 92.0821 | -2.0821 | -46.6798 | 54.8583 | 0 | 2.545 | 0.8 | 1 | 0.67867 | 3.2237 | 1 | 1.1007 | 1.0836 | 0.0028645
2016-02-21 09:00 | 5.09 | 5.09 | 0 | 0 | -10.9387 | -32.7767 | 89.9257 | 0.074265 | -32.109 | 42.76 | 0 | 3.8175 | 0.8 | 1 | 1.018 | 4.8355 | 0.9 | 1.0511 | 1.0838 | 0.0042975
2016-02-21 10:00 | 7.1267 | 7.1267 | 0 | 0 | -10.9238 | -17.7759 | 88.4965 | 1.5035 | -17.4495 | 32.9646 | 0 | 5.345 | 0.8 | 1 | 1.4253 | 6.7703 | 0.5 | 0.71157 | 1.085 | 0.0060236
2016-02-21 11:00 | 9.1633 | 9.1633 | 0 | 0 | -10.9088 | -2.775 | 87.8904 | 2.1096 | -2.7267 | 28.0102 | 0 | 6.8725 | 0.8 | 1 | 1.8327 | 8.7052 | 0.9 | 1.172 | 1.0834 | 0.0077336
2016-02-21 12:00 | 11.2 | 11.2 | 0 | 0 | -10.8939 | 12.2259 | 88.1485 | 1.8515 | 12.0086 | 30.3691 | 0 | 8.4 | 0.8 | 1 | 2.24 | 10.64 | 0.7 | 1.0325 | 1.0839 | 0.0094567
2016-02-21 13:00 | 7.4933 | 7.4933 | 0 | 0 | -10.8789 | 27.2268 | 89.252 | 0.74804 | 26.7007 | 38.7266 | 0 | 5.62 | 0.8 | 1 | 1.4987 | 7.1187 | 0.6 | 0.82246 | 1.0846 | 0.0063313
2016-02-21 14:00 | 3.7867 | 3.7867 | 0 | 0 | -10.8639 | 42.2276 | 91.1244 | -1.1244 | 41.3121 | 50.1667 | 0 | 2.84 | 0.8 | 1 | 0.75733 | 3.5973 | 0.6 | 0.71242 | 1.085 | 0.0032006
2016-02-21 15:00 | 0.08 | 0.08 | 0 | 0 | -10.8489 | 57.2285 | 93.6398 | -3.6398 | 55.8404 | 63.0283 | 0 | 0.06 | 0.8 | 1 | 0.016 | 0.076 | 0.4 | 0.40237 | 1.0861 | 6.7685e-05
2016-02-21 16:00 | 0.053333 | 0.053333 | 0 | 0 | -10.834 | 72.2294 | 96.6335 | -6.6335 | 70.3248 | 76.5929 | 0 | 0.04 | 0.8 | 1 | 0.010667 | 0.050667 | 0.2 | 0.20158 | 1.0868 | 4.5153e-05
2016-02-21 17:00 | 0.026667 | 0.026667 | 0 | 0 | -10.819 | 87.2303 | 99.9139 | -9.9139 | 84.8414 | 90.5374 | 0 | 0.02 | 0.8 | 1 | 0.0053333 | 0.025333 | 0.3 | 0.30079 | 1.0864 | 2.2569e-05
2016-02-21 18:00 | 0 | 0 | 0 | 0 | -10.804 | 102.2312 | 103.2707 | -13.2707 | 99.4897 | 104.6992 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.1 | 0.1 | 1.0872 | 0
2016-02-21 19:00 | 0 | 0 | 0 | 0 | -10.789 | 117.2321 | 106.4837 | -16.4837 | 114.3729 | 118.9842 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-02-21 20:00 | 0 | 0 | 0 | 0 | -10.774 | 132.2331 | 109.3312 | -19.3312 | 129.5721 | 133.323 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-02-21 21:00 | 0 | 0 | 0 | 0 | -10.759 | 147.234 | 111.6028 | -21.6028 | 145.1197 | 147.6318 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-02-21 22:00 | 0 | 0 | 0 | 0 | -10.744 | 162.2349 | 113.1175 | -23.1175 | 160.9775 | 161.6769 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-02-21 23:00 | 0 | 0 | 0 | 0 | -10.7289 | 177.2358 | 113.7461 | -23.7461 | 177.0328 | 173.21 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-02-22 | 0 | 0 | 0 | 0 | -10.7139 | -167.7632 | 113.4325 | -23.4325 | -166.8809 | 166.581 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-02-22 01:00 | 0 | 0 | 0 | 0 | -10.6989 | -152.7623 | 112.2031 | -22.2031 | -150.9387 | 152.8491 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.4 | 0.4 | 1.0861 | 0
2016-02-22 02:00 | 0 | 0 | 0 | 0 | -10.6839 | -137.7613 | 110.1624 | -20.1624 | -135.2762 | 138.5862 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-02-22 03:00 | 0 | 0 | 0 | 0 | -10.6688 | -122.7604 | 107.4748 | -17.4748 | -119.9583 | 124.2394 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-02-22 04:00 | 0 | 0 | 0 | 0 | -10.6538 | -107.7594 | 104.3422 | -14.3422 | -104.9753 | 109.9174 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-02-22 05:00 | 0 | 0 | 0 | 0 | -10.6387 | -92.7585 | 100.9835 | -10.9835 | -90.2595 | 95.6881 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-02-22 06:00 | 0 | 0 | 0 | 0 | -10.6237 | -77.7575 | 97.6203 | -7.6203 | -75.7117 | 81.6311 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-02-22 07:00 | 2.1233 | 2.1033 | 0.02 | 0 | -10.6086 | -62.7565 | 94.467 | -4.467 | -61.2272 | 67.8742 | 0 | 1.5775 | 0.8 | 1 | 0.42467 | 2.0022 | 0.3 | 0.36257 | 1.0862 | 0.0017833
2016-02-22 08:00 | 4.2467 | 4.2067 | 0.04 | 0 | -10.5936 | -47.7556 | 91.7234 | -1.7234 | -46.7186 | 54.6601 | 0 | 3.155 | 0.8 | 1 | 0.84933 | 4.0043 | 0.6 | 0.72514 | 1.085 | 0.0035625
2016-02-22 09:00 | 6.37 | 6.31 | 0.06 | 0 | -10.5785 | -32.7546 | 89.5655 | 0.43446 | -32.1313 | 42.511 | 0 | 4.7325 | 0.8 | 1 | 1.274 | 6.0065 | 1 | 1.1877 | 1.0833 | 0.0053358
2016-02-22 10:00 | 10.12 | 9.8233 | 0.29667 | 0 | -10.5634 | -17.7536 | 88.1355 | 1.8645 | -17.4525 | 32.6492 | 0 | 7.3675 | 0.8 | 1 | 2.024 | 9.3915 | 0.9 | 1.1935 | 1.0833 | 0.0083427
2016-02-22 11:00 | 13.87 | 13.3367 | 0.53333 | 0 | -10.5484 | -2.7526 | 87.5297 | 2.4703 | -2.7086 | 27.6493 | 0 | 10.0025 | 0.8 | 1 | 2.774 | 12.7765 | 0 | 0.39927 | 1.0861 | 0.011379
2016-02-22 12:00 | 17.62 | 16.85 | 0.77 | 0 | -10.5333 | 12.2484 | 87.7894 | 2.2106 | 12.048 | 30.048 | 0 | 12.6375 | 0.8 | 1 | 3.524 | 16.1615 | 0.1 | 0.60505 | 1.0854 | 0.014384
2016-02-22 13:00 | 11.8367 | 11.3233 | 0.51333 | 0 | -10.5182 | 27.2494 | 88.8955 | 1.1045 | 26.76 | 38.4852 | 0 | 8.4925 | 0.8 | 1 | 2.3673 | 10.8598 | 1 | 1.3394 | 1.0828 | 0.0096425
2016-02-22 14:00 | 6.0533 | 5.7967 | 0.25667 | 0 | -10.5031 | 42.2504 | 90.7711 | -0.77115 | 41.3889 | 49.9887 | 0 | 4.3475 | 0.8 | 1 | 1.2107 | 5.5582 | 1.2 | 1.3737 | 1.0827 | 0.0049346
2016-02-22 15:00 | 0.27 | 0.27 | 0 | 0 | -10.488 | 57.2514 | 93.2897 | -3.2897 | 55.9312 | 62.8936 | 0 | 0.2025 | 0.8 | 1 | 0.054 | 0.2565 | 1.3 | 1.308 | 1.0829 | 0.00022777
2016-02-22 16:00 | 0.18 | 0.18 | 0 | 0 | -10.4729 | 72.2524 | 96.2859 | -6.2859 | 70.4256 | 76.4876 | 0 | 0.135 | 0.8 | 1 | 0.036 | 0.171 | 1.7 | 1.7053 | 1.0815 | 0.00015165
2016-02-22 17:00 | 0.09 | 0.09 | 0 | 0 | -10.4578 | 87.2535 | 99.5675 | -9.5675 | 84.9476 | 90.4525 | 0 | 0.0675 | 0.8 | 1 | 0.018 | 0.0855 | 1.1 | 1.1027 | 1.0836 | 7.5974e-05
2016-02-22 18:00 | 0 | 0 | 0 | 0 | -10.4427 | 102.2545 | 102.9239 | -12.9239 | 99.5965 | 104.6282 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.4 | 1.4 | 1.0826 | 0
2016-02-22 19:00 | 0 | 0 | 0 | 0 | -10.4276 | 117.2555 | 106.1351 | -16.1351 | 114.475 | 118.9214 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.3 | 1.3 | 1.083 | 0
2016-02-22 20:00 | 0 | 0 | 0 | 0 | -10.4125 | 132.2566 | 108.9795 | -18.9795 | 129.6638 | 133.2617 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.2 | 1.2 | 1.0833 | 0
2016-02-22 21:00 | 0 | 0 | 0 | 0 | -10.3974 | 147.2576 | 111.2474 | -21.2474 | 145.1953 | 147.5603 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.3 | 1.3 | 1.083 | 0
2016-02-22 22:00 | 0 | 0 | 0 | 0 | -10.3822 | 162.2586 | 112.7585 | -22.7585 | 161.0321 | 161.5609 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.6 | 1.6 | 1.0819 | 0
2016-02-22 23:00 | 0 | 0 | 0 | 0 | -10.3671 | 177.2597 | 113.3846 | -23.3846 | 177.063 | 172.8842 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-02-23 | 0 | 0 | 0 | 0 | -10.352 | -167.7392 | 113.0698 | -23.0698 | -166.8758 | 166.3809 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.2 | 1.2 | 1.0833 | 0
2016-02-23 01:00 | 0 | 0 | 0 | 0 | -10.3368 | -152.7382 | 111.8407 | -21.8407 | -150.9568 | 152.7222 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-02-23 02:00 | 0 | 0 | 0 | 0 | -10.3217 | -137.7371 | 109.8011 | -19.8011 | -135.3134 | 138.4767 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1 | 1 | 1.084 | 0
2016-02-23 03:00 | 0 | 0 | 0 | 0 | -10.3066 | -122.736 | 107.115 | -17.115 | -120.0091 | 124.1317 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-02-23 04:00 | 0 | 0 | 0 | 0 | -10.2914 | -107.735 | 103.9835 | -13.9835 | -105.0339 | 109.804 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.9 | 0.9 | 1.0843 | 0
2016-02-23 05:00 | 0 | 0 | 0 | 0 | -10.2762 | -92.7339 | 100.6251 | -10.6251 | -90.3202 | 95.5634 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.1 | 0.1 | 1.0872 | 0
2016-02-23 06:00 | 0 | 0 | 0 | 0 | -10.2611 | -77.7328 | 97.2613 | -7.2613 | -75.7691 | 81.4895 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.2 | 1.2 | 1.0833 | 0
2016-02-23 07:00 | 2.75 | 2.56 | 0.19 | 0 | -10.2459 | -62.7317 | 94.1068 | -4.1068 | -61.2764 | 67.7083 | 0 | 1.92 | 0.8 | 1 | 0.55 | 2.47 | 1.3 | 1.3772 | 1.0827 | 0.0021929
2016-02-23 08:00 | 5.5 | 5.12 | 0.38 | 0 | -10.2307 | -47.7306 | 91.3616 | -1.3616 | -46.755 | 54.4592 | 0 | 3.84 | 0.8 | 1 | 1.1 | 4.94 | 1.4 | 1.5544 | 1.0821 | 0.0043832
2016-02-23 09:00 | 8.25 | 7.68 | 0.57 | 0 | -10.2156 | -32.7295 | 89.2023 | 0.7977 | -32.1511 | 42.2594 | 0 | 5.76 | 0.8 | 1 | 1.65 | 7.41 | 1.4 | 1.6316 | 1.0818 | 0.0065732
2016-02-23 10:00 | 11.03 | 10.18 | 0.85 | 0 | -10.2004 | -17.7284 | 87.7716 | 2.2284 | -17.4528 | 32.3308 | 0 | 7.635 | 0.8 | 1 | 2.206 | 9.841 | 1.6 | 1.9075 | 1.0808 | 0.0087218
2016-02-23 11:00 | 13.81 | 12.68 | 1.13 | 0 | -10.1852 | -2.7273 | 87.1663 | 2.8337 | -2.6876 | 27.2855 | 0 | 9.51 | 0.8 | 1 | 2.762 | 12.272 | 0.4 | 0.7835 | 1.0848 | 0.010916
2016-02-23 12:00 | 16.59 | 15.18 | 1.41 | 0 | -10.17 | 12.2738 | 87.4277 | 2.5723 | 12.0904 | 29.7265 | 0 | 11.385 | 0.8 | 1 | 3.318 | 14.703 | 0.7 | 1.1595 | 1.0834 | 0.013062
2016-02-23 13:00 | 11.23 | 10.29 | 0.94 | 0 | -10.1548 | 27.2749 | 88.5367 | 1.4633 | 26.8226 | 38.2456 | 0 | 7.7175 | 0.8 | 1 | 2.246 | 9.9635 | 0.9 | 1.2114 | 1.0833 | 0.0088503
2016-02-23 14:00 | 5.87 | 5.4 | 0.47 | 0 | -10.1396 | 42.2761 | 90.4157 | -0.4157 | 41.469 | 49.8133 | 0 | 4.05 | 0.8 | 1 | 1.174 | 5.224 | 0.8 | 0.96325 | 1.0841 | 0.0046441
2016-02-23 15:00 | 0.51 | 0.51 | 0 | 0 | -10.1244 | 57.2772 | 92.9375 | -2.9375 | 56.0254 | 62.7613 | 0 | 0.3825 | 0.8 | 1 | 0.102 | 0.4845 | -0.1 | -0.084859 | 1.0878 | 0.00043217
2016-02-23 16:00 | 0.34 | 0.34 | 0 | 0 | -10.1092 | 72.2783 | 95.9363 | -5.9363 | 70.5296 | 76.3846 | 0 | 0.255 | 0.8 | 1 | 0.068 | 0.323 | -0.2 | -0.18991 | 1.0882 | 0.00028821
2016-02-23 17:00 | 0.17 | 0.17 | 0 | 0 | -10.094 | 87.2795 | 99.2191 | -9.2191 | 85.057 | 90.3695 | 0 | 0.1275 | 0.8 | 1 | 0.034 | 0.1615 | -0.5 | -0.49495 | 1.0892 | 0.00014425
2016-02-23 18:00 | 0 | 0 | 0 | 0 | -10.0788 | 102.2806 | 102.5752 | -12.5752 | 99.7065 | 104.5586 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-02-23 19:00 | 0 | 0 | 0 | 0 | -10.0636 | 117.2818 | 105.7844 | -15.7844 | 114.5802 | 118.8595 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-02-23 20:00 | 0 | 0 | 0 | 0 | -10.0484 | 132.2829 | 108.6257 | -18.6257 | 129.7586 | 133.2005 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-02-23 21:00 | 0 | 0 | 0 | 0 | -10.0331 | 147.2841 | 110.8897 | -20.8897 | 145.274 | 147.4873 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-02-23 22:00 | 0 | 0 | 0 | 0 | -10.0179 | 162.2852 | 112.3971 | -22.3971 | 161.0898 | 161.4404 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-02-23 23:00 | 0 | 0 | 0 | 0 | -10.0027 | 177.2864 | 113.0205 | -23.0205 | 177.0963 | 172.5535 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-02-24 | 0 | 0 | 0 | 0 | -9.9874 | -167.7124 | 112.7044 | -22.7044 | -166.8677 | 166.1704 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-02-24 01:00 | 0 | 0 | 0 | 0 | -9.9722 | -152.7112 | 111.4753 | -21.4753 | -150.9721 | 152.5878 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-02-24 02:00 | 0 | 0 | 0 | 0 | -9.9569 | -137.71 | 109.4368 | -19.4368 | -135.3478 | 138.3615 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-02-24 03:00 | 0 | 0 | 0 | 0 | -9.9417 | -122.7089 | 106.7521 | -16.7521 | -120.0573 | 124.0192 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-02-24 04:00 | 0 | 0 | 0 | 0 | -9.9264 | -107.7077 | 103.6216 | -13.6216 | -105.09 | 109.6863 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-02-24 05:00 | 0 | 0 | 0 | 0 | -9.9111 | -92.7065 | 100.2636 | -10.2636 | -90.3785 | 95.435 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-02-24 06:00 | 0 | 0 | 0 | 0 | -9.8959 | -77.7053 | 96.8992 | -6.8992 | -75.8241 | 81.3446 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-02-24 07:00 | 3.1067 | 3.1067 | 0 | 0 | -9.8806 | -62.704 | 93.7435 | -3.7435 | -61.3232 | 67.5395 | 0 | 2.33 | 0.8 | 1 | 0.62133 | 2.9513 | -0.7 | -0.60777 | 1.0896 | 0.002637
2016-02-24 08:00 | 6.2133 | 6.2133 | 0 | 0 | -9.8653 | -47.7028 | 90.9967 | -0.99673 | -46.789 | 54.2557 | 0 | 4.66 | 0.8 | 1 | 1.2427 | 5.9027 | -1.2 | -1.0155 | 1.0911 | 0.0052809
2016-02-24 09:00 | 9.32 | 9.32 | 0 | 0 | -9.85 | -32.7016 | 88.8362 | 1.1638 | -32.1684 | 42.0052 | 0 | 6.99 | 0.8 | 1 | 1.864 | 8.854 | -0.8 | -0.52331 | 1.0893 | 0.0079089
2016-02-24 10:00 | 12.41 | 12.32 | 0.09 | 0 | -9.8348 | -17.7004 | 87.4049 | 2.5951 | -17.4503 | 32.0095 | 0 | 9.24 | 0.8 | 1 | 2.482 | 11.722 | -1 | -0.63369 | 1.0897 | 0.010474
2016-02-24 11:00 | 15.5 | 15.32 | 0.18 | 3.2249 | -9.8195 | -2.6992 | 86.8003 | 3.1997 | -2.6637 | 26.9188 | 2.8754 | 11.49 | 0.8 | 1 | 3.1 | 17.4654 | -1.1 | -0.55421 | 1.0894 | 0.015603
2016-02-24 12:00 | 18.59 | 18.32 | 0.27 | 0 | -9.8042 | 12.3021 | 87.0636 | 2.9364 | 12.1358 | 29.4047 | 0 | 13.74 | 0.8 | 1 | 3.718 | 17.458 | -1.2 | -0.65444 | 1.0898 | 0.015601
2016-02-24 13:00 | 12.7067 | 12.5267 | 0.18 | 0 | -9.7889 | 27.3033 | 88.1756 | 1.8244 | 26.8883 | 38.0078 | 0 | 9.395 | 0.8 | 1 | 2.5413 | 11.9363 | -1.5 | -1.127 | 1.0914 | 0.010683
2016-02-24 14:00 | 6.8233 | 6.7333 | 0.09 | 0 | -9.7736 | 42.3046 | 90.0581 | -0.058145 | 41.5523 | 49.6404 | 0 | 5.05 | 0.8 | 1 | 1.3647 | 6.4147 | -2 | -1.7995 | 1.0938 | 0.0057534
2016-02-24 15:00 | 0.94 | 0.94 | 0 | 0 | -9.7583 | 57.3058 | 92.5834 | -2.5834 | 56.1227 | 62.6316 | 0 | 0.705 | 0.8 | 1 | 0.188 | 0.893 | -2.1 | -2.0721 | 1.0948 | 0.00080164
2016-02-24 16:00 | 0.62667 | 0.62667 | 0 | 0 | -9.743 | 72.3071 | 95.5848 | -5.5848 | 70.6369 | 76.2839 | 0 | 0.47 | 0.8 | 1 | 0.12533 | 0.59533 | -2.2 | -2.1814 | 1.0951 | 0.00053462
2016-02-24 17:00 | 0.31333 | 0.31333 | 0 | 0 | -9.7277 | 87.3083 | 98.8689 | -8.8689 | 85.1697 | 90.2885 | 0 | 0.235 | 0.8 | 1 | 0.062667 | 0.29767 | -2.5 | -2.4907 | 1.0962 | 0.00026757
2016-02-24 18:00 | 0 | 0 | 0 | 0 | -9.7123 | 102.3096 | 102.2247 | -12.2247 | 99.8196 | 104.4906 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-02-24 19:00 | 0 | 0 | 0 | 0 | -9.697 | 117.3108 | 105.4319 | -15.4319 | 114.6885 | 118.7985 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-02-24 20:00 | 0 | 0 | 0 | 0 | -9.6817 | 132.3121 | 108.2698 | -18.2698 | 129.8564 | 133.1393 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-02-24 21:00 | 0 | 0 | 0 | 0 | -9.6664 | 147.3134 | 110.5298 | -20.5298 | 145.3557 | 147.4129 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-02-24 22:00 | 0 | 0 | 0 | 0 | -9.651 | 162.3147 | 112.0334 | -22.0334 | 161.1503 | 161.3153 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.8 | -2.8 | 1.0973 | 0
2016-02-24 23:00 | 0 | 0 | 0 | 0 | -9.6357 | 177.316 | 112.6539 | -22.6539 | 177.1325 | 172.2183 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-02-25 | 0 | 0 | 0 | 0 | -9.6203 | -167.6828 | 112.3363 | -22.3363 | -166.8568 | 165.95 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-02-25 01:00 | 0 | 0 | 0 | 0 | -9.605 | -152.6815 | 111.1071 | -21.1071 | -150.9845 | 152.4461 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-02-25 02:00 | 0 | 0 | 0 | 0 | -9.5896 | -137.6802 | 109.0696 | -19.0696 | -135.3796 | 138.2405 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-02-25 03:00 | 0 | 0 | 0 | 0 | -9.5743 | -122.6789 | 106.3861 | -16.3861 | -120.103 | 123.9019 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-02-25 04:00 | 0 | 0 | 0 | 0 | -9.5589 | -107.6775 | 103.2567 | -13.2567 | -105.1437 | 109.5646 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-02-25 05:00 | 0 | 0 | 0 | 0 | -9.5436 | -92.6762 | 99.8989 | -9.8989 | -90.4344 | 95.3031 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-02-25 06:00 | 0 | 0 | 0 | 0 | -9.5282 | -77.6749 | 96.5341 | -6.5341 | -75.8769 | 81.1965 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-02-25 07:00 | 4.95 | 4.82 | 0.13 | 0 | -9.5128 | -62.6736 | 93.3771 | -3.3771 | -61.3677 | 67.3679 | 0 | 3.615 | 0.8 | 1 | 0.99 | 4.605 | -2.7 | -2.5561 | 1.0964 | 0.0041403
2016-02-25 08:00 | 9.9 | 9.64 | 0.26 | 0 | -9.4974 | -47.6723 | 90.629 | -0.62896 | -46.8207 | 54.0497 | 0 | 7.23 | 0.8 | 1 | 1.98 | 9.21 | -2.8 | -2.5122 | 1.0963 | 0.0082794
2016-02-25 09:00 | 14.85 | 14.46 | 0.39 | 0 | -9.4821 | -32.6709 | 88.4672 | 1.5328 | -32.1832 | 41.7487 | 0 | 10.845 | 0.8 | 1 | 2.97 | 13.815 | -3 | -2.5683 | 1.0965 | 0.012421
2016-02-25 10:00 | 16.93 | 16.4367 | 0.49333 | 0 | -9.4667 | -17.6696 | 87.0356 | 2.9644 | -17.4453 | 31.6855 | 0 | 12.3275 | 0.8 | 1 | 3.386 | 15.7135 | -2.8 | -2.309 | 1.0956 | 0.014117
2016-02-25 11:00 | 19.01 | 18.4133 | 0.59667 | 9.5871 | -9.4513 | -2.6682 | 86.4318 | 3.5682 | -2.6371 | 26.5494 | 8.5761 | 13.81 | 0.8 | 1 | 3.802 | 26.1881 | -2.9 | -2.0816 | 1.0948 | 0.02351
2016-02-25 12:00 | 21.09 | 20.39 | 0.7 | 12.1502 | -9.4359 | 12.3331 | 86.6972 | 3.3028 | 12.1842 | 29.0829 | 10.6183 | 15.2925 | 0.8 | 1 | 4.218 | 30.1288 | -3.5 | -2.5585 | 1.0965 | 0.027089
2016-02-25 13:00 | 14.59 | 14.11 | 0.48 | 0 | -9.4205 | 27.3345 | 87.8123 | 2.1877 | 26.957 | 37.7721 | 0 | 10.5825 | 0.8 | 1 | 2.918 | 13.5005 | -3.6 | -3.1781 | 1.0986 | 0.012162
2016-02-25 14:00 | 8.09 | 7.83 | 0.26 | 0 | -9.4051 | 42.3358 | 89.6986 | 0.30139 | 41.6387 | 49.4701 | 0 | 5.8725 | 0.8 | 1 | 1.618 | 7.4905 | -3.8 | -3.5659 | 1.1 | 0.0067563
2016-02-25 15:00 | 1.59 | 1.55 | 0.04 | 0 | -9.3897 | 57.3372 | 92.2274 | -2.2274 | 56.2232 | 62.5045 | 0 | 1.1625 | 0.8 | 1 | 0.318 | 1.4805 | -3.7 | -3.6537 | 1.1003 | 0.0013358
2016-02-25 16:00 | 1.06 | 1.0333 | 0.026667 | 0 | -9.3743 | 72.3386 | 95.2315 | -5.2315 | 70.7473 | 76.1855 | 0 | 0.775 | 0.8 | 1 | 0.212 | 0.987 | -3.4 | -3.3692 | 1.0993 | 0.0008897
2016-02-25 17:00 | 0.53 | 0.51667 | 0.013333 | 0 | -9.3589 | 87.3399 | 98.5169 | -8.5169 | 85.2854 | 90.2094 | 0 | 0.3875 | 0.8 | 1 | 0.106 | 0.4935 | -3.3 | -3.2846 | 1.099 | 0.00044473
2016-02-25 18:00 | 0 | 0 | 0 | 0 | -9.3434 | 102.3413 | 101.8723 | -11.8723 | 99.9357 | 104.424 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3 | -3 | 1.098 | 0
2016-02-25 19:00 | 0 | 0 | 0 | 0 | -9.328 | 117.3427 | 105.0774 | -15.0774 | 114.7997 | 118.7383 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-02-25 20:00 | 0 | 0 | 0 | 0 | -9.3126 | 132.3441 | 107.9119 | -17.9119 | 129.9571 | 133.078 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-02-25 21:00 | 0 | 0 | 0 | 0 | -9.2972 | 147.3455 | 110.1678 | -20.1678 | 145.4402 | 147.337 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1004 | 0
2016-02-25 22:00 | 0 | 0 | 0 | 0 | -9.2817 | 162.3469 | 111.6674 | -21.6674 | 161.2138 | 161.1855 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1004 | 0
2016-02-25 23:00 | 0 | 0 | 0 | 0 | -9.2663 | 177.3483 | 112.2849 | -22.2849 | 177.1715 | 171.8788 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.6 | -3.6 | 1.1001 | 0
2016-02-26 | 0 | 0 | 0 | 0 | -9.2509 | -167.6503 | 111.9656 | -21.9656 | -166.8431 | 165.72 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-02-26 01:00 | 0 | 0 | 0 | 0 | -9.2354 | -152.6489 | 110.7363 | -20.7363 | -150.9942 | 152.2971 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.3 | -4.3 | 1.1025 | 0
2016-02-26 02:00 | 0 | 0 | 0 | 0 | -9.22 | -137.6475 | 108.6995 | -18.6995 | -135.4087 | 138.1138 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.7 | -4.7 | 1.1039 | 0
2016-02-26 03:00 | 0 | 0 | 0 | 0 | -9.2045 | -122.6461 | 106.0173 | -16.0173 | -120.1461 | 123.7799 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.6 | -4.6 | 1.1036 | 0
2016-02-26 04:00 | 0 | 0 | 0 | 0 | -9.1891 | -107.6447 | 102.8888 | -12.8888 | -105.195 | 109.4388 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.1033 | 0
2016-02-26 05:00 | 0 | 0 | 0 | 0 | -9.1736 | -92.6432 | 99.5313 | -9.5313 | -90.4881 | 95.1675 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.3 | -4.3 | 1.1025 | 0
2016-02-26 06:00 | 0 | 0 | 0 | 0 | -9.1581 | -77.6418 | 96.166 | -6.166 | -75.9274 | 81.0454 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.3 | -4.3 | 1.1025 | 0
2016-02-26 07:00 | 5.8333 | 5.0767 | 0.75667 | 0 | -9.1427 | -62.6404 | 93.0079 | -3.0079 | -61.4099 | 67.1936 | 0 | 3.8075 | 0.8 | 1 | 1.1667 | 4.9742 | -4.3 | -4.1446 | 1.102 | 0.0044949
2016-02-26 08:00 | 11.6667 | 10.1533 | 1.5133 | 0 | -9.1272 | -47.6389 | 90.2584 | -0.25841 | -46.8499 | 53.8413 | 0 | 7.615 | 0.8 | 1 | 2.3333 | 9.9483 | -4.2 | -3.8891 | 1.1011 | 0.0089825
2016-02-26 09:00 | 17.5 | 15.23 | 2.27 | 0 | -9.1117 | -32.6375 | 88.0956 | 1.9044 | -32.1956 | 41.49 | 0 | 11.4225 | 0.8 | 1 | 3.5 | 14.9225 | -4.3 | -3.8337 | 1.1009 | 0.013471
2016-02-26 10:00 | 21.95 | 18.0833 | 3.8667 | 66.4428 | -9.0962 | -17.636 | 86.6638 | 3.3362 | -17.4376 | 31.359 | 56.7371 | 13.5625 | 0.8 | 1 | 4.39 | 74.6896 | -4.4 | -2.066 | 1.0947 | 0.067047
2016-02-26 11:00 | 26.4 | 20.9367 | 5.4633 | 79.5295 | -9.0807 | -2.6346 | 86.0609 | 3.9391 | -2.6077 | 26.1774 | 71.3724 | 15.7025 | 0.8 | 1 | 5.28 | 92.3549 | -4.2 | -1.3139 | 1.0921 | 0.082706
2016-02-26 12:00 | 30.85 | 23.79 | 7.06 | 110.2553 | -9.0653 | 12.3669 | 86.3287 | 3.6713 | 12.2355 | 28.7612 | 96.6534 | 17.8425 | 0.8 | 1 | 6.17 | 120.6659 | -4.4 | -0.62919 | 1.0897 | 0.10782
2016-02-26 13:00 | 21.3133 | 16.46 | 4.8533 | 0 | -9.0498 | 27.3684 | 87.4471 | 2.5529 | 27.0288 | 37.5387 | 0 | 12.345 | 0.8 | 1 | 4.2627 | 16.6077 | -4.6 | -4.081 | 1.1018 | 0.015004
2016-02-26 14:00 | 11.7767 | 9.13 | 2.6467 | 0 | -9.0343 | 42.3698 | 89.3372 | 0.66281 | 41.7282 | 49.3025 | 0 | 6.8475 | 0.8 | 1 | 2.3553 | 9.2028 | -4.7 | -4.4124 | 1.1029 | 0.0083232
2016-02-26 15:00 | 2.24 | 1.8 | 0.44 | 0 | -9.0188 | 57.3713 | 91.8696 | -1.8696 | 56.3268 | 62.3801 | 0 | 1.35 | 0.8 | 1 | 0.448 | 1.798 | -4.6 | -4.5438 | 1.1034 | 0.0016268
2016-02-26 16:00 | 1.4933 | 1.2 | 0.29333 | 0 | -9.0033 | 72.3728 | 94.8765 | -4.8765 | 70.8608 | 76.0894 | 0 | 0.9 | 0.8 | 1 | 0.29867 | 1.1987 | -4.2 | -4.1625 | 1.1021 | 0.0010832
2016-02-26 17:00 | 0.74667 | 0.6 | 0.14667 | 0 | -8.9878 | 87.3743 | 98.1633 | -8.1633 | 85.4042 | 90.1323 | 0 | 0.45 | 0.8 | 1 | 0.14933 | 0.59933 | -4.5 | -4.4813 | 1.1032 | 0.00054216
2016-02-26 18:00 | 0 | 0 | 0 | 0 | -8.9722 | 102.3758 | 101.5183 | -11.5183 | 100.0549 | 104.3589 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.1033 | 0
2016-02-26 19:00 | 0 | 0 | 0 | 0 | -8.9567 | 117.3772 | 104.7213 | -14.7213 | 114.9139 | 118.679 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.1033 | 0
2016-02-26 20:00 | 0 | 0 | 0 | 0 | -8.9412 | 132.3787 | 107.5523 | -17.5523 | 130.0608 | 133.0167 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-02-26 21:00 | 0 | 0 | 0 | 0 | -8.9257 | 147.3802 | 109.8039 | -19.8039 | 145.5276 | 147.2593 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.1 | -5.1 | 1.1054 | 0
2016-02-26 22:00 | 0 | 0 | 0 | 0 | -8.9102 | 162.3818 | 111.2994 | -21.2994 | 161.28 | 161.0509 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-02-26 23:00 | 0 | 0 | 0 | 0 | -8.8946 | 177.3833 | 111.9136 | -21.9136 | 177.2133 | 171.5354 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.1 | -6.1 | 1.1088 | 0
2016-02-27 | 0 | 0 | 0 | 0 | -8.8791 | -167.6152 | 111.5926 | -21.5926 | -166.8266 | 165.4807 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.6 | -5.6 | 1.1071 | 0
2016-02-27 01:00 | 0 | 0 | 0 | 0 | -8.8636 | -152.6137 | 110.3629 | -20.3629 | -151.0013 | 152.1409 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.5 | -5.5 | 1.1067 | 0
2016-02-27 02:00 | 0 | 0 | 0 | 0 | -8.848 | -137.6122 | 108.3268 | -18.3268 | -135.4352 | 137.9815 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.9 | -5.9 | 1.1081 | 0
2016-02-27 03:00 | 0 | 0 | 0 | 0 | -8.8325 | -122.6106 | 105.6456 | -15.6456 | -120.1868 | 123.6532 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.7 | -5.7 | 1.1075 | 0
2016-02-27 04:00 | 0 | 0 | 0 | 0 | -8.8169 | -107.6091 | 102.518 | -12.518 | -105.2439 | 109.3091 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.7 | -5.7 | 1.1075 | 0
2016-02-27 05:00 | 0 | 0 | 0 | 0 | -8.8014 | -92.6076 | 99.1609 | -9.1609 | -90.5394 | 95.0286 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.5 | -6.5 | 1.1102 | 0
2016-02-27 06:00 | 0 | 0 | 0 | 0 | -8.7858 | -77.606 | 95.7951 | -5.7951 | -75.9756 | 80.8912 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7 | -7 | 1.112 | 0
2016-02-27 07:00 | 7.0867 | 5.1033 | 1.9833 | 0 | -8.7703 | -62.6045 | 92.636 | -2.636 | -61.4499 | 67.0167 | 0 | 3.8275 | 0.8 | 1 | 1.4173 | 5.2448 | -7.2 | -7.0361 | 1.1121 | 0.004783
2016-02-27 08:00 | 14.1733 | 10.2067 | 3.9667 | 0 | -8.7547 | -47.6029 | 89.8852 | 0.11481 | -46.8769 | 53.6307 | 0 | 7.655 | 0.8 | 1 | 2.8347 | 10.4897 | -7.1 | -6.7722 | 1.1112 | 0.009558
2016-02-27 09:00 | 21.26 | 15.31 | 5.95 | 0 | -8.7391 | -32.6014 | 87.7214 | 2.2786 | -32.2055 | 41.2291 | 0 | 11.4825 | 0.8 | 1 | 4.252 | 15.7345 | -6.7 | -6.2083 | 1.1092 | 0.014312
2016-02-27 10:00 | 26.0767 | 18.0467 | 8.03 | 124.0825 | -8.7235 | -17.5998 | 86.2895 | 3.7105 | -17.4274 | 31.0299 | 106.326 | 13.535 | 0.8 | 1 | 5.2153 | 125.0764 | -6.2 | -2.2914 | 1.0955 | 0.11236
2016-02-27 11:00 | 30.8933 | 20.7833 | 10.11 | 134.4577 | -8.708 | -2.5982 | 85.6878 | 4.3122 | -2.5756 | 25.8029 | 121.0519 | 15.5875 | 0.8 | 1 | 6.1787 | 142.8181 | -7.1 | -2.6369 | 1.0967 | 0.12844
2016-02-27 12:00 | 35.71 | 23.52 | 12.19 | 172.9372 | -8.6924 | 12.4033 | 85.958 | 4.042 | 12.2897 | 28.4397 | 152.0669 | 17.64 | 0.8 | 1 | 7.142 | 176.8489 | -8.2 | -2.6735 | 1.0969 | 0.15906
2016-02-27 13:00 | 24.79 | 16.6333 | 8.1567 | 0 | -8.6768 | 27.4049 | 87.0799 | 2.9201 | 27.1035 | 37.3076 | 0 | 12.475 | 0.8 | 1 | 4.958 | 17.433 | -8 | -7.4552 | 1.1136 | 0.015919
2016-02-27 14:00 | 13.87 | 9.7467 | 4.1233 | 0 | -8.6612 | 42.4065 | 88.974 | 1.026 | 41.8207 | 49.1378 | 0 | 7.31 | 0.8 | 1 | 2.774 | 10.084 | -7.7 | -7.3849 | 1.1133 | 0.0092061
2016-02-27 15:00 | 2.95 | 2.86 | 0.09 | 0 | -8.6456 | 57.4081 | 91.5102 | -1.5102 | 56.4334 | 62.2583 | 0 | 2.145 | 0.8 | 1 | 0.59 | 2.735 | -7.6 | -7.5145 | 1.1138 | 0.0024979
2016-02-27 16:00 | 1.9667 | 1.9067 | 0.06 | 0 | -8.63 | 72.4097 | 94.52 | -4.52 | 70.9772 | 75.9957 | 0 | 1.43 | 0.8 | 1 | 0.39333 | 1.8233 | -8.8 | -8.743 | 1.1181 | 0.0016717
2016-02-27 17:00 | 0.98333 | 0.95333 | 0.03 | 0 | -8.6144 | 87.4113 | 97.8081 | -7.8081 | 85.5259 | 90.0571 | 0 | 0.715 | 0.8 | 1 | 0.19667 | 0.91167 | -8.6 | -8.5715 | 1.1175 | 0.00083541
2016-02-27 18:00 | 0 | 0 | 0 | 0 | -8.5988 | 102.4129 | 101.1627 | -11.1627 | 100.1769 | 104.2952 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.8 | -8.8 | 1.1183 | 0
2016-02-27 19:00 | 0 | 0 | 0 | 0 | -8.5832 | 117.4145 | 104.3635 | -14.3635 | 115.0309 | 118.6204 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9 | -9 | 1.119 | 0
2016-02-27 20:00 | 0 | 0 | 0 | 0 | -8.5676 | 132.4161 | 107.1909 | -17.1909 | 130.1671 | 132.9551 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.2 | -8.2 | 1.1162 | 0
2016-02-27 21:00 | 0 | 0 | 0 | 0 | -8.552 | 147.4177 | 109.4382 | -19.4382 | 145.6178 | 147.18 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.3 | -8.3 | 1.1165 | 0
2016-02-27 22:00 | 0 | 0 | 0 | 0 | -8.5364 | 162.4193 | 110.9294 | -20.9294 | 161.349 | 160.9116 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-02-27 23:00 | 0 | 0 | 0 | 0 | -8.5208 | 177.4209 | 111.5402 | -21.5402 | 177.2578 | 171.1882 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8 | -8 | 1.1155 | 0
2016-02-28 | 0 | 0 | 0 | 0 | -8.5052 | -167.5775 | 111.2172 | -21.2172 | -166.8075 | 165.2325 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.5 | -8.5 | 1.1173 | 0
2016-02-28 01:00 | 0 | 0 | 0 | 0 | -8.4895 | -152.5758 | 109.987 | -19.987 | -151.0057 | 151.9777 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.3 | -8.3 | 1.1165 | 0
2016-02-28 02:00 | 0 | 0 | 0 | 0 | -8.4739 | -137.5742 | 107.9515 | -17.9515 | -135.4592 | 137.8437 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.7 | -7.7 | 1.1144 | 0
2016-02-28 03:00 | 0 | 0 | 0 | 0 | -8.4583 | -122.5725 | 105.2714 | -15.2714 | -120.225 | 123.522 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.6 | -7.6 | 1.1141 | 0
2016-02-28 04:00 | 0 | 0 | 0 | 0 | -8.4426 | -107.5709 | 102.1446 | -12.1446 | -105.2905 | 109.1754 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.4 | -6.4 | 1.1099 | 0
2016-02-28 05:00 | 0 | 0 | 0 | 0 | -8.427 | -92.5693 | 98.7877 | -8.7877 | -90.5885 | 94.8863 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.8 | -7.8 | 1.1148 | 0
2016-02-28 06:00 | 0 | 0 | 0 | 0 | -8.4114 | -77.5676 | 95.4215 | -5.4215 | -76.0217 | 80.7342 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.3 | -6.3 | 1.1096 | 0
2016-02-28 07:00 | 7.86 | 6.2933 | 1.5667 | 0 | -8.3957 | -62.5659 | 92.2614 | -2.2614 | -61.4877 | 66.8373 | 0 | 4.72 | 0.8 | 1 | 1.572 | 6.292 | -5.6 | -5.4034 | 1.1064 | 0.0057085
2016-02-28 08:00 | 15.72 | 12.5867 | 3.1333 | 0 | -8.3801 | -47.5643 | 89.5094 | 0.49056 | -46.9016 | 53.4179 | 0 | 9.44 | 0.8 | 1 | 3.144 | 12.584 | -5.6 | -5.2068 | 1.1057 | 0.01141
2016-02-28 09:00 | 23.58 | 18.88 | 4.7 | 0 | -8.3644 | -32.5626 | 87.3449 | 2.6551 | -32.213 | 40.9663 | 0 | 14.16 | 0.8 | 1 | 4.716 | 18.876 | -5.5 | -4.9101 | 1.1047 | 0.017099
2016-02-28 10:00 | 27.9033 | 22.94 | 4.9633 | 69.6396 | -8.3488 | -17.561 | 85.913 | 4.087 | -17.4146 | 30.6986 | 59.8806 | 17.205 | 0.8 | 1 | 5.5807 | 82.6663 | -5.8 | -3.2167 | 1.0988 | 0.074481
2016-02-28 11:00 | 32.2267 | 27 | 5.2267 | 63.9581 | -8.3331 | -2.5593 | 85.3126 | 4.6874 | -2.5407 | 25.426 | 57.7632 | 20.25 | 0.8 | 1 | 6.4453 | 84.4585 | -5.6 | -2.9607 | 1.0979 | 0.076034
2016-02-28 12:00 | 36.55 | 31.06 | 5.49 | 71.3226 | -8.3174 | 12.4424 | 85.5853 | 4.4147 | 12.3467 | 28.1187 | 62.9046 | 23.295 | 0.8 | 1 | 7.31 | 93.5096 | -6.3 | -3.3778 | 1.0993 | 0.084294
2016-02-28 13:00 | 25.55 | 21.8133 | 3.7367 | 65.1281 | -8.3018 | 27.4441 | 86.7109 | 3.2891 | 27.1812 | 37.079 | 51.9596 | 16.36 | 0.8 | 1 | 5.11 | 73.4296 | -6.8 | -4.5053 | 1.1033 | 0.06643
2016-02-28 14:00 | 14.55 | 12.5667 | 1.9833 | 0 | -8.2861 | 42.4458 | 88.6091 | 1.3909 | 41.9162 | 48.976 | 0 | 9.425 | 0.8 | 1 | 2.91 | 12.335 | -6.2 | -5.8145 | 1.1079 | 0.011206
2016-02-28 15:00 | 3.55 | 3.32 | 0.23 | 0 | -8.2704 | 57.4475 | 91.1492 | -1.1492 | 56.5431 | 62.1392 | 0 | 2.49 | 0.8 | 1 | 0.71 | 3.2 | -6.2 | -6.1 | 1.1088 | 0.0029096
2016-02-28 16:00 | 2.3667 | 2.2133 | 0.15333 | 0 | -8.2547 | 72.4492 | 94.1619 | -4.1619 | 71.0966 | 75.9044 | 0 | 1.66 | 0.8 | 1 | 0.47333 | 2.1333 | -6.4 | -6.3333 | 1.1097 | 0.0019412
2016-02-28 17:00 | 1.1833 | 1.1067 | 0.076667 | 0 | -8.2391 | 87.4509 | 97.4514 | -7.4514 | 85.6504 | 89.9838 | 0 | 0.83 | 0.8 | 1 | 0.23667 | 1.0667 | -7.9 | -7.8667 | 1.115 | 0.00097528
2016-02-28 18:00 | 0 | 0 | 0 | 0 | -8.2234 | 102.4526 | 100.8056 | -10.8056 | 100.3017 | 104.2329 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.8 | -8.8 | 1.1183 | 0
2016-02-28 19:00 | 0 | 0 | 0 | 0 | -8.2077 | 117.4543 | 104.0041 | -14.0041 | 115.1506 | 118.5625 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.5 | -8.5 | 1.1173 | 0
2016-02-28 20:00 | 0 | 0 | 0 | 0 | -8.192 | 132.456 | 106.8278 | -16.8278 | 130.2762 | 132.8934 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.5 | -8.5 | 1.1173 | 0
2016-02-28 21:00 | 0 | 0 | 0 | 0 | -8.1763 | 147.4577 | 109.0706 | -19.0706 | 145.7105 | 147.0988 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.8 | -10.8 | 1.1253 | 0
2016-02-28 22:00 | 0 | 0 | 0 | 0 | -8.1606 | 162.4594 | 110.5574 | -20.5574 | 161.4206 | 160.7676 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.3 | -10.3 | 1.1236 | 0
2016-02-28 23:00 | 0 | 0 | 0 | 0 | -8.1449 | 177.4612 | 111.1648 | -21.1648 | 177.3049 | 170.8375 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.2 | -10.2 | 1.1232 | 0
2016-02-29 | 0 | 0 | 0 | 0 | -8.1292 | -167.5371 | 110.8397 | -20.8397 | -166.7857 | 164.9757 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.2 | -8.2 | 1.1162 | 0
2016-02-29 01:00 | 0 | 0 | 0 | 0 | -8.1135 | -152.5354 | 109.6088 | -19.6088 | -151.0076 | 151.8076 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.2 | -9.2 | 1.1197 | 0
2016-02-29 02:00 | 0 | 0 | 0 | 0 | -8.0978 | -137.5336 | 107.5738 | -17.5738 | -135.4807 | 137.7005 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.7 | -7.7 | 1.1144 | 0
2016-02-29 03:00 | 0 | 0 | 0 | 0 | -8.0821 | -122.5319 | 104.8946 | -14.8946 | -120.2609 | 123.3862 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.5 | -7.5 | 1.1138 | 0
2016-02-29 04:00 | 0.026667 | 0.026667 | 0 | 0 | -8.0663 | -107.5301 | 101.7686 | -11.7686 | -105.3348 | 109.0379 | 0 | 0.02 | 0.8 | 1 | 0.0053333 | 0.025333 | -7.2 | -7.1992 | 1.1127 | 2.3114e-05
2016-02-29 05:00 | 0.053333 | 0.053333 | 0 | 0 | -8.0506 | -92.5284 | 98.412 | -8.412 | -90.6354 | 94.7407 | 0 | 0.04 | 0.8 | 1 | 0.010667 | 0.050667 | -7.2 | -7.1984 | 1.1127 | 4.6229e-05
2016-02-29 06:00 | 0.08 | 0.08 | 0 | 0 | -8.0349 | -77.5266 | 95.0454 | -5.0454 | -76.0656 | 80.5743 | 0 | 0.06 | 0.8 | 1 | 0.016 | 0.076 | -6.5 | -6.4976 | 1.1102 | 6.919e-05
2016-02-29 07:00 | 8.8533 | 7.3267 | 1.5267 | 0 | -8.0192 | -62.5249 | 91.8843 | -1.8843 | -61.5233 | 66.6555 | 0 | 5.495 | 0.8 | 1 | 1.7707 | 7.2657 | -8.1 | -7.8729 | 1.1151 | 0.0066433
2016-02-29 08:00 | 17.6267 | 14.5733 | 3.0533 | 0 | -8.0034 | -47.5231 | 89.1313 | 0.86874 | -46.9241 | 53.2032 | 0 | 10.93 | 0.8 | 1 | 3.5253 | 14.4553 | -9.3 | -8.8483 | 1.1185 | 0.013258
2016-02-29 09:00 | 26.4 | 21.82 | 4.58 | 86.5306 | -7.9877 | -32.5213 | 86.966 | 3.034 | -32.2182 | 40.7016 | 65.6002 | 16.365 | 0.8 | 1 | 5.28 | 87.2452 | -8.2 | -5.4736 | 1.1067 | 0.079171
2016-02-29 10:00 | 30.6767 | 26.3967 | 4.28 | 54.9682 | -7.972 | -17.5195 | 85.5342 | 4.4658 | -17.3993 | 30.3651 | 47.4278 | 19.7975 | 0.8 | 1 | 6.1353 | 73.3606 | -6.5 | -4.2075 | 1.1022 | 0.066305
2016-02-29 11:00 | 34.9533 | 30.9733 | 3.98 | 45.0833 | -7.9562 | -2.5178 | 84.9353 | 5.0647 | -2.5033 | 25.0469 | 40.8437 | 23.23 | 0.8 | 1 | 6.9907 | 71.0644 | -6.3 | -4.0792 | 1.1018 | 0.064204
2016-02-29 12:00 | 39.23 | 35.55 | 3.68 | 44.0775 | -7.9405 | 12.484 | 85.2108 | 4.7892 | 12.4064 | 27.7984 | 38.9907 | 26.6625 | 0.8 | 1 | 7.846 | 73.4992 | -5.8 | -3.5032 | 1.0998 | 0.066282
2016-02-29 13:00 | 27.7133 | 25.1733 | 2.54 | 39.792 | -7.9247 | 27.4858 | 86.3402 | 3.6598 | 27.2617 | 36.853 | 31.8406 | 18.88 | 0.8 | 1 | 5.5427 | 56.2633 | -5.2 | -3.4418 | 1.0995 | 0.050729
2016-02-29 14:00 | 16.1967 | 14.7967 | 1.4 | 0 | -7.909 | 42.4876 | 88.2427 | 1.7573 | 42.0147 | 48.8172 | 0 | 11.0975 | 0.8 | 1 | 3.2393 | 14.3368 | -4.9 | -4.452 | 1.1031 | 0.012968
2016-02-29 15:00 | 4.68 | 4.42 | 0.26 | 0 | -7.8932 | 57.4894 | 90.7868 | -0.78681 | 56.6556 | 62.0229 | 0 | 3.315 | 0.8 | 1 | 0.936 | 4.251 | -5.1 | -4.9672 | 1.1049 | 0.0038514
2016-02-29 16:00 | 3.12 | 2.9467 | 0.17333 | 0 | -7.8775 | 72.4912 | 93.8025 | -3.8025 | 71.2189 | 75.8154 | 0 | 2.21 | 0.8 | 1 | 0.624 | 2.834 | -5 | -4.9114 | 1.1047 | 0.0025672
2016-02-29 17:00 | 1.56 | 1.4733 | 0.086667 | 0 | -7.8617 | 87.493 | 97.0934 | -7.0934 | 85.7778 | 89.9124 | 0 | 1.105 | 0.8 | 1 | 0.312 | 1.417 | -4.9 | -4.8557 | 1.1045 | 0.0012834
2016-02-29 18:00 | 0 | 0 | 0 | 0 | -7.8459 | 102.4948 | 100.4471 | -10.4471 | 100.4292 | 104.172 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6 | -6 | 1.1085 | 0
2016-02-29 19:00 | 0 | 0 | 0 | 0 | -7.8302 | 117.4966 | 103.6434 | -13.6434 | 115.273 | 118.5053 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.6 | -4.6 | 1.1036 | 0
2016-02-29 20:00 | 0 | 0 | 0 | 0 | -7.8144 | 132.4984 | 106.4632 | -16.4632 | 130.3878 | 132.8313 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.105 | 0
2016-02-29 21:00 | 0 | 0 | 0 | 0 | -7.7986 | 147.5003 | 108.7015 | -18.7015 | 145.8059 | 147.0158 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-02-29 22:00 | 0 | 0 | 0 | 0 | -7.7828 | 162.5021 | 110.1837 | -20.1837 | 161.4947 | 160.6187 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.8 | -3.8 | 1.1008 | 0
2016-02-29 23:00 | 0 | 0 | 0 | 0 | -7.7671 | 177.5039 | 110.7874 | -20.7874 | 177.3545 | 170.4836 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.9 | -3.9 | 1.1012 | 0
2016-03-01 | 0 | 0 | 0 | 0 | -7.7513 | -167.4942 | 110.46 | -20.46 | -166.7614 | 164.7109 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4 | -4 | 1.1015 | 0
2016-03-01 01:00 | 0 | 0 | 0 | 0 | -7.7355 | -152.4924 | 109.2284 | -19.2284 | -151.007 | 151.6307 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-03-01 02:00 | 0 | 0 | 0 | 0 | -7.7197 | -137.4905 | 107.1938 | -17.1938 | -135.4998 | 137.5519 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-03-01 03:00 | 0 | 0 | 0 | 0 | -7.7039 | -122.4887 | 104.5154 | -14.5154 | -120.2944 | 123.2461 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.8 | -3.8 | 1.1008 | 0
2016-03-01 04:00 | 0.053333 | 0.053333 | 0 | 0 | -7.6881 | -107.4868 | 101.3902 | -11.3902 | -105.3769 | 108.8967 | 0 | 0.04 | 0.8 | 1 | 0.010667 | 0.050667 | -5 | -4.9984 | 1.105 | 4.5909e-05
2016-03-01 05:00 | 0.10667 | 0.10667 | 0 | 0 | -7.6723 | -92.485 | 98.0339 | -8.0339 | -90.6802 | 94.5919 | 0 | 0.08 | 0.8 | 1 | 0.021333 | 0.10133 | -3.9 | -3.8968 | 1.1011 | 9.1497e-05
2016-03-01 06:00 | 0.16 | 0.16 | 0 | 0 | -7.6565 | -77.4831 | 94.6668 | -4.6668 | -76.1073 | 80.4118 | 0 | 0.12 | 0.8 | 1 | 0.032 | 0.152 | -5.5 | -5.4953 | 1.1067 | 0.00013794
2016-03-01 07:00 | 7.6767 | 6.4533 | 1.2233 | 0 | -7.6407 | -62.4813 | 91.5049 | -1.5049 | -61.5567 | 66.4715 | 0 | 4.84 | 0.8 | 1 | 1.5353 | 6.3753 | -7.3 | -7.1008 | 1.1124 | 0.0058151
2016-03-01 08:00 | 15.1933 | 12.7467 | 2.4467 | 0 | -7.6249 | -47.4794 | 88.7508 | 1.2492 | -46.9444 | 52.9865 | 0 | 9.56 | 0.8 | 1 | 3.0387 | 12.5987 | -6 | -5.6063 | 1.1071 | 0.011438
2016-03-01 09:00 | 22.71 | 19.04 | 3.67 | 61.6083 | -7.6091 | -32.4775 | 86.5849 | 3.4151 | -32.2211 | 40.4353 | 46.8925 | 14.28 | 0.8 | 1 | 4.542 | 65.7145 | -6.2 | -4.1464 | 1.102 | 0.059383
2016-03-01 10:00 | 26.28 | 23.6867 | 2.5933 | 30.695 | -7.5933 | -17.4756 | 85.1535 | 4.8465 | -17.3816 | 30.0295 | 26.5748 | 17.765 | 0.8 | 1 | 5.256 | 49.5958 | -7.3 | -5.7501 | 1.1076 | 0.045046
2016-03-01 11:00 | 29.85 | 28.3333 | 1.5167 | 15.9866 | -7.5774 | -2.4738 | 84.5561 | 5.4439 | -2.4633 | 24.6657 | 14.528 | 21.25 | 0.8 | 1 | 5.97 | 41.748 | -5.5 | -4.1954 | 1.1022 | 0.037731
2016-03-01 12:00 | 33.42 | 32.98 | 0.44 | 4.8872 | -7.5616 | 12.5281 | 84.8346 | 5.1654 | 12.4689 | 27.4789 | 4.3358 | 24.735 | 0.8 | 1 | 6.684 | 35.7548 | -6.3 | -5.1827 | 1.1056 | 0.032416
2016-03-01 13:00 | 23.8167 | 23.5233 | 0.29333 | 4.1717 | -7.5458 | 27.53 | 85.9679 | 4.0321 | 27.345 | 36.6299 | 3.3478 | 17.6425 | 0.8 | 1 | 4.7633 | 25.7537 | -4.8 | -3.9952 | 1.1015 | 0.023261
2016-03-01 14:00 | 14.2133 | 14.0667 | 0.14667 | 0 | -7.53 | 42.5319 | 87.8749 | 2.1251 | 42.1159 | 48.6614 | 0 | 10.55 | 0.8 | 1 | 2.8427 | 13.3927 | -4.4 | -3.9815 | 1.1014 | 0.012096
2016-03-01 15:00 | 4.61 | 4.61 | 0 | 0 | -7.5141 | 57.5338 | 90.423 | -0.42303 | 56.7709 | 61.9094 | 0 | 3.4575 | 0.8 | 1 | 0.922 | 4.3795 | -3.9 | -3.7631 | 1.1007 | 0.0039527
2016-03-01 16:00 | 3.0733 | 3.0733 | 0 | 0 | -7.4983 | 72.5357 | 93.4417 | -3.4417 | 71.344 | 75.7287 | 0 | 2.305 | 0.8 | 1 | 0.61467 | 2.9197 | -3.7 | -3.6088 | 1.1001 | 0.0026339
2016-03-01 17:00 | 1.5367 | 1.5367 | 0 | 0 | -7.4825 | 87.5376 | 96.7341 | -6.7341 | 85.9079 | 89.8429 | 0 | 1.1525 | 0.8 | 1 | 0.30733 | 1.4598 | -3.4 | -3.3544 | 1.0992 | 0.0013159
2016-03-01 18:00 | 0 | 0 | 0 | 0 | -7.4666 | 102.5395 | 100.0873 | -10.0873 | 100.5593 | 104.1123 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.4 | -3.4 | 1.0994 | 0
2016-03-01 19:00 | 0 | 0 | 0 | 0 | -7.4508 | 117.5414 | 103.2812 | -13.2812 | 115.3979 | 118.4487 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-03-01 20:00 | 0 | 0 | 0 | 0 | -7.4349 | 132.5434 | 106.0972 | -16.0972 | 130.5019 | 132.7688 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-03-01 21:00 | 0 | 0 | 0 | 0 | -7.4191 | 147.5453 | 108.3308 | -18.3308 | 145.9037 | 146.9309 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-03-01 22:00 | 0 | 0 | 0 | 0 | -7.4032 | 162.5472 | 109.8083 | -19.8083 | 161.5713 | 160.465 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-03-01 23:00 | 0 | 0 | 0 | 0 | -7.3874 | 177.5492 | 110.4082 | -20.4082 | 177.4066 | 170.1265 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-03-02 | 0 | 0 | 0 | 0 | -7.3715 | -167.4489 | 110.0785 | -20.0785 | -166.7347 | 164.4382 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-03-02 01:00 | 0 | 0 | 0 | 0 | -7.3557 | -152.447 | 108.846 | -18.846 | -151.0039 | 151.4471 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-03-02 02:00 | 0 | 0 | 0 | 0 | -7.3398 | -137.445 | 106.8115 | -16.8115 | -135.5166 | 137.398 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-03-02 03:00 | 0 | 0 | 0 | 0 | -7.3239 | -122.4431 | 104.1339 | -14.1339 | -120.3256 | 123.1016 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-03-02 04:00 | 0.13667 | 0.13667 | 0 | 0 | -7.3081 | -107.4411 | 101.0095 | -11.0095 | -105.4168 | 108.7519 | 0 | 0.1025 | 0.8 | 1 | 0.027333 | 0.12983 | -1.7 | -1.6959 | 1.0934 | 0.00011641
2016-03-02 05:00 | 0.27333 | 0.27333 | 0 | 0 | -7.2922 | -92.4392 | 97.6534 | -7.6534 | -90.7228 | 94.4401 | 0 | 0.205 | 0.8 | 1 | 0.054667 | 0.25967 | -0.1 | -0.091885 | 1.0878 | 0.00023163
2016-03-02 06:00 | 0.41 | 0.41 | 0 | 0 | -7.2763 | -77.4372 | 94.286 | -4.286 | -76.147 | 80.2466 | 0 | 0.3075 | 0.8 | 1 | 0.082 | 0.3895 | 0.1 | 0.11217 | 1.0871 | 0.00034721
2016-03-02 07:00 | 8.6133 | 8.5933 | 0.02 | 0 | -7.2604 | -62.4352 | 91.1232 | -1.1232 | -61.5881 | 66.2854 | 0 | 6.445 | 0.8 | 1 | 1.7227 | 8.1677 | -0.3 | -0.04476 | 1.0877 | 0.0072846
2016-03-02 08:00 | 16.8167 | 16.7767 | 0.04 | 0 | -7.2446 | -47.4333 | 88.3682 | 1.6318 | -46.9625 | 52.7682 | 0 | 12.5825 | 0.8 | 1 | 3.3633 | 15.9458 | -0.7 | -0.20169 | 1.0882 | 0.014229
2016-03-02 09:00 | 25.02 | 24.96 | 0.06 | 0.90574 | -7.2287 | -32.4313 | 86.2017 | 3.7983 | -32.2217 | 40.1674 | 0.69214 | 18.72 | 0.8 | 1 | 5.004 | 24.4161 | 0.5 | 1.263 | 1.0831 | 0.021685
2016-03-02 10:00 | 28.5433 | 28.5033 | 0.04 | 0.43888 | -7.2128 | -17.4293 | 84.7708 | 5.2292 | -17.3616 | 29.6921 | 0.38126 | 21.3775 | 0.8 | 1 | 5.7087 | 27.4674 | 0.8 | 1.6584 | 1.0817 | 0.024363
2016-03-02 11:00 | 32.0667 | 32.0467 | 0.02 | 0.19707 | -7.1969 | -2.4273 | 84.1751 | 5.8249 | -2.4207 | 24.2825 | 0.17963 | 24.035 | 0.8 | 1 | 6.4133 | 30.628 | 1.5 | 2.4571 | 1.0789 | 0.027097
2016-03-02 12:00 | 35.59 | 35.59 | 0 | 0 | -7.181 | 12.5747 | 84.4567 | 5.5433 | 12.534 | 27.1605 | 0 | 26.6925 | 0.8 | 1 | 7.118 | 33.8105 | 1.2 | 2.2566 | 1.0796 | 0.029932
2016-03-02 13:00 | 25.5333 | 25.5133 | 0.02 | 0.26035 | -7.1651 | 27.5766 | 85.5942 | 4.4058 | 27.4311 | 36.4097 | 0.20953 | 19.135 | 0.8 | 1 | 5.1067 | 24.4512 | 1.2 | 1.9641 | 1.0806 | 0.021667
2016-03-02 14:00 | 15.4767 | 15.4367 | 0.04 | 0 | -7.1492 | 42.5786 | 87.5056 | 2.4944 | 42.2199 | 48.5087 | 0 | 11.5775 | 0.8 | 1 | 3.0953 | 14.6728 | 0.6 | 1.0585 | 1.0838 | 0.01304
2016-03-02 15:00 | 5.42 | 5.36 | 0.06 | 0 | -7.1333 | 57.5806 | 90.058 | -0.058 | 56.889 | 61.7986 | 0 | 4.02 | 0.8 | 1 | 1.084 | 5.104 | 0.2 | 0.3595 | 1.0862 | 0.0045462
2016-03-02 16:00 | 3.6133 | 3.5733 | 0.04 | 0 | -7.1174 | 72.5826 | 93.0798 | -3.0798 | 71.4717 | 75.6444 | 0 | 2.68 | 0.8 | 1 | 0.72267 | 3.4027 | 0.8 | 0.90633 | 1.0843 | 0.0030255
2016-03-02 17:00 | 1.8067 | 1.7867 | 0.02 | 0 | -7.1015 | 87.5846 | 96.3736 | -6.3736 | 86.0406 | 89.7752 | 0 | 1.34 | 0.8 | 1 | 0.36133 | 1.7013 | 1.4 | 1.4532 | 1.0824 | 0.0015101
2016-03-02 18:00 | 0 | 0 | 0 | 0 | -7.0856 | 102.5867 | 99.7264 | -9.7264 | 100.692 | 104.0539 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.3 | 1.3 | 1.083 | 0
2016-03-02 19:00 | 0 | 0 | 0 | 0 | -7.0697 | 117.5887 | 102.9178 | -12.9178 | 115.5253 | 118.3926 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.4 | 1.4 | 1.0826 | 0
2016-03-02 20:00 | 0 | 0 | 0 | 0 | -7.0538 | 132.5907 | 105.7299 | -15.7299 | 130.6185 | 132.706 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.9 | 0.9 | 1.0843 | 0
2016-03-02 21:00 | 0 | 0 | 0 | 0 | -7.0378 | 147.5927 | 107.9586 | -17.9586 | 146.0038 | 146.8439 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.9 | 0.9 | 1.0843 | 0
2016-03-02 22:00 | 0 | 0 | 0 | 0 | -7.0219 | 162.5947 | 109.4314 | -19.4314 | 161.6503 | 160.3065 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.1 | 1.1 | 1.0837 | 0
2016-03-02 23:00 | 0 | 0 | 0 | 0 | -7.006 | 177.5968 | 110.0273 | -20.0273 | 177.4611 | 169.7664 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.2 | 1.2 | 1.0833 | 0
2016-03-03 | 0 | 0 | 0 | 0 | -6.9901 | -167.4012 | 109.6951 | -19.6951 | -166.7056 | 164.1582 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1 | 1 | 1.084 | 0
2016-03-03 01:00 | 0 | 0 | 0 | 0 | -6.9741 | -152.3992 | 108.4615 | -18.4615 | -150.9985 | 151.257 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.9 | 0.9 | 1.0843 | 0
2016-03-03 02:00 | 0 | 0 | 0 | 0 | -6.9582 | -137.3971 | 106.4272 | -16.4272 | -135.531 | 137.239 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-03-03 03:00 | 0 | 0 | 0 | 0 | -6.9423 | -122.3951 | 103.7504 | -13.7504 | -120.3546 | 122.9529 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-03-03 04:00 | 0.16 | 0.16 | 0 | 0 | -6.9263 | -107.393 | 100.6266 | -10.6266 | -105.4545 | 108.6036 | 0 | 0.12 | 0.8 | 1 | 0.032 | 0.152 | 0.4 | 0.40475 | 1.0861 | 0.00013537
2016-03-03 05:00 | 0.32 | 0.32 | 0 | 0 | -6.9104 | -92.391 | 97.2707 | -7.2707 | -90.7633 | 94.2853 | 0 | 0.24 | 0.8 | 1 | 0.064 | 0.304 | 0.5 | 0.5095 | 1.0857 | 0.00027065
2016-03-03 06:00 | 0.48 | 0.48 | 0 | 0 | -6.8944 | -77.3889 | 93.9029 | -3.9029 | -76.1846 | 80.079 | 0 | 0.36 | 0.8 | 1 | 0.096 | 0.456 | 0.6 | 0.61425 | 1.0854 | 0.00040583
2016-03-03 07:00 | 12 | 8.05 | 3.95 | 0 | -6.8785 | -62.3868 | 90.7394 | -0.73937 | -61.6174 | 66.0972 | 0 | 6.0375 | 0.8 | 1 | 2.4 | 8.4375 | 0.7 | 0.96367 | 1.0841 | 0.0075008
2016-03-03 08:00 | 23.52 | 15.62 | 7.9 | 0 | -6.8626 | -47.3848 | 87.9835 | 2.0165 | -46.9785 | 52.5482 | 0 | 11.715 | 0.8 | 1 | 4.704 | 16.419 | 0.5 | 1.0131 | 1.084 | 0.014594
2016-03-03 09:00 | 35.04 | 23.19 | 11.85 | 162.4426 | -6.8466 | -32.3827 | 85.8166 | 4.1834 | -32.2201 | 39.8982 | 124.6235 | 17.3925 | 0.8 | 1 | 7.008 | 149.024 | -0.2 | 4.457 | 1.0719 | 0.13099
2016-03-03 10:00 | 37.85 | 25.42 | 12.43 | 127.0673 | -6.8306 | -17.3806 | 84.3862 | 5.6138 | -17.3392 | 29.3529 | 110.754 | 19.065 | 0.8 | 1 | 7.57 | 137.389 | 0.7 | 4.9934 | 1.07 | 0.12055
2016-03-03 11:00 | 40.66 | 27.65 | 13.01 | 120.3182 | -6.8147 | -2.3786 | 83.7925 | 6.2075 | -2.3757 | 23.8974 | 110.0037 | 20.7375 | 0.8 | 1 | 8.132 | 138.8732 | 1 | 5.3398 | 1.0688 | 0.12171
2016-03-03 12:00 | 43.47 | 29.88 | 13.59 | 131.7031 | -6.7987 | 12.6235 | 84.0773 | 5.9227 | 12.6017 | 26.8433 | 117.5114 | 22.41 | 0.8 | 1 | 8.694 | 148.6154 | 0.5 | 5.1442 | 1.0695 | 0.13033
2016-03-03 13:00 | 30.94 | 21.7167 | 9.2233 | 110.6621 | -6.7828 | 27.6256 | 85.219 | 4.781 | 27.5198 | 36.1926 | 89.3085 | 16.2875 | 0.8 | 1 | 6.188 | 111.784 | 0.7 | 4.1932 | 1.0728 | 0.098338
2016-03-03 14:00 | 18.41 | 13.5533 | 4.8567 | 0 | -6.7668 | 42.6277 | 87.1352 | 2.8648 | 42.3266 | 48.3592 | 0 | 10.165 | 0.8 | 1 | 3.682 | 13.847 | 0.6 | 1.0327 | 1.0839 | 0.012307
2016-03-03 15:00 | 5.88 | 5.39 | 0.49 | 0 | -6.7508 | 57.6298 | 89.6918 | 0.30818 | 57.0097 | 61.6907 | 0 | 4.0425 | 0.8 | 1 | 1.176 | 5.2185 | 1.2 | 1.3631 | 1.0827 | 0.0046332
2016-03-03 16:00 | 3.92 | 3.5933 | 0.32667 | 0 | -6.7349 | 72.6319 | 92.7168 | -2.7168 | 71.602 | 75.5625 | 0 | 2.695 | 0.8 | 1 | 0.784 | 3.479 | 1.5 | 1.6087 | 1.0819 | 0.0030863
2016-03-03 17:00 | 1.96 | 1.7967 | 0.16333 | 0 | -6.7189 | 87.634 | 96.0121 | -6.0121 | 86.1758 | 89.7093 | 0 | 1.3475 | 0.8 | 1 | 0.392 | 1.7395 | 1.6 | 1.6544 | 1.0817 | 0.0015429
2016-03-03 18:00 | 0 | 0 | 0 | 0 | -6.7029 | 102.6361 | 99.3643 | -9.3643 | 100.8271 | 103.9968 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.4 | 1.4 | 1.0826 | 0
2016-03-03 19:00 | 0 | 0 | 0 | 0 | -6.6869 | 117.6382 | 102.5533 | -12.5533 | 115.6551 | 118.3371 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.6 | 1.6 | 1.0819 | 0
2016-03-03 20:00 | 0 | 0 | 0 | 0 | -6.671 | 132.6403 | 105.3613 | -15.3613 | 130.7373 | 132.6426 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.6 | 1.6 | 1.0819 | 0
2016-03-03 21:00 | 0 | 0 | 0 | 0 | -6.655 | 147.6424 | 107.5851 | -17.5851 | 146.1062 | 146.7548 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1 | 1 | 1.084 | 0
2016-03-03 22:00 | 0 | 0 | 0 | 0 | -6.639 | 162.6446 | 109.053 | -19.053 | 161.7315 | 160.1432 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.8 | 0.8 | 1.0847 | 0
2016-03-03 23:00 | 0 | 0 | 0 | 0 | -6.623 | 177.6467 | 109.6448 | -19.6448 | 177.5178 | 169.4037 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.8 | 0.8 | 1.0847 | 0
2016-03-04 | 0 | 0 | 0 | 0 | -6.607 | -167.3512 | 109.3099 | -19.3099 | -166.6743 | 163.8711 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.3 | 1.3 | 1.083 | 0
2016-03-04 01:00 | 0 | 0 | 0 | 0 | -6.591 | -152.349 | 108.0753 | -18.0753 | -150.9909 | 151.0606 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.6 | 1.6 | 1.0819 | 0
2016-03-04 02:00 | 0 | 0 | 0 | 0 | -6.575 | -137.3469 | 106.041 | -16.041 | -135.5432 | 137.075 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.7 | 1.7 | 1.0816 | 0
2016-03-04 03:00 | 0 | 0 | 0 | 0 | -6.559 | -122.3448 | 103.3647 | -13.3647 | -120.3815 | 122.8001 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-03-04 04:00 | 0.35333 | 0.34333 | 0.01 | 0 | -6.543 | -107.3426 | 100.2416 | -10.2416 | -105.4901 | 108.4517 | 0 | 0.2575 | 0.8 | 1 | 0.070667 | 0.32817 | 1.9 | 1.9103 | 1.0808 | 0.00029084
2016-03-04 05:00 | 0.70667 | 0.68667 | 0.02 | 0 | -6.527 | -92.3405 | 96.8859 | -6.8859 | -90.8018 | 94.1276 | 0 | 0.515 | 0.8 | 1 | 0.14133 | 0.65633 | 2 | 2.0205 | 1.0804 | 0.00058148
2016-03-04 06:00 | 1.06 | 1.03 | 0.03 | 0 | -6.511 | -77.3383 | 93.5179 | -3.5179 | -76.2202 | 79.9091 | 0 | 0.7725 | 0.8 | 1 | 0.212 | 0.9845 | 1.9 | 1.9308 | 1.0807 | 0.00087247
2016-03-04 07:00 | 8.9833 | 8.57 | 0.41333 | 0 | -6.495 | -62.3362 | 90.3535 | -0.35354 | -61.6447 | 65.9072 | 0 | 6.4275 | 0.8 | 1 | 1.7967 | 8.2242 | 0 | 0.25701 | 1.0866 | 0.0073278
2016-03-04 08:00 | 16.9067 | 16.11 | 0.79667 | 0 | -6.479 | -47.334 | 87.5968 | 2.4032 | -46.9925 | 52.3268 | 0 | 12.0825 | 0.8 | 1 | 3.3813 | 15.4638 | -0.7 | -0.21676 | 1.0883 | 0.013799
2016-03-04 09:00 | 24.83 | 23.65 | 1.18 | 14.8088 | -6.463 | -32.3318 | 85.4297 | 4.5703 | -32.2164 | 39.6278 | 11.4058 | 17.7375 | 0.8 | 1 | 4.966 | 34.1093 | -0.9 | 0.16592 | 1.0869 | 0.030401
2016-03-04 10:00 | 30.4 | 29.6133 | 0.78667 | 7.5258 | -6.447 | -17.3297 | 84 | 6 | -17.3145 | 29.0121 | 6.5815 | 22.21 | 0.8 | 1 | 6.08 | 34.8715 | -1 | 0.089734 | 1.0872 | 0.031088
2016-03-04 11:00 | 35.97 | 35.5767 | 0.39333 | 3.4264 | -6.4309 | -2.3275 | 83.4083 | 6.5917 | -2.3282 | 23.5105 | 3.142 | 26.6825 | 0.8 | 1 | 7.194 | 37.0185 | -0.8 | 0.35683 | 1.0863 | 0.032973
2016-03-04 12:00 | 41.54 | 41.54 | 0 | 0 | -6.4149 | 12.6747 | 83.6965 | 6.3035 | 12.6719 | 26.5275 | 0 | 31.155 | 0.8 | 1 | 8.308 | 39.463 | -1 | 0.23322 | 1.0867 | 0.035165
2016-03-04 13:00 | 30.3367 | 30.3267 | 0.01 | 0.11125 | -6.3989 | 27.6769 | 84.8426 | 5.1574 | 27.611 | 35.9786 | 0.090024 | 22.745 | 0.8 | 1 | 6.0673 | 28.9024 | -1.3 | -0.3968 | 1.0889 | 0.025807
2016-03-04 14:00 | 19.1333 | 19.1133 | 0.02 | 0.35425 | -6.3829 | 42.679 | 86.7635 | 3.2365 | 42.4359 | 48.2129 | 0.23606 | 14.335 | 0.8 | 1 | 3.8267 | 18.3977 | -1.4 | -0.82507 | 1.0904 | 0.01645
2016-03-04 15:00 | 7.93 | 7.9 | 0.03 | 0 | -6.3668 | 57.6812 | 89.3246 | 0.67542 | 57.133 | 61.5856 | 0 | 5.925 | 0.8 | 1 | 1.586 | 7.511 | -1.4 | -1.1653 | 1.0916 | 0.0067231
2016-03-04 16:00 | 5.2867 | 5.2667 | 0.02 | 0 | -6.3508 | 72.6834 | 92.3528 | -2.3528 | 71.7349 | 75.4829 | 0 | 3.95 | 0.8 | 1 | 1.0573 | 5.0073 | -1.4 | -1.2435 | 1.0919 | 0.0044832
2016-03-04 17:00 | 2.6433 | 2.6333 | 0.01 | 0 | -6.3348 | 87.6856 | 95.6495 | -5.6495 | 86.3135 | 89.6453 | 0 | 1.975 | 0.8 | 1 | 0.52867 | 2.5037 | -1.3 | -1.2218 | 1.0918 | 0.0022414
2016-03-04 18:00 | 0 | 0 | 0 | 0 | -6.3187 | 102.6878 | 99.0012 | -9.0012 | 100.9646 | 103.9408 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-03-04 19:00 | 0 | 0 | 0 | 0 | -6.3027 | 117.69 | 102.1877 | -12.1877 | 115.7871 | 118.282 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-03-04 20:00 | 0 | 0 | 0 | 0 | -6.2866 | 132.6922 | 104.9916 | -14.9916 | 130.8583 | 132.5786 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-03-04 21:00 | 0 | 0 | 0 | 0 | -6.2706 | 147.6944 | 107.2103 | -17.2103 | 146.2109 | 146.6636 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-03-04 22:00 | 0 | 0 | 0 | 0 | -6.2546 | 162.6966 | 108.6732 | -18.6732 | 161.8148 | 159.9752 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-03-04 23:00 | 0 | 0 | 0 | 0 | -6.2385 | 177.6989 | 109.2609 | -19.2609 | 177.5768 | 169.0384 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-03-05 | 0 | 0 | 0 | 0 | -6.2225 | -167.2989 | 108.9232 | -18.9232 | -166.6407 | 163.5774 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-03-05 01:00 | 0 | 0 | 0 | 0 | -6.2064 | -152.2967 | 107.6873 | -17.6873 | -150.981 | 150.858 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-03-05 02:00 | 0 | 0 | 0 | 0 | -6.1903 | -137.2945 | 105.6529 | -15.6529 | -135.5533 | 136.906 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-03-05 03:00 | 0 | 0 | 0 | 0 | -6.1743 | -122.2922 | 102.9772 | -12.9772 | -120.4063 | 122.6432 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-03-05 04:00 | 0.51 | 0.43333 | 0.076667 | 0 | -6.1582 | -107.29 | 99.8547 | -9.8547 | -105.5237 | 108.2966 | 0 | 0.325 | 0.8 | 1 | 0.102 | 0.427 | -0.1 | -0.086656 | 1.0878 | 0.00038088
2016-03-05 05:00 | 1.02 | 0.86667 | 0.15333 | 0 | -6.1422 | -92.2878 | 96.4992 | -6.4992 | -90.8383 | 93.9672 | 0 | 0.65 | 0.8 | 1 | 0.204 | 0.854 | -0.1 | -0.073313 | 1.0878 | 0.00076173
2016-03-05 06:00 | 1.53 | 1.3 | 0.23 | 0 | -6.1261 | -77.2855 | 93.1308 | -3.1308 | -76.2539 | 79.7368 | 0 | 0.975 | 0.8 | 1 | 0.306 | 1.281 | -1.6 | -1.56 | 1.093 | 0.0011481
2016-03-05 07:00 | 11.6067 | 9.5767 | 2.03 | 0 | -6.11 | -62.2833 | 89.9658 | 0.034176 | -61.67 | 65.7154 | 0 | 7.1825 | 0.8 | 1 | 2.3213 | 9.5038 | -1.9 | -1.603 | 1.0931 | 0.0085188
2016-03-05 08:00 | 21.6833 | 17.8533 | 3.83 | 0 | -6.094 | -47.281 | 87.2084 | 2.7916 | -47.0044 | 52.104 | 0 | 13.39 | 0.8 | 1 | 4.3367 | 17.7267 | -2.1 | -1.546 | 1.0929 | 0.015886
2016-03-05 09:00 | 31.76 | 26.13 | 5.63 | 65.1305 | -6.0779 | -32.2788 | 85.0411 | 4.9589 | -32.2106 | 39.3563 | 50.3601 | 19.5975 | 0.8 | 1 | 6.352 | 76.3096 | -2.3 | 0.084674 | 1.0872 | 0.068031
2016-03-05 10:00 | 37.3333 | 29.5167 | 7.8167 | 70.257 | -6.0618 | -17.2765 | 83.6122 | 6.3878 | -17.2876 | 28.6699 | 61.6434 | 22.1375 | 0.8 | 1 | 7.4667 | 91.2476 | -2.1 | 0.75149 | 1.0849 | 0.081173
2016-03-05 11:00 | 42.9067 | 32.9033 | 10.0033 | 82.3469 | -6.0457 | -2.2742 | 83.0226 | 6.9774 | -2.2785 | 23.122 | 75.7321 | 24.6775 | 0.8 | 1 | 8.5813 | 108.9909 | -1.9 | 1.506 | 1.0822 | 0.096722
2016-03-05 12:00 | 48.48 | 36.29 | 12.19 | 104.7052 | -6.0297 | 12.728 | 83.3143 | 6.6857 | 12.7445 | 26.2132 | 93.937 | 27.2175 | 0.8 | 1 | 9.696 | 130.8505 | -1.9 | 2.1891 | 1.0798 | 0.11586
2016-03-05 13:00 | 35.5633 | 26.8767 | 8.6867 | 90.0612 | -6.0136 | 27.7303 | 84.465 | 5.535 | 27.7049 | 35.768 | 73.0748 | 20.1575 | 0.8 | 1 | 7.1127 | 100.345 | -2.2 | 0.93578 | 1.0842 | 0.089213
2016-03-05 14:00 | 22.6467 | 17.4633 | 5.1833 | 82.3411 | -5.9975 | 42.7326 | 86.3909 | 3.6091 | 42.5477 | 48.07 | 55.0222 | 13.0975 | 0.8 | 1 | 4.5293 | 72.649 | -2.4 | -0.12972 | 1.088 | 0.064812
2016-03-05 15:00 | 9.73 | 8.05 | 1.68 | 0 | -5.9814 | 57.7348 | 88.9564 | 1.0436 | 57.2589 | 61.4834 | 0 | 6.0375 | 0.8 | 1 | 1.946 | 7.9835 | -2.4 | -2.1505 | 1.095 | 0.0071686
2016-03-05 16:00 | 6.4867 | 5.3667 | 1.12 | 0 | -5.9653 | 72.7371 | 91.9879 | -1.9879 | 71.8702 | 75.4056 | 0 | 4.025 | 0.8 | 1 | 1.2973 | 5.3223 | -2.5 | -2.3337 | 1.0957 | 0.0047818
2016-03-05 17:00 | 3.2433 | 2.6833 | 0.56 | 0 | -5.9492 | 87.7394 | 95.2861 | -5.2861 | 86.4535 | 89.583 | 0 | 2.0125 | 0.8 | 1 | 0.64867 | 2.6612 | -2 | -1.9168 | 1.0942 | 0.0023877
2016-03-05 18:00 | 0 | 0 | 0 | 0 | -5.9331 | 102.7417 | 98.6372 | -8.6372 | 101.1043 | 103.886 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-03-05 19:00 | 0 | 0 | 0 | 0 | -5.917 | 117.744 | 101.8211 | -11.8211 | 115.9213 | 118.2273 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-03-05 20:00 | 0 | 0 | 0 | 0 | -5.9009 | 132.7463 | 104.6208 | -14.6208 | 130.9815 | 132.5141 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-03-05 21:00 | 0 | 0 | 0 | 0 | -5.8848 | 147.7486 | 106.8344 | -16.8344 | 146.3175 | 146.5702 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-03-05 22:00 | 0 | 0 | 0 | 0 | -5.8687 | 162.7509 | 108.2921 | -18.2921 | 161.9003 | 159.8023 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.4 | -3.4 | 1.0994 | 0
2016-03-05 23:00 | 0 | 0 | 0 | 0 | -5.8526 | 177.7532 | 108.8755 | -18.8755 | 177.6378 | 168.6706 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-03-06 | 0 | 0 | 0 | 0 | -5.8365 | -167.2445 | 108.5349 | -18.5349 | -166.605 | 163.2774 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-03-06 01:00 | 0 | 0 | 0 | 0 | -5.8204 | -152.2422 | 107.2976 | -17.2976 | -150.969 | 150.6495 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-03-06 02:00 | 0 | 0 | 0 | 0 | -5.8043 | -137.2399 | 105.2632 | -15.2632 | -135.5613 | 136.7321 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-03-06 03:00 | 0 | 0 | 0 | 0 | -5.7882 | -122.2375 | 102.588 | -12.588 | -120.429 | 122.4825 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-03-06 04:00 | 0.68333 | 0.66333 | 0.02 | 0 | -5.7721 | -107.2352 | 99.466 | -9.466 | -105.5554 | 108.1382 | 0 | 0.4975 | 0.8 | 1 | 0.13667 | 0.63417 | -4.8 | -4.7802 | 1.1042 | 0.00057422
2016-03-06 05:00 | 1.3667 | 1.3267 | 0.04 | 0 | -5.756 | -92.2329 | 96.1107 | -6.1107 | -90.873 | 93.804 | 0 | 0.995 | 0.8 | 1 | 0.27333 | 1.2683 | -4.6 | -4.5604 | 1.1035 | 0.0011476
2016-03-06 06:00 | 2.05 | 1.99 | 0.06 | 0 | -5.7398 | -77.2306 | 92.742 | -2.742 | -76.2857 | 79.5625 | 0 | 1.4925 | 0.8 | 1 | 0.41 | 1.9025 | -5.2 | -5.1405 | 1.1055 | 0.0017246
2016-03-06 07:00 | 20.6 | 11.8233 | 8.7767 | 0 | -5.7237 | -62.2282 | 89.5764 | 0.42365 | -61.6935 | 65.5219 | 0 | 8.8675 | 0.8 | 1 | 4.12 | 12.9875 | -6 | -5.5941 | 1.1071 | 0.01179
2016-03-06 08:00 | 39.15 | 21.6567 | 17.4933 | 315.1808 | -5.7076 | -47.2259 | 86.8183 | 3.1817 | -47.0144 | 51.8801 | 194.5641 | 16.2425 | 0.8 | 1 | 7.83 | 218.6366 | -6.2 | 0.63239 | 1.0853 | 0.19457
2016-03-06 09:00 | 57.7 | 31.49 | 26.21 | 281.1476 | -5.6915 | -32.2235 | 84.6508 | 5.3492 | -32.2027 | 39.0838 | 218.2335 | 23.6175 | 0.8 | 1 | 11.54 | 253.391 | -6.7 | 1.2185 | 1.0832 | 0.22508
2016-03-06 10:00 | 65.1467 | 34.1933 | 30.9533 | 262.2987 | -5.6753 | -17.2212 | 83.2229 | 6.7771 | -17.2585 | 28.3264 | 230.8907 | 25.645 | 0.8 | 1 | 13.0293 | 269.565 | -6 | 2.4239 | 1.079 | 0.23851
2016-03-06 11:00 | 72.5933 | 36.8967 | 35.6967 | 278.4895 | -5.6592 | -2.2189 | 82.6356 | 7.3644 | -2.2264 | 22.7319 | 256.8573 | 27.6725 | 0.8 | 1 | 14.5187 | 299.0485 | -5.7 | 3.6453 | 1.0747 | 0.26355
2016-03-06 12:00 | 80.04 | 39.6 | 40.44 | 328.6088 | -5.6431 | 12.7835 | 82.931 | 7.069 | 12.8196 | 25.9008 | 295.6006 | 29.7 | 0.8 | 1 | 16.008 | 341.3086 | -5.3 | 5.3659 | 1.0687 | 0.29911
2016-03-06 13:00 | 58.2867 | 29.67 | 28.6167 | 277.7548 | -5.6269 | 27.7859 | 84.0864 | 5.9136 | 27.8011 | 35.5608 | 225.9533 | 22.2525 | 0.8 | 1 | 11.6573 | 259.8632 | -6.5 | 1.6207 | 1.0818 | 0.23052
2016-03-06 14:00 | 36.5333 | 19.74 | 16.7933 | 241.7838 | -5.6108 | 42.7882 | 86.0173 | 3.9827 | 42.662 | 47.9303 | 162.0033 | 14.805 | 0.8 | 1 | 7.3067 | 184.115 | -6.6 | -0.84641 | 1.0905 | 0.16463
2016-03-06 15:00 | 14.78 | 9.81 | 4.97 | 0 | -5.5947 | 57.7906 | 88.5873 | 1.4127 | 57.3871 | 61.3839 | 0 | 7.3575 | 0.8 | 1 | 2.956 | 10.3135 | -6.5 | -6.1777 | 1.1091 | 0.0093799
2016-03-06 16:00 | 9.8533 | 6.54 | 3.3133 | 0 | -5.5785 | 72.7929 | 91.6221 | -1.6221 | 72.0079 | 75.3305 | 0 | 4.905 | 0.8 | 1 | 1.9707 | 6.8757 | -6.4 | -6.1851 | 1.1091 | 0.0062534
2016-03-06 17:00 | 4.9267 | 3.27 | 1.6567 | 0 | -5.5624 | 87.7953 | 94.9219 | -4.9219 | 86.5958 | 89.5224 | 0 | 2.4525 | 0.8 | 1 | 0.98533 | 3.4378 | -5.9 | -5.7926 | 1.1078 | 0.0031228
2016-03-06 18:00 | 0 | 0 | 0 | 0 | -5.5462 | 102.7977 | 98.2724 | -8.2724 | 101.2462 | 103.8322 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.8 | -6.8 | 1.1113 | 0
2016-03-06 19:00 | 0 | 0 | 0 | 0 | -5.5301 | 117.8001 | 101.4536 | -11.4536 | 116.0575 | 118.1729 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.6 | -7.6 | 1.1141 | 0
2016-03-06 20:00 | 0 | 0 | 0 | 0 | -5.5139 | 132.8024 | 104.249 | -14.249 | 131.1067 | 132.4488 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.8 | -8.8 | 1.1183 | 0
2016-03-06 21:00 | 0 | 0 | 0 | 0 | -5.4978 | 147.8048 | 106.4574 | -16.4574 | 146.4262 | 146.4745 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8 | -8 | 1.1155 | 0
2016-03-06 22:00 | 0 | 0 | 0 | 0 | -5.4816 | 162.8072 | 107.9099 | -17.9099 | 161.9877 | 159.6248 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.8 | -7.8 | 1.1148 | 0
2016-03-06 23:00 | 0 | 0 | 0 | 0 | -5.4655 | 177.8096 | 108.4889 | -18.4889 | 177.7008 | 168.3006 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.5 | -8.5 | 1.1173 | 0
2016-03-07 | 0 | 0 | 0 | 0 | -5.4493 | -167.188 | 108.1453 | -18.1453 | -166.5673 | 162.9714 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.7 | -8.7 | 1.1179 | 0
2016-03-07 01:00 | 0 | 0 | 0 | 0 | -5.4332 | -152.1856 | 106.9065 | -16.9065 | -150.955 | 150.435 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.1 | -8.1 | 1.1159 | 0
2016-03-07 02:00 | 0 | 0 | 0 | 0 | -5.417 | -137.1832 | 104.8718 | -14.8718 | -135.5672 | 136.5536 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-03-07 03:00 | 0 | 0 | 0 | 0 | -5.4008 | -122.1808 | 102.197 | -12.197 | -120.4497 | 122.3179 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.3 | -4.3 | 1.1025 | 0
2016-03-07 04:00 | 1.0467 | 0.81 | 0.23667 | 0 | -5.3847 | -107.1784 | 99.0755 | -9.0755 | -105.5851 | 107.9767 | 0 | 0.6075 | 0.8 | 1 | 0.20933 | 0.81683 | -4 | -3.9745 | 1.1014 | 0.00073773
2016-03-07 05:00 | 2.0933 | 1.62 | 0.47333 | 0 | -5.3685 | -92.176 | 95.7205 | -5.7205 | -90.9057 | 93.6384 | 0 | 1.215 | 0.8 | 1 | 0.41867 | 1.6337 | -3.6 | -3.5489 | 1.0999 | 0.0014735
2016-03-07 06:00 | 3.14 | 2.43 | 0.71 | 0 | -5.3523 | -77.1735 | 92.3515 | -2.3515 | -76.3157 | 79.3861 | 0 | 1.8225 | 0.8 | 1 | 0.628 | 2.4505 | -2.4 | -2.3234 | 1.0956 | 0.0022016
2016-03-07 07:00 | 19.7733 | 12.39 | 7.3833 | 0 | -5.3362 | -62.1711 | 89.1853 | 0.81475 | -61.7151 | 65.327 | 0 | 9.2925 | 0.8 | 1 | 3.9547 | 13.2472 | -2 | -1.586 | 1.0931 | 0.011873
2016-03-07 08:00 | 36.4067 | 22.35 | 14.0567 | 225.5319 | -5.32 | -47.1687 | 86.4266 | 3.5734 | -47.0226 | 51.6551 | 139.9187 | 16.7625 | 0.8 | 1 | 7.2813 | 163.9625 | -2.2 | 2.9238 | 1.0773 | 0.14484
2016-03-07 09:00 | 53.04 | 32.31 | 20.73 | 207.2388 | -5.3038 | -32.1663 | 84.2591 | 5.7409 | -32.1929 | 38.8107 | 161.4848 | 24.2325 | 0.8 | 1 | 10.608 | 196.3253 | -2.1 | 4.0352 | 1.0734 | 0.1728
2016-03-07 10:00 | 58.79 | 34.98 | 23.81 | 190.8222 | -5.2876 | -17.1639 | 82.8322 | 7.1678 | -17.2274 | 27.9818 | 168.5144 | 26.235 | 0.8 | 1 | 11.758 | 206.5074 | -2.2 | 4.2534 | 1.0726 | 0.18163
2016-03-07 11:00 | 64.54 | 37.65 | 26.89 | 199.3378 | -5.2715 | -2.1614 | 82.2474 | 7.7526 | -2.1721 | 22.3405 | 184.3758 | 28.2375 | 0.8 | 1 | 12.908 | 225.5213 | -2.7 | 4.3475 | 1.0723 | 0.19829
2016-03-07 12:00 | 70.29 | 40.32 | 29.97 | 231.0363 | -5.2553 | 12.841 | 82.5466 | 7.4534 | 12.8969 | 25.5903 | 208.3729 | 30.24 | 0.8 | 1 | 14.058 | 252.6709 | -3 | 4.896 | 1.0704 | 0.22177
2016-03-07 13:00 | 52.3067 | 30.5833 | 21.7233 | 198.1762 | -5.2391 | 27.8435 | 83.7068 | 6.2932 | 27.8998 | 35.3571 | 161.6248 | 22.9375 | 0.8 | 1 | 10.4613 | 195.0236 | -2.2 | 3.8945 | 1.0739 | 0.17173
2016-03-07 14:00 | 34.3233 | 20.8467 | 13.4767 | 177.3845 | -5.2229 | 42.8459 | 85.6428 | 4.3572 | 42.7787 | 47.7941 | 119.1665 | 15.635 | 0.8 | 1 | 6.8647 | 141.6662 | -2.5 | 1.9271 | 1.0808 | 0.12555
2016-03-07 15:00 | 16.34 | 11.11 | 5.23 | 0 | -5.2067 | 57.8483 | 88.2175 | 1.7825 | 57.5177 | 61.2873 | 0 | 8.3325 | 0.8 | 1 | 3.268 | 11.6005 | -2.4 | -2.0375 | 1.0946 | 0.010413
2016-03-07 16:00 | 10.8933 | 7.4067 | 3.4867 | 0 | -5.1905 | 72.8508 | 91.2557 | -1.2557 | 72.1478 | 75.2578 | 0 | 5.555 | 0.8 | 1 | 2.1787 | 7.7337 | -3.2 | -2.9583 | 1.0979 | 0.0069622
2016-03-07 17:00 | 5.4467 | 3.7033 | 1.7433 | 0 | -5.1743 | 87.8533 | 94.5569 | -4.5569 | 86.7402 | 89.4634 | 0 | 2.7775 | 0.8 | 1 | 1.0893 | 3.8668 | -3.9 | -3.7792 | 1.1007 | 0.0034902
2016-03-07 18:00 | 0 | 0 | 0 | 0 | -5.1581 | 102.8557 | 97.9068 | -7.9068 | 101.3902 | 103.7795 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-03-07 19:00 | 0 | 0 | 0 | 0 | -5.1419 | 117.8582 | 101.0854 | -11.0854 | 116.1958 | 118.1188 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-03-07 20:00 | 0 | 0 | 0 | 0 | -5.1258 | 132.8606 | 103.8764 | -13.8764 | 131.2337 | 132.3828 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.2 | -2.2 | 1.0952 | 0
2016-03-07 21:00 | 0 | 0 | 0 | 0 | -5.1096 | 147.8631 | 106.0795 | -16.0795 | 146.5367 | 146.3765 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-03-07 22:00 | 0 | 0 | 0 | 0 | -5.0934 | 162.8656 | 107.5266 | -17.5266 | 162.0771 | 159.4425 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-03-07 23:00 | 0 | 0 | 0 | 0 | -5.0772 | 177.868 | 108.1011 | -18.1011 | 177.7658 | 167.9285 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-03-08 | 0 | 0 | 0 | 0 | -5.0609 | -167.1295 | 107.7544 | -17.7544 | -166.5276 | 162.6597 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-03-08 01:00 | 0 | 0 | 0 | 0 | -5.0447 | -152.127 | 106.5141 | -16.5141 | -150.9391 | 150.215 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-03-08 02:00 | 0 | 0 | 0 | 0 | -5.0285 | -137.1245 | 104.479 | -14.479 | -135.5713 | 136.3706 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-03-08 03:00 | 0 | 0 | 0 | 0 | -5.0123 | -122.122 | 101.8046 | -11.8046 | -120.4686 | 122.1496 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-03-08 04:00 | 1.0133 | 0.82667 | 0.18667 | 0 | -4.9961 | -107.1195 | 98.6836 | -8.6836 | -105.613 | 107.8122 | 0 | 0.62 | 0.8 | 1 | 0.20267 | 0.82267 | -1.9 | -1.8743 | 1.0941 | 0.00073804
2016-03-08 05:00 | 2.0267 | 1.6533 | 0.37333 | 0 | -4.9799 | -92.117 | 95.3287 | -5.3287 | -90.9367 | 93.4703 | 0 | 1.24 | 0.8 | 1 | 0.40533 | 1.6453 | -1.4 | -1.3486 | 1.0922 | 0.0014736
2016-03-08 06:00 | 3.04 | 2.48 | 0.56 | 0 | -4.9637 | -77.1146 | 91.9595 | -1.9595 | -76.3439 | 79.2078 | 0 | 1.86 | 0.8 | 1 | 0.608 | 2.468 | -1.1 | -1.0229 | 1.0911 | 0.0022081
2016-03-08 07:00 | 17.26 | 14.8533 | 2.4067 | 0 | -4.9475 | -62.1121 | 88.7926 | 1.2074 | -61.735 | 65.1306 | 0 | 11.14 | 0.8 | 1 | 3.452 | 14.592 | -0.9 | -0.444 | 1.0891 | 0.013031
2016-03-08 08:00 | 31.48 | 27.2267 | 4.2533 | 61.4882 | -4.9313 | -47.1095 | 86.0335 | 3.9665 | -47.0289 | 51.4292 | 38.3368 | 20.42 | 0.8 | 1 | 6.296 | 65.0528 | -2.6 | -0.5671 | 1.0895 | 0.058117
2016-03-08 09:00 | 45.7 | 39.6 | 6.1 | 57.0879 | -4.915 | -32.107 | 83.8661 | 6.1339 | -32.1811 | 38.5369 | 44.6545 | 29.7 | 0.8 | 1 | 9.14 | 83.4945 | -1.4 | 1.2092 | 1.0833 | 0.074166
2016-03-08 10:00 | 48.34 | 39.4167 | 8.9233 | 67.8274 | -4.8988 | -17.1045 | 82.4403 | 7.5597 | -17.1942 | 27.6363 | 60.089 | 29.5625 | 0.8 | 1 | 9.668 | 99.3195 | -1.1 | 2.0037 | 1.0805 | 0.087997
2016-03-08 11:00 | 50.98 | 39.2333 | 11.7467 | 82.9409 | -4.8826 | -2.102 | 81.858 | 8.142 | -2.1157 | 21.9478 | 76.9298 | 29.425 | 0.8 | 1 | 10.196 | 116.5508 | -1.2 | 2.4422 | 1.079 | 0.10312
2016-03-08 12:00 | 53.62 | 39.05 | 14.57 | 106.8286 | -4.8664 | 12.9005 | 82.1612 | 7.8388 | 12.9765 | 25.282 | 96.5962 | 29.2875 | 0.8 | 1 | 10.724 | 136.6077 | -0.4 | 3.869 | 1.074 | 0.1203
2016-03-08 13:00 | 40.6233 | 30.3533 | 10.27 | 88.3714 | -4.8501 | 27.903 | 83.3263 | 6.6737 | 28.0007 | 35.1571 | 72.2503 | 22.765 | 0.8 | 1 | 8.1247 | 103.14 | -0.5 | 2.7231 | 1.078 | 0.091169
2016-03-08 14:00 | 27.6267 | 21.6567 | 5.97 | 72.3615 | -4.8339 | 42.9055 | 85.2676 | 4.7324 | 42.8977 | 47.6612 | 48.7364 | 16.2425 | 0.8 | 1 | 5.5253 | 70.5042 | -1 | 1.2033 | 1.0833 | 0.062629
2016-03-08 15:00 | 14.63 | 12.96 | 1.67 | 0 | -4.8177 | 57.9081 | 87.847 | 2.153 | 57.6505 | 61.1936 | 0 | 9.72 | 0.8 | 1 | 2.926 | 12.646 | -0.9 | -0.50481 | 1.0893 | 0.011295
2016-03-08 16:00 | 9.7533 | 8.64 | 1.1133 | 0 | -4.8014 | 72.9106 | 90.8886 | -0.88856 | 72.2899 | 75.1873 | 0 | 6.48 | 0.8 | 1 | 1.9507 | 8.4307 | -1 | -0.73654 | 1.0901 | 0.0075359
2016-03-08 17:00 | 4.8767 | 4.32 | 0.55667 | 0 | -4.7852 | 87.9131 | 94.1914 | -4.1914 | 86.8867 | 89.4061 | 0 | 3.24 | 0.8 | 1 | 0.97533 | 4.2153 | -1.8 | -1.6683 | 1.0933 | 0.0037792
2016-03-08 18:00 | 0 | 0 | 0 | 0 | -4.769 | 102.9157 | 97.5406 | -7.5406 | 101.5361 | 103.7278 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-03-08 19:00 | 0 | 0 | 0 | 0 | -4.7527 | 117.9182 | 100.7164 | -10.7164 | 116.3359 | 118.0648 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2 | -2 | 1.0945 | 0
2016-03-08 20:00 | 0 | 0 | 0 | 0 | -4.7365 | 132.9207 | 103.503 | -13.503 | 131.3626 | 132.3159 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.4 | -3.4 | 1.0994 | 0
2016-03-08 21:00 | 0 | 0 | 0 | 0 | -4.7203 | 147.9233 | 105.7007 | -15.7007 | 146.6491 | 146.2761 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-03-08 22:00 | 0 | 0 | 0 | 0 | -4.704 | 162.9258 | 107.1424 | -17.1424 | 162.1682 | 159.2556 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3 | -3 | 1.098 | 0
2016-03-08 23:00 | 0 | 0 | 0 | 0 | -4.6878 | 177.9284 | 107.7123 | -17.7123 | 177.8325 | 167.5544 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.8 | -3.8 | 1.1008 | 0
2016-03-09 | 0 | 0 | 0 | 0 | -4.6715 | -167.069 | 107.3624 | -17.3624 | -166.4861 | 162.3428 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.6 | -3.6 | 1.1001 | 0
2016-03-09 01:00 | 0 | 0 | 0 | 0 | -4.6553 | -152.0665 | 106.1203 | -16.1203 | -150.9213 | 149.9895 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-03-09 02:00 | 0 | 0 | 0 | 0 | -4.639 | -137.0639 | 104.0848 | -14.0848 | -135.5734 | 136.1831 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-03-09 03:00 | 0 | 0 | 0 | 0 | -4.6228 | -122.0614 | 101.4107 | -11.4107 | -120.4856 | 121.9778 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2 | -2 | 1.0945 | 0
2016-03-09 04:00 | 1.1033 | 1.01 | 0.093333 | 0 | -4.6065 | -107.0588 | 98.2902 | -8.2902 | -105.6391 | 107.6448 | 0 | 0.7575 | 0.8 | 1 | 0.22067 | 0.97817 | -2 | -1.9694 | 1.0944 | 0.00087781
2016-03-09 05:00 | 2.2067 | 2.02 | 0.18667 | 0 | -4.5903 | -92.0562 | 94.9355 | -4.9355 | -90.9659 | 93.2999 | 0 | 1.515 | 0.8 | 1 | 0.44133 | 1.9563 | -1.7 | -1.6389 | 1.0932 | 0.0017538
2016-03-09 06:00 | 3.31 | 3.03 | 0.28 | 0 | -4.574 | -77.0536 | 91.566 | -1.566 | -76.3704 | 79.0278 | 0 | 2.2725 | 0.8 | 1 | 0.662 | 2.9345 | -1.6 | -1.5083 | 1.0928 | 0.0026295
2016-03-09 07:00 | 21.4933 | 14.5067 | 6.9867 | 0 | -4.5578 | -62.0511 | 88.3986 | 1.6014 | -61.7531 | 64.933 | 0 | 10.88 | 0.8 | 1 | 4.2987 | 15.1787 | -1.6 | -1.1257 | 1.0914 | 0.013585
2016-03-09 08:00 | 39.6767 | 25.9833 | 13.6933 | 180.0821 | -4.5415 | -47.0485 | 85.6391 | 4.3609 | -47.0334 | 51.2025 | 112.8339 | 19.4875 | 0.8 | 1 | 7.9353 | 140.2568 | -1.8 | 2.583 | 1.0785 | 0.12403
2016-03-09 09:00 | 57.86 | 37.46 | 20.4 | 179.4312 | -4.5252 | -32.0459 | 83.4718 | 6.5282 | -32.1675 | 38.2627 | 140.8856 | 28.095 | 0.8 | 1 | 11.572 | 180.5526 | -1.6 | 4.0423 | 1.0734 | 0.15891
2016-03-09 10:00 | 59.6067 | 39.78 | 19.8267 | 143.3013 | -4.509 | -17.0433 | 82.0472 | 7.9528 | -17.159 | 27.2899 | 127.3516 | 29.835 | 0.8 | 1 | 11.9213 | 169.1079 | -1.6 | 3.6846 | 1.0746 | 0.14901
2016-03-09 11:00 | 61.3533 | 42.1 | 19.2533 | 129.7674 | -4.4927 | -2.0407 | 81.4676 | 8.5324 | -2.0572 | 21.5539 | 120.6931 | 31.575 | 0.8 | 1 | 12.2707 | 164.5388 | -2 | 3.1418 | 1.0765 | 0.14524
2016-03-09 12:00 | 63.1 | 44.42 | 18.68 | 130.5723 | -4.4764 | 12.9619 | 81.7749 | 8.2251 | 13.0583 | 24.9761 | 118.3617 | 33.315 | 0.8 | 1 | 12.62 | 164.2967 | -1.9 | 3.2343 | 1.0762 | 0.14499
2016-03-09 13:00 | 47.0433 | 33.77 | 13.2733 | 108.0714 | -4.4602 | 27.9645 | 82.9451 | 7.0549 | 28.1038 | 34.9609 | 88.5693 | 25.3275 | 0.8 | 1 | 9.4087 | 123.3054 | -1.7 | 2.1533 | 1.08 | 0.1092
2016-03-09 14:00 | 30.9867 | 23.12 | 7.8667 | 88.3513 | -4.4439 | 42.9671 | 84.8917 | 5.1083 | 43.0188 | 47.5318 | 59.6531 | 17.34 | 0.8 | 1 | 6.1973 | 83.1905 | -2.2 | 0.3997 | 1.0861 | 0.07409
2016-03-09 15:00 | 14.93 | 12.47 | 2.46 | 0 | -4.4276 | 57.9697 | 87.4759 | 2.5241 | 57.7855 | 61.1027 | 0 | 9.3525 | 0.8 | 1 | 2.986 | 12.3385 | -3.3 | -2.9144 | 1.0977 | 0.011106
2016-03-09 16:00 | 9.9533 | 8.3133 | 1.64 | 0 | -4.4114 | 72.9723 | 90.5209 | -0.52092 | 72.434 | 75.1189 | 0 | 6.235 | 0.8 | 1 | 1.9907 | 8.2257 | -3.7 | -3.4429 | 1.0996 | 0.0074165
2016-03-09 17:00 | 4.9767 | 4.1567 | 0.82 | 0 | -4.3951 | 87.9749 | 93.8253 | -3.8253 | 87.0351 | 89.3504 | 0 | 3.1175 | 0.8 | 1 | 0.99533 | 4.1128 | -3.6 | -3.4715 | 1.0997 | 0.0037086
2016-03-09 18:00 | 0 | 0 | 0 | 0 | -4.3788 | 102.9775 | 97.1738 | -7.1738 | 101.6839 | 103.6769 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-03-09 19:00 | 0 | 0 | 0 | 0 | -4.3625 | 117.9801 | 100.3468 | -10.3468 | 116.4777 | 118.011 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-03-09 20:00 | 0 | 0 | 0 | 0 | -4.3463 | 132.9827 | 103.1289 | -13.1289 | 131.4932 | 132.2481 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-03-09 21:00 | 0 | 0 | 0 | 0 | -4.33 | 147.9853 | 105.3212 | -15.3212 | 146.7631 | 146.1732 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.3 | -6.3 | 1.1096 | 0
2016-03-09 22:00 | 0 | 0 | 0 | 0 | -4.3137 | 162.988 | 106.7573 | -16.7573 | 162.261 | 159.0642 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.7 | -6.7 | 1.111 | 0
2016-03-09 23:00 | 0 | 0 | 0 | 0 | -4.2974 | 177.9906 | 107.3225 | -17.3225 | 177.901 | 167.1784 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.2 | -6.2 | 1.1092 | 0
2016-03-10 | 0 | 0 | 0 | 0 | -4.2811 | -167.0068 | 106.9692 | -16.9692 | -166.4429 | 162.021 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.7 | -5.7 | 1.1075 | 0
2016-03-10 01:00 | 0 | 0 | 0 | 0 | -4.2649 | -152.0041 | 105.7255 | -15.7255 | -150.9017 | 149.7587 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-03-10 02:00 | 0 | 0 | 0 | 0 | -4.2486 | -137.0015 | 103.6895 | -13.6895 | -135.5738 | 135.9914 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.9 | -5.9 | 1.1081 | 0
2016-03-10 03:00 | 0 | 0 | 0 | 0 | -4.2323 | -121.9989 | 101.0156 | -11.0156 | -120.5009 | 121.8025 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-03-10 04:00 | 1.7933 | 1.4033 | 0.39 | 0 | -4.216 | -106.9962 | 97.8954 | -7.8954 | -105.6636 | 107.4746 | 0 | 1.0525 | 0.8 | 1 | 0.35867 | 1.4112 | -6.4 | -6.3559 | 1.1097 | 0.0012841
2016-03-10 05:00 | 3.5867 | 2.8067 | 0.78 | 0 | -4.1997 | -91.9936 | 94.5409 | -4.5409 | -90.9935 | 93.1273 | 0 | 2.105 | 0.8 | 1 | 0.71733 | 2.8223 | -5.7 | -5.6118 | 1.1071 | 0.0025623
2016-03-10 06:00 | 5.38 | 4.21 | 1.17 | 0 | -4.1834 | -76.9909 | 91.1712 | -1.1712 | -76.3953 | 78.846 | 0 | 3.1575 | 0.8 | 1 | 1.076 | 4.2335 | -5.7 | -5.5677 | 1.107 | 0.0038429
2016-03-10 07:00 | 23.5133 | 15.2467 | 8.2667 | 0 | -4.1671 | -61.9883 | 88.0034 | 1.9966 | -61.7696 | 64.7342 | 0 | 11.435 | 0.8 | 1 | 4.7027 | 16.1377 | -5.7 | -5.1957 | 1.1057 | 0.014631
2016-03-10 08:00 | 41.6467 | 26.2833 | 15.3633 | 185.2723 | -4.1508 | -46.9856 | 85.2434 | 4.7566 | -47.0362 | 50.9753 | 116.6578 | 19.7125 | 0.8 | 1 | 8.3293 | 144.6996 | -6 | -1.4781 | 1.0927 | 0.12965
2016-03-10 09:00 | 59.78 | 37.32 | 22.46 | 186.3183 | -4.1345 | -31.983 | 83.0764 | 6.9236 | -32.1522 | 37.9883 | 146.8442 | 27.99 | 0.8 | 1 | 11.956 | 186.7902 | -5.6 | 0.23719 | 1.0867 | 0.16644
2016-03-10 10:00 | 67.19 | 40.4433 | 26.7467 | 184.2505 | -4.1182 | -16.9803 | 81.6532 | 8.3468 | -17.122 | 26.9429 | 164.2517 | 30.3325 | 0.8 | 1 | 13.438 | 208.0222 | -6 | 0.50069 | 1.0857 | 0.1852
2016-03-10 11:00 | 74.6 | 43.5667 | 31.0333 | 200.0631 | -4.1019 | -1.9776 | 81.0764 | 8.9236 | -1.9968 | 21.159 | 186.5753 | 32.675 | 0.8 | 1 | 14.92 | 234.1703 | -5.7 | 1.6178 | 1.0818 | 0.20773
2016-03-10 12:00 | 82.01 | 46.69 | 35.32 | 235.8671 | -4.0856 | 13.025 | 81.3878 | 8.6122 | 13.1421 | 24.6727 | 214.3341 | 35.0175 | 0.8 | 1 | 16.402 | 265.7536 | -4.9 | 3.4048 | 1.0756 | 0.23439
2016-03-10 13:00 | 64.4433 | 36.3233 | 28.12 | 217.2571 | -4.0693 | 28.0277 | 82.5632 | 7.4368 | 28.209 | 34.7685 | 178.4687 | 27.2425 | 0.8 | 1 | 12.8887 | 218.5999 | -4.1 | 2.7312 | 1.0779 | 0.19322
2016-03-10 14:00 | 46.8767 | 25.9567 | 20.92 | 218.8731 | -4.053 | 43.0304 | 84.5153 | 5.4847 | 43.1421 | 47.4058 | 148.1336 | 19.4675 | 0.8 | 1 | 9.3753 | 176.9764 | -4.7 | 0.83051 | 1.0846 | 0.1574
2016-03-10 15:00 | 29.31 | 15.59 | 13.72 | 0 | -4.0367 | 58.033 | 87.1043 | 2.8957 | 57.9225 | 61.0145 | 0 | 11.6925 | 0.8 | 1 | 5.862 | 17.5545 | -6.3 | -5.7514 | 1.1076 | 0.015944
2016-03-10 16:00 | 19.54 | 10.3933 | 9.1467 | 0 | -4.0204 | 73.0357 | 90.1528 | -0.15282 | 72.5801 | 75.0528 | 0 | 7.795 | 0.8 | 1 | 3.908 | 11.703 | -6.1 | -5.7343 | 1.1076 | 0.010629
2016-03-10 17:00 | 9.77 | 5.1967 | 4.5733 | 0 | -4.0041 | 88.0384 | 93.4587 | -3.4587 | 87.1854 | 89.2962 | 0 | 3.8975 | 0.8 | 1 | 1.954 | 5.8515 | -5.6 | -5.4171 | 1.1065 | 0.005309
2016-03-10 18:00 | 0 | 0 | 0 | 0 | -3.9878 | 103.0411 | 96.8066 | -6.8066 | 101.8334 | 103.627 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.4 | -6.4 | 1.1099 | 0
2016-03-10 19:00 | 0 | 0 | 0 | 0 | -3.9715 | 118.0438 | 99.9767 | -9.9767 | 116.6213 | 117.9573 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.3 | -5.3 | 1.106 | 0
2016-03-10 20:00 | 0 | 0 | 0 | 0 | -3.9552 | 133.0465 | 102.7542 | -12.7542 | 131.6254 | 132.1794 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.1033 | 0
2016-03-10 21:00 | 0 | 0 | 0 | 0 | -3.9389 | 148.0491 | 104.9409 | -14.9409 | 146.8786 | 146.0679 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.105 | 0
2016-03-10 22:00 | 0 | 0 | 0 | 0 | -3.9226 | 163.0518 | 106.3715 | -16.3715 | 162.3553 | 158.8681 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1004 | 0
2016-03-10 23:00 | 0 | 0 | 0 | 0 | -3.9062 | 178.0545 | 106.9318 | -16.9318 | 177.9711 | 166.8008 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-03-11 | 0 | 0 | 0 | 0 | -3.8899 | -166.9428 | 106.5752 | -16.5752 | -166.398 | 161.6945 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.0991 | 0
2016-03-11 01:00 | 0 | 0 | 0 | 0 | -3.8736 | -151.9401 | 105.3295 | -15.3295 | -150.8804 | 149.5229 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-03-11 02:00 | 0 | 0 | 0 | 0 | -3.8573 | -136.9373 | 103.293 | -13.293 | -135.5725 | 135.7955 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-03-11 03:00 | 0 | 0 | 0 | 0 | -3.841 | -121.9346 | 100.6193 | -10.6193 | -120.5145 | 121.6238 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-03-11 04:00 | 2.8567 | 1.84 | 1.0167 | 0 | -3.8247 | -106.9319 | 97.4995 | -7.4995 | -105.6863 | 107.3017 | 0 | 1.38 | 0.8 | 1 | 0.57133 | 1.9513 | -3 | -2.939 | 1.0978 | 0.0017566
2016-03-11 05:00 | 5.7133 | 3.68 | 2.0333 | 0 | -3.8083 | -91.9292 | 94.1451 | -4.1451 | -91.0195 | 92.9526 | 0 | 2.76 | 0.8 | 1 | 1.1427 | 3.9027 | -2.9 | -2.778 | 1.0972 | 0.0035113
2016-03-11 06:00 | 8.57 | 5.52 | 3.05 | 0 | -3.792 | -76.9265 | 90.7753 | -0.77525 | -76.4185 | 78.6628 | 0 | 4.14 | 0.8 | 1 | 1.714 | 5.854 | -1.5 | -1.3171 | 1.0921 | 0.0052424
2016-03-11 07:00 | 34.64 | 17.01 | 17.63 | 0 | -3.7757 | -61.9238 | 87.6069 | 2.3931 | -61.7845 | 64.5345 | 0 | 12.7575 | 0.8 | 1 | 6.928 | 19.6855 | 0.1 | 0.71517 | 1.085 | 0.017514
2016-03-11 08:00 | 60.71 | 28.5 | 32.21 | 358.6 | -3.7594 | -46.921 | 84.8467 | 5.1533 | -47.0375 | 50.7475 | 226.9001 | 21.375 | 0.8 | 1 | 12.142 | 260.4171 | 1.2 | 9.338 | 1.0548 | 0.22525
2016-03-11 09:00 | 86.78 | 39.99 | 46.79 | 367.2342 | -3.743 | -31.9183 | 82.6799 | 7.3201 | -32.1351 | 37.7138 | 290.5103 | 29.9925 | 0.8 | 1 | 17.356 | 337.8588 | 0.8 | 11.3581 | 1.0477 | 0.29027
2016-03-11 10:00 | 93.8767 | 42.18 | 51.6967 | 340.1509 | -3.7267 | -16.9156 | 81.2582 | 8.7418 | -17.0832 | 26.5954 | 304.1596 | 31.635 | 0.8 | 1 | 18.7753 | 354.5699 | 1.6 | 12.6803 | 1.0431 | 0.30328
2016-03-11 11:00 | 100.9733 | 44.37 | 56.6033 | 349.6754 | -3.7104 | -1.9128 | 80.6843 | 9.3157 | -1.9344 | 20.7632 | 326.9653 | 33.2775 | 0.8 | 1 | 20.1947 | 380.4375 | 1.5 | 13.3887 | 1.0406 | 0.32464
2016-03-11 12:00 | 108.07 | 46.56 | 61.51 | 393.2037 | -3.694 | 13.0899 | 81.0001 | 8.9999 | 13.228 | 24.3721 | 358.1633 | 34.92 | 0.8 | 1 | 21.614 | 414.6973 | 1.7 | 14.6593 | 1.0362 | 0.35236
2016-03-11 13:00 | 81.08 | 36.7933 | 44.2867 | 325.523 | -3.6777 | 28.0926 | 82.1808 | 7.8192 | 28.3163 | 34.58 | 268.0142 | 27.595 | 0.8 | 1 | 16.216 | 311.8252 | 1.8 | 11.5445 | 1.0471 | 0.26774
2016-03-11 14:00 | 54.09 | 27.0267 | 27.0633 | 264.9981 | -3.6614 | 43.0954 | 84.1384 | 5.8616 | 43.2674 | 47.2833 | 179.7677 | 20.27 | 0.8 | 1 | 10.818 | 210.8557 | 1.7 | 8.2892 | 1.0585 | 0.18301
2016-03-11 15:00 | 27.1 | 17.26 | 9.84 | 172.6308 | -3.645 | 58.0981 | 86.7324 | 3.2676 | 58.0615 | 60.9292 | 83.8796 | 12.945 | 0.8 | 1 | 5.42 | 102.2446 | 1.6 | 4.7951 | 1.0707 | 0.08977
2016-03-11 16:00 | 18.0667 | 11.5067 | 6.56 | 0 | -3.6287 | 73.1009 | 89.7843 | 0.21565 | 72.7281 | 74.9887 | 0 | 8.63 | 0.8 | 1 | 3.6133 | 12.2433 | 2.2 | 2.5826 | 1.0785 | 0.010827
2016-03-11 17:00 | 9.0333 | 5.7533 | 3.28 | 0 | -3.6124 | 88.1036 | 93.0917 | -3.0917 | 87.3375 | 89.2435 | 0 | 4.315 | 0.8 | 1 | 1.8067 | 6.1217 | 2.2 | 2.3913 | 1.0791 | 0.005417
2016-03-11 18:00 | 0 | 0 | 0 | 0 | -3.596 | 103.1064 | 96.4389 | -6.4389 | 101.9846 | 103.5778 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-03-11 19:00 | 0 | 0 | 0 | 0 | -3.5797 | 118.1091 | 99.6061 | -9.6061 | 116.7664 | 117.9036 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-03-11 20:00 | 0 | 0 | 0 | 0 | -3.5633 | 133.1119 | 102.379 | -12.379 | 131.7591 | 132.1097 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-03-11 21:00 | 0 | 0 | 0 | 0 | -3.547 | 148.1146 | 104.5601 | -14.5601 | 146.9956 | 145.96 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.7 | 1.7 | 1.0816 | 0
2016-03-11 22:00 | 0 | 0 | 0 | 0 | -3.5307 | 163.1174 | 105.985 | -15.985 | 162.4511 | 158.6676 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.9 | 0.9 | 1.0843 | 0
2016-03-11 23:00 | 0 | 0 | 0 | 0 | -3.5143 | 178.1202 | 106.5404 | -16.5404 | 178.0427 | 166.4217 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.1 | 2.1 | 1.0801 | 0
2016-03-12 | 0 | 0 | 0 | 0 | -3.498 | -166.8771 | 106.1803 | -16.1803 | -166.3515 | 161.3636 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-03-12 01:00 | 0 | 0 | 0 | 0 | -3.4816 | -151.8743 | 104.9327 | -14.9327 | -150.8575 | 149.2823 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-03-12 02:00 | 0 | 0 | 0 | 0 | -3.4653 | -136.8715 | 102.8955 | -12.8955 | -135.5696 | 135.5956 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-03-12 03:00 | 0 | 0 | 0 | 0 | -3.4489 | -121.8687 | 100.2219 | -10.2219 | -120.5265 | 121.442 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-03-12 04:00 | 3.2167 | 2.1733 | 1.0433 | 0 | -3.4326 | -106.866 | 97.1025 | -7.1025 | -105.7075 | 107.1264 | 0 | 1.63 | 0.8 | 1 | 0.64333 | 2.2733 | 0.2 | 0.27104 | 1.0866 | 0.0020255
2016-03-12 05:00 | 6.4333 | 4.3467 | 2.0867 | 0 | -3.4162 | -91.8632 | 93.7483 | -3.7483 | -91.044 | 92.776 | 0 | 3.26 | 0.8 | 1 | 1.2867 | 4.5467 | 0.5 | 0.64208 | 1.0853 | 0.0040461
2016-03-12 06:00 | 9.65 | 6.52 | 3.13 | 0 | -3.3999 | -76.8604 | 90.3782 | -0.37822 | -76.4403 | 78.4782 | 0 | 4.89 | 0.8 | 1 | 1.93 | 6.82 | 0.6 | 0.81312 | 1.0847 | 0.0060658
2016-03-12 07:00 | 36.88 | 18.03 | 18.85 | 0 | -3.3835 | -61.8576 | 87.2095 | 2.7905 | -61.7979 | 64.3339 | 0 | 13.5225 | 0.8 | 1 | 7.376 | 20.8985 | 0.3 | 0.95308 | 1.0842 | 0.018579
2016-03-12 08:00 | 64.11 | 29.54 | 34.57 | 357.3772 | -3.3672 | -46.8548 | 84.449 | 5.551 | -47.0371 | 50.5195 | 227.226 | 22.155 | 0.8 | 1 | 12.822 | 262.203 | 0.1 | 8.2938 | 1.0585 | 0.22758
2016-03-12 09:00 | 91.34 | 41.05 | 50.29 | 374.4974 | -3.3508 | -31.852 | 82.2826 | 7.7174 | -32.1164 | 37.4393 | 297.35 | 30.7875 | 0.8 | 1 | 18.268 | 346.4055 | -0.1 | 10.7252 | 1.05 | 0.29824
2016-03-12 10:00 | 106.6667 | 41.23 | 65.4367 | 412.0569 | -3.3345 | -16.8492 | 80.8625 | 9.1375 | -17.0426 | 26.2476 | 369.5701 | 30.9225 | 0.8 | 1 | 21.3333 | 421.8259 | 0.3 | 13.4821 | 1.0403 | 0.35984
2016-03-12 11:00 | 121.9933 | 41.41 | 80.5833 | 477.8584 | -3.3181 | -1.8464 | 80.2916 | 9.7084 | -1.8701 | 20.3666 | 447.9852 | 31.0575 | 0.8 | 1 | 24.3987 | 503.4414 | 0.5 | 16.2325 | 1.0307 | 0.42549
2016-03-12 12:00 | 137.32 | 41.59 | 95.73 | 586.8572 | -3.3018 | 13.1564 | 80.6118 | 9.3882 | 13.3157 | 24.0744 | 535.8104 | 31.1925 | 0.8 | 1 | 27.464 | 594.4669 | 0.4 | 18.9771 | 1.0211 | 0.49774
2016-03-12 13:00 | 98.2667 | 33.1533 | 65.1133 | 456.4054 | -3.2854 | 28.1592 | 81.7979 | 8.2021 | 28.4255 | 34.3956 | 376.6059 | 24.865 | 0.8 | 1 | 19.6533 | 421.1242 | 0.7 | 13.8601 | 1.039 | 0.35879
2016-03-12 14:00 | 59.2133 | 24.7167 | 34.4967 | 317.4306 | -3.269 | 43.162 | 83.7611 | 6.2389 | 43.3946 | 47.1643 | 215.8206 | 18.5375 | 0.8 | 1 | 11.8427 | 246.2007 | 0.5 | 8.1938 | 1.0588 | 0.21376
2016-03-12 15:00 | 20.16 | 16.28 | 3.88 | 61.1155 | -3.2527 | 58.1648 | 86.3601 | 3.6399 | 58.2024 | 60.8466 | 29.7724 | 12.21 | 0.8 | 1 | 4.032 | 46.0144 | 1.8 | 3.2379 | 1.0762 | 0.040606
2016-03-12 16:00 | 13.44 | 10.8533 | 2.5867 | 0 | -3.2363 | 73.1676 | 89.4156 | 0.58441 | 72.8778 | 74.9268 | 0 | 8.14 | 0.8 | 1 | 2.688 | 10.828 | 2 | 2.3384 | 1.0793 | 0.0095832
2016-03-12 17:00 | 6.72 | 5.4267 | 1.2933 | 0 | -3.22 | 88.1704 | 92.7245 | -2.7245 | 87.4913 | 89.1922 | 0 | 4.07 | 0.8 | 1 | 1.344 | 5.414 | 2.1 | 2.2692 | 1.0796 | 0.0047927
2016-03-12 18:00 | 0 | 0 | 0 | 0 | -3.2036 | 103.1732 | 96.0709 | -6.0709 | 102.1373 | 103.5294 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.3 | 1.3 | 1.083 | 0
2016-03-12 19:00 | 0 | 0 | 0 | 0 | -3.1872 | 118.1761 | 99.2352 | -9.2352 | 116.9129 | 117.8499 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-03-12 20:00 | 0 | 0 | 0 | 0 | -3.1709 | 133.1789 | 102.0034 | -12.0034 | 131.8941 | 132.0388 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.9 | 0.9 | 1.0843 | 0
2016-03-12 21:00 | 0 | 0 | 0 | 0 | -3.1545 | 148.1817 | 104.1788 | -14.1788 | 147.114 | 145.8496 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1 | 1 | 1.084 | 0
2016-03-12 22:00 | 0 | 0 | 0 | 0 | -3.1381 | 163.1845 | 105.5979 | -15.5979 | 162.5483 | 158.4628 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.8 | 0.8 | 1.0847 | 0
2016-03-12 23:00 | 0 | 0 | 0 | 0 | -3.1218 | 178.1874 | 106.1484 | -16.1484 | 178.1157 | 166.0411 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-03-13 | 0 | 0 | 0 | 0 | -3.1054 | -166.8098 | 105.7847 | -15.7847 | -166.3036 | 161.0288 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.3 | 1.3 | 1.083 | 0
2016-03-13 01:00 | 0 | 0 | 0 | 0 | -3.089 | -151.807 | 104.5351 | -14.5351 | -150.8331 | 149.037 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-03-13 02:00 | 0 | 0 | 0 | 0 | -3.0726 | -136.8041 | 102.4972 | -12.4972 | -135.5651 | 135.3919 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.7 | 1.7 | 1.0816 | 0
2016-03-13 03:00 | 0 | 0 | 0 | 0 | -3.0563 | -121.8013 | 99.8237 | -9.8237 | -120.537 | 121.2571 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-03-13 04:00 | 2.0767 | 1.98 | 0.096667 | 0 | -3.0399 | -106.7984 | 96.7045 | -6.7045 | -105.7273 | 106.9486 | 0 | 1.485 | 0.8 | 1 | 0.41533 | 1.9003 | 2.9 | 2.9594 | 1.0771 | 0.0016785
2016-03-13 05:00 | 4.1533 | 3.96 | 0.19333 | 0 | -3.0235 | -91.7956 | 93.3505 | -3.3505 | -91.067 | 92.5976 | 0 | 2.97 | 0.8 | 1 | 0.83067 | 3.8007 | 2.9 | 3.0188 | 1.0769 | 0.0033563
2016-03-13 06:00 | 6.23 | 5.94 | 0.29 | 0 | -3.0072 | -76.7928 | 89.9802 | 0.019754 | -76.4607 | 78.2922 | 0 | 4.455 | 0.8 | 1 | 1.246 | 5.701 | 3 | 3.1782 | 1.0764 | 0.0050319
2016-03-13 07:00 | 21.1967 | 18.7033 | 2.4933 | 44.8221 | -2.9908 | -61.7899 | 86.8111 | 3.1889 | -61.8098 | 64.1326 | 19.5554 | 14.0275 | 0.8 | 1 | 4.2393 | 37.8223 | 2.8 | 3.9819 | 1.0736 | 0.033296
2016-03-13 08:00 | 36.1633 | 31.4667 | 4.6967 | 45.3112 | -2.9744 | -46.787 | 84.0504 | 5.9496 | -47.0353 | 50.2913 | 28.9486 | 23.6 | 0.8 | 1 | 7.2327 | 59.7813 | 2 | 3.8682 | 1.074 | 0.052646
2016-03-13 09:00 | 51.13 | 44.23 | 6.9 | 48.8778 | -2.958 | -31.7842 | 81.8845 | 8.1155 | -32.0961 | 37.1651 | 38.9506 | 33.1725 | 0.8 | 1 | 10.226 | 82.3491 | 0.9 | 3.4734 | 1.0753 | 0.072614
2016-03-13 10:00 | 67.03 | 46.4633 | 20.5667 | 124.1705 | -2.9416 | -16.7813 | 80.466 | 9.534 | -17.0004 | 25.8998 | 111.6987 | 34.8475 | 0.8 | 1 | 13.406 | 159.9522 | 1.8 | 6.7985 | 1.0637 | 0.13952
2016-03-13 11:00 | 82.93 | 48.6967 | 34.2333 | 195.1765 | -2.9253 | -1.7785 | 79.8983 | 10.1017 | -1.8041 | 19.9693 | 183.4417 | 36.5225 | 0.8 | 1 | 16.586 | 236.5502 | 1.6 | 8.9922 | 1.056 | 0.20484
2016-03-13 12:00 | 98.83 | 50.93 | 47.9 | 282.0733 | -2.9089 | 13.2244 | 80.223 | 9.777 | 13.4053 | 23.7798 | 258.1257 | 38.1975 | 0.8 | 1 | 19.766 | 316.0892 | 1.7 | 11.5778 | 1.047 | 0.27137
2016-03-13 13:00 | 75.6433 | 40.6067 | 35.0367 | 234.699 | -2.8925 | 28.2273 | 81.4146 | 8.5854 | 28.5366 | 34.2153 | 194.0797 | 30.455 | 0.8 | 1 | 15.1287 | 239.6633 | 1.1 | 8.5895 | 1.0574 | 0.20781
2016-03-13 14:00 | 52.4567 | 30.2833 | 22.1733 | 192.4383 | -2.8761 | 43.2301 | 83.3835 | 6.6165 | 43.5237 | 47.0488 | 131.1228 | 22.7125 | 0.8 | 1 | 10.4913 | 164.3266 | 1.4 | 6.5352 | 1.0646 | 0.14346
2016-03-13 15:00 | 29.27 | 19.96 | 9.31 | 133.0501 | -2.8597 | 58.233 | 85.9875 | 4.0125 | 58.345 | 60.7668 | 64.9771 | 14.97 | 0.8 | 1 | 5.854 | 85.8011 | 1 | 3.6813 | 1.0746 | 0.075607
2016-03-13 16:00 | 19.5133 | 13.3067 | 6.2067 | 0 | -2.8434 | 73.2359 | 89.0466 | 0.95338 | 73.0292 | 74.8669 | 0 | 9.98 | 0.8 | 1 | 3.9027 | 13.8827 | 0.4 | 0.83383 | 1.0846 | 0.012347
2016-03-13 17:00 | 9.7567 | 6.6533 | 3.1033 | 0 | -2.827 | 88.2387 | 92.3571 | -2.3571 | 87.6465 | 89.1423 | 0 | 4.99 | 0.8 | 1 | 1.9513 | 6.9413 | 0.1 | 0.31692 | 1.0864 | 0.0061836
2016-03-13 18:00 | 0 | 0 | 0 | 0 | -2.8106 | 103.2416 | 95.7027 | -5.7027 | 102.2914 | 103.4816 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-03-13 19:00 | 0 | 0 | 0 | 0 | -2.7942 | 118.2445 | 98.864 | -8.864 | 117.0608 | 117.796 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-03-13 20:00 | 0 | 0 | 0 | 0 | -2.7778 | 133.2474 | 101.6274 | -11.6274 | 132.0304 | 131.9669 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-03-13 21:00 | 0 | 0 | 0 | 0 | -2.7614 | 148.2503 | 103.7971 | -13.7971 | 147.2336 | 145.7365 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-03-13 22:00 | 0 | 0 | 0 | 0 | -2.7451 | 163.2532 | 105.2103 | -15.2103 | 162.6468 | 158.2536 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.1 | 0.1 | 1.0872 | 0
2016-03-13 23:00 | 0 | 0 | 0 | 0 | -2.7287 | 178.256 | 105.7558 | -15.7558 | 178.19 | 165.6593 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-03-14 | 0 | 0 | 0 | 0 | -2.7123 | -166.7411 | 105.3885 | -15.3885 | -166.2542 | 160.6902 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-03-14 01:00 | 0 | 0 | 0 | 0 | -2.6959 | -151.7382 | 104.1368 | -14.1368 | -150.8073 | 148.7873 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-03-14 02:00 | 0 | 0 | 0 | 0 | -2.6795 | -136.7353 | 102.0981 | -12.0981 | -135.5592 | 135.1845 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-03-14 03:00 | 0 | 0 | 0 | 0 | -2.6631 | -121.7324 | 99.4246 | -9.4246 | -120.5461 | 121.0694 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.0991 | 0
2016-03-14 04:00 | 4.2867 | 2.97 | 1.3167 | 0 | -2.6467 | -106.7295 | 96.3058 | -6.3058 | -105.7456 | 106.7685 | 0 | 2.2275 | 0.8 | 1 | 0.85733 | 3.0848 | -3.7 | -3.6036 | 1.1001 | 0.0027828
2016-03-14 05:00 | 8.5733 | 5.94 | 2.6333 | 0 | -2.6303 | -91.7266 | 92.9519 | -2.9519 | -91.0886 | 92.4174 | 0 | 4.455 | 0.8 | 1 | 1.7147 | 6.1697 | -3.9 | -3.7072 | 1.1005 | 0.0055674
2016-03-14 06:00 | 12.86 | 8.91 | 3.95 | 0 | -2.6139 | -76.7236 | 89.5815 | 0.41855 | -76.4797 | 78.1052 | 0 | 6.6825 | 0.8 | 1 | 2.572 | 9.2545 | -4.1 | -3.8108 | 1.1008 | 0.0083539
2016-03-14 07:00 | 28.3333 | 21.9167 | 6.4167 | 102.5333 | -2.5975 | -61.7207 | 86.412 | 3.588 | -61.8204 | 63.9307 | 45.0591 | 16.4375 | 0.8 | 1 | 5.6667 | 67.1633 | -4.8 | -2.7011 | 1.097 | 0.060413
2016-03-14 08:00 | 43.8067 | 34.9233 | 8.8833 | 80.3322 | -2.5811 | -46.7178 | 83.6511 | 6.3489 | -47.0321 | 50.063 | 51.5688 | 26.1925 | 0.8 | 1 | 8.7613 | 86.5227 | -4.4 | -1.6962 | 1.0934 | 0.077578
2016-03-14 09:00 | 59.28 | 47.93 | 11.35 | 76.6609 | -2.5647 | -31.7149 | 81.4858 | 8.5142 | -32.0743 | 36.8914 | 61.3115 | 35.9475 | 0.8 | 1 | 11.856 | 109.115 | -4.2 | -0.79016 | 1.0903 | 0.097551
2016-03-14 10:00 | 58.7767 | 50.33 | 8.4467 | 48.977 | -2.5483 | -16.712 | 80.069 | 9.931 | -16.9566 | 25.5519 | 44.1868 | 37.7475 | 0.8 | 1 | 11.7553 | 93.6896 | -3.6 | -0.6722 | 1.0899 | 0.083728
2016-03-14 11:00 | 58.2733 | 52.73 | 5.5433 | 30.4313 | -2.5319 | -1.7091 | 79.5045 | 10.4955 | -1.7365 | 19.5714 | 28.6731 | 39.5475 | 0.8 | 1 | 11.6547 | 79.8753 | -4.1 | -1.6039 | 1.0931 | 0.071596
2016-03-14 12:00 | 57.77 | 55.13 | 2.64 | 14.9572 | -2.5156 | 13.2938 | 79.8338 | 10.1662 | 13.4966 | 23.4886 | 13.7179 | 41.3475 | 0.8 | 1 | 11.554 | 66.6194 | -3.9 | -1.8181 | 1.0939 | 0.059755
2016-03-14 13:00 | 46.8567 | 44.73 | 2.1267 | 13.6413 | -2.4992 | 28.2968 | 81.031 | 8.969 | 28.6495 | 34.0392 | 11.3039 | 33.5475 | 0.8 | 1 | 9.3713 | 54.2227 | -3.2 | -1.5055 | 1.0928 | 0.048587
2016-03-14 14:00 | 35.9433 | 34.33 | 1.6133 | 13.249 | -2.4828 | 43.2997 | 83.0057 | 6.9943 | 43.6545 | 46.9368 | 9.0465 | 25.7475 | 0.8 | 1 | 7.1887 | 41.9827 | -2.5 | -1.188 | 1.0917 | 0.037581
2016-03-14 15:00 | 25.03 | 23.93 | 1.1 | 14.3865 | -2.4664 | 58.3026 | 85.6149 | 4.3851 | 58.4893 | 60.6897 | 7.0428 | 17.9475 | 0.8 | 1 | 5.006 | 29.9963 | -2.4 | -1.4626 | 1.0926 | 0.026875
2016-03-14 16:00 | 16.6867 | 15.9533 | 0.73333 | 0 | -2.45 | 73.3056 | 88.6775 | 1.3225 | 73.1822 | 74.8089 | 0 | 11.965 | 0.8 | 1 | 3.3373 | 15.3023 | -2.9 | -2.4218 | 1.096 | 0.013752
2016-03-14 17:00 | 8.3433 | 7.9767 | 0.36667 | 0 | -2.4336 | 88.3085 | 91.9895 | -1.9895 | 87.8033 | 89.0937 | 0 | 5.9825 | 0.8 | 1 | 1.6687 | 7.6512 | -0.3 | -0.060901 | 1.0877 | 0.0068243
2016-03-14 18:00 | 0 | 0 | 0 | 0 | -2.4172 | 103.3114 | 95.3343 | -5.3343 | 102.4469 | 103.4345 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.3 | 1.3 | 1.083 | 0
2016-03-14 19:00 | 0 | 0 | 0 | 0 | -2.4008 | 118.3144 | 98.4926 | -8.4926 | 117.2099 | 117.7419 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-03-14 20:00 | 0 | 0 | 0 | 0 | -2.3843 | 133.3173 | 101.2512 | -11.2512 | 132.1679 | 131.8937 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-03-14 21:00 | 0 | 0 | 0 | 0 | -2.3679 | 148.3202 | 103.4151 | -13.4151 | 147.3544 | 145.6208 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-03-14 22:00 | 0 | 0 | 0 | 0 | -2.3515 | 163.3232 | 104.8224 | -14.8224 | 162.7464 | 158.0401 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-03-14 23:00 | 0 | 0 | 0 | 0 | -2.3351 | 178.3261 | 105.3628 | -15.3628 | 178.2655 | 165.2763 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-03-15 | 0 | 0 | 0 | 0 | -2.3187 | -166.6709 | 104.9917 | -14.9917 | -166.2036 | 160.3482 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-03-15 01:00 | 0 | 0 | 0 | 0 | -2.3023 | -151.668 | 103.7379 | -13.7379 | -150.7801 | 148.5333 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.1 | 0.1 | 1.0872 | 0
2016-03-15 02:00 | 0 | 0 | 0 | 0 | -2.2859 | -136.665 | 101.6984 | -11.6984 | -135.552 | 134.9736 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-03-15 03:00 | 0 | 0 | 0 | 0 | -2.2695 | -121.6621 | 99.0249 | -9.0249 | -120.5538 | 120.8788 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-03-15 04:00 | 3.4167 | 3.3333 | 0.083333 | 0 | -2.2531 | -106.6591 | 95.9063 | -5.9063 | -105.7626 | 106.5863 | 0 | 2.5 | 0.8 | 1 | 0.68333 | 3.1833 | -0.6 | -0.50052 | 1.0893 | 0.0028433
2016-03-15 05:00 | 6.8333 | 6.6667 | 0.16667 | 0 | -2.2367 | -91.6561 | 92.5525 | -2.5525 | -91.1089 | 92.2357 | 0 | 5 | 0.8 | 1 | 1.3667 | 6.3667 | -0.7 | -0.50104 | 1.0893 | 0.0056866
2016-03-15 06:00 | 10.25 | 10 | 0.25 | 0 | -2.2203 | -76.6532 | 89.182 | 0.81803 | -76.4974 | 77.9171 | 0 | 7.5 | 0.8 | 1 | 2.05 | 9.55 | -0.6 | -0.30156 | 1.0886 | 0.0085245
2016-03-15 07:00 | 27.3967 | 23.3333 | 4.0633 | 58.4284 | -2.2039 | -61.6502 | 86.0122 | 3.9878 | -61.8297 | 63.7284 | 25.862 | 17.5 | 0.8 | 1 | 5.4793 | 48.8413 | -0.5 | 1.0263 | 1.0839 | 0.04341
2016-03-15 08:00 | 44.5433 | 36.6667 | 7.8767 | 67.0261 | -2.1875 | -46.6472 | 83.2512 | 6.7488 | -47.0275 | 49.8349 | 43.2313 | 27.5 | 0.8 | 1 | 8.9087 | 79.6399 | -0.4 | 2.0887 | 1.0802 | 0.070541
2016-03-15 09:00 | 61.69 | 50 | 11.69 | 75.447 | -2.1711 | -31.6443 | 81.0865 | 8.9135 | -32.0511 | 36.6182 | 60.5559 | 37.5 | 0.8 | 1 | 12.338 | 110.3939 | 0.6 | 4.0498 | 1.0733 | 0.097161
2016-03-15 10:00 | 66.36 | 58.55 | 7.81 | 43.5604 | -2.1547 | -16.6413 | 79.6715 | 10.3285 | -16.9113 | 25.2043 | 39.4132 | 43.9125 | 0.8 | 1 | 13.272 | 96.5977 | -1.1 | 1.9187 | 1.0808 | 0.085609
2016-03-15 11:00 | 71.03 | 67.1 | 3.93 | 20.8026 | -2.1382 | -1.6383 | 79.1103 | 10.8897 | -1.6672 | 19.1732 | 19.6486 | 50.325 | 0.8 | 1 | 14.206 | 84.1796 | -1 | 1.6306 | 1.0818 | 0.074673
2016-03-15 12:00 | 75.7 | 75.65 | 0.05 | 0.27294 | -2.1218 | 13.3646 | 79.4444 | 10.5556 | 13.5896 | 23.2008 | 0.25087 | 56.7375 | 0.8 | 1 | 15.14 | 72.1284 | -0.3 | 1.954 | 1.0807 | 0.063916
2016-03-15 13:00 | 59.54 | 59.43 | 0.11 | 0.67688 | -2.1054 | 28.3676 | 80.6473 | 9.3527 | 28.764 | 33.8674 | 0.56203 | 44.5725 | 0.8 | 1 | 11.908 | 57.0425 | -2.6 | -0.81742 | 1.0904 | 0.051001
2016-03-15 14:00 | 43.38 | 43.21 | 0.17 | 1.3249 | -2.089 | 43.3706 | 82.6279 | 7.3721 | 43.7869 | 46.8282 | 0.90647 | 32.4075 | 0.8 | 1 | 8.676 | 41.99 | -3.3 | -1.9878 | 1.0945 | 0.037684
2016-03-15 15:00 | 27.22 | 26.99 | 0.23 | 2.7729 | -2.0726 | 58.3736 | 85.2421 | 4.7579 | 58.6352 | 60.6152 | 1.3606 | 20.2425 | 0.8 | 1 | 5.444 | 27.0471 | -3.6 | -2.7548 | 1.0971 | 0.024333
2016-03-15 16:00 | 18.1567 | 18.0033 | 0.15333 | 0 | -2.0562 | 73.3766 | 88.3084 | 1.6916 | 73.3367 | 74.7529 | 0 | 13.5025 | 0.8 | 1 | 3.6313 | 17.1338 | -3.8 | -3.2646 | 1.0989 | 0.01544
2016-03-15 17:00 | 9.0933 | 9.0167 | 0.076667 | 0 | -2.0398 | 88.3796 | 91.6219 | -1.6219 | 87.9614 | 89.0463 | 0 | 6.7625 | 0.8 | 1 | 1.8187 | 8.5812 | -4.1 | -3.8318 | 1.1009 | 0.0077466
2016-03-15 18:00 | 0.03 | 0.03 | 0 | 0 | -2.0234 | 103.3825 | 94.9658 | -4.9658 | 102.6036 | 103.3879 | 0 | 0.0225 | 0.8 | 1 | 0.006 | 0.0285 | -4.7 | -4.6991 | 1.1039 | 2.5799e-05
2016-03-15 19:00 | 0.02 | 0.02 | 0 | 0 | -2.0069 | 118.3855 | 98.121 | -8.121 | 117.3602 | 117.6876 | 0 | 0.015 | 0.8 | 1 | 0.004 | 0.019 | -5 | -4.9994 | 1.105 | 1.7216e-05
2016-03-15 20:00 | 0.01 | 0.01 | 0 | 0 | -1.9905 | 133.3885 | 100.8748 | -10.8748 | 132.3065 | 131.8192 | 0 | 0.0075 | 0.8 | 1 | 0.002 | 0.0095 | -5.9 | -5.8997 | 1.1081 | 8.6325e-06
2016-03-15 21:00 | 0 | 0 | 0 | 0 | -1.9741 | 148.3915 | 103.0328 | -13.0328 | 147.4762 | 145.5024 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.3 | -6.3 | 1.1096 | 0
2016-03-15 22:00 | 0 | 0 | 0 | 0 | -1.9577 | 163.3945 | 104.4342 | -14.4342 | 162.8471 | 157.8225 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.5 | -6.5 | 1.1102 | 0
2016-03-15 23:00 | 0 | 0 | 0 | 0 | -1.9413 | 178.3975 | 104.9694 | -14.9694 | 178.3422 | 164.8922 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.9 | -6.9 | 1.1117 | 0
2016-03-16 | 0 | 0 | 0 | 0 | -1.9249 | -166.5995 | 104.5946 | -14.5946 | -166.1519 | 160.003 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.8 | -6.8 | 1.1113 | 0
2016-03-16 01:00 | 0 | 0 | 0 | 0 | -1.9085 | -151.5965 | 103.3386 | -13.3386 | -150.7517 | 148.2754 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-03-16 02:00 | 0 | 0 | 0 | 0 | -1.892 | -136.5935 | 101.2981 | -11.2981 | -135.5435 | 134.7594 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-03-16 03:00 | 0 | 0 | 0 | 0 | -1.8756 | -121.5905 | 98.6246 | -8.6246 | -120.5603 | 120.6856 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.6 | -7.6 | 1.1141 | 0
2016-03-16 04:00 | 4.9367 | 4.2367 | 0.7 | 0 | -1.8592 | -106.5874 | 95.5062 | -5.5062 | -105.7783 | 106.4021 | 0 | 3.1775 | 0.8 | 1 | 0.98733 | 4.1648 | -8.6 | -8.4698 | 1.1171 | 0.0038152
2016-03-16 05:00 | 9.8733 | 8.4733 | 1.4 | 0 | -1.8428 | -91.5844 | 92.1526 | -2.1526 | -91.128 | 92.0526 | 0 | 6.355 | 0.8 | 1 | 1.9747 | 8.3297 | -9 | -8.7397 | 1.1181 | 0.0076369
2016-03-16 06:00 | 14.81 | 12.71 | 2.1 | 0 | -1.8264 | -76.5814 | 88.7819 | 1.2181 | -76.5138 | 77.7282 | 0 | 9.5325 | 0.8 | 1 | 2.962 | 12.4945 | -9.6 | -9.2095 | 1.1197 | 0.011472
2016-03-16 07:00 | 39.6533 | 25.1433 | 14.51 | 189.6425 | -1.8099 | -61.5784 | 85.6119 | 4.3881 | -61.8378 | 63.5257 | 84.5418 | 18.8575 | 0.8 | 1 | 7.9307 | 111.33 | -10 | -6.5209 | 1.1103 | 0.10136
2016-03-16 08:00 | 64.4967 | 37.5767 | 26.92 | 216.3059 | -1.7935 | -46.5754 | 82.8508 | 7.1492 | -47.0217 | 49.6071 | 140.1716 | 28.1825 | 0.8 | 1 | 12.8993 | 181.2534 | -10.4 | -4.7358 | 1.1041 | 0.1641
2016-03-16 09:00 | 89.34 | 50.01 | 39.33 | 243.0302 | -1.7771 | -31.5724 | 80.6868 | 9.3132 | -32.0266 | 36.3457 | 195.75 | 37.5075 | 0.8 | 1 | 17.868 | 251.1255 | -11 | -3.1523 | 1.0985 | 0.22621
2016-03-16 10:00 | 94.28 | 51.5533 | 42.7267 | 229.5678 | -1.7607 | -16.5693 | 79.2737 | 10.7263 | -16.8645 | 24.8572 | 208.3003 | 38.665 | 0.8 | 1 | 18.856 | 265.8213 | -11.3 | -2.9931 | 1.098 | 0.23933
2016-03-16 11:00 | 99.22 | 53.0967 | 46.1233 | 235.7142 | -1.7443 | -1.5663 | 78.7159 | 11.2841 | -1.5965 | 18.7746 | 223.1723 | 39.8225 | 0.8 | 1 | 19.844 | 282.8388 | -11.2 | -2.3613 | 1.0958 | 0.25414
2016-03-16 12:00 | 104.16 | 54.64 | 49.52 | 260.8103 | -1.7278 | 13.4367 | 79.0548 | 10.9452 | 13.6841 | 22.9168 | 240.2249 | 40.98 | 0.8 | 1 | 20.832 | 302.0369 | -11.5 | -2.0613 | 1.0947 | 0.27113
2016-03-16 13:00 | 82.0467 | 45.65 | 36.3967 | 215.2154 | -1.7114 | 28.4397 | 80.2635 | 9.7365 | 28.8801 | 33.6999 | 179.0496 | 34.2375 | 0.8 | 1 | 16.4093 | 229.6965 | -11.5 | -4.322 | 1.1026 | 0.20768
2016-03-16 14:00 | 59.9333 | 36.66 | 23.2733 | 172.5854 | -1.695 | 43.4428 | 82.25 | 7.75 | 43.9209 | 46.7232 | 118.3114 | 27.495 | 0.8 | 1 | 11.9867 | 157.7931 | -12.5 | -7.569 | 1.114 | 0.14414
2016-03-16 15:00 | 37.82 | 27.67 | 10.15 | 113.5017 | -1.6786 | 58.4458 | 84.8694 | 5.1306 | 58.7825 | 60.5433 | 55.8162 | 20.7525 | 0.8 | 1 | 7.564 | 84.1327 | -13.1 | -10.4709 | 1.1241 | 0.077554
2016-03-16 16:00 | 25.2333 | 18.4667 | 6.7667 | 0 | -1.6622 | 73.4488 | 87.9393 | 2.0607 | 73.4925 | 74.6988 | 0 | 13.85 | 0.8 | 1 | 5.0467 | 18.8967 | -13.1 | -12.5095 | 1.1313 | 0.01753
2016-03-16 17:00 | 12.6467 | 9.2633 | 3.3833 | 0 | -1.6457 | 88.4519 | 91.2543 | -1.2543 | 88.1207 | 89.0002 | 0 | 6.9475 | 0.8 | 1 | 2.5293 | 9.4768 | -13.6 | -13.3038 | 1.1341 | 0.0088128
2016-03-16 18:00 | 0.06 | 0.06 | 0 | 0 | -1.6293 | 103.4549 | 94.5974 | -4.5974 | 102.7615 | 103.3418 | 0 | 0.045 | 0.8 | 1 | 0.012 | 0.057 | -14.1 | -14.0982 | 1.1368 | 5.3136e-05
2016-03-16 19:00 | 0.04 | 0.04 | 0 | 0 | -1.6129 | 118.4579 | 97.7494 | -7.7494 | 117.5114 | 117.633 | 0 | 0.03 | 0.8 | 1 | 0.008 | 0.038 | -15.1 | -15.0988 | 1.1403 | 3.5533e-05
2016-03-16 20:00 | 0.02 | 0.02 | 0 | 0 | -1.5965 | 133.461 | 100.4983 | -10.4983 | 132.446 | 131.7434 | 0 | 0.015 | 0.8 | 1 | 0.004 | 0.019 | -15.8 | -15.7994 | 1.1428 | 1.7805e-05
2016-03-16 21:00 | 0 | 0 | 0 | 0 | -1.5801 | 148.464 | 102.6504 | -12.6504 | 147.5989 | 145.3813 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.1 | -16.1 | 1.1439 | 0
2016-03-16 22:00 | 0 | 0 | 0 | 0 | -1.5636 | 163.4671 | 104.0458 | -14.0458 | 162.9487 | 157.6009 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.6 | -16.6 | 1.1456 | 0
2016-03-16 23:00 | 0 | 0 | 0 | 0 | -1.5472 | 178.4701 | 104.5758 | -14.5758 | 178.4198 | 164.5073 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.2 | -16.2 | 1.1442 | 0
2016-03-17 | 0 | 0 | 0 | 0 | -1.5308 | -166.5268 | 104.1971 | -14.1971 | -166.099 | 159.6549 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.7 | -16.7 | 1.146 | 0
2016-03-17 01:00 | 0 | 0 | 0 | 0 | -1.5144 | -151.5238 | 102.9389 | -12.9389 | -150.7222 | 148.0136 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.9 | -16.9 | 1.1466 | 0
2016-03-17 02:00 | 0 | 0 | 0 | 0 | -1.4979 | -136.5207 | 100.8975 | -10.8975 | -135.5337 | 134.542 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.3 | -16.3 | 1.1445 | 0
2016-03-17 03:00 | 0 | 0 | 0 | 0 | -1.4815 | -121.5177 | 98.2239 | -8.2239 | -120.5655 | 120.4898 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.5 | -15.5 | 1.1418 | 0
2016-03-17 04:00 | 6.17 | 5.42 | 0.75 | 0 | -1.4651 | -106.5146 | 95.1057 | -5.1057 | -105.7929 | 106.216 | 0 | 4.065 | 0.8 | 1 | 1.234 | 5.299 | -16.3 | -16.1344 | 1.144 | 0.0049708
2016-03-17 05:00 | 12.34 | 10.84 | 1.5 | 0 | -1.4487 | -91.5115 | 91.7522 | -1.7522 | -91.1459 | 91.8682 | 0 | 8.13 | 0.8 | 1 | 2.468 | 10.598 | -16.6 | -16.2688 | 1.1444 | 0.0099456
2016-03-17 06:00 | 18.51 | 16.26 | 2.25 | 0 | -1.4322 | -76.5085 | 88.3814 | 1.6186 | -76.5292 | 77.5385 | 0 | 12.195 | 0.8 | 1 | 3.702 | 15.897 | -16.7 | -16.2032 | 1.1442 | 0.014915
2016-03-17 07:00 | 41.1833 | 37.28 | 3.9033 | 46.7551 | -1.4158 | -61.5054 | 85.2111 | 4.7889 | -61.8447 | 63.3229 | 20.9912 | 27.96 | 0.8 | 1 | 8.2367 | 57.1879 | -16.4 | -14.6129 | 1.1386 | 0.053396
2016-03-17 08:00 | 63.8567 | 58.3 | 5.5567 | 42.2911 | -1.3994 | -46.5024 | 82.45 | 7.55 | -47.0147 | 49.3798 | 27.5333 | 43.725 | 0.8 | 1 | 12.7713 | 84.0296 | -16.3 | -13.6741 | 1.1354 | 0.078231
2016-03-17 09:00 | 86.53 | 79.32 | 7.21 | 42.7341 | -1.383 | -31.4993 | 80.2867 | 9.7133 | -32.0009 | 36.0743 | 34.54 | 59.49 | 0.8 | 1 | 17.306 | 111.336 | -15.8 | -12.3208 | 1.1306 | 0.10322
2016-03-17 10:00 | 88.8667 | 81.2433 | 7.6233 | 39.5115 | -1.3665 | -16.4962 | 78.8756 | 11.1244 | -16.8165 | 24.5106 | 35.9509 | 60.9325 | 0.8 | 1 | 17.7733 | 114.6567 | -15.7 | -12.117 | 1.1299 | 0.10623
2016-03-17 11:00 | 91.2033 | 83.1667 | 8.0367 | 39.7022 | -1.3501 | -1.4932 | 78.3213 | 11.6787 | -1.5243 | 18.3759 | 37.6777 | 62.375 | 0.8 | 1 | 18.2407 | 118.2934 | -15 | -11.3033 | 1.1271 | 0.10933
2016-03-17 12:00 | 93.54 | 85.09 | 8.45 | 42.9932 | -1.3337 | 13.5099 | 78.6651 | 11.3349 | 13.7801 | 22.6366 | 39.6812 | 63.8175 | 0.8 | 1 | 18.708 | 122.2067 | -14.9 | -11.081 | 1.1263 | 0.11286
2016-03-17 13:00 | 77.0067 | 68.3267 | 8.68 | 49.3979 | -1.3173 | 28.513 | 79.8797 | 10.1203 | 28.9977 | 33.5367 | 41.1748 | 51.245 | 0.8 | 1 | 15.4013 | 107.8211 | -14.9 | -11.5306 | 1.1279 | 0.099718
2016-03-17 14:00 | 60.4733 | 51.5633 | 8.91 | 63.0207 | -1.3008 | 43.5161 | 81.8722 | 8.1278 | 44.0563 | 46.6216 | 43.2835 | 38.6725 | 0.8 | 1 | 12.0947 | 94.0507 | -15.3 | -12.3609 | 1.1308 | 0.087206
2016-03-17 15:00 | 43.94 | 34.8 | 9.14 | 95.3066 | -1.2844 | 58.5191 | 84.4968 | 5.5032 | 58.9312 | 60.4741 | 46.9687 | 26.1 | 0.8 | 1 | 8.788 | 81.8567 | -15.8 | -13.242 | 1.1338 | 0.076107
2016-03-17 16:00 | 29.3633 | 23.27 | 6.0933 | 0 | -1.268 | 73.5222 | 87.5704 | 2.4296 | 73.6495 | 74.6465 | 0 | 17.4525 | 0.8 | 1 | 5.8727 | 23.3252 | -16.1 | -15.3711 | 1.1413 | 0.021829
2016-03-17 17:00 | 14.7867 | 11.74 | 3.0467 | 0 | -1.2516 | 88.5253 | 90.8868 | -0.8868 | 88.2811 | 88.9551 | 0 | 8.805 | 0.8 | 1 | 2.9573 | 11.7623 | -16.5 | -16.1324 | 1.144 | 0.011034
2016-03-17 18:00 | 0.21 | 0.21 | 0 | 0 | -1.2351 | 103.5284 | 94.229 | -4.229 | 102.9203 | 103.2961 | 0 | 0.1575 | 0.8 | 1 | 0.042 | 0.1995 | -17.8 | -17.7938 | 1.1498 | 0.00018809
2016-03-17 19:00 | 0.14 | 0.14 | 0 | 0 | -1.2187 | 118.5315 | 97.3779 | -7.3779 | 117.6636 | 117.578 | 0 | 0.105 | 0.8 | 1 | 0.028 | 0.133 | -16.5 | -16.4958 | 1.1452 | 0.0001249
2016-03-17 20:00 | 0.07 | 0.07 | 0 | 0 | -1.2023 | 133.5346 | 100.1219 | -10.1219 | 132.5863 | 131.6662 | 0 | 0.0525 | 0.8 | 1 | 0.014 | 0.0665 | -17 | -16.9979 | 1.147 | 6.2546e-05
2016-03-17 21:00 | 0 | 0 | 0 | 0 | -1.1859 | 148.5377 | 102.268 | -12.268 | 147.7225 | 145.2575 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.1 | -17.1 | 1.1474 | 0
2016-03-17 22:00 | 0 | 0 | 0 | 0 | -1.1694 | 163.5407 | 103.6573 | -13.6573 | 163.0512 | 157.3753 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.8 | -16.8 | 1.1463 | 0
2016-03-17 23:00 | 0 | 0 | 0 | 0 | -1.153 | 178.5438 | 104.182 | -14.182 | 178.4984 | 164.1215 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.4 | -17.4 | 1.1484 | 0
2016-03-18 | 0 | 0 | 0 | 0 | -1.1366 | -166.4531 | 103.7995 | -13.7995 | -166.0452 | 159.3041 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.3 | -16.3 | 1.1445 | 0
2016-03-18 01:00 | 0 | 0 | 0 | 0 | -1.1201 | -151.45 | 102.5389 | -12.5389 | -150.6916 | 147.7483 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.4 | -16.4 | 1.1449 | 0
2016-03-18 02:00 | 0 | 0 | 0 | 0 | -1.1037 | -136.4469 | 100.4966 | -10.4966 | -135.523 | 134.3215 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.7 | -15.7 | 1.1424 | 0
2016-03-18 03:00 | 0 | 0 | 0 | 0 | -1.0873 | -121.4438 | 97.8228 | -7.8228 | -120.5696 | 120.2918 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.9 | -16.9 | 1.1466 | 0
2016-03-18 04:00 | 8.1267 | 5.9467 | 2.18 | 0 | -1.0709 | -106.4407 | 94.7049 | -4.7049 | -105.8063 | 106.0282 | 0 | 4.46 | 0.8 | 1 | 1.6253 | 6.0853 | -17.1 | -16.9098 | 1.1467 | 0.0057219
2016-03-18 05:00 | 16.2533 | 11.8933 | 4.36 | 0 | -1.0544 | -91.4376 | 91.3515 | -1.3515 | -91.1628 | 91.6825 | 0 | 8.92 | 0.8 | 1 | 3.2507 | 12.1707 | -16.7 | -16.3197 | 1.1446 | 0.011423
2016-03-18 06:00 | 24.38 | 17.84 | 6.54 | 0 | -1.038 | -76.4345 | 87.9805 | 2.0195 | -76.5435 | 77.3482 | 0 | 13.38 | 0.8 | 1 | 4.876 | 18.256 | -16.1 | -15.5295 | 1.1419 | 0.017093
2016-03-18 07:00 | 56.2067 | 33.43 | 22.7767 | 251.7922 | -1.0216 | -61.4314 | 84.81 | 5.19 | -61.8506 | 63.1201 | 113.8407 | 25.0725 | 0.8 | 1 | 11.2413 | 150.1545 | -14.8 | -10.1077 | 1.1229 | 0.13826
2016-03-18 08:00 | 88.0333 | 49.02 | 39.0133 | 282.0381 | -1.0052 | -46.4283 | 82.049 | 7.951 | -47.0066 | 49.153 | 184.4646 | 36.765 | 0.8 | 1 | 17.6067 | 238.8363 | -15 | -7.5364 | 1.1139 | 0.21815
2016-03-18 09:00 | 119.86 | 64.61 | 55.25 | 314.6366 | -0.98874 | -31.4251 | 79.8865 | 10.1135 | -31.974 | 35.8039 | 255.1778 | 48.4575 | 0.8 | 1 | 23.972 | 327.6073 | -14 | -3.7623 | 1.1007 | 0.29568
2016-03-18 10:00 | 126.6433 | 68.62 | 58.0233 | 290.4729 | -0.97231 | -16.422 | 78.4774 | 11.5226 | -16.7672 | 24.1648 | 265.0192 | 51.465 | 0.8 | 1 | 25.3287 | 341.8129 | -13.6 | -2.9183 | 1.0977 | 0.30767
2016-03-18 11:00 | 133.4267 | 72.63 | 60.7967 | 290.6643 | -0.95589 | -1.4189 | 77.9266 | 12.0734 | -1.4508 | 17.9771 | 276.4741 | 54.4725 | 0.8 | 1 | 26.6853 | 357.6319 | -14.1 | -2.924 | 1.0977 | 0.32192
2016-03-18 12:00 | 140.21 | 76.64 | 63.57 | 312.8349 | -0.93946 | 13.5842 | 78.2755 | 11.7245 | 13.8775 | 22.3605 | 289.3124 | 57.48 | 0.8 | 1 | 28.042 | 374.8344 | -11.2 | 0.51358 | 1.0857 | 0.33371
2016-03-18 13:00 | 110.8633 | 63.3333 | 47.53 | 260.7172 | -0.92303 | 28.5873 | 79.496 | 10.504 | 29.1167 | 33.3779 | 217.7145 | 47.5 | 0.8 | 1 | 22.1727 | 287.3872 | -12.5 | -3.5192 | 1.0998 | 0.25918
2016-03-18 14:00 | 81.5167 | 50.0267 | 31.49 | 212.908 | -0.90661 | 43.5904 | 81.4945 | 8.5055 | 44.1931 | 46.5234 | 146.4931 | 37.52 | 0.8 | 1 | 16.3033 | 200.3165 | -12.8 | -6.5401 | 1.1104 | 0.18239
2016-03-18 15:00 | 52.17 | 36.72 | 15.45 | 150.925 | -0.89018 | 58.5936 | 84.1244 | 5.8756 | 59.0812 | 60.4073 | 74.5314 | 27.54 | 0.8 | 1 | 10.434 | 112.5054 | -13.6 | -10.0842 | 1.1228 | 0.10358
2016-03-18 16:00 | 34.9233 | 24.6033 | 10.32 | 0 | -0.87375 | 73.5967 | 87.2016 | 2.7984 | 73.8077 | 74.5959 | 0 | 18.4525 | 0.8 | 1 | 6.9847 | 25.4372 | -13.2 | -12.4051 | 1.1309 | 0.023589
2016-03-18 17:00 | 17.6767 | 12.4867 | 5.19 | 0 | -0.85733 | 88.5998 | 90.5195 | -0.51952 | 88.4426 | 88.9111 | 0 | 9.365 | 0.8 | 1 | 3.5353 | 12.9003 | -14.4 | -13.9969 | 1.1365 | 0.012022
2016-03-18 18:00 | 0.43 | 0.37 | 0.06 | 0 | -0.8409 | 103.6029 | 93.8608 | -3.8608 | 103.0801 | 103.2508 | 0 | 0.2775 | 0.8 | 1 | 0.086 | 0.3635 | -14 | -13.9886 | 1.1365 | 0.00033874
2016-03-18 19:00 | 0.28667 | 0.24667 | 0.04 | 0 | -0.82448 | 118.6061 | 97.0065 | -7.0065 | 117.8165 | 117.5225 | 0 | 0.185 | 0.8 | 1 | 0.057333 | 0.24233 | -14.5 | -14.4924 | 1.1382 | 0.00022618
2016-03-18 20:00 | 0.14333 | 0.12333 | 0.02 | 0 | -0.80805 | 133.6092 | 99.7455 | -9.7455 | 132.7274 | 131.5876 | 0 | 0.0925 | 0.8 | 1 | 0.028667 | 0.12117 | -14.8 | -14.7962 | 1.1393 | 0.0001132
2016-03-18 21:00 | 0 | 0 | 0 | 0 | -0.79163 | 148.6123 | 101.8856 | -11.8856 | 147.8467 | 145.1309 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.7 | -14.7 | 1.1389 | 0
2016-03-18 22:00 | 0 | 0 | 0 | 0 | -0.7752 | 163.6154 | 103.2689 | -13.2689 | 163.1544 | 157.1458 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.5 | -14.5 | 1.1382 | 0
2016-03-18 23:00 | 0 | 0 | 0 | 0 | -0.75877 | 178.6186 | 103.7882 | -13.7882 | 178.5777 | 163.7351 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.1 | -15.1 | 1.1403 | 0
2016-03-19 | 0 | 0 | 0 | 0 | -0.74235 | -166.3783 | 103.4018 | -13.4018 | -165.9905 | 158.951 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.6 | -14.6 | 1.1386 | 0
2016-03-19 01:00 | 0 | 0 | 0 | 0 | -0.72592 | -151.3752 | 102.1388 | -12.1388 | -150.6601 | 147.4796 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.4 | -13.4 | 1.1344 | 0
2016-03-19 02:00 | 0 | 0 | 0 | 0 | -0.7095 | -136.372 | 100.0955 | -10.0955 | -135.5112 | 134.0982 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.3 | -13.3 | 1.1341 | 0
2016-03-19 03:00 | 0 | 0 | 0 | 0 | -0.69307 | -121.3689 | 97.4215 | -7.4215 | -120.5728 | 120.0915 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.9 | -11.9 | 1.1292 | 0
2016-03-19 04:00 | 7.9867 | 5.91 | 2.0767 | 0 | -0.67665 | -106.3657 | 94.3038 | -4.3038 | -105.8188 | 105.8388 | 0 | 4.4325 | 0.8 | 1 | 1.5973 | 6.0298 | -12 | -11.8116 | 1.1288 | 0.0055815
2016-03-19 05:00 | 15.9733 | 11.82 | 4.1533 | 0 | -0.66023 | -91.3626 | 90.9505 | -0.95049 | -91.1786 | 91.4959 | 0 | 8.865 | 0.8 | 1 | 3.1947 | 12.0597 | -11.8 | -11.4231 | 1.1275 | 0.01115
2016-03-19 06:00 | 23.96 | 17.73 | 6.23 | 0 | -0.6438 | -76.3595 | 87.5795 | 2.4205 | -76.5568 | 77.1575 | 0 | 13.2975 | 0.8 | 1 | 4.792 | 18.0895 | -12.4 | -11.8347 | 1.1289 | 0.016746
2016-03-19 07:00 | 53.3533 | 37.1033 | 16.25 | 166.7855 | -0.62738 | -61.3563 | 84.4088 | 5.5912 | -61.8554 | 62.9174 | 75.9331 | 27.8275 | 0.8 | 1 | 10.6707 | 114.4313 | -10.7 | -7.124 | 1.1124 | 0.10438
2016-03-19 08:00 | 82.7467 | 56.4767 | 26.27 | 180.8507 | -0.61095 | -46.3532 | 81.6478 | 8.3522 | -46.9974 | 48.927 | 118.8227 | 42.3575 | 0.8 | 1 | 16.5493 | 177.7295 | -11.3 | -5.746 | 1.1076 | 0.16142
2016-03-19 09:00 | 112.14 | 75.85 | 36.29 | 198.8776 | -0.59453 | -31.35 | 79.4861 | 10.5139 | -31.946 | 35.5348 | 161.8391 | 56.8875 | 0.8 | 1 | 22.428 | 241.1546 | -10.9 | -3.3639 | 1.0993 | 0.21738
2016-03-19 10:00 | 117.5267 | 80.3567 | 37.17 | 179.9471 | -0.57811 | -16.3469 | 78.0791 | 11.9209 | -16.7168 | 23.82 | 164.619 | 60.2675 | 0.8 | 1 | 23.5053 | 248.3918 | -10.2 | -2.4378 | 1.096 | 0.22324
2016-03-19 11:00 | 122.9133 | 84.8633 | 38.05 | 176.2435 | -0.56168 | -1.3437 | 77.532 | 12.468 | -1.3761 | 17.5783 | 168.0138 | 63.6475 | 0.8 | 1 | 24.5827 | 256.244 | -10.2 | -2.1924 | 1.0952 | 0.23012
2016-03-19 12:00 | 128.3 | 89.37 | 38.93 | 185.5062 | -0.54526 | 13.6594 | 77.886 | 12.114 | 13.9761 | 22.0887 | 171.8906 | 67.0275 | 0.8 | 1 | 25.66 | 264.5781 | -11.4 | -3.1319 | 1.0985 | 0.23832
2016-03-19 13:00 | 102.9533 | 72.55 | 30.4033 | 160.9644 | -0.52884 | 28.6626 | 79.1124 | 10.8876 | 29.2369 | 33.2236 | 134.6529 | 54.4125 | 0.8 | 1 | 20.5907 | 209.6561 | -11.3 | -4.7482 | 1.1041 | 0.18982
2016-03-19 14:00 | 77.6067 | 55.73 | 21.8767 | 141.6738 | -0.51241 | 43.6658 | 81.1171 | 8.8829 | 44.3311 | 46.4287 | 97.6497 | 41.7975 | 0.8 | 1 | 15.5213 | 154.9685 | -11.3 | -6.4572 | 1.1101 | 0.14107
2016-03-19 15:00 | 52.26 | 38.91 | 13.35 | 122.6713 | -0.49599 | 58.6689 | 83.7523 | 6.2477 | 59.2323 | 60.3431 | 60.6984 | 29.1825 | 0.8 | 1 | 10.452 | 100.3329 | -11.7 | -8.5646 | 1.1175 | 0.091938
2016-03-19 16:00 | 35.0967 | 26.1167 | 8.98 | 162.5508 | -0.47957 | 73.6721 | 86.8331 | 3.1669 | 73.9669 | 74.5471 | 43.311 | 19.5875 | 0.8 | 1 | 7.0193 | 69.9179 | -12.4 | -10.2151 | 1.1233 | 0.064399
2016-03-19 17:00 | 17.9333 | 13.3233 | 4.61 | 0 | -0.46315 | 88.6752 | 90.1525 | -0.15249 | 88.6049 | 88.8681 | 0 | 9.9925 | 0.8 | 1 | 3.5867 | 13.5792 | -13.9 | -13.4757 | 1.1347 | 0.012634
2016-03-19 18:00 | 0.77 | 0.53 | 0.24 | 0 | -0.44673 | 103.6784 | 93.4928 | -3.4928 | 103.2406 | 103.2057 | 0 | 0.3975 | 0.8 | 1 | 0.154 | 0.5515 | -13.8 | -13.7828 | 1.1357 | 0.00051362
2016-03-19 19:00 | 0.51333 | 0.35333 | 0.16 | 0 | -0.4303 | 118.6816 | 96.6353 | -6.6353 | 117.9702 | 117.4665 | 0 | 0.265 | 0.8 | 1 | 0.10267 | 0.36767 | -12.9 | -12.8885 | 1.1326 | 0.00034147
2016-03-19 20:00 | 0.25667 | 0.17667 | 0.08 | 0 | -0.41388 | 133.6847 | 99.3692 | -9.3692 | 132.8691 | 131.5075 | 0 | 0.1325 | 0.8 | 1 | 0.051333 | 0.18383 | -14 | -13.9943 | 1.1365 | 0.00017132
2016-03-19 21:00 | 0 | 0 | 0 | 0 | -0.39746 | 148.6879 | 101.5033 | -11.5033 | 147.9716 | 145.0016 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.9 | -13.9 | 1.1361 | 0
2016-03-19 22:00 | 0 | 0 | 0 | 0 | -0.38104 | 163.6911 | 102.8805 | -12.8805 | 163.2582 | 156.9126 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.1 | -13.1 | 1.1334 | 0
2016-03-19 23:00 | 0 | 0 | 0 | 0 | -0.36462 | 178.6942 | 103.3945 | -13.3945 | 178.6577 | 163.3482 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.9 | -13.9 | 1.1361 | 0
2016-03-20 | 0 | 0 | 0 | 0 | -0.3482 | -166.3026 | 103.0041 | -13.0041 | -165.935 | 158.5957 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.5 | -13.5 | 1.1347 | 0
2016-03-20 01:00 | 0 | 0 | 0 | 0 | -0.33178 | -151.2994 | 101.7387 | -11.7387 | -150.6277 | 147.2077 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.1 | -13.1 | 1.1334 | 0
2016-03-20 02:00 | 0 | 0 | 0 | 0 | -0.31536 | -136.2963 | 99.6943 | -9.6943 | -135.4985 | 133.8722 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.5 | -13.5 | 1.1347 | 0
2016-03-20 03:00 | 0 | 0 | 0 | 0 | -0.29894 | -121.2931 | 97.0202 | -7.0202 | -120.575 | 119.8892 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.8 | -13.8 | 1.1358 | 0
2016-03-20 04:00 | 8.3 | 6.7633 | 1.5367 | 0 | -0.28253 | -106.2899 | 93.9026 | -3.9026 | -105.8303 | 105.6479 | 0 | 5.0725 | 0.8 | 1 | 1.66 | 6.7325 | -13.9 | -13.6896 | 1.1354 | 0.0062682
2016-03-20 05:00 | 16.6 | 13.5267 | 3.0733 | 0 | -0.26611 | -91.2867 | 90.5494 | -0.54941 | -91.1936 | 91.3084 | 0 | 10.145 | 0.8 | 1 | 3.32 | 13.465 | -13.9 | -13.4792 | 1.1347 | 0.012528
2016-03-20 06:00 | 24.9 | 20.29 | 4.61 | 0 | -0.24969 | -76.2835 | 87.1783 | 2.8217 | -76.5692 | 76.9664 | 0 | 15.2175 | 0.8 | 1 | 4.98 | 20.1975 | -14 | -13.3688 | 1.1343 | 0.018786
2016-03-20 07:00 | 52.9767 | 37.2033 | 15.7733 | 151.0864 | -0.23327 | -61.2804 | 84.0074 | 5.9926 | -61.8594 | 62.715 | 69.2606 | 27.9025 | 0.8 | 1 | 10.5953 | 107.7585 | -13.7 | -10.3325 | 1.1237 | 0.099289
2016-03-20 08:00 | 81.0533 | 54.1167 | 26.9367 | 177.002 | -0.21685 | -46.2772 | 81.2466 | 8.7534 | -46.9874 | 48.7018 | 116.8174 | 40.5875 | 0.8 | 1 | 16.2107 | 173.6155 | -12.6 | -7.1745 | 1.1126 | 0.1584
2016-03-20 09:00 | 109.13 | 71.03 | 38.1 | 201.2258 | -0.20044 | -31.274 | 79.0858 | 10.9142 | -31.9171 | 35.2672 | 164.2944 | 53.2725 | 0.8 | 1 | 21.826 | 239.3929 | -12 | -4.519 | 1.1033 | 0.21658
2016-03-20 10:00 | 119.88 | 72.6933 | 47.1867 | 221.1647 | -0.18402 | -16.2708 | 77.6809 | 12.3191 | -16.6652 | 23.4764 | 202.8576 | 54.52 | 0.8 | 1 | 23.976 | 281.3536 | -12.2 | -3.4077 | 1.0994 | 0.25365
2016-03-20 11:00 | 130.63 | 74.3567 | 56.2733 | 252.7868 | -0.16761 | -1.2676 | 77.1375 | 12.8625 | -1.3003 | 17.1797 | 241.5082 | 55.7675 | 0.8 | 1 | 26.126 | 323.4017 | -11.3 | -1.1937 | 1.0917 | 0.2895
2016-03-20 12:00 | 141.38 | 76.02 | 65.36 | 301.898 | -0.15119 | 13.7356 | 77.4966 | 12.5034 | 14.076 | 21.8212 | 280.2664 | 57.015 | 0.8 | 1 | 28.276 | 365.5574 | -11.6 | -0.17633 | 1.0881 | 0.32617
2016-03-20 13:00 | 112.08 | 64.3533 | 47.7267 | 244.1928 | -0.13477 | 28.7388 | 78.7292 | 11.2708 | 29.3584 | 33.0738 | 204.6259 | 48.265 | 0.8 | 1 | 22.416 | 275.3069 | -11.6 | -2.9967 | 1.098 | 0.24787
2016-03-20 14:00 | 82.78 | 52.6867 | 30.0933 | 187.0138 | -0.11836 | 43.7419 | 80.74 | 9.26 | 44.4703 | 46.3373 | 129.1165 | 39.515 | 0.8 | 1 | 16.556 | 185.1875 | -11.6 | -5.8129 | 1.1078 | 0.16823
2016-03-20 15:00 | 53.48 | 41.02 | 12.46 | 108.089 | -0.10194 | 58.7451 | 83.3805 | 6.6195 | 59.3844 | 60.2812 | 53.5843 | 30.765 | 0.8 | 1 | 10.696 | 95.0453 | -12.5 | -9.5298 | 1.1209 | 0.087356
2016-03-20 16:00 | 36.0433 | 27.64 | 8.4033 | 136.2886 | -0.08553 | 73.7483 | 86.465 | 3.535 | 74.1271 | 74.4999 | 36.4218 | 20.73 | 0.8 | 1 | 7.2087 | 64.3605 | -13 | -10.9887 | 1.126 | 0.059423
2016-03-20 17:00 | 18.6067 | 14.26 | 4.3467 | 0 | -0.069117 | 88.7515 | 89.7858 | 0.2142 | 88.7681 | 88.826 | 0 | 10.695 | 0.8 | 1 | 3.7213 | 14.4163 | -15.3 | -14.8495 | 1.1395 | 0.01347
2016-03-20 18:00 | 1.17 | 0.88 | 0.29 | 0 | -0.052704 | 103.7547 | 93.1251 | -3.1251 | 103.4018 | 103.1608 | 0 | 0.66 | 0.8 | 1 | 0.234 | 0.894 | -14.9 | -14.8721 | 1.1396 | 0.00083538
2016-03-20 19:00 | 0.78 | 0.58667 | 0.19333 | 0 | -0.036291 | 118.7579 | 96.2644 | -6.2644 | 118.1244 | 117.41 | 0 | 0.44 | 0.8 | 1 | 0.156 | 0.596 | -14.6 | -14.5814 | 1.1385 | 0.00055642
2016-03-20 20:00 | 0.39 | 0.29333 | 0.096667 | 0 | -0.019878 | 133.7611 | 98.9933 | -8.9933 | 133.0113 | 131.4258 | 0 | 0.22 | 0.8 | 1 | 0.078 | 0.298 | -15 | -14.9907 | 1.14 | 0.00027856
2016-03-20 21:00 | 0 | 0 | 0 | 0 | -0.0034665 | 148.7643 | 101.1213 | -11.1213 | 148.0969 | 144.8695 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.1 | -15.1 | 1.1403 | 0
2016-03-20 22:00 | 0 | 0 | 0 | 0 | 0.012945 | 163.7675 | 102.4923 | -12.4923 | 163.3626 | 156.6758 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.9 | -14.9 | 1.1397 | 0
2016-03-20 23:00 | 0 | 0 | 0 | 0 | 0.029356 | 178.7707 | 103.0009 | -13.0009 | 178.7384 | 162.9609 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.3 | -15.3 | 1.141 | 0
2016-03-21 | 0 | 0 | 0 | 0 | 0.045766 | -166.2261 | 102.6065 | -12.6065 | -165.8789 | 158.2386 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.7 | -15.7 | 1.1424 | 0
2016-03-21 01:00 | 0 | 0 | 0 | 0 | 0.062177 | -151.2229 | 101.3387 | -11.3387 | -150.5946 | 146.9329 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.7 | -15.7 | 1.1424 | 0
2016-03-21 02:00 | 0 | 0 | 0 | 0 | 0.078586 | -136.2197 | 99.2932 | -9.2932 | -135.4849 | 133.6437 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.4 | -15.4 | 1.1414 | 0
2016-03-21 03:00 | 0 | 0 | 0 | 0 | 0.094995 | -121.2165 | 96.6189 | -6.6189 | -120.5763 | 119.6849 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.8 | -15.8 | 1.1428 | 0
2016-03-21 04:00 | 10.9733 | 7.5767 | 3.3967 | 0 | 0.1114 | -106.2133 | 93.5014 | -3.5014 | -105.841 | 105.4557 | 0 | 5.6825 | 0.8 | 1 | 2.1947 | 7.8772 | -13.7 | -13.4538 | 1.1346 | 0.0073286
2016-03-21 05:00 | 21.9467 | 15.1533 | 6.7933 | 0 | 0.12781 | -91.21 | 90.1483 | -0.14835 | -91.2077 | 91.1201 | 0 | 11.365 | 0.8 | 1 | 4.3893 | 15.7543 | -14.8 | -14.3077 | 1.1376 | 0.014696
2016-03-21 06:00 | 32.92 | 22.73 | 10.19 | 181.2538 | 0.14422 | -76.2068 | 86.7772 | 3.2228 | -76.5808 | 76.7751 | 41.4662 | 17.0475 | 0.8 | 1 | 6.584 | 65.0977 | -13.8 | -11.7657 | 1.1287 | 0.060249
2016-03-21 07:00 | 70.8067 | 36.3833 | 34.4233 | 309.111 | 0.16063 | -61.2036 | 83.6061 | 6.3939 | -61.8625 | 62.5129 | 142.6697 | 27.2875 | 0.8 | 1 | 14.1613 | 184.1185 | -13.4 | -7.6463 | 1.1143 | 0.16823
2016-03-21 08:00 | 108.6933 | 50.0367 | 58.6567 | 368.6804 | 0.17703 | -46.2004 | 80.8454 | 9.1546 | -46.9765 | 48.4777 | 244.4023 | 37.5275 | 0.8 | 1 | 21.7387 | 303.6684 | -12.2 | -2.7104 | 1.097 | 0.27316
2016-03-21 09:00 | 146.58 | 63.69 | 82.89 | 422.4906 | 0.19344 | -31.1972 | 78.6855 | 11.3145 | -31.8872 | 35.0013 | 346.0785 | 47.7675 | 0.8 | 1 | 29.316 | 423.162 | -12 | 1.2238 | 1.0832 | 0.37587
2016-03-21 10:00 | 152.8533 | 64.8533 | 88 | 399.7517 | 0.20984 | -16.194 | 77.2829 | 12.7171 | -16.6128 | 23.1342 | 367.6065 | 48.64 | 0.8 | 1 | 30.5707 | 446.8172 | -12 | 1.963 | 1.0806 | 0.39593
2016-03-21 11:00 | 159.1267 | 66.0167 | 93.11 | 406.0363 | 0.22625 | -1.1908 | 76.7433 | 13.2567 | -1.2234 | 16.7815 | 388.7444 | 49.5125 | 0.8 | 1 | 31.8253 | 470.0822 | -12.3 | 2.3901 | 1.0791 | 0.41597
2016-03-21 12:00 | 165.4 | 67.18 | 98.22 | 440.2106 | 0.24265 | 13.8125 | 77.1076 | 12.8924 | 14.1769 | 21.5584 | 409.4149 | 50.385 | 0.8 | 1 | 33.08 | 492.8799 | -11.9 | 3.5025 | 1.0752 | 0.43457
2016-03-21 13:00 | 131.7133 | 60.11 | 71.6033 | 354.479 | 0.25906 | 28.8157 | 78.3463 | 11.6537 | 29.4809 | 32.9285 | 297.5319 | 45.0825 | 0.8 | 1 | 26.3427 | 368.9571 | -12.1 | -0.57009 | 1.0895 | 0.32962
2016-03-21 14:00 | 98.0267 | 53.04 | 44.9867 | 268.7371 | 0.27546 | 43.8189 | 80.3633 | 9.6367 | 44.6105 | 46.2493 | 185.8376 | 39.78 | 0.8 | 1 | 19.6053 | 245.2229 | -11.5 | -3.8368 | 1.1009 | 0.22138
2016-03-21 15:00 | 64.34 | 45.97 | 18.37 | 150.9312 | 0.29186 | 58.8221 | 83.0091 | 6.9909 | 59.5375 | 60.2218 | 74.9591 | 34.4775 | 0.8 | 1 | 12.868 | 122.3046 | -11.8 | -7.978 | 1.1154 | 0.11187
2016-03-21 16:00 | 43.3967 | 31.08 | 12.3167 | 180.9614 | 0.30826 | 73.8253 | 86.0973 | 3.9027 | 74.2881 | 74.4542 | 48.4991 | 23.31 | 0.8 | 1 | 8.6793 | 80.4884 | -11.7 | -9.1847 | 1.1196 | 0.073897
2016-03-21 17:00 | 22.4533 | 16.19 | 6.2633 | 0 | 0.32467 | 88.8286 | 89.4195 | 0.58047 | 88.9319 | 88.7848 | 0 | 12.1425 | 0.8 | 1 | 4.4907 | 16.6332 | -12.2 | -11.6802 | 1.1284 | 0.01539
2016-03-21 18:00 | 1.51 | 1.3 | 0.21 | 0 | 0.34107 | 103.8318 | 92.7578 | -2.7578 | 103.5635 | 103.1161 | 0 | 0.975 | 0.8 | 1 | 0.302 | 1.277 | -11.4 | -11.3601 | 1.1273 | 0.0011804
2016-03-21 19:00 | 1.0067 | 0.86667 | 0.14 | 0 | 0.35747 | 118.835 | 95.8938 | -5.8938 | 118.2791 | 117.3528 | 0 | 0.65 | 0.8 | 1 | 0.20133 | 0.85133 | -11.4 | -11.3734 | 1.1273 | 0.00078697
2016-03-21 20:00 | 0.50333 | 0.43333 | 0.07 | 0 | 0.37387 | 133.8382 | 98.6176 | -8.6176 | 133.1539 | 131.3426 | 0 | 0.325 | 0.8 | 1 | 0.10067 | 0.42567 | -11.4 | -11.3867 | 1.1274 | 0.0003935
2016-03-21 21:00 | 0 | 0 | 0 | 0 | 0.39027 | 148.8415 | 100.7395 | -10.7395 | 148.2226 | 144.7346 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.3 | -11.3 | 1.1271 | 0
2016-03-21 22:00 | 0 | 0 | 0 | 0 | 0.40666 | 163.8447 | 102.1043 | -12.1043 | 163.4674 | 156.4354 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.1 | -11.1 | 1.1263 | 0
2016-03-21 23:00 | 0 | 0 | 0 | 0 | 0.42306 | 178.8479 | 102.6076 | -12.6076 | 178.8195 | 162.5732 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.9 | -12.9 | 1.1326 | 0
2016-03-22 | 0 | 0 | 0 | 0 | 0.43946 | -166.1488 | 102.2092 | -12.2092 | -165.8221 | 157.8798 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.1 | -11.1 | 1.1263 | 0
2016-03-22 01:00 | 0 | 0 | 0 | 0 | 0.45585 | -151.1456 | 100.9389 | -10.9389 | -150.5607 | 146.6553 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.4 | -11.4 | 1.1274 | 0
2016-03-22 02:00 | 0 | 0 | 0 | 0 | 0.47225 | -136.1424 | 98.8923 | -8.8923 | -135.4707 | 133.4129 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.5 | -11.5 | 1.1278 | 0
2016-03-22 03:00 | 0 | 0 | 0 | 0 | 0.48865 | -121.1391 | 96.2177 | -6.2177 | -120.5769 | 119.4789 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.9 | -10.9 | 1.1257 | 0
2016-03-22 04:00 | 8.44 | 8.3167 | 0.12333 | 0 | 0.50504 | -106.1359 | 93.1004 | -3.1004 | -105.8509 | 105.2623 | 0 | 6.2375 | 0.8 | 1 | 1.688 | 7.9255 | -13.7 | -13.4523 | 1.1346 | 0.0073736
2016-03-22 05:00 | 16.88 | 16.6333 | 0.24667 | 0 | 0.52143 | -91.1327 | 89.7474 | 0.25258 | -91.2211 | 90.9311 | 0 | 12.475 | 0.8 | 1 | 3.376 | 15.851 | -12.2 | -11.7047 | 1.1285 | 0.014668
2016-03-22 06:00 | 25.32 | 24.95 | 0.37 | 5.8539 | 0.53783 | -76.1294 | 86.3762 | 3.6238 | -76.5916 | 76.5837 | 1.3582 | 18.7125 | 0.8 | 1 | 5.064 | 25.1347 | -11.2 | -10.4145 | 1.124 | 0.023165
2016-03-22 07:00 | 48.93 | 41.1533 | 7.7767 | 65.7273 | 0.55422 | -61.1262 | 83.205 | 6.795 | -61.8649 | 62.3114 | 30.5412 | 30.865 | 0.8 | 1 | 9.786 | 71.1922 | -12.2 | -9.9752 | 1.1224 | 0.065524
2016-03-22 08:00 | 72.54 | 57.3567 | 15.1833 | 91.4637 | 0.57061 | -46.123 | 80.4444 | 9.5556 | -46.9648 | 48.2549 | 60.8982 | 43.0175 | 0.8 | 1 | 14.508 | 118.4237 | -11.9 | -8.1993 | 1.1162 | 0.10839
2016-03-22 09:00 | 96.15 | 73.56 | 22.59 | 111.262 | 0.587 | -31.1197 | 78.2855 | 11.7145 | -31.8565 | 34.7372 | 91.4322 | 55.17 | 0.8 | 1 | 19.23 | 165.8322 | -12.7 | -7.5177 | 1.1138 | 0.15146
2016-03-22 10:00 | 100.9633 | 82.3133 | 18.65 | 82.1939 | 0.60339 | -16.1165 | 76.8852 | 13.1148 | -16.5594 | 22.7935 | 75.7751 | 61.735 | 0.8 | 1 | 20.1927 | 157.7028 | -13.1 | -8.1718 | 1.1161 | 0.14433
2016-03-22 11:00 | 105.7767 | 91.0667 | 14.71 | 62.3304 | 0.61978 | -1.1132 | 76.3494 | 13.6506 | -1.1455 | 16.3836 | 59.7994 | 68.3 | 0.8 | 1 | 21.1553 | 149.2548 | -11.6 | -6.9358 | 1.1118 | 0.13607
2016-03-22 12:00 | 110.59 | 99.82 | 10.77 | 46.8818 | 0.63617 | 13.89 | 76.719 | 13.281 | 14.2788 | 21.3004 | 43.6792 | 74.865 | 0.8 | 1 | 22.118 | 140.6622 | -12.5 | -8.1043 | 1.1159 | 0.12871
2016-03-22 13:00 | 95.5633 | 82.08 | 13.4833 | 64.6594 | 0.65256 | 28.8933 | 77.9639 | 12.0361 | 29.6044 | 32.7877 | 54.3581 | 61.56 | 0.8 | 1 | 19.1127 | 135.0307 | -12.3 | -8.0803 | 1.1158 | 0.12355
2016-03-22 14:00 | 80.5367 | 64.34 | 16.1967 | 93.1539 | 0.66895 | 43.8965 | 79.9871 | 10.0129 | 44.7516 | 46.1646 | 64.5174 | 48.255 | 0.8 | 1 | 16.1073 | 128.8798 | -12.9 | -8.8725 | 1.1186 | 0.11821
2016-03-22 15:00 | 65.51 | 46.6 | 18.91 | 147.5812 | 0.68533 | 58.8998 | 82.6383 | 7.3617 | 59.6914 | 60.1646 | 73.4231 | 34.95 | 0.8 | 1 | 13.102 | 121.4751 | -14 | -10.2039 | 1.1232 | 0.11188
2016-03-22 16:00 | 44.34 | 31.63 | 12.71 | 170.7075 | 0.70172 | 73.903 | 85.7301 | 4.2699 | 74.4497 | 74.4101 | 45.8777 | 23.7225 | 0.8 | 1 | 8.868 | 78.4682 | -15.2 | -12.7479 | 1.1321 | 0.072845
2016-03-22 17:00 | 23.17 | 16.66 | 6.51 | 0 | 0.7181 | 88.9063 | 89.0537 | 0.94625 | 89.0964 | 88.7444 | 0 | 12.495 | 0.8 | 1 | 4.634 | 17.129 | -14.9 | -14.3647 | 1.1378 | 0.015981
2016-03-22 18:00 | 2 | 1.69 | 0.31 | 0 | 0.73449 | 103.9095 | 92.391 | -2.391 | 103.7257 | 103.0715 | 0 | 1.2675 | 0.8 | 1 | 0.4 | 1.6675 | -14.9 | -14.8479 | 1.1395 | 0.0015581
2016-03-22 19:00 | 1.3333 | 1.1267 | 0.20667 | 0 | 0.75087 | 118.9128 | 95.5236 | -5.5236 | 118.4341 | 117.2949 | 0 | 0.845 | 0.8 | 1 | 0.26667 | 1.1117 | -14 | -13.9653 | 1.1364 | 0.0010359
2016-03-22 20:00 | 0.66667 | 0.56333 | 0.10333 | 0 | 0.76725 | 133.916 | 98.2423 | -8.2423 | 133.2968 | 131.2577 | 0 | 0.4225 | 0.8 | 1 | 0.13333 | 0.55583 | -14.3 | -14.2826 | 1.1375 | 0.00051845
2016-03-22 21:00 | 0 | 0 | 0 | 0 | 0.78363 | 148.9193 | 100.3581 | -10.3581 | 148.3487 | 144.5969 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.1 | -14.1 | 1.1368 | 0
2016-03-22 22:00 | 0 | 0 | 0 | 0 | 0.80002 | 163.9225 | 101.7168 | -11.7168 | 163.5724 | 156.1917 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.4 | -14.4 | 1.1379 | 0
2016-03-22 23:00 | 0 | 0 | 0 | 0 | 0.8164 | 178.9258 | 102.2146 | -12.2146 | 178.901 | 162.1854 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.5 | -13.5 | 1.1347 | 0
2016-03-23 | 0 | 0 | 0 | 0 | 0.83278 | -166.071 | 101.8121 | -11.8121 | -165.7649 | 157.5195 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.6 | -13.6 | 1.1351 | 0
2016-03-23 01:00 | 0 | 0 | 0 | 0 | 0.84915 | -151.0677 | 100.5394 | -10.5394 | -150.5264 | 146.3753 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.6 | -13.6 | 1.1351 | 0
2016-03-23 02:00 | 0 | 0 | 0 | 0 | 0.86553 | -136.0645 | 98.4916 | -8.4916 | -135.4558 | 133.1799 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14 | -14 | 1.1365 | 0
2016-03-23 03:00 | 0 | 0 | 0 | 0 | 0.88191 | -121.0612 | 95.8168 | -5.8168 | -120.5768 | 119.2714 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.2 | -14.2 | 1.1372 | 0
2016-03-23 04:00 | 10.8767 | 9.74 | 1.1367 | 0 | 0.89828 | -106.0579 | 92.6996 | -2.6996 | -105.8601 | 105.0678 | 0 | 7.305 | 0.8 | 1 | 2.1753 | 9.4803 | -14.9 | -14.6037 | 1.1386 | 0.0088514
2016-03-23 05:00 | 21.7533 | 19.48 | 2.2733 | 0 | 0.91466 | -91.0547 | 89.3467 | 0.65327 | -91.2338 | 90.7417 | 0 | 14.61 | 0.8 | 1 | 4.3507 | 18.9607 | -14.8 | -14.2075 | 1.1372 | 0.017681
2016-03-23 06:00 | 32.63 | 29.22 | 3.41 | 48.5863 | 0.93103 | -76.0514 | 85.9754 | 4.0246 | -76.6018 | 76.3924 | 11.4309 | 21.915 | 0.8 | 1 | 6.526 | 39.8719 | -14.3 | -13.054 | 1.1332 | 0.03705
2016-03-23 07:00 | 64.2233 | 51.9 | 12.3233 | 98.3811 | 0.94741 | -61.0482 | 82.8042 | 7.1958 | -61.8667 | 62.1106 | 46.0194 | 38.925 | 0.8 | 1 | 12.8447 | 97.7891 | -13.7 | -10.6441 | 1.1248 | 0.090191
2016-03-23 08:00 | 95.8167 | 74.58 | 21.2367 | 122.8294 | 0.96378 | -46.0449 | 80.0438 | 9.9562 | -46.9525 | 48.0333 | 82.1358 | 55.935 | 0.8 | 1 | 19.1633 | 157.2341 | -13.3 | -8.3864 | 1.1169 | 0.144
2016-03-23 09:00 | 127.41 | 97.26 | 30.15 | 143.6677 | 0.98015 | -31.0416 | 77.8859 | 12.1141 | -31.8251 | 34.4751 | 118.4357 | 72.945 | 0.8 | 1 | 25.482 | 216.8627 | -13.1 | -6.323 | 1.1096 | 0.19732
2016-03-23 10:00 | 131.8533 | 97.6667 | 34.1867 | 146.3151 | 0.99652 | -16.0384 | 76.4879 | 13.5121 | -16.5052 | 22.4547 | 135.2218 | 73.25 | 0.8 | 1 | 26.3707 | 234.8424 | -12.7 | -5.3612 | 1.1063 | 0.21303
2016-03-23 11:00 | 136.2967 | 98.0733 | 38.2233 | 157.5129 | 1.0129 | -1.0351 | 75.9559 | 14.0441 | -1.0668 | 15.9863 | 151.4216 | 73.555 | 0.8 | 1 | 27.2593 | 252.2359 | -12.6 | -4.7176 | 1.104 | 0.22835
2016-03-23 12:00 | 140.74 | 98.48 | 42.26 | 178.8296 | 1.0293 | 13.9682 | 76.3309 | 13.6691 | 14.3816 | 21.0474 | 166.8988 | 73.86 | 0.8 | 1 | 28.148 | 268.9068 | -12 | -3.5967 | 1.1001 | 0.24257
2016-03-23 13:00 | 117.2867 | 82.4 | 34.8867 | 162.2314 | 1.0456 | 28.9714 | 77.582 | 12.418 | 29.7287 | 32.6514 | 136.5938 | 61.8 | 0.8 | 1 | 23.4573 | 221.8511 | -11.5 | -4.5672 | 1.1035 | 0.20074
2016-03-23 14:00 | 93.8333 | 66.32 | 27.5133 | 152.5788 | 1.062 | 43.9747 | 79.6115 | 10.3885 | 44.8935 | 46.0831 | 105.8308 | 49.74 | 0.8 | 1 | 18.7667 | 174.3375 | -11.3 | -5.852 | 1.108 | 0.15839
2016-03-23 15:00 | 70.38 | 50.24 | 20.14 | 149.6962 | 1.0784 | 58.978 | 82.268 | 7.732 | 59.846 | 60.1097 | 74.5997 | 37.68 | 0.8 | 1 | 14.076 | 126.3557 | -11 | -7.0514 | 1.1122 | 0.11523
2016-03-23 16:00 | 47.8733 | 34.21 | 13.6633 | 169.0293 | 1.0947 | 73.9812 | 85.3635 | 4.6365 | 74.612 | 74.3674 | 45.5481 | 25.6575 | 0.8 | 1 | 9.5747 | 80.7802 | -11.6 | -9.0756 | 1.1193 | 0.07414
2016-03-23 17:00 | 25.3667 | 18.18 | 7.1867 | 0 | 1.1111 | 88.9845 | 88.6885 | 1.3115 | 89.2612 | 88.7046 | 0 | 13.635 | 0.8 | 1 | 5.0733 | 18.7083 | -12.2 | -11.6154 | 1.1282 | 0.017307
2016-03-23 18:00 | 2.86 | 2.15 | 0.71 | 0 | 1.1275 | 103.9878 | 92.0247 | -2.0247 | 103.8883 | 103.0268 | 0 | 1.6125 | 0.8 | 1 | 0.572 | 2.1845 | -11.6 | -11.5317 | 1.1279 | 0.0020203
2016-03-23 19:00 | 1.9067 | 1.4333 | 0.47333 | 0 | 1.1438 | 118.991 | 95.154 | -5.154 | 118.5894 | 117.2362 | 0 | 1.075 | 0.8 | 1 | 0.38133 | 1.4563 | -12 | -11.9545 | 1.1293 | 0.0013487
2016-03-23 20:00 | 0.95333 | 0.71667 | 0.23667 | 0 | 1.1602 | 133.9943 | 97.8676 | -7.8676 | 133.4399 | 131.1711 | 0 | 0.5375 | 0.8 | 1 | 0.19067 | 0.72817 | -12.5 | -12.4772 | 1.1312 | 0.00067542
2016-03-23 21:00 | 0 | 0 | 0 | 0 | 1.1765 | 148.9976 | 99.9772 | -9.9772 | 148.4748 | 144.4564 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.4 | -13.4 | 1.1344 | 0
2016-03-23 22:00 | 0 | 0 | 0 | 0 | 1.1929 | 164.0009 | 101.3296 | -11.3296 | 163.6777 | 155.9446 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.6 | -13.6 | 1.1351 | 0
2016-03-23 23:00 | 0 | 0 | 0 | 0 | 1.2093 | 179.0041 | 101.8221 | -11.8221 | 178.9828 | 161.7976 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14 | -14 | 1.1365 | 0
2016-03-24 | 0 | 0 | 0 | 0 | 1.2256 | -165.9926 | 101.4156 | -11.4156 | -165.7073 | 157.1581 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.4 | -13.4 | 1.1344 | 0
2016-03-24 01:00 | 0 | 0 | 0 | 0 | 1.242 | -150.9893 | 100.1403 | -10.1403 | -150.4915 | 146.0929 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.2 | -13.2 | 1.1337 | 0
2016-03-24 02:00 | 0 | 0 | 0 | 0 | 1.2583 | -135.986 | 98.0914 | -8.0914 | -135.4404 | 132.9448 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.1 | -14.1 | 1.1368 | 0
2016-03-24 03:00 | 0 | 0 | 0 | 0 | 1.2747 | -120.9828 | 95.4163 | -5.4163 | -120.5761 | 119.0623 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.3 | -14.3 | 1.1376 | 0
2016-03-24 04:00 | 15.4367 | 9.4433 | 5.9933 | 0 | 1.291 | -105.9795 | 92.2992 | -2.2992 | -105.8687 | 104.8725 | 0 | 7.0825 | 0.8 | 1 | 3.0873 | 10.1698 | -15 | -14.6822 | 1.1389 | 0.0094975
2016-03-24 05:00 | 30.8733 | 18.8867 | 11.9867 | 0 | 1.3074 | -90.9762 | 88.9464 | 1.0536 | -91.2459 | 90.5519 | 0 | 14.165 | 0.8 | 1 | 6.1747 | 20.3397 | -14.2 | -13.5644 | 1.135 | 0.01893
2016-03-24 06:00 | 46.31 | 28.33 | 17.98 | 233.043 | 1.3237 | -75.9729 | 85.5751 | 4.4249 | -76.6114 | 76.2014 | 55.5832 | 21.2475 | 0.8 | 1 | 9.262 | 86.0927 | -13.6 | -10.9096 | 1.1257 | 0.079469
2016-03-24 07:00 | 82.41 | 44.6867 | 37.7233 | 285.367 | 1.3401 | -60.9696 | 82.4037 | 7.5963 | -61.8679 | 61.9106 | 134.3648 | 33.515 | 0.8 | 1 | 16.482 | 184.3618 | -12 | -6.2387 | 1.1093 | 0.16771
2016-03-24 08:00 | 118.51 | 61.0433 | 57.4667 | 319.6648 | 1.3564 | -45.9664 | 79.6435 | 10.3565 | -46.9395 | 47.8133 | 214.6705 | 45.7825 | 0.8 | 1 | 23.702 | 284.155 | -11.9 | -3.0202 | 1.0981 | 0.25586
2016-03-24 09:00 | 154.61 | 77.4 | 77.21 | 356.3546 | 1.3728 | -30.9631 | 77.4867 | 12.5133 | -31.7931 | 34.2151 | 294.681 | 58.05 | 0.8 | 1 | 30.922 | 383.653 | -11.4 | 0.58916 | 1.0854 | 0.34147
2016-03-24 10:00 | 155.8433 | 83.41 | 72.4333 | 301.3287 | 1.3891 | -15.9598 | 76.091 | 13.909 | -16.4504 | 22.1178 | 279.1543 | 62.5575 | 0.8 | 1 | 31.1687 | 372.8805 | -11.4 | 0.25252 | 1.0866 | 0.33225
2016-03-24 11:00 | 157.0767 | 89.42 | 67.6567 | 271.3705 | 1.4055 | -0.9565 | 75.563 | 14.437 | -0.9874 | 15.5896 | 261.3871 | 67.065 | 0.8 | 1 | 31.4153 | 359.8675 | -10.7 | 0.54586 | 1.0856 | 0.32035
2016-03-24 12:00 | 158.31 | 95.43 | 62.88 | 258.8922 | 1.4218 | 14.0468 | 75.9434 | 14.0566 | 14.4852 | 20.7994 | 242.02 | 71.5725 | 0.8 | 1 | 31.662 | 345.2545 | -10.5 | 0.2892 | 1.0865 | 0.30759
2016-03-24 13:00 | 135.6533 | 81.8733 | 53.78 | 242.7591 | 1.4382 | 29.0501 | 77.2007 | 12.7993 | 29.8539 | 32.5197 | 204.6961 | 61.405 | 0.8 | 1 | 27.1307 | 293.2318 | -10.5 | -1.3365 | 1.0922 | 0.26261
2016-03-24 14:00 | 112.9967 | 68.3167 | 44.68 | 239.2434 | 1.4545 | 44.0533 | 79.2365 | 10.7635 | 45.0361 | 46.0049 | 166.1778 | 51.2375 | 0.8 | 1 | 22.5993 | 240.0146 | -10.6 | -3.0995 | 1.0983 | 0.21617
2016-03-24 15:00 | 90.34 | 54.76 | 35.58 | 252.4687 | 1.4709 | 59.0566 | 81.8984 | 8.1016 | 60.0013 | 60.057 | 126.0169 | 41.07 | 0.8 | 1 | 18.068 | 185.1549 | -10.6 | -4.8139 | 1.1043 | 0.16767
2016-03-24 16:00 | 61.4833 | 37.4733 | 24.01 | 275.3481 | 1.4872 | 74.0599 | 84.9975 | 5.0025 | 74.7748 | 74.326 | 74.3891 | 28.105 | 0.8 | 1 | 12.2967 | 114.7907 | -10.9 | -7.3128 | 1.1131 | 0.10477
2016-03-24 17:00 | 32.6267 | 20.1867 | 12.44 | 0 | 1.5035 | 89.0632 | 88.3239 | 1.6761 | 89.4265 | 88.6655 | 0 | 15.14 | 0.8 | 1 | 6.5253 | 21.6653 | -10.6 | -9.923 | 1.1222 | 0.019937
2016-03-24 18:00 | 3.77 | 2.9 | 0.87 | 0 | 1.5199 | 104.0665 | 91.659 | -1.659 | 104.0511 | 102.9821 | 0 | 2.175 | 0.8 | 1 | 0.754 | 2.929 | -11.3 | -11.2085 | 1.1267 | 0.0027062
2016-03-24 19:00 | 2.5133 | 1.9333 | 0.58 | 0 | 1.5362 | 119.0698 | 94.7849 | -4.7849 | 118.7448 | 117.1767 | 0 | 1.45 | 0.8 | 1 | 0.50267 | 1.9527 | -11.6 | -11.539 | 1.1279 | 0.001806
2016-03-24 20:00 | 1.2567 | 0.96667 | 0.29 | 0 | 1.5526 | 134.0731 | 97.4933 | -7.4933 | 133.5831 | 131.0828 | 0 | 0.725 | 0.8 | 1 | 0.25133 | 0.97633 | -11.4 | -11.3695 | 1.1273 | 0.0009025
2016-03-24 21:00 | 0 | 0 | 0 | 0 | 1.5689 | 149.0764 | 99.5969 | -9.5969 | 148.6011 | 144.3132 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.6 | -13.6 | 1.1351 | 0
2016-03-24 22:00 | 0 | 0 | 0 | 0 | 1.5852 | 164.0797 | 100.9431 | -10.9431 | 163.7831 | 155.6944 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.4 | -11.4 | 1.1274 | 0
2016-03-24 23:00 | 0 | 0 | 0 | 0 | 1.6016 | 179.0829 | 101.4301 | -11.4301 | 179.0648 | 161.4097 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.5 | -13.5 | 1.1347 | 0
2016-03-25 | 0 | 0 | 0 | 0 | 1.6179 | -165.9138 | 101.0195 | -11.0195 | -165.6494 | 156.7956 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.2 | -13.2 | 1.1337 | 0
2016-03-25 01:00 | 0.023333 | 0.023333 | 0 | 0 | 1.6342 | -150.9105 | 99.7417 | -9.7417 | -150.4562 | 145.8085 | 0 | 0.0175 | 0.8 | 1 | 0.0046667 | 0.022167 | -13.9 | -13.8993 | 1.1361 | 2.0651e-05
2016-03-25 02:00 | 0.046667 | 0.046667 | 0 | 0 | 1.6506 | -135.9072 | 97.6916 | -7.6916 | -135.4245 | 132.708 | 0 | 0.035 | 0.8 | 1 | 0.0093333 | 0.044333 | -13.3 | -13.2986 | 1.134 | 4.1226e-05
2016-03-25 03:00 | 0.07 | 0.07 | 0 | 0 | 1.6669 | -120.9039 | 95.0162 | -5.0162 | -120.5749 | 118.852 | 0 | 0.0525 | 0.8 | 1 | 0.014 | 0.0665 | -14.4 | -14.3979 | 1.1379 | 6.2049e-05
2016-03-25 04:00 | 18.3067 | 9.6733 | 8.6333 | 0 | 1.6832 | -105.9006 | 91.8992 | -1.8992 | -105.8769 | 104.6764 | 0 | 7.255 | 0.8 | 1 | 3.6613 | 10.9163 | -14.2 | -13.8589 | 1.136 | 0.010169
2016-03-25 05:00 | 36.5433 | 19.2767 | 17.2667 | 0 | 1.6995 | -90.8973 | 88.5466 | 1.4534 | -91.2575 | 90.362 | 0 | 14.4575 | 0.8 | 1 | 7.3087 | 21.7662 | -14.1 | -13.4198 | 1.1345 | 0.020248
2016-03-25 06:00 | 54.78 | 28.88 | 25.9 | 307.932 | 1.7159 | -75.894 | 85.1752 | 4.8248 | -76.6206 | 76.0106 | 74.4401 | 21.66 | 0.8 | 1 | 10.956 | 107.0561 | -11.7 | -8.3545 | 1.1167 | 0.098034
2016-03-25 07:00 | 105.0967 | 34.46 | 70.6367 | 507.7819 | 1.7322 | -60.8907 | 82.0038 | 7.9962 | -61.8686 | 61.7115 | 240.6436 | 25.845 | 0.8 | 1 | 21.0193 | 287.5079 | -12.7 | -3.7154 | 1.1005 | 0.25945
2016-03-25 08:00 | 155.4133 | 40.04 | 115.3733 | 618.1934 | 1.7485 | -45.8874 | 79.2438 | 10.7562 | -46.9261 | 47.5949 | 416.8898 | 30.03 | 0.8 | 1 | 31.0827 | 478.0025 | -12 | 2.9376 | 1.0772 | 0.42223
2016-03-25 09:00 | 205.73 | 45.62 | 160.11 | 716.5258 | 1.7648 | -30.8841 | 77.0881 | 12.9119 | -31.7605 | 33.9576 | 594.3232 | 34.215 | 0.8 | 1 | 41.146 | 669.6842 | -11 | 9.9276 | 1.0528 | 0.57811
2016-03-25 10:00 | 209.5567 | 49.3533 | 160.2033 | 648.368 | 1.7812 | -15.8808 | 75.6948 | 14.3052 | -16.3949 | 21.7832 | 602.071 | 37.015 | 0.8 | 1 | 41.9113 | 680.9973 | -10.9 | 10.3812 | 1.0512 | 0.58699
2016-03-25 11:00 | 213.3833 | 53.0867 | 160.2967 | 626.3077 | 1.7975 | -0.87752 | 75.1708 | 14.8292 | -0.90731 | 15.1937 | 604.4153 | 39.815 | 0.8 | 1 | 42.6767 | 686.9069 | -10.4 | 11.0658 | 1.0488 | 0.59073
2016-03-25 12:00 | 217.21 | 56.82 | 160.39 | 643.0385 | 1.8138 | 14.1258 | 75.5565 | 14.4435 | 14.5894 | 20.5568 | 602.0929 | 42.615 | 0.8 | 1 | 43.442 | 688.1499 | -11.3 | 10.2047 | 1.0518 | 0.5935
2016-03-25 13:00 | 176.5833 | 54.1233 | 122.46 | 537.0855 | 1.8301 | 29.1291 | 76.8202 | 13.1798 | 29.9797 | 32.3925 | 453.5139 | 40.5925 | 0.8 | 1 | 35.3167 | 529.4231 | -11.4 | 5.1445 | 1.0695 | 0.4643
2016-03-25 14:00 | 135.9567 | 51.4267 | 84.53 | 437.598 | 1.8464 | 44.1324 | 78.8623 | 11.1377 | 45.1793 | 45.9298 | 304.3667 | 38.57 | 0.8 | 1 | 27.1913 | 370.128 | -11.1 | 0.4665 | 1.0859 | 0.32957
2016-03-25 15:00 | 95.33 | 48.73 | 46.6 | 316.3635 | 1.8627 | 59.1357 | 81.5296 | 8.4704 | 60.157 | 60.0063 | 158.1515 | 36.5475 | 0.8 | 1 | 19.066 | 213.765 | -11.3 | -4.6198 | 1.1037 | 0.19346
2016-03-25 16:00 | 65.13 | 33.5867 | 31.5433 | 337.1921 | 1.8791 | 74.139 | 84.6323 | 5.3677 | 74.9379 | 74.2859 | 91.3242 | 25.19 | 0.8 | 1 | 13.026 | 129.5402 | -11.8 | -7.7519 | 1.1146 | 0.1184
2016-03-25 17:00 | 34.93 | 18.4433 | 16.4867 | 0 | 1.8954 | 89.1423 | 87.96 | 2.04 | 89.592 | 88.627 | 0 | 13.8325 | 0.8 | 1 | 6.986 | 20.8185 | -13 | -12.3494 | 1.1307 | 0.019303
2016-03-25 18:00 | 4.73 | 3.3 | 1.43 | 0 | 1.9117 | 104.1456 | 91.294 | -1.294 | 104.214 | 102.9373 | 0 | 2.475 | 0.8 | 1 | 0.946 | 3.421 | -13.6 | -13.4931 | 1.1347 | 0.0031832
2016-03-25 19:00 | 3.1533 | 2.2 | 0.95333 | 0 | 1.928 | 119.1489 | 94.4165 | -4.4165 | 118.9003 | 117.1163 | 0 | 1.65 | 0.8 | 1 | 0.63067 | 2.2807 | -13.4 | -13.3287 | 1.1342 | 0.002121
2016-03-25 20:00 | 1.5767 | 1.1 | 0.47667 | 0 | 1.9443 | 134.1522 | 97.1198 | -7.1198 | 133.7262 | 130.9928 | 0 | 0.825 | 0.8 | 1 | 0.31533 | 1.1403 | -12.2 | -12.1644 | 1.1301 | 0.0010567
2016-03-25 21:00 | 0 | 0 | 0 | 0 | 1.9606 | 149.1555 | 99.2172 | -9.2172 | 148.7273 | 144.1671 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.3 | -13.3 | 1.1341 | 0
2016-03-25 22:00 | 0 | 0 | 0 | 0 | 1.9769 | 164.1588 | 100.5571 | -10.5571 | 163.8885 | 155.4412 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.4 | -12.4 | 1.1309 | 0
2016-03-25 23:00 | 0 | 0 | 0 | 0 | 1.9932 | 179.1621 | 101.0387 | -11.0387 | 179.1468 | 161.0221 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.4 | -12.4 | 1.1309 | 0
2016-03-26 | 0 | 0 | 0 | 0 | 2.0095 | -165.8346 | 100.6241 | -10.6241 | -165.5913 | 156.4323 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.3 | -12.3 | 1.1305 | 0
2016-03-26 01:00 | 0.07 | 0.046667 | 0.023333 | 0 | 2.0258 | -150.8313 | 99.3438 | -9.3438 | -150.4207 | 145.5222 | 0 | 0.035 | 0.8 | 1 | 0.014 | 0.049 | -12.8 | -12.7985 | 1.1323 | 4.5496e-05
2016-03-26 02:00 | 0.14 | 0.093333 | 0.046667 | 0 | 2.0421 | -135.828 | 97.2925 | -7.2925 | -135.4082 | 132.4696 | 0 | 0.07 | 0.8 | 1 | 0.028 | 0.098 | -12.2 | -12.1969 | 1.1302 | 9.0822e-05
2016-03-26 03:00 | 0.21 | 0.14 | 0.07 | 0 | 2.0584 | -120.8247 | 94.6168 | -4.6168 | -120.5734 | 118.6405 | 0 | 0.105 | 0.8 | 1 | 0.042 | 0.147 | -12.6 | -12.5954 | 1.1316 | 0.0001364
2016-03-26 04:00 | 15.76 | 11.5133 | 4.2467 | 0 | 2.0747 | -105.8214 | 91.4999 | -1.4999 | -105.8846 | 104.4797 | 0 | 8.635 | 0.8 | 1 | 3.152 | 11.787 | -12.6 | -12.2317 | 1.1303 | 0.010925
2016-03-26 05:00 | 31.31 | 22.8867 | 8.4233 | 0 | 2.091 | -90.8181 | 88.1474 | 1.8526 | -91.2687 | 90.1719 | 0 | 17.165 | 0.8 | 1 | 6.262 | 23.427 | -9.8 | -9.0679 | 1.1192 | 0.021501
2016-03-26 06:00 | 46.86 | 34.26 | 12.6 | 138.3837 | 2.1073 | -75.8148 | 84.7759 | 5.2241 | -76.6293 | 75.8204 | 33.8989 | 25.695 | 0.8 | 1 | 9.372 | 68.9659 | -9.1 | -6.9448 | 1.1118 | 0.062875
2016-03-26 07:00 | 83.4767 | 48.7433 | 34.7333 | 237.8886 | 2.1236 | -60.8115 | 81.6044 | 8.3956 | -61.8689 | 61.5135 | 113.4612 | 36.5575 | 0.8 | 1 | 16.6953 | 166.7141 | -10.2 | -4.9902 | 1.105 | 0.15105
2016-03-26 08:00 | 120.0933 | 63.2267 | 56.8667 | 293.9333 | 2.1399 | -45.8082 | 78.8448 | 11.1552 | -46.9122 | 47.3783 | 199.0382 | 47.42 | 0.8 | 1 | 24.0187 | 270.4768 | -8.9 | -0.4476 | 1.0891 | 0.24155
2016-03-26 09:00 | 156.71 | 77.71 | 79 | 343.1528 | 2.1562 | -30.8049 | 76.6901 | 13.3099 | -31.7274 | 33.7026 | 285.4789 | 58.2825 | 0.8 | 1 | 31.342 | 375.1034 | -9 | 2.722 | 1.078 | 0.33157
2016-03-26 10:00 | 160.9067 | 81.4433 | 79.4633 | 313.1304 | 2.1725 | -15.8016 | 75.2992 | 14.7008 | -16.339 | 21.451 | 291.44 | 61.0825 | 0.8 | 1 | 32.1813 | 384.7039 | -8.4 | 3.622 | 1.0748 | 0.33906
2016-03-26 11:00 | 165.1033 | 85.1767 | 79.9267 | 304.437 | 2.1888 | -0.79825 | 74.7792 | 15.2208 | -0.82667 | 14.7987 | 294.3385 | 63.8825 | 0.8 | 1 | 33.0207 | 391.2417 | -8.5 | 3.7263 | 1.0745 | 0.34471
2016-03-26 12:00 | 169.3 | 88.91 | 80.39 | 314.0909 | 2.205 | 14.2051 | 75.1704 | 14.8296 | 14.6942 | 20.3196 | 294.5452 | 66.6825 | 0.8 | 1 | 33.86 | 395.0877 | -7.7 | 4.6465 | 1.0712 | 0.34705
2016-03-26 13:00 | 139.46 | 77.7333 | 61.7267 | 263.2753 | 2.2213 | 29.2084 | 76.4404 | 13.5596 | 30.106 | 32.2698 | 222.6106 | 58.3 | 0.8 | 1 | 27.892 | 308.8026 | -7.9 | 1.7501 | 1.0814 | 0.27382
2016-03-26 14:00 | 109.62 | 66.5567 | 43.0633 | 215.7928 | 2.2376 | 44.2117 | 78.4888 | 11.5112 | 45.323 | 45.8578 | 150.2871 | 49.9175 | 0.8 | 1 | 21.924 | 222.1286 | -8 | -1.0585 | 1.0912 | 0.19876
2016-03-26 15:00 | 79.78 | 55.38 | 24.4 | 158.8031 | 2.2539 | 59.215 | 81.1615 | 8.8385 | 60.3131 | 59.9577 | 79.503 | 41.535 | 0.8 | 1 | 15.956 | 136.994 | -8 | -3.7189 | 1.1005 | 0.12363
2016-03-26 16:00 | 54.68 | 38.2433 | 16.4367 | 164.5679 | 2.2702 | 74.2183 | 84.2679 | 5.7321 | 75.1013 | 74.247 | 44.6786 | 28.6825 | 0.8 | 1 | 10.936 | 84.2971 | -10 | -7.3657 | 1.1133 | 0.076954
2016-03-26 17:00 | 29.58 | 21.1067 | 8.4733 | 0 | 2.2864 | 89.2216 | 87.5969 | 2.4031 | 89.7576 | 88.5889 | 0 | 15.83 | 0.8 | 1 | 5.916 | 21.746 | -8.6 | -7.9204 | 1.1152 | 0.019886
2016-03-26 18:00 | 4.48 | 3.97 | 0.51 | 0 | 2.3027 | 104.2249 | 90.9298 | -0.92979 | 104.3769 | 102.8923 | 0 | 2.9775 | 0.8 | 1 | 0.896 | 3.8735 | -8.9 | -8.779 | 1.1182 | 0.0035518
2016-03-26 19:00 | 2.9867 | 2.6467 | 0.34 | 0 | 2.319 | 119.2282 | 94.0489 | -4.0489 | 119.0556 | 117.055 | 0 | 1.985 | 0.8 | 1 | 0.59733 | 2.5823 | -7.6 | -7.5193 | 1.1138 | 0.0023585
2016-03-26 20:00 | 1.4933 | 1.3233 | 0.17 | 0 | 2.3353 | 134.2315 | 96.7469 | -6.7469 | 133.8692 | 130.901 | 0 | 0.9925 | 0.8 | 1 | 0.29867 | 1.2912 | -7.6 | -7.5597 | 1.114 | 0.0011794
2016-03-26 21:00 | 0 | 0 | 0 | 0 | 2.3515 | 149.2348 | 98.8382 | -8.8382 | 148.8533 | 144.0184 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.1 | -6.1 | 1.1088 | 0
2016-03-26 22:00 | 0 | 0 | 0 | 0 | 2.3678 | 164.2382 | 100.1719 | -10.1719 | 163.9938 | 155.1851 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.9 | -6.9 | 1.1117 | 0
2016-03-26 23:00 | 0 | 0 | 0 | 0 | 2.3841 | 179.2415 | 100.6481 | -10.6481 | 179.2288 | 160.6348 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.6 | -5.6 | 1.1071 | 0
2016-03-27 | 0 | 0 | 0 | 0 | 2.4004 | -165.7552 | 100.2294 | -10.2294 | -165.5331 | 156.0685 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.7 | -4.7 | 1.1039 | 0
2016-03-27 01:00 | 0 | 0 | 0 | 0 | 2.4166 | -150.7519 | 98.9465 | -8.9465 | -150.385 | 145.2341 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-03-27 02:00 | 0 | 0 | 0 | 0 | 2.4329 | -135.7486 | 96.894 | -6.894 | -135.3917 | 132.2296 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-03-27 03:00 | 0 | 0 | 0 | 0 | 2.4492 | -120.7453 | 94.2181 | -4.2181 | -120.5715 | 118.428 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-03-27 04:00 | 2.79 | 2.6667 | 0.12333 | 0 | 2.4654 | -105.742 | 91.1013 | -1.1013 | -105.8919 | 104.2826 | 0 | 2 | 0.8 | 1 | 0.558 | 2.558 | -2.3 | -2.2201 | 1.0953 | 0.0022974
2016-03-27 05:00 | 5.58 | 5.3333 | 0.24667 | 0 | 2.4817 | -90.7387 | 87.7488 | 2.2512 | -91.2795 | 89.9819 | 0 | 4 | 0.8 | 1 | 1.116 | 5.116 | -2.1 | -1.9401 | 1.0943 | 0.0045907
2016-03-27 06:00 | 8.37 | 8 | 0.37 | 3.7764 | 2.4979 | -75.7354 | 84.3774 | 5.6226 | -76.6377 | 75.6307 | 0.9372 | 6 | 0.8 | 1 | 1.674 | 8.6112 | -1.9 | -1.6309 | 1.0932 | 0.0077193
2016-03-27 07:00 | 18.76 | 12.87 | 5.89 | 38.5256 | 2.5142 | -60.732 | 81.2058 | 8.7942 | -61.8688 | 61.3168 | 18.491 | 9.6525 | 0.8 | 1 | 3.752 | 31.8955 | -1.8 | -0.80327 | 1.0903 | 0.028516
2016-03-27 08:00 | 29.15 | 17.74 | 11.41 | 56.9692 | 2.5305 | -45.7287 | 78.4464 | 11.5536 | -46.898 | 47.1637 | 38.7337 | 13.305 | 0.8 | 1 | 5.83 | 57.8687 | -1.6 | 0.2084 | 1.0868 | 0.05157
2016-03-27 09:00 | 39.54 | 22.61 | 16.93 | 71.447 | 2.5467 | -30.7254 | 76.2929 | 13.7071 | -31.694 | 33.4503 | 59.6129 | 16.9575 | 0.8 | 1 | 7.908 | 84.4784 | -1.4 | 1.2399 | 1.0832 | 0.075033
2016-03-27 10:00 | 40.9233 | 23.0133 | 17.91 | 68.7712 | 2.563 | -15.7221 | 74.9045 | 15.0955 | -16.2826 | 21.1215 | 64.151 | 17.26 | 0.8 | 1 | 8.1847 | 89.5957 | -1.3 | 1.4999 | 1.0823 | 0.079511
2016-03-27 11:00 | 42.3067 | 23.4167 | 18.89 | 70.1935 | 2.5792 | -0.71879 | 74.3885 | 15.6115 | -0.74557 | 14.4048 | 67.9868 | 17.5625 | 0.8 | 1 | 8.4613 | 94.0106 | -0.9 | 2.0378 | 1.0804 | 0.083284
2016-03-27 12:00 | 43.69 | 23.82 | 19.87 | 75.7129 | 2.5955 | 14.2845 | 74.7852 | 15.2148 | 14.7995 | 20.0879 | 71.107 | 17.865 | 0.8 | 1 | 8.738 | 97.71 | -0.4 | 2.6534 | 1.0782 | 0.086389
2016-03-27 13:00 | 35.6933 | 20.83 | 14.8633 | 61.7043 | 2.6117 | 29.2878 | 76.0615 | 13.9385 | 30.2328 | 32.1517 | 52.2415 | 15.6225 | 0.8 | 1 | 7.1387 | 75.0027 | -0.4 | 1.9438 | 1.0807 | 0.066465
2016-03-27 14:00 | 27.6967 | 17.84 | 9.8567 | 47.8652 | 2.628 | 44.2912 | 78.1163 | 11.8837 | 45.4671 | 45.7888 | 33.3766 | 13.38 | 0.8 | 1 | 5.5393 | 52.296 | -0.5 | 1.1342 | 1.0835 | 0.046465
2016-03-27 15:00 | 19.7 | 14.85 | 4.85 | 30.3166 | 2.6442 | 59.2945 | 80.7944 | 9.2056 | 60.4695 | 59.9111 | 15.199 | 11.1375 | 0.8 | 1 | 3.94 | 30.2765 | -0.4 | 0.54614 | 1.0856 | 0.026952
2016-03-27 16:00 | 14.5133 | 10.7767 | 3.7367 | 35.1888 | 2.6605 | 74.2978 | 83.9043 | 6.0957 | 75.2648 | 74.2093 | 9.5757 | 8.0825 | 0.8 | 1 | 2.9027 | 20.5609 | -0.5 | 0.14253 | 1.087 | 0.018327
2016-03-27 17:00 | 9.3267 | 6.7033 | 2.6233 | 0 | 2.6767 | 89.3011 | 87.2347 | 2.7653 | 89.9232 | 88.5513 | 0 | 5.0275 | 0.8 | 1 | 1.8653 | 6.8928 | -0.3 | -0.084599 | 1.0878 | 0.0061484
2016-03-27 18:00 | 4.14 | 2.63 | 1.51 | 0 | 2.6929 | 104.3044 | 90.5664 | -0.56637 | 104.5397 | 102.847 | 0 | 1.9725 | 0.8 | 1 | 0.828 | 2.8005 | 0 | 0.087516 | 1.0872 | 0.0024966
2016-03-27 19:00 | 2.76 | 1.7533 | 1.0067 | 0 | 2.7092 | 119.3077 | 93.682 | -3.682 | 119.2108 | 116.9928 | 0 | 1.315 | 0.8 | 1 | 0.552 | 1.867 | -0.3 | -0.24166 | 1.0883 | 0.0016662
2016-03-27 20:00 | 1.38 | 0.87667 | 0.50333 | 0 | 2.7254 | 134.311 | 96.3749 | -6.3749 | 134.0119 | 130.8073 | 0 | 0.6575 | 0.8 | 1 | 0.276 | 0.9335 | -0.1 | -0.070828 | 1.0877 | 0.00083264
2016-03-27 21:00 | 0 | 0 | 0 | 0 | 2.7417 | 149.3143 | 98.46 | -8.46 | 148.9791 | 143.8669 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-03-27 22:00 | 0 | 0 | 0 | 0 | 2.7579 | 164.3177 | 99.7875 | -9.7875 | 164.0989 | 154.9262 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-03-27 23:00 | 0 | 0 | 0 | 0 | 2.7741 | 179.321 | 100.2583 | -10.2583 | 179.3108 | 160.2478 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-03-28 | 0 | 0 | 0 | 0 | 2.7904 | -165.6757 | 99.8355 | -9.8355 | -165.475 | 155.7043 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.4 | 0.4 | 1.0861 | 0
2016-03-28 01:00 | 0.18667 | 0.18667 | 0 | 0 | 2.8066 | -150.6724 | 98.5501 | -8.5501 | -150.3492 | 144.9447 | 0 | 0.14 | 0.8 | 1 | 0.037333 | 0.17733 | 0 | 0.0055417 | 1.0875 | 0.00015813
2016-03-28 02:00 | 0.37333 | 0.37333 | 0 | 0 | 2.8228 | -135.6691 | 96.4965 | -6.4965 | -135.375 | 131.9884 | 0 | 0.28 | 0.8 | 1 | 0.074667 | 0.35467 | -0.1 | -0.088917 | 1.0878 | 0.00031636
2016-03-28 03:00 | 0.56 | 0.56 | 0 | 0 | 2.839 | -120.6658 | 93.8202 | -3.8202 | -120.5693 | 118.2147 | 0 | 0.42 | 0.8 | 1 | 0.112 | 0.532 | 0.2 | 0.21663 | 1.0867 | 0.00047408
2016-03-28 04:00 | 13.03 | 12.9167 | 0.11333 | 0 | 2.8553 | -105.6624 | 90.7035 | -0.70346 | -105.899 | 104.0851 | 0 | 9.6875 | 0.8 | 1 | 2.606 | 12.2935 | 0.8 | 1.1842 | 1.0834 | 0.010921
2016-03-28 05:00 | 25.5 | 25.2733 | 0.22667 | 0 | 2.8715 | -90.6591 | 87.3512 | 2.6488 | -91.2901 | 89.792 | 0 | 18.955 | 0.8 | 1 | 5.1 | 24.055 | 1.2 | 1.9517 | 1.0807 | 0.021316
2016-03-28 06:00 | 37.97 | 37.63 | 0.34 | 3.2418 | 2.8877 | -75.6558 | 83.9797 | 6.0203 | -76.6458 | 75.4418 | 0.81486 | 28.2225 | 0.8 | 1 | 7.594 | 36.6314 | 1.3 | 2.4447 | 1.0789 | 0.032409
2016-03-28 07:00 | 77.77 | 50.9033 | 26.8667 | 168.1879 | 2.9039 | -60.6525 | 80.8081 | 9.1919 | -61.8686 | 61.1214 | 81.2272 | 38.1775 | 0.8 | 1 | 15.554 | 134.9587 | 0.9 | 5.1175 | 1.0696 | 0.11837
2016-03-28 08:00 | 117.57 | 64.1767 | 53.3933 | 257.845 | 2.9202 | -45.6492 | 78.049 | 11.951 | -46.8836 | 46.9512 | 176.0105 | 48.1325 | 0.8 | 1 | 23.514 | 247.657 | 1.4 | 9.1393 | 1.0555 | 0.21435
2016-03-28 09:00 | 157.37 | 77.45 | 79.92 | 327.9803 | 2.9364 | -30.6459 | 75.8966 | 14.1034 | -31.6603 | 33.2008 | 274.4395 | 58.0875 | 0.8 | 1 | 31.474 | 364.001 | 1.1 | 12.475 | 1.0438 | 0.31157
2016-03-28 10:00 | 161.5733 | 82.2167 | 79.3567 | 297.1497 | 2.9526 | -15.6426 | 74.5106 | 15.4894 | -16.2259 | 20.7948 | 277.7928 | 61.6625 | 0.8 | 1 | 32.3147 | 371.7699 | -0.6 | 11.0178 | 1.0489 | 0.31977
2016-03-28 11:00 | 165.7767 | 86.9833 | 78.7933 | 285.8362 | 2.9688 | -0.63924 | 73.9987 | 16.0013 | -0.66412 | 14.0119 | 277.3312 | 65.2375 | 0.8 | 1 | 33.1553 | 375.724 | -0.5 | 11.2414 | 1.0482 | 0.32293
2016-03-28 12:00 | 169.98 | 91.75 | 78.23 | 290.9209 | 2.985 | 14.3641 | 74.4009 | 15.5991 | 14.9052 | 19.8621 | 273.615 | 68.8125 | 0.8 | 1 | 33.996 | 376.4235 | -0.9 | 10.8632 | 1.0495 | 0.32394
2016-03-28 13:00 | 144.5167 | 78.9633 | 65.5533 | 265.1018 | 3.0012 | 29.3674 | 75.6836 | 14.3164 | 30.36 | 32.038 | 224.7258 | 59.2225 | 0.8 | 1 | 28.9033 | 312.8517 | -1.3 | 8.4766 | 1.0578 | 0.27137
2016-03-28 14:00 | 119.0533 | 66.1767 | 52.8767 | 249.1044 | 3.0174 | 44.3707 | 77.7448 | 12.2552 | 45.6115 | 45.7228 | 173.9073 | 49.6325 | 0.8 | 1 | 23.8107 | 247.3505 | -1.9 | 5.8297 | 1.0671 | 0.21644
2016-03-28 15:00 | 93.59 | 53.39 | 40.2 | 241.7555 | 3.0336 | 59.374 | 80.4282 | 9.5718 | 60.6261 | 59.8663 | 121.3659 | 40.0425 | 0.8 | 1 | 18.718 | 180.1264 | -2 | 3.6289 | 1.0748 | 0.15875
2016-03-28 16:00 | 64.4567 | 37.4433 | 27.0133 | 240.1611 | 3.0498 | 74.3773 | 83.5417 | 6.4583 | 75.4284 | 74.1726 | 65.5017 | 28.0825 | 0.8 | 1 | 12.8913 | 106.4755 | -2.3 | 1.0274 | 1.0839 | 0.094636
2016-03-28 17:00 | 35.3233 | 21.4967 | 13.8267 | 253.499 | 3.066 | 89.3806 | 86.8733 | 3.1267 | 90.0887 | 88.514 | 6.5739 | 16.1225 | 0.8 | 1 | 7.0647 | 29.761 | -3 | -2.07 | 1.0947 | 0.026716
2016-03-28 18:00 | 6.19 | 5.55 | 0.64 | 0 | 3.0822 | 104.384 | 90.2038 | -0.20384 | 104.7023 | 102.8014 | 0 | 4.1625 | 0.8 | 1 | 1.238 | 5.4005 | -3.5 | -3.3312 | 1.0992 | 0.0048675
2016-03-28 19:00 | 4.1267 | 3.7 | 0.42667 | 0 | 3.0984 | 119.3873 | 93.316 | -3.316 | 119.3656 | 116.9294 | 0 | 2.775 | 0.8 | 1 | 0.82533 | 3.6003 | -3.9 | -3.7875 | 1.1008 | 0.0032497
2016-03-28 20:00 | 2.0633 | 1.85 | 0.21333 | 0 | 3.1146 | 134.3906 | 96.0037 | -6.0037 | 134.1542 | 130.7118 | 0 | 1.3875 | 0.8 | 1 | 0.41267 | 1.8002 | -3.8 | -3.7437 | 1.1006 | 0.0016246
2016-03-28 21:00 | 0 | 0 | 0 | 0 | 3.1308 | 149.3939 | 98.0827 | -8.0827 | 149.1045 | 143.7127 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4 | -4 | 1.1015 | 0
2016-03-28 22:00 | 0 | 0 | 0 | 0 | 3.147 | 164.3972 | 99.4041 | -9.4041 | 164.2036 | 154.6647 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.3 | -4.3 | 1.1025 | 0
2016-03-28 23:00 | 0 | 0 | 0 | 0 | 3.1632 | 179.4005 | 99.8694 | -9.8694 | 179.3925 | 159.8614 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-03-29 | 0 | 0 | 0 | 0 | 3.1794 | -165.5962 | 99.4426 | -9.4426 | -165.4169 | 155.3398 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.1033 | 0
2016-03-29 01:00 | 0.34667 | 0.31333 | 0.033333 | 0 | 3.1956 | -150.5928 | 98.1547 | -8.1547 | -150.3133 | 144.6539 | 0 | 0.235 | 0.8 | 1 | 0.069333 | 0.30433 | -4.1 | -4.0905 | 1.1018 | 0.00027496
2016-03-29 02:00 | 0.69333 | 0.62667 | 0.066667 | 0 | 3.2118 | -135.5895 | 96.0998 | -6.0998 | -135.3581 | 131.746 | 0 | 0.47 | 0.8 | 1 | 0.13867 | 0.60867 | -4.5 | -4.481 | 1.1032 | 0.00055061
2016-03-29 03:00 | 1.04 | 0.94 | 0.1 | 0 | 3.228 | -120.5862 | 93.4232 | -3.4232 | -120.567 | 118.0008 | 0 | 0.705 | 0.8 | 1 | 0.208 | 0.913 | -5 | -4.9715 | 1.1049 | 0.00082719
2016-03-29 04:00 | 20.2567 | 13.77 | 6.4867 | 0 | 3.2441 | -105.5829 | 90.3066 | -0.30661 | -105.9059 | 103.8874 | 0 | 10.3275 | 0.8 | 1 | 4.0513 | 14.3788 | -4.5 | -4.0507 | 1.1017 | 0.012989
2016-03-29 05:00 | 39.4733 | 26.6 | 12.8733 | 242.2982 | 3.2603 | -90.5796 | 86.9544 | 3.0456 | -91.3005 | 89.6025 | 1.6808 | 19.95 | 0.8 | 1 | 7.8947 | 29.5254 | -4.6 | -3.6773 | 1.1004 | 0.026641
2016-03-29 06:00 | 58.69 | 39.43 | 19.26 | 172.3259 | 3.2765 | -75.5763 | 83.5829 | 6.4171 | -76.6538 | 75.2538 | 43.8636 | 29.5725 | 0.8 | 1 | 11.738 | 85.1741 | -4.6 | -1.9383 | 1.0943 | 0.076428
2016-03-29 07:00 | 87.1933 | 59.2967 | 27.8967 | 167.4728 | 3.2927 | -60.573 | 80.4113 | 9.5887 | -61.8681 | 60.9275 | 81.3776 | 44.4725 | 0.8 | 1 | 17.4387 | 143.2888 | -3.8 | 0.67777 | 1.0851 | 0.1275
2016-03-29 08:00 | 115.6967 | 79.1633 | 36.5333 | 170.844 | 3.3089 | -45.5696 | 77.6525 | 12.3475 | -46.869 | 46.7409 | 117.0793 | 59.3725 | 0.8 | 1 | 23.1393 | 199.5911 | -4.2 | 2.0372 | 1.0804 | 0.17682
2016-03-29 09:00 | 144.2 | 99.03 | 45.17 | 180.4207 | 3.325 | -30.5663 | 75.5012 | 14.4988 | -31.6265 | 32.9545 | 151.3915 | 74.2725 | 0.8 | 1 | 28.84 | 254.504 | -3.4 | 4.5533 | 1.0716 | 0.22363
2016-03-29 10:00 | 139.9333 | 97.0233 | 42.91 | 156.8 | 3.3412 | -15.563 | 74.1178 | 15.8822 | -16.1691 | 20.4713 | 146.8977 | 72.7675 | 0.8 | 1 | 27.9867 | 247.6519 | -3.1 | 4.6391 | 1.0713 | 0.21755
2016-03-29 11:00 | 135.6667 | 95.0167 | 40.65 | 144.0595 | 3.3574 | -0.55971 | 73.6099 | 16.3901 | -0.58241 | 13.6204 | 140.0081 | 71.2625 | 0.8 | 1 | 27.1333 | 238.404 | -2.4 | 5.0501 | 1.0698 | 0.20914
2016-03-29 12:00 | 131.4 | 93.01 | 38.39 | 139.427 | 3.3735 | 14.4436 | 74.0177 | 15.9823 | 15.0111 | 19.6421 | 131.3139 | 69.7575 | 0.8 | 1 | 26.28 | 227.3514 | -2.4 | 4.7047 | 1.071 | 0.19967
2016-03-29 13:00 | 105.8633 | 78.9067 | 26.9567 | 106.2776 | 3.3897 | 29.4469 | 75.3068 | 14.6932 | 30.4874 | 31.9288 | 90.1985 | 59.18 | 0.8 | 1 | 21.1727 | 170.5511 | -2.7 | 2.6297 | 1.0783 | 0.1508
2016-03-29 14:00 | 80.3267 | 64.8033 | 15.5233 | 71.0184 | 3.4059 | 44.4502 | 77.3742 | 12.6258 | 45.756 | 45.6597 | 49.6361 | 48.6025 | 0.8 | 1 | 16.0653 | 114.3039 | -2.3 | 1.272 | 1.083 | 0.10151
2016-03-29 15:00 | 54.79 | 50.7 | 4.09 | 23.7013 | 3.422 | 59.4535 | 80.063 | 9.937 | 60.7827 | 59.8234 | 11.9138 | 38.025 | 0.8 | 1 | 10.958 | 60.8968 | -2.2 | -0.29697 | 1.0885 | 0.054357
2016-03-29 16:00 | 38.22 | 35.4667 | 2.7533 | 23.1862 | 3.4382 | 74.4569 | 83.1801 | 6.8199 | 75.5919 | 74.1369 | 6.3377 | 26.6 | 0.8 | 1 | 7.644 | 40.5817 | -1.8 | -0.53182 | 1.0894 | 0.036251
2016-03-29 17:00 | 21.65 | 20.2333 | 1.4167 | 23.292 | 3.4544 | 89.4602 | 86.513 | 3.487 | 90.2541 | 88.477 | 0.61906 | 15.175 | 0.8 | 1 | 4.33 | 20.1241 | -1.5 | -0.87112 | 1.0905 | 0.017996
2016-03-29 18:00 | 5.08 | 5 | 0.08 | 0 | 3.4705 | 104.4635 | 89.8423 | 0.15772 | 104.8646 | 102.7554 | 0 | 3.75 | 0.8 | 1 | 1.016 | 4.766 | -1.3 | -1.1511 | 1.0915 | 0.0042658
2016-03-29 19:00 | 3.3867 | 3.3333 | 0.053333 | 0 | 3.4867 | 119.4668 | 92.951 | -2.951 | 119.52 | 116.865 | 0 | 2.5 | 0.8 | 1 | 0.67733 | 3.1773 | -1.1 | -1.0007 | 1.091 | 0.0028425
2016-03-29 20:00 | 1.6933 | 1.6667 | 0.026667 | 0 | 3.5028 | 134.4701 | 95.6335 | -5.6335 | 134.2961 | 130.6144 | 0 | 1.25 | 0.8 | 1 | 0.33867 | 1.5887 | -1.1 | -1.0504 | 1.0912 | 0.0014215
2016-03-29 21:00 | 0 | 0 | 0 | 0 | 3.519 | 149.4734 | 97.7063 | -7.7063 | 149.2295 | 143.5559 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-03-29 22:00 | 0 | 0 | 0 | 0 | 3.5351 | 164.4767 | 99.0216 | -9.0216 | 164.308 | 154.4006 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-03-29 23:00 | 0 | 0 | 0 | 0 | 3.5513 | 179.48 | 99.4815 | -9.4815 | 179.4738 | 159.4756 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-03-30 | 0 | 0 | 0 | 0 | 3.5674 | -165.5167 | 99.0507 | -9.0507 | -165.3591 | 154.9754 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-03-30 01:00 | 0.30667 | 0.30667 | 0 | 0 | 3.5835 | -150.5134 | 97.7603 | -7.7603 | -150.2775 | 144.3621 | 0 | 0.23 | 0.8 | 1 | 0.061333 | 0.29133 | -1.2 | -1.1909 | 1.0917 | 0.00026079
2016-03-30 02:00 | 0.61333 | 0.61333 | 0 | 0 | 3.5997 | -135.51 | 95.7042 | -5.7042 | -135.3413 | 131.5027 | 0 | 0.46 | 0.8 | 1 | 0.12267 | 0.58267 | -1.2 | -1.1818 | 1.0916 | 0.00052157
2016-03-30 03:00 | 0.92 | 0.92 | 0 | 0 | 3.6158 | -120.5067 | 93.0273 | -3.0273 | -120.5646 | 117.7862 | 0 | 0.69 | 0.8 | 1 | 0.184 | 0.874 | -1.3 | -1.2727 | 1.092 | 0.00078258
2016-03-30 04:00 | 12.21 | 12.21 | 0 | 0 | 3.632 | -105.5034 | 89.9108 | 0.089179 | -105.9128 | 103.6896 | 0 | 9.1575 | 0.8 | 1 | 2.442 | 11.5995 | -1.9 | -1.5375 | 1.0929 | 0.010395
2016-03-30 05:00 | 23.5 | 23.5 | 0 | 0 | 3.6481 | -90.5001 | 86.5588 | 3.4412 | -91.3109 | 89.4135 | 0 | 17.625 | 0.8 | 1 | 4.7 | 22.325 | -2.2 | -1.5023 | 1.0928 | 0.020005
2016-03-30 06:00 | 34.79 | 34.79 | 0 | 0 | 3.6642 | -75.4968 | 83.1873 | 6.8127 | -76.6617 | 75.0667 | 0 | 26.0925 | 0.8 | 1 | 6.958 | 33.0505 | -2 | -0.96717 | 1.0909 | 0.029565
2016-03-30 07:00 | 46.42 | 46.2567 | 0.16333 | 0.94205 | 3.6804 | -60.4935 | 80.0156 | 9.9844 | -61.8677 | 60.7353 | 0.46052 | 34.6925 | 0.8 | 1 | 9.284 | 44.437 | -1.9 | -0.51134 | 1.0893 | 0.039692
2016-03-30 08:00 | 58.05 | 57.7233 | 0.32667 | 1.481 | 3.6965 | -45.4902 | 77.2571 | 12.7429 | -46.8543 | 46.5329 | 1.0188 | 43.2925 | 0.8 | 1 | 11.61 | 55.9213 | -1.8 | -0.052459 | 1.0877 | 0.049876
2016-03-30 09:00 | 69.68 | 69.19 | 0.49 | 1.9065 | 3.7126 | -30.4869 | 75.107 | 14.893 | -31.5925 | 32.7114 | 1.6041 | 51.8925 | 0.8 | 1 | 13.936 | 67.4326 | -1.7 | 0.40727 | 1.0861 | 0.060054
2016-03-30 10:00 | 75.5433 | 73.4933 | 2.05 | 7.3154 | 3.7287 | -15.4836 | 73.726 | 16.274 | -16.112 | 20.151 | 6.8676 | 55.12 | 0.8 | 1 | 15.1087 | 77.0963 | -1.8 | 0.60926 | 1.0854 | 0.068616
2016-03-30 11:00 | 81.4067 | 77.7967 | 3.61 | 12.5061 | 3.7449 | -0.48027 | 73.2223 | 16.7777 | -0.50056 | 13.2302 | 12.1741 | 58.3475 | 0.8 | 1 | 16.2813 | 86.803 | -2.1 | 0.61259 | 1.0854 | 0.077254
2016-03-30 12:00 | 87.27 | 82.1 | 5.17 | 18.3498 | 3.761 | 14.523 | 73.6355 | 16.3645 | 15.1172 | 19.4281 | 17.305 | 61.575 | 0.8 | 1 | 17.454 | 96.334 | -2.1 | 0.91044 | 1.0843 | 0.085654
2016-03-30 13:00 | 76.9667 | 73.4833 | 3.4833 | 13.3984 | 3.7771 | 29.5263 | 74.931 | 15.069 | 30.6149 | 31.824 | 11.3842 | 55.1125 | 0.8 | 1 | 15.3933 | 81.8901 | -2.1 | 0.45906 | 1.0859 | 0.072918
2016-03-30 14:00 | 66.6633 | 64.8667 | 1.7967 | 7.9899 | 3.7932 | 44.5296 | 77.0049 | 12.9951 | 45.9006 | 45.5994 | 5.5903 | 48.65 | 0.8 | 1 | 13.3327 | 67.5729 | -2.2 | -0.088346 | 1.0878 | 0.060275
2016-03-30 15:00 | 56.36 | 56.25 | 0.11 | 0.61515 | 3.8093 | 59.5329 | 79.699 | 10.301 | 60.9393 | 59.7821 | 0.3096 | 42.1875 | 0.8 | 1 | 11.272 | 53.7691 | -2.5 | -0.81972 | 1.0904 | 0.048075
2016-03-30 16:00 | 39.7033 | 39.6267 | 0.076667 | 0.61336 | 3.8254 | 74.5363 | 82.8196 | 7.1804 | 75.7552 | 74.1021 | 0.16802 | 29.72 | 0.8 | 1 | 7.9407 | 37.8287 | -2.8 | -1.6179 | 1.0932 | 0.033909
2016-03-30 17:00 | 23.0467 | 23.0033 | 0.043333 | 0.646 | 3.8416 | 89.5396 | 86.1537 | 3.8463 | 90.4191 | 88.4402 | 0.017584 | 17.2525 | 0.8 | 1 | 4.6093 | 21.8794 | -2.8 | -2.1163 | 1.0949 | 0.019644
2016-03-30 18:00 | 6.39 | 6.38 | 0.01 | 0 | 3.8577 | 104.5429 | 89.4818 | 0.51824 | 105.0264 | 102.7089 | 0 | 4.785 | 0.8 | 1 | 1.278 | 6.063 | -2.6 | -2.4105 | 1.0959 | 0.0054486
2016-03-30 19:00 | 4.26 | 4.2533 | 0.0066667 | 0 | 3.8738 | 119.5462 | 92.587 | -2.587 | 119.674 | 116.7995 | 0 | 3.19 | 0.8 | 1 | 0.852 | 4.042 | -2.3 | -2.1737 | 1.0951 | 0.0036297
2016-03-30 20:00 | 2.13 | 2.1267 | 0.0033333 | 0 | 3.8899 | 134.5495 | 95.2643 | -5.2643 | 134.4375 | 130.5151 | 0 | 1.595 | 0.8 | 1 | 0.426 | 2.021 | -2.8 | -2.7368 | 1.0971 | 0.0018181
2016-03-30 21:00 | 0 | 0 | 0 | 0 | 3.906 | 149.5528 | 97.331 | -7.331 | 149.3539 | 143.3964 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.8 | -2.8 | 1.0973 | 0
2016-03-30 22:00 | 0 | 0 | 0 | 0 | 3.9221 | 164.5561 | 98.6401 | -8.6401 | 164.4118 | 154.1342 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-03-30 23:00 | 0 | 0 | 0 | 0 | 3.9382 | 179.5594 | 99.0948 | -9.0948 | 179.5548 | 159.0906 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-03-31 | 0 | 0 | 0 | 0 | 3.9543 | -165.4373 | 98.6599 | -8.6599 | -165.3015 | 154.6111 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3 | -3 | 1.098 | 0
2016-03-31 01:00 | 0.65 | 0.48333 | 0.16667 | 0 | 3.9704 | -150.434 | 97.367 | -7.367 | -150.242 | 144.0694 | 0 | 0.3625 | 0.8 | 1 | 0.13 | 0.4925 | -3.2 | -3.1846 | 1.0986 | 0.00044369
2016-03-31 02:00 | 1.3 | 0.96667 | 0.33333 | 0 | 3.9865 | -135.4307 | 95.3098 | -5.3098 | -135.3245 | 131.2586 | 0 | 0.725 | 0.8 | 1 | 0.26 | 0.985 | -2.6 | -2.5692 | 1.0965 | 0.00088564
2016-03-31 03:00 | 1.95 | 1.45 | 0.5 | 0 | 4.0025 | -120.4274 | 92.6326 | -2.6326 | -120.5623 | 117.5714 | 0 | 1.0875 | 0.8 | 1 | 0.39 | 1.4775 | -2.6 | -2.5538 | 1.0964 | 0.0013284
2016-03-31 04:00 | 21.95 | 13.6767 | 8.2733 | 0 | 4.0186 | -105.4241 | 89.5162 | 0.4838 | -105.9196 | 103.492 | 0 | 10.2575 | 0.8 | 1 | 4.39 | 14.6475 | -2.7 | -2.2423 | 1.0953 | 0.013156
2016-03-31 05:00 | 41.95 | 25.9033 | 16.0467 | 239.8747 | 4.0347 | -90.4208 | 86.1643 | 3.8357 | -91.3212 | 89.2251 | 3.2442 | 19.4275 | 0.8 | 1 | 8.39 | 31.0617 | -2.7 | -1.7293 | 1.0936 | 0.027853
2016-03-31 06:00 | 61.95 | 38.13 | 23.82 | 189.8634 | 4.0508 | -75.4175 | 82.7928 | 7.2072 | -76.6696 | 74.8808 | 49.5215 | 28.5975 | 0.8 | 1 | 12.39 | 90.509 | -2.6 | 0.22841 | 1.0867 | 0.080652
2016-03-31 07:00 | 77.9167 | 58.33 | 19.5867 | 108.7197 | 4.0669 | -60.4142 | 79.6211 | 10.3789 | -61.8672 | 60.5448 | 53.4621 | 43.7475 | 0.8 | 1 | 15.5833 | 112.793 | -2.6 | 0.92478 | 1.0843 | 0.10028
2016-03-31 08:00 | 93.8833 | 78.53 | 15.3533 | 67.5519 | 4.083 | -45.4109 | 76.8629 | 13.1371 | -46.8397 | 46.3275 | 46.6469 | 58.8975 | 0.8 | 1 | 18.7767 | 124.3211 | -2.3 | 1.585 | 1.082 | 0.1103
2016-03-31 09:00 | 109.85 | 98.73 | 11.12 | 42.1789 | 4.099 | -30.4076 | 74.7139 | 15.2861 | -31.5586 | 32.4717 | 35.5846 | 74.0475 | 0.8 | 1 | 21.97 | 131.6021 | -2.3 | 1.8126 | 1.0812 | 0.11667
2016-03-31 10:00 | 117.93 | 100.27 | 17.66 | 61.583 | 4.1151 | -15.4043 | 73.3355 | 16.6645 | -16.055 | 19.8344 | 57.9297 | 75.2025 | 0.8 | 1 | 23.586 | 156.7182 | -2.3 | 2.5974 | 1.0784 | 0.13859
2016-03-31 11:00 | 126.01 | 101.81 | 24.2 | 82.0031 | 4.1312 | -0.40105 | 72.8358 | 17.1642 | -0.41865 | 12.8415 | 79.9521 | 76.3575 | 0.8 | 1 | 25.202 | 181.5116 | -2.2 | 3.4722 | 1.0753 | 0.16005
2016-03-31 12:00 | 134.09 | 103.35 | 30.74 | 106.6921 | 4.1472 | 14.6022 | 73.2546 | 16.7454 | 15.2233 | 19.2202 | 100.7451 | 77.5125 | 0.8 | 1 | 26.818 | 205.0756 | -2.9 | 3.5086 | 1.0752 | 0.18081
2016-03-31 13:00 | 122.9967 | 94.5367 | 28.46 | 106.8768 | 4.1633 | 29.6055 | 74.5565 | 15.4435 | 30.7424 | 31.7235 | 90.9089 | 70.9025 | 0.8 | 1 | 24.5993 | 186.4108 | -3.2 | 2.6253 | 1.0783 | 0.16483
2016-03-31 14:00 | 111.9033 | 85.7233 | 26.18 | 113.272 | 4.1794 | 44.6088 | 76.6367 | 13.3633 | 46.0452 | 45.5419 | 79.3343 | 64.2925 | 0.8 | 1 | 22.3807 | 166.0075 | -3.1 | 2.0877 | 1.0802 | 0.14704
2016-03-31 15:00 | 100.81 | 76.91 | 23.9 | 129.1564 | 4.1954 | 59.6121 | 79.3361 | 10.6639 | 61.0957 | 59.7426 | 65.0801 | 57.6825 | 0.8 | 1 | 20.162 | 142.9246 | -3.8 | 0.66639 | 1.0852 | 0.12718
2016-03-31 16:00 | 71.01 | 54.0767 | 16.9333 | 129.0512 | 4.2115 | 74.6154 | 82.4602 | 7.5398 | 75.9182 | 74.0681 | 35.4239 | 40.5575 | 0.8 | 1 | 14.202 | 90.1834 | -4 | -1.1818 | 1.0916 | 0.080727
2016-03-31 17:00 | 41.21 | 31.2433 | 9.9667 | 135.9422 | 4.2276 | 89.6187 | 85.7956 | 4.2044 | 90.5837 | 88.4036 | 3.7873 | 23.4325 | 0.8 | 1 | 8.242 | 35.4618 | -4.4 | -3.2918 | 1.099 | 0.031958
2016-03-31 18:00 | 11.41 | 8.41 | 3 | 0 | 4.2436 | 104.622 | 89.1224 | 0.87765 | 105.1877 | 102.6619 | 0 | 6.3075 | 0.8 | 1 | 2.282 | 8.5895 | -4.8 | -4.5316 | 1.1034 | 0.0077714
2016-03-31 19:00 | 7.6067 | 5.6067 | 2 | 0 | 4.2597 | 119.6253 | 92.2241 | -2.2241 | 119.8272 | 116.7327 | 0 | 4.205 | 0.8 | 1 | 1.5213 | 5.7263 | -5 | -4.8211 | 1.1044 | 0.0051857
2016-03-31 20:00 | 3.8033 | 2.8033 | 1 | 0 | 4.2757 | 134.6286 | 94.8963 | -4.8963 | 134.5781 | 130.4139 | 0 | 2.1025 | 0.8 | 1 | 0.76067 | 2.8632 | -5.4 | -5.3105 | 1.1061 | 0.0025969
2016-03-31 21:00 | 0 | 0 | 0 | 0 | 4.2918 | 149.6319 | 96.9569 | -6.9569 | 149.4776 | 143.2343 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.6 | -5.6 | 1.1071 | 0
2016-03-31 22:00 | 0 | 0 | 0 | 0 | 4.3078 | 164.6352 | 98.2599 | -8.2599 | 164.5151 | 153.8656 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.6 | -5.6 | 1.1071 | 0
2016-03-31 23:00 | 0 | 0 | 0 | 0 | 4.3239 | 179.6385 | 98.7092 | -8.7092 | 179.6353 | 158.7065 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6 | -6 | 1.1085 | 0
2016-04-01 | 0 | 0 | 0 | 0 | 4.3399 | -165.3582 | 98.2704 | -8.2704 | -165.2443 | 154.2472 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.1 | -6.1 | 1.1088 | 0
2016-04-01 01:00 | 1.06 | 0.89333 | 0.16667 | 0 | 4.3559 | -150.355 | 96.9751 | -6.9751 | -150.2066 | 143.776 | 0 | 0.67 | 0.8 | 1 | 0.212 | 0.882 | -6.2 | -6.1724 | 1.1091 | 0.00080215
2016-04-01 02:00 | 2.12 | 1.7867 | 0.33333 | 0 | 4.372 | -135.3517 | 94.9167 | -4.9167 | -135.3079 | 131.0139 | 0 | 1.34 | 0.8 | 1 | 0.424 | 1.764 | -6.8 | -6.7449 | 1.1111 | 0.0016072
2016-04-01 03:00 | 3.18 | 2.68 | 0.5 | 0 | 4.388 | -120.3484 | 92.2392 | -2.2392 | -120.56 | 117.3562 | 0 | 2.01 | 0.8 | 1 | 0.636 | 2.646 | -6.9 | -6.8173 | 1.1114 | 0.0024113
2016-04-01 04:00 | 30.2233 | 20.05 | 10.1733 | 0 | 4.404 | -105.3451 | 89.1229 | 0.87713 | -105.9265 | 103.2946 | 0 | 15.0375 | 0.8 | 1 | 6.0447 | 21.0822 | -8.3 | -7.6412 | 1.1142 | 0.019262
2016-04-01 05:00 | 57.2667 | 37.42 | 19.8467 | 269.1377 | 4.4201 | -90.3418 | 85.7711 | 4.2289 | -91.3316 | 89.0374 | 4.5217 | 28.065 | 0.8 | 1 | 11.4533 | 44.04 | -7.9 | -6.5237 | 1.1103 | 0.040097
2016-04-01 06:00 | 84.31 | 54.79 | 29.52 | 223.1899 | 4.4361 | -75.3385 | 82.3996 | 7.6004 | -76.6776 | 74.6962 | 58.908 | 41.0925 | 0.8 | 1 | 16.862 | 116.8625 | -7.9 | -4.248 | 1.1024 | 0.10564
2016-04-01 07:00 | 127.25 | 74.2133 | 53.0367 | 283.7643 | 4.4521 | -60.3352 | 79.2278 | 10.7722 | -61.8668 | 60.3562 | 140.3517 | 55.66 | 0.8 | 1 | 25.45 | 221.4617 | -8.1 | -1.1793 | 1.0916 | 0.19824
2016-04-01 08:00 | 170.19 | 93.6367 | 76.5533 | 327.214 | 4.4682 | -45.332 | 76.47 | 13.53 | -46.8252 | 46.1248 | 226.7888 | 70.2275 | 0.8 | 1 | 34.038 | 331.0543 | -7.8 | 2.5454 | 1.0786 | 0.2928
2016-04-01 09:00 | 213.13 | 113.06 | 100.07 | 370.3169 | 4.4842 | -30.3287 | 74.3222 | 15.6778 | -31.5247 | 32.2355 | 313.2372 | 84.795 | 0.8 | 1 | 42.626 | 440.6582 | -7.1 | 6.6706 | 1.0642 | 0.38452
2016-04-01 10:00 | 222.6567 | 109.42 | 113.2367 | 386.1184 | 4.5002 | -15.3254 | 72.9462 | 17.0538 | -15.998 | 19.5216 | 363.9226 | 82.065 | 0.8 | 1 | 44.5313 | 490.5189 | -7 | 8.3287 | 1.0583 | 0.4257
2016-04-01 11:00 | 232.1833 | 105.78 | 126.4033 | 419.2109 | 4.5162 | -0.32212 | 72.4507 | 17.5493 | -0.33679 | 12.4545 | 409.3459 | 79.335 | 0.8 | 1 | 46.4367 | 535.1175 | -7 | 9.7224 | 1.0535 | 0.46226
2016-04-01 12:00 | 241.71 | 102.14 | 139.57 | 473.9911 | 4.5322 | 14.6812 | 72.875 | 17.125 | 15.3294 | 19.0186 | 448.1173 | 76.605 | 0.8 | 1 | 48.342 | 573.0643 | -7 | 10.9083 | 1.0493 | 0.49309
2016-04-01 13:00 | 210.1633 | 87.0867 | 123.0767 | 451.5566 | 4.5482 | 29.6844 | 74.1833 | 15.8167 | 30.8698 | 31.6274 | 384.4898 | 65.315 | 0.8 | 1 | 42.0327 | 491.8375 | -7.1 | 8.2699 | 1.0586 | 0.42692
2016-04-01 14:00 | 178.6167 | 72.0333 | 106.5833 | 449.0546 | 4.5642 | 44.6877 | 76.2698 | 13.7302 | 46.1895 | 45.487 | 314.8192 | 54.025 | 0.8 | 1 | 35.7233 | 404.5676 | -8.1 | 4.5427 | 1.0716 | 0.3555
2016-04-01 15:00 | 147.07 | 56.98 | 90.09 | 471.0702 | 4.5803 | 59.691 | 78.9745 | 11.0255 | 61.2518 | 59.7045 | 237.6356 | 42.735 | 0.8 | 1 | 29.414 | 309.7846 | -7.8 | 1.8808 | 1.0809 | 0.27458
2016-04-01 16:00 | 102.8567 | 41.3133 | 61.5433 | 447.8879 | 4.5963 | 74.6943 | 82.1021 | 7.8979 | 76.0809 | 74.0349 | 123.1926 | 30.985 | 0.8 | 1 | 20.5713 | 174.7489 | -7.9 | -2.4391 | 1.096 | 0.15706
2016-04-01 17:00 | 58.6433 | 25.6467 | 32.9967 | 414.9099 | 4.6123 | 89.6976 | 85.4386 | 4.5614 | 90.7477 | 88.367 | 11.8241 | 19.235 | 0.8 | 1 | 11.7287 | 42.7878 | -8.1 | -6.7629 | 1.1112 | 0.038986
2016-04-01 18:00 | 14.43 | 9.98 | 4.45 | 0 | 4.6283 | 104.7008 | 88.7641 | 1.2359 | 105.3484 | 102.6144 | 0 | 7.485 | 0.8 | 1 | 2.886 | 10.371 | -7.7 | -7.3759 | 1.1133 | 0.0094679
2016-04-01 19:00 | 9.62 | 6.6533 | 2.9667 | 0 | 4.6443 | 119.7041 | 91.8624 | -1.8624 | 119.9798 | 116.6647 | 0 | 4.99 | 0.8 | 1 | 1.924 | 6.914 | -7.8 | -7.5839 | 1.114 | 0.006316
2016-04-01 20:00 | 4.81 | 3.3267 | 1.4833 | 0 | 4.6603 | 134.7074 | 94.5294 | -4.5294 | 134.718 | 130.3108 | 0 | 2.495 | 0.8 | 1 | 0.962 | 3.457 | -7.9 | -7.792 | 1.1148 | 0.0031601
2016-04-01 21:00 | 0 | 0 | 0 | 0 | 4.6762 | 149.7107 | 96.584 | -6.584 | 149.6006 | 143.0696 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.4 | -7.4 | 1.1134 | 0
2016-04-01 22:00 | 0 | 0 | 0 | 0 | 4.6922 | 164.7139 | 97.8809 | -7.8809 | 164.6176 | 153.5949 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.1 | -7.1 | 1.1123 | 0
2016-04-01 23:00 | 0 | 0 | 0 | 0 | 4.7082 | 179.7172 | 98.325 | -8.325 | 179.7152 | 158.3233 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.2 | -7.2 | 1.1127 | 0
2016-04-02 | 0 | 0 | 0 | 0 | 4.7242 | -165.2795 | 97.8822 | -7.8822 | -165.1876 | 153.8839 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.9 | -6.9 | 1.1117 | 0
2016-04-02 01:00 | 1.0567 | 0.95333 | 0.10333 | 0 | 4.7402 | -150.2763 | 96.5844 | -6.5844 | -150.1716 | 143.4822 | 0 | 0.715 | 0.8 | 1 | 0.21133 | 0.92633 | -6.6 | -6.5711 | 1.1105 | 0.00084353
2016-04-02 02:00 | 2.1133 | 1.9067 | 0.20667 | 0 | 4.7562 | -135.273 | 94.5249 | -4.5249 | -135.2916 | 130.7688 | 0 | 1.43 | 0.8 | 1 | 0.42267 | 1.8527 | -6.4 | -6.3421 | 1.1097 | 0.0016858
2016-04-02 03:00 | 3.17 | 2.86 | 0.31 | 0 | 4.7721 | -120.2697 | 91.8471 | -1.8471 | -120.5579 | 117.1411 | 0 | 2.145 | 0.8 | 1 | 0.634 | 2.779 | -5.9 | -5.8132 | 1.1078 | 0.0025245
2016-04-02 04:00 | 25.85 | 18.5533 | 7.2967 | 0 | 4.7881 | -105.2664 | 88.7309 | 1.2691 | -105.9335 | 103.0976 | 0 | 13.915 | 0.8 | 1 | 5.17 | 19.085 | -6 | -5.4036 | 1.1064 | 0.017315
2016-04-02 05:00 | 48.53 | 34.2467 | 14.2833 | 177.3018 | 4.8041 | -90.2632 | 85.3793 | 4.6207 | -91.3421 | 88.8505 | 3.5569 | 25.685 | 0.8 | 1 | 9.706 | 38.9479 | -5.4 | -4.1829 | 1.1021 | 0.035199
2016-04-02 06:00 | 71.21 | 49.94 | 21.27 | 152.9788 | 4.8201 | -75.2599 | 82.0078 | 7.9922 | -76.6858 | 74.513 | 40.8484 | 37.455 | 0.8 | 1 | 14.242 | 92.5454 | -5.4 | -2.508 | 1.0963 | 0.083193
2016-04-02 07:00 | 102.5467 | 69.35 | 33.1967 | 171.4549 | 4.836 | -60.2566 | 78.836 | 11.164 | -61.8667 | 60.1696 | 85.2876 | 52.0125 | 0.8 | 1 | 20.5093 | 157.8094 | -5 | -0.068457 | 1.0877 | 0.14076
2016-04-02 08:00 | 133.8833 | 88.76 | 45.1233 | 187.5506 | 4.852 | -45.2534 | 76.0785 | 13.9215 | -46.8108 | 45.9248 | 130.4605 | 66.57 | 0.8 | 1 | 26.7767 | 223.8072 | -4.8 | 2.194 | 1.0798 | 0.19817
2016-04-02 09:00 | 165.22 | 108.17 | 57.05 | 206.1195 | 4.868 | -30.2501 | 73.9318 | 16.0682 | -31.4911 | 32.0032 | 174.7932 | 81.1275 | 0.8 | 1 | 33.044 | 288.9647 | -4.7 | 4.3301 | 1.0723 | 0.25409
2016-04-02 10:00 | 161.81 | 111.8833 | 49.9267 | 166.5698 | 4.8839 | -15.2468 | 72.5584 | 17.4416 | -15.9412 | 19.2129 | 157.2922 | 83.9125 | 0.8 | 1 | 32.362 | 273.5667 | -4.4 | 4.149 | 1.073 | 0.2407
2016-04-02 11:00 | 158.4 | 115.5967 | 42.8033 | 139.0142 | 4.8999 | -0.24358 | 72.0669 | 17.9331 | -0.25508 | 12.0691 | 135.9414 | 86.6975 | 0.8 | 1 | 31.68 | 254.3189 | -3.7 | 4.2475 | 1.0726 | 0.22369
2016-04-02 12:00 | 154.99 | 119.31 | 35.68 | 118.6332 | 4.9158 | 14.7597 | 72.4968 | 17.5032 | 15.4354 | 18.8233 | 112.2884 | 89.4825 | 0.8 | 1 | 30.998 | 232.7689 | -3.5 | 3.774 | 1.0743 | 0.20505
2016-04-02 13:00 | 135.93 | 103.4067 | 32.5233 | 116.655 | 4.9318 | 29.7629 | 73.8114 | 16.1886 | 30.9971 | 31.5355 | 99.4269 | 77.555 | 0.8 | 1 | 27.186 | 204.1679 | -3 | 3.3802 | 1.0757 | 0.18009
2016-04-02 14:00 | 116.87 | 87.5033 | 29.3667 | 120.5809 | 4.9477 | 44.7662 | 75.9042 | 14.0958 | 46.3336 | 45.4347 | 84.6142 | 65.6275 | 0.8 | 1 | 23.374 | 173.6157 | -3.5 | 1.9255 | 1.0808 | 0.15386
2016-04-02 15:00 | 97.81 | 71.6 | 26.21 | 132.767 | 4.9637 | 59.7695 | 78.6143 | 11.3857 | 61.4075 | 59.668 | 67.0486 | 53.7 | 0.8 | 1 | 19.562 | 140.3106 | -3.2 | 1.1847 | 1.0834 | 0.12464
2016-04-02 16:00 | 68.7133 | 51.2333 | 17.48 | 121.7492 | 4.9796 | 74.7727 | 81.7453 | 8.2547 | 76.243 | 74.0023 | 33.5539 | 38.425 | 0.8 | 1 | 13.7427 | 85.7216 | -3.1 | -0.4212 | 1.089 | 0.076546
2016-04-02 17:00 | 39.6167 | 30.8667 | 8.75 | 102.0837 | 4.9956 | 89.776 | 85.0829 | 4.9171 | 90.9111 | 88.3304 | 2.9744 | 23.15 | 0.8 | 1 | 7.9233 | 34.0477 | -3.3 | -2.236 | 1.0953 | 0.030581
2016-04-02 18:00 | 10.52 | 10.5 | 0.02 | 0 | 5.0115 | 104.7792 | 88.4071 | 1.5929 | 105.5083 | 102.5662 | 0 | 7.875 | 0.8 | 1 | 2.104 | 9.979 | -3.1 | -2.7882 | 1.0973 | 0.0089786
2016-04-02 19:00 | 7.0133 | 7 | 0.013333 | 0 | 5.0275 | 119.7825 | 91.5019 | -1.5019 | 120.1315 | 116.5955 | 0 | 5.25 | 0.8 | 1 | 1.4027 | 6.6527 | -3.2 | -2.9921 | 1.098 | 0.0059896
2016-04-02 20:00 | 3.5067 | 3.5 | 0.0066667 | 0 | 5.0434 | 134.7857 | 94.1638 | -4.1638 | 134.857 | 130.2057 | 0 | 2.625 | 0.8 | 1 | 0.70133 | 3.3263 | -3.6 | -3.4961 | 1.0997 | 0.0029996
2016-04-02 21:00 | 0 | 0 | 0 | 0 | 5.0593 | 149.789 | 96.2123 | -6.2123 | 149.7227 | 142.9025 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-04-02 22:00 | 0 | 0 | 0 | 0 | 5.0752 | 164.7923 | 97.5032 | -7.5032 | 164.7193 | 153.3223 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1004 | 0
2016-04-02 23:00 | 0 | 0 | 0 | 0 | 5.0912 | 179.7955 | 97.9421 | -7.9421 | 179.7943 | 157.9412 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-04-03 | 0 | 0 | 0 | 0 | 5.1071 | -165.2012 | 97.4954 | -7.4954 | -165.1314 | 153.5212 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-04-03 01:00 | 0.94667 | 0.94667 | 0 | 0 | 5.123 | -150.198 | 96.1952 | -6.1952 | -150.1371 | 143.188 | 0 | 0.71 | 0.8 | 1 | 0.18933 | 0.89933 | -2.9 | -2.8719 | 1.0976 | 0.00080939
2016-04-03 02:00 | 1.8933 | 1.8933 | 0 | 0 | 5.1389 | -135.1947 | 94.1346 | -4.1346 | -135.2755 | 130.5234 | 0 | 1.42 | 0.8 | 1 | 0.37867 | 1.7987 | -2.5 | -2.4438 | 1.0961 | 0.0016166
2016-04-03 03:00 | 2.84 | 2.84 | 0 | 0 | 5.1549 | -120.1915 | 91.4566 | -1.4566 | -120.5561 | 116.926 | 0 | 2.13 | 0.8 | 1 | 0.568 | 2.698 | -2.8 | -2.7157 | 1.097 | 0.002427
2016-04-03 04:00 | 17.52 | 17.47 | 0.05 | 0 | 5.1708 | -105.1882 | 88.3405 | 1.6595 | -105.9408 | 102.9011 | 0 | 13.1025 | 0.8 | 1 | 3.504 | 16.6065 | -3 | -2.481 | 1.0962 | 0.014927
2016-04-03 05:00 | 32.2 | 32.1 | 0.1 | 1.1449 | 5.1867 | -90.185 | 84.989 | 5.011 | -91.3529 | 88.6646 | 0.026681 | 24.075 | 0.8 | 1 | 6.44 | 30.5417 | -3 | -2.0456 | 1.0947 | 0.027415
2016-04-03 06:00 | 46.88 | 46.73 | 0.15 | 1.0289 | 5.2026 | -75.1818 | 81.6175 | 8.3825 | -76.6942 | 74.3313 | 0.27789 | 35.0475 | 0.8 | 1 | 9.376 | 44.7014 | -2.4 | -1.0031 | 1.091 | 0.039991
2016-04-03 07:00 | 67.6767 | 67.1833 | 0.49333 | 2.463 | 5.2185 | -60.1785 | 78.4457 | 11.5543 | -61.8667 | 59.9851 | 1.2321 | 50.3875 | 0.8 | 1 | 13.5353 | 65.1549 | -2.6 | -0.56391 | 1.0895 | 0.058207
2016-04-03 08:00 | 88.4733 | 87.6367 | 0.83667 | 3.3847 | 5.2344 | -45.1753 | 75.6885 | 14.3115 | -46.7968 | 45.7278 | 2.3627 | 65.7275 | 0.8 | 1 | 17.6947 | 85.7849 | -2.2 | 0.48078 | 1.0858 | 0.07638
2016-04-03 09:00 | 109.27 | 108.09 | 1.18 | 4.1653 | 5.2503 | -30.172 | 73.543 | 16.457 | -31.4577 | 31.7747 | 3.541 | 81.0675 | 0.8 | 1 | 21.854 | 106.4625 | -2 | 1.327 | 1.0829 | 0.094532
2016-04-03 10:00 | 110.1133 | 108.8667 | 1.2467 | 4.0719 | 5.2662 | -15.1688 | 72.172 | 17.828 | -15.8847 | 18.9085 | 3.8522 | 81.65 | 0.8 | 1 | 22.0227 | 107.5249 | -1.6 | 1.7602 | 1.0813 | 0.095342
2016-04-03 11:00 | 110.9567 | 109.6433 | 1.3133 | 4.1793 | 5.2821 | -0.16554 | 71.6846 | 18.3154 | -0.17363 | 11.6857 | 4.0927 | 82.2325 | 0.8 | 1 | 22.1913 | 108.5165 | -1.8 | 1.5911 | 1.0819 | 0.096274
2016-04-03 12:00 | 111.8 | 110.42 | 1.38 | 4.4948 | 5.298 | 14.8377 | 72.1201 | 17.8799 | 15.541 | 18.6345 | 4.2591 | 82.815 | 0.8 | 1 | 22.36 | 109.4341 | -1.3 | 2.1198 | 1.0801 | 0.096922
2016-04-03 13:00 | 95.32 | 94.3967 | 0.92333 | 3.2397 | 5.3139 | 29.8409 | 73.4411 | 16.5589 | 31.124 | 31.4478 | 2.7639 | 70.7975 | 0.8 | 1 | 19.064 | 92.6254 | -1.4 | 1.4945 | 1.0823 | 0.082201
2016-04-03 14:00 | 78.84 | 78.3733 | 0.46667 | 1.8689 | 5.3298 | 44.8442 | 75.5401 | 14.4599 | 46.4773 | 45.3849 | 1.3126 | 58.78 | 0.8 | 1 | 15.768 | 75.8606 | -2 | 0.37064 | 1.0862 | 0.067568
2016-04-03 15:00 | 62.36 | 62.35 | 0.01 | 0.049128 | 5.3456 | 59.8474 | 78.2554 | 11.7446 | 61.5628 | 59.6329 | 0.024836 | 46.7625 | 0.8 | 1 | 12.472 | 59.2593 | -2.1 | -0.24815 | 1.0884 | 0.052887
2016-04-03 16:00 | 44.5367 | 44.5067 | 0.03 | 0.20039 | 5.3615 | 74.8507 | 81.3898 | 8.6102 | 76.4044 | 73.9704 | 0.055334 | 33.38 | 0.8 | 1 | 8.9073 | 42.3427 | -2.3 | -0.97679 | 1.0909 | 0.037878
2016-04-03 17:00 | 26.7133 | 26.6633 | 0.05 | 0.54422 | 5.3774 | 89.8539 | 84.7286 | 5.2714 | 91.0738 | 88.2937 | 0.016205 | 19.9975 | 0.8 | 1 | 5.3427 | 25.3564 | -2.1 | -1.3076 | 1.0921 | 0.022707
2016-04-03 18:00 | 8.89 | 8.82 | 0.07 | 0 | 5.3933 | 104.8571 | 88.0515 | 1.9485 | 105.6673 | 102.5174 | 0 | 6.615 | 0.8 | 1 | 1.778 | 8.393 | -2.4 | -2.1377 | 1.095 | 0.007536
2016-04-03 19:00 | 5.9267 | 5.88 | 0.046667 | 0 | 5.4092 | 119.8604 | 91.1428 | -1.1428 | 120.2823 | 116.525 | 0 | 4.41 | 0.8 | 1 | 1.1853 | 5.5953 | -2.3 | -2.1251 | 1.0949 | 0.0050238
2016-04-03 20:00 | 2.9633 | 2.94 | 0.023333 | 0 | 5.425 | 134.8636 | 93.7995 | -3.7995 | 134.9951 | 130.0987 | 0 | 2.205 | 0.8 | 1 | 0.59267 | 2.7977 | -2.5 | -2.4126 | 1.0959 | 0.0025142
2016-04-03 21:00 | 0 | 0 | 0 | 0 | 5.4409 | 149.8668 | 95.8421 | -5.8421 | 149.8438 | 142.7329 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-04-03 22:00 | 0 | 0 | 0 | 0 | 5.4568 | 164.87 | 97.127 | -7.127 | 164.8202 | 153.0479 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-04-03 23:00 | 0 | 0 | 0 | 0 | 5.4726 | 179.8733 | 97.5607 | -7.5607 | 179.8727 | 157.5604 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.2 | -2.2 | 1.0952 | 0
2016-04-04 | 0 | 0 | 0 | 0 | 5.4885 | -165.1235 | 97.1102 | -7.1102 | -165.0759 | 153.1594 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-04-04 01:00 | 1.07 | 1.07 | 0 | 0 | 5.5043 | -150.1203 | 95.8076 | -5.8076 | -150.103 | 142.8937 | 0 | 0.8025 | 0.8 | 1 | 0.214 | 1.0165 | -2.2 | -2.1682 | 1.0951 | 0.00091279
2016-04-04 02:00 | 2.14 | 2.14 | 0 | 0 | 5.5202 | -135.117 | 93.7459 | -3.7459 | -135.2599 | 130.2779 | 0 | 1.605 | 0.8 | 1 | 0.428 | 2.033 | -2.4 | -2.3365 | 1.0957 | 0.0018266
2016-04-04 03:00 | 3.21 | 3.21 | 0 | 0 | 5.536 | -120.1138 | 91.0676 | -1.0676 | -120.5546 | 116.7111 | 0 | 2.4075 | 0.8 | 1 | 0.642 | 3.0495 | -1.7 | -1.6047 | 1.0931 | 0.0027334
2016-04-04 04:00 | 17.41 | 17.41 | 0 | 0 | 5.5519 | -105.1106 | 87.9517 | 2.0483 | -105.9483 | 102.7052 | 0 | 13.0575 | 0.8 | 1 | 3.482 | 16.5395 | -1.9 | -1.3831 | 1.0923 | 0.014815
2016-04-04 05:00 | 31.61 | 31.61 | 0 | 0 | 5.5677 | -90.1074 | 84.6003 | 5.3997 | -91.3639 | 88.4798 | 0 | 23.7075 | 0.8 | 1 | 6.322 | 30.0295 | -1.2 | -0.26158 | 1.0884 | 0.026801
2016-04-04 06:00 | 45.81 | 45.81 | 0 | 0 | 5.5836 | -75.1042 | 81.2288 | 8.7712 | -76.7029 | 74.1512 | 0 | 34.3575 | 0.8 | 1 | 9.162 | 43.5195 | -1.6 | -0.24002 | 1.0883 | 0.038838
2016-04-04 07:00 | 66.4433 | 64.7167 | 1.7267 | 8.3439 | 5.5994 | -60.1009 | 78.0571 | 11.9429 | -61.8672 | 59.8029 | 4.1968 | 48.5375 | 0.8 | 1 | 13.2887 | 66.0229 | -1.4 | 0.66322 | 1.0852 | 0.05875
2016-04-04 08:00 | 87.0767 | 83.6233 | 3.4533 | 13.6089 | 5.6153 | -45.0977 | 75.3001 | 14.6999 | -46.7831 | 45.5338 | 9.5329 | 62.7175 | 0.8 | 1 | 17.4153 | 89.6657 | -0.9 | 1.9021 | 1.0808 | 0.07947
2016-04-04 09:00 | 107.71 | 102.53 | 5.18 | 17.8762 | 5.6311 | -30.0945 | 73.1557 | 16.8443 | -31.4247 | 31.5502 | 15.2337 | 76.8975 | 0.8 | 1 | 21.542 | 113.6732 | -1.5 | 2.0523 | 1.0803 | 0.1007
2016-04-04 10:00 | 108.95 | 105.4033 | 3.5467 | 11.3476 | 5.6469 | -15.0913 | 71.7872 | 18.2128 | -15.8285 | 18.6086 | 10.7544 | 79.0525 | 0.8 | 1 | 21.79 | 111.5969 | -1.3 | 2.1874 | 1.0798 | 0.098816
2016-04-04 11:00 | 110.19 | 108.2767 | 1.9133 | 5.9689 | 5.6627 | -0.088071 | 71.3039 | 18.6961 | -0.092523 | 11.3042 | 5.8531 | 81.2075 | 0.8 | 1 | 22.038 | 109.0986 | -1.6 | 1.8093 | 1.0812 | 0.096722
2016-04-04 12:00 | 111.43 | 111.15 | 0.28 | 0.89386 | 5.6786 | 14.9151 | 71.7449 | 18.2551 | 15.6463 | 18.4522 | 0.8479 | 83.3625 | 0.8 | 1 | 22.286 | 106.4964 | -1.7 | 1.628 | 1.0818 | 0.094471
2016-04-04 13:00 | 95.7333 | 93.5 | 2.2333 | 7.6703 | 5.6944 | 29.9184 | 73.0722 | 16.9278 | 31.2506 | 31.3643 | 6.5495 | 70.125 | 0.8 | 1 | 19.1467 | 95.8211 | -1.9 | 1.0944 | 1.0837 | 0.085148
2016-04-04 14:00 | 80.0367 | 75.85 | 4.1867 | 16.3654 | 5.7102 | 44.9216 | 75.1775 | 14.8225 | 46.6205 | 45.3375 | 11.5037 | 56.8875 | 0.8 | 1 | 16.0073 | 84.3985 | -1.4 | 1.2375 | 1.0832 | 0.074963
2016-04-04 15:00 | 64.34 | 58.2 | 6.14 | 29.2865 | 5.726 | 59.9248 | 77.898 | 12.102 | 61.7174 | 59.5991 | 14.8204 | 43.65 | 0.8 | 1 | 12.868 | 71.3384 | -1.7 | 0.52932 | 1.0856 | 0.063508
2016-04-04 16:00 | 46.42 | 42.1067 | 4.3133 | 27.682 | 5.7418 | 74.928 | 81.0358 | 8.9642 | 76.5652 | 73.9389 | 7.6586 | 31.58 | 0.8 | 1 | 9.284 | 48.5226 | -1.6 | -0.08367 | 1.0878 | 0.043282
2016-04-04 17:00 | 28.5 | 26.0133 | 2.4867 | 25.3726 | 5.7577 | 89.9312 | 84.3756 | 5.6244 | 91.2356 | 88.2569 | 0.77178 | 19.51 | 0.8 | 1 | 5.7 | 25.9818 | -2 | -1.1881 | 1.0917 | 0.023258
2016-04-04 18:00 | 10.58 | 9.92 | 0.66 | 0 | 5.7735 | 104.9344 | 87.6972 | 2.3028 | 105.8254 | 102.4678 | 0 | 7.44 | 0.8 | 1 | 2.116 | 9.556 | -3.1 | -2.8014 | 1.0973 | 0.0085984
2016-04-04 19:00 | 7.0533 | 6.6133 | 0.44 | 0 | 5.7893 | 119.9376 | 90.785 | -0.78502 | 120.432 | 116.4531 | 0 | 4.96 | 0.8 | 1 | 1.4107 | 6.3707 | -5.9 | -5.7009 | 1.1075 | 0.0057853
2016-04-04 20:00 | 3.5267 | 3.3067 | 0.22 | 0 | 5.8051 | 134.9408 | 93.4366 | -3.4366 | 135.132 | 129.9897 | 0 | 2.48 | 0.8 | 1 | 0.70533 | 3.1853 | -5.2 | -5.1005 | 1.1054 | 0.0028871
2016-04-04 21:00 | 0 | 0 | 0 | 0 | 5.8209 | 149.944 | 95.4733 | -5.4733 | 149.9639 | 142.5609 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.9 | -6.9 | 1.1117 | 0
2016-04-04 22:00 | 0 | 0 | 0 | 0 | 5.8367 | 164.9472 | 96.7523 | -6.7523 | 164.92 | 152.7718 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.4 | -7.4 | 1.1134 | 0
2016-04-04 23:00 | 0 | 0 | 0 | 0 | 5.8525 | 179.9504 | 97.1809 | -7.1809 | 179.9503 | 157.1808 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.2 | -7.2 | 1.1127 | 0
2016-04-05 | 0 | 0 | 0 | 0 | 5.8683 | -165.0464 | 96.7266 | -6.7266 | -165.0211 | 152.7986 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.7 | -7.7 | 1.1144 | 0
2016-04-05 01:00 | 1.85 | 1.75 | 0.1 | 0 | 5.884 | -150.0432 | 95.4217 | -5.4217 | -150.0696 | 142.5996 | 0 | 1.3125 | 0.8 | 1 | 0.37 | 1.6825 | -7.3 | -7.2474 | 1.1129 | 0.0015354
2016-04-05 02:00 | 3.7 | 3.5 | 0.2 | 0 | 5.8998 | -135.04 | 93.3589 | -3.3589 | -135.2448 | 130.0324 | 0 | 2.625 | 0.8 | 1 | 0.74 | 3.365 | -6.1 | -5.9948 | 1.1085 | 0.0030586
2016-04-05 03:00 | 5.55 | 5.25 | 0.3 | 0 | 5.9156 | -120.0368 | 90.6804 | -0.68039 | -120.5535 | 116.4966 | 0 | 3.9375 | 0.8 | 1 | 1.11 | 5.0475 | -5.5 | -5.3423 | 1.1062 | 0.0045785
2016-04-05 04:00 | 27.9767 | 23.6633 | 4.3133 | 0 | 5.9314 | -105.0336 | 87.5646 | 2.4354 | -105.9563 | 102.5101 | 0 | 17.7475 | 0.8 | 1 | 5.5953 | 23.3428 | -4.9 | -4.1705 | 1.1021 | 0.021095
2016-04-05 05:00 | 50.4033 | 42.0767 | 8.3267 | 82.5869 | 5.9472 | -90.0304 | 84.2134 | 5.7866 | -91.3754 | 88.2963 | 2.4553 | 31.5575 | 0.8 | 1 | 10.0807 | 44.0935 | -5.1 | -3.7221 | 1.1005 | 0.039791
2016-04-05 06:00 | 72.83 | 60.49 | 12.34 | 77.5328 | 5.9629 | -75.0272 | 80.8419 | 9.1581 | -76.7121 | 73.9728 | 21.4063 | 45.3675 | 0.8 | 1 | 14.566 | 81.3398 | -4.6 | -2.0581 | 1.0947 | 0.073015
2016-04-05 07:00 | 102.8767 | 81.2967 | 21.58 | 101.0585 | 5.9787 | -60.024 | 77.6701 | 12.3299 | -61.868 | 59.6231 | 51.1038 | 60.9725 | 0.8 | 1 | 20.5753 | 132.6517 | -4.3 | -0.15464 | 1.088 | 0.11835
2016-04-05 08:00 | 132.9233 | 102.1033 | 30.82 | 118.4119 | 5.9945 | -45.0208 | 74.9135 | 15.0865 | -46.7699 | 45.3429 | 83.2272 | 76.5775 | 0.8 | 1 | 26.5847 | 186.3894 | -4 | 1.8247 | 1.0811 | 0.16524
2016-04-05 09:00 | 162.97 | 122.91 | 40.06 | 135.2442 | 6.0102 | -30.0177 | 72.7702 | 17.2298 | -31.3921 | 31.33 | 115.5238 | 92.1825 | 0.8 | 1 | 32.594 | 240.3003 | -2.6 | 4.9094 | 1.0703 | 0.2109
2016-04-05 10:00 | 164.0733 | 127.7667 | 36.3067 | 113.8531 | 6.026 | -15.0145 | 71.4042 | 18.5958 | -15.7728 | 18.3136 | 108.0865 | 95.825 | 0.8 | 1 | 32.8147 | 236.7262 | -1.7 | 5.6977 | 1.0676 | 0.20723
2016-04-05 11:00 | 165.1767 | 132.6233 | 32.5533 | 99.6103 | 6.0418 | -0.01128 | 70.9249 | 19.0751 | -0.011869 | 10.9249 | 97.805 | 99.4675 | 0.8 | 1 | 33.0353 | 230.3078 | -3.3 | 3.8971 | 1.0739 | 0.2028
2016-04-05 12:00 | 166.28 | 137.48 | 28.8 | 90.1596 | 6.0575 | 14.9919 | 71.3713 | 18.6287 | 15.7512 | 18.2765 | 85.6114 | 103.11 | 0.8 | 1 | 33.256 | 221.9774 | -4.1 | 2.8368 | 1.0776 | 0.19614
2016-04-05 13:00 | 144.7167 | 125.25 | 19.4667 | 65.4799 | 6.0733 | 29.9951 | 72.705 | 17.295 | 31.3766 | 31.2847 | 55.9589 | 93.9375 | 0.8 | 1 | 28.9433 | 178.8398 | -3.7 | 1.8887 | 1.0809 | 0.15851
2016-04-05 14:00 | 123.1533 | 113.02 | 10.1333 | 38.69 | 6.089 | 44.9983 | 74.8165 | 15.1835 | 46.7631 | 45.2925 | 27.2179 | 84.765 | 0.8 | 1 | 24.6307 | 136.6136 | -3.7 | 0.56917 | 1.0855 | 0.1216
2016-04-05 15:00 | 101.59 | 100.79 | 0.8 | 3.7085 | 6.1048 | 60.0014 | 77.5421 | 12.4579 | 61.8713 | 59.5665 | 1.8785 | 75.5925 | 0.8 | 1 | 20.318 | 97.789 | -3.2 | -0.14409 | 1.088 | 0.087244
2016-04-05 16:00 | 73.4 | 72.23 | 1.17 | 7.2271 | 6.1205 | 75.0046 | 80.6833 | 9.3167 | 76.7251 | 73.9079 | 2.0032 | 54.1725 | 0.8 | 1 | 14.68 | 70.8557 | -3.7 | -1.4858 | 1.0927 | 0.063488
2016-04-05 17:00 | 45.21 | 43.67 | 1.54 | 14.7922 | 6.1362 | 90.0078 | 84.0242 | 5.9758 | 91.3965 | 88.2199 | 0.4595 | 32.7525 | 0.8 | 1 | 9.042 | 42.254 | -3.9 | -2.5796 | 1.0965 | 0.037993
2016-04-05 18:00 | 17.02 | 15.11 | 1.91 | 0 | 6.152 | 105.011 | 87.3444 | 2.6556 | 105.9824 | 102.4174 | 0 | 11.3325 | 0.8 | 1 | 3.404 | 14.7365 | -3.8 | -3.3395 | 1.0992 | 0.013283
2016-04-05 19:00 | 11.3467 | 10.0733 | 1.2733 | 0 | 6.1677 | 120.0142 | 90.4287 | -0.42874 | 120.5807 | 116.3799 | 0 | 7.555 | 0.8 | 1 | 2.2693 | 9.8243 | -3.5 | -3.193 | 1.0987 | 0.0088509
2016-04-05 20:00 | 5.6733 | 5.0367 | 0.63667 | 0 | 6.1834 | 135.0173 | 93.0753 | -3.0753 | 135.2678 | 129.8788 | 0 | 3.7775 | 0.8 | 1 | 1.1347 | 4.9122 | -3.5 | -3.3465 | 1.0992 | 0.0044276
2016-04-05 21:00 | 0 | 0 | 0 | 0 | 6.1992 | 150.0205 | 95.106 | -5.106 | 150.0828 | 142.3865 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-04-05 22:00 | 0 | 0 | 0 | 0 | 6.2149 | 165.0237 | 96.3792 | -6.3792 | 165.0188 | 152.4942 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.8 | -3.8 | 1.1008 | 0
2016-04-05 23:00 | 0 | 0 | 0 | 0 | 6.2306 | 180.0268 | 96.8027 | -6.8027 | -179.9731 | 156.8027 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4 | -4 | 1.1015 | 0
2016-04-06 | 0 | 0 | 0 | 0 | 6.2463 | -164.97 | 96.3447 | -6.3447 | -164.9671 | 152.4391 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.1033 | 0
2016-04-06 01:00 | 1.96 | 1.5567 | 0.40333 | 0 | 6.262 | -149.9668 | 95.0375 | -5.0375 | -150.0368 | 142.3056 | 0 | 1.1675 | 0.8 | 1 | 0.392 | 1.5595 | -5 | -4.9513 | 1.1048 | 0.0014128
2016-04-06 02:00 | 3.92 | 3.1133 | 0.80667 | 0 | 6.2778 | -134.9637 | 92.9737 | -2.9737 | -135.2302 | 129.7872 | 0 | 2.335 | 0.8 | 1 | 0.784 | 3.119 | -5.5 | -5.4025 | 1.1064 | 0.0028297
2016-04-06 03:00 | 5.88 | 4.67 | 1.21 | 0 | 6.2935 | -119.9605 | 90.295 | -0.29499 | -120.5529 | 116.2826 | 0 | 3.5025 | 0.8 | 1 | 1.176 | 4.6785 | -7.3 | -7.1538 | 1.1125 | 0.0042681
2016-04-06 04:00 | 27.4867 | 18.1933 | 9.2933 | 0 | 6.3092 | -104.9573 | 87.1794 | 2.8206 | -105.9646 | 102.3159 | 0 | 13.645 | 0.8 | 1 | 5.4973 | 19.1423 | -7.1 | -6.5018 | 1.1103 | 0.017427
2016-04-06 05:00 | 49.0933 | 31.7167 | 17.3767 | 161.6327 | 6.3249 | -89.9542 | 83.8284 | 6.1716 | -91.3873 | 88.1142 | 5.3191 | 23.7875 | 0.8 | 1 | 9.8187 | 38.9252 | -7.5 | -6.2836 | 1.1095 | 0.035414
2016-04-06 06:00 | 70.7 | 45.24 | 25.46 | 153.5682 | 6.3406 | -74.951 | 80.4569 | 9.5431 | -76.7217 | 73.7964 | 42.8535 | 33.93 | 0.8 | 1 | 14.14 | 90.9235 | -7.5 | -4.6586 | 1.1038 | 0.082297
2016-04-06 07:00 | 95.71 | 66.5267 | 29.1833 | 132.5907 | 6.3563 | -59.9479 | 77.285 | 12.715 | -61.8694 | 59.4458 | 67.4029 | 49.895 | 0.8 | 1 | 19.142 | 136.4399 | -5.6 | -1.3363 | 1.0922 | 0.12219
2016-04-06 08:00 | 120.72 | 87.8133 | 32.9067 | 123.3584 | 6.372 | -44.9447 | 74.5286 | 15.4714 | -46.7572 | 45.1554 | 86.9906 | 65.86 | 0.8 | 1 | 24.144 | 176.9946 | -5.1 | 0.43108 | 1.086 | 0.15762
2016-04-06 09:00 | 145.73 | 109.1 | 36.63 | 121.053 | 6.3877 | -29.9416 | 72.3865 | 17.6135 | -31.3601 | 31.1142 | 103.6382 | 81.825 | 0.8 | 1 | 29.146 | 214.6092 | -3.3 | 3.4065 | 1.0756 | 0.18928
2016-04-06 10:00 | 152.4967 | 104.2067 | 48.29 | 148.4975 | 6.4033 | -14.9384 | 71.0229 | 18.9771 | -15.7176 | 18.0236 | 141.2106 | 78.155 | 0.8 | 1 | 30.4993 | 249.8649 | -3.6 | 4.2083 | 1.0728 | 0.2198
2016-04-06 11:00 | 159.2633 | 99.3133 | 59.95 | 180.0177 | 6.419 | 0.064747 | 70.5476 | 19.4524 | 0.068236 | 10.5478 | 176.9758 | 74.485 | 0.8 | 1 | 31.8527 | 283.3135 | -3.6 | 5.2535 | 1.0691 | 0.24837
2016-04-06 12:00 | 166.03 | 94.42 | 71.61 | 219.9485 | 6.4347 | 15.0679 | 70.9995 | 19.0005 | 15.8555 | 18.1075 | 209.0556 | 70.815 | 0.8 | 1 | 33.206 | 313.0766 | -3 | 6.7836 | 1.0638 | 0.27309
2016-04-06 13:00 | 162.5367 | 87.9267 | 74.61 | 245.9312 | 6.4504 | 30.071 | 72.3394 | 17.6606 | 31.502 | 31.2092 | 210.3403 | 65.945 | 0.8 | 1 | 32.5073 | 308.7926 | -2.9 | 6.7498 | 1.0639 | 0.26938
2016-04-06 14:00 | 159.0433 | 81.4333 | 77.61 | 289.6337 | 6.4661 | 45.0742 | 74.4571 | 15.5429 | 46.905 | 45.2496 | 203.9077 | 61.075 | 0.8 | 1 | 31.8087 | 296.7914 | -2.7 | 6.5747 | 1.0645 | 0.25906
2016-04-06 15:00 | 155.55 | 74.94 | 80.61 | 363.5101 | 6.4817 | 60.0773 | 77.1879 | 12.8121 | 62.0244 | 59.5351 | 184.3036 | 56.205 | 0.8 | 1 | 31.11 | 271.6186 | -1.6 | 6.8881 | 1.0634 | 0.23685
2016-04-06 16:00 | 109.89 | 54.2933 | 55.5967 | 331.0657 | 6.4974 | 75.0805 | 80.3324 | 9.6676 | 76.8841 | 73.8773 | 91.9354 | 40.72 | 0.8 | 1 | 21.978 | 154.6334 | -1.1 | 3.7323 | 1.0744 | 0.13624
2016-04-06 17:00 | 64.23 | 33.6467 | 30.5833 | 277.5743 | 6.5131 | 90.0836 | 83.6743 | 6.3257 | 91.5563 | 88.1826 | 8.8029 | 25.235 | 0.8 | 1 | 12.846 | 46.8839 | -0.2 | 1.2651 | 1.0831 | 0.041638
2016-04-06 18:00 | 18.57 | 13 | 5.57 | 106.1866 | 6.5287 | 105.0868 | 86.9932 | 3.0068 | 106.1383 | 102.3662 | 0 | 9.75 | 0.8 | 1 | 3.714 | 13.464 | -1.2 | -0.77925 | 1.0902 | 0.012037
2016-04-06 19:00 | 12.38 | 8.6667 | 3.7133 | 0 | 6.5444 | 120.0899 | 90.074 | -0.074009 | 120.728 | 116.3052 | 0 | 6.5 | 0.8 | 1 | 2.476 | 8.976 | -0.4 | -0.1195 | 1.0879 | 0.0080074
2016-04-06 20:00 | 6.19 | 4.3333 | 1.8567 | 0 | 6.56 | 135.093 | 92.7155 | -2.7155 | 135.4023 | 129.766 | 0 | 3.25 | 0.8 | 1 | 1.238 | 4.488 | -0.9 | -0.75975 | 1.0902 | 0.004012
2016-04-06 21:00 | 0 | 0 | 0 | 0 | 6.5757 | 150.0962 | 94.7404 | -4.7404 | 150.2005 | 142.2099 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-04-06 22:00 | 0 | 0 | 0 | 0 | 6.5913 | 165.0993 | 96.0078 | -6.0078 | 165.1164 | 152.2153 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-04-06 23:00 | 0 | 0 | 0 | 0 | 6.607 | 180.1024 | 96.4263 | -6.4263 | -179.8976 | 156.4261 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-04-07 | 0 | 0 | 0 | 0 | 6.6226 | -164.8944 | 95.9646 | -5.9646 | -164.914 | 152.0809 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-04-07 01:00 | 3.4133 | 2.9567 | 0.45667 | 0 | 6.6383 | -149.8913 | 94.6552 | -4.6552 | -150.0047 | 142.0122 | 0 | 2.2175 | 0.8 | 1 | 0.68267 | 2.9002 | 0.3 | 0.39063 | 1.0861 | 0.002583
2016-04-07 02:00 | 6.8267 | 5.9133 | 0.91333 | 0 | 6.6539 | -134.8882 | 92.5904 | -2.5904 | -135.2162 | 129.5424 | 0 | 4.435 | 0.8 | 1 | 1.3653 | 5.8003 | 0.1 | 0.28126 | 1.0865 | 0.0051678
2016-04-07 03:00 | 10.24 | 8.87 | 1.37 | 0 | 6.6695 | -119.885 | 89.9115 | 0.08848 | -120.5529 | 116.0692 | 0 | 6.6525 | 0.8 | 1 | 2.048 | 8.7005 | 0.3 | 0.57189 | 1.0855 | 0.0077444
2016-04-07 04:00 | 44.7433 | 31.5367 | 13.2067 | 236.3009 | 6.6852 | -104.8819 | 86.7961 | 3.2039 | -105.9736 | 102.1228 | 0 | 23.6525 | 0.8 | 1 | 8.9487 | 32.6012 | 0 | 1.0188 | 1.0839 | 0.028977
2016-04-07 05:00 | 79.2467 | 54.2033 | 25.0433 | 219.3852 | 6.7008 | -89.8788 | 83.4453 | 6.5547 | -91.3997 | 87.9335 | 7.911 | 40.6525 | 0.8 | 1 | 15.8493 | 64.4128 | -0.1 | 1.9129 | 1.0808 | 0.057087
2016-04-07 06:00 | 113.75 | 76.87 | 36.88 | 213.9467 | 6.7164 | -74.8757 | 80.0738 | 9.9262 | -76.7318 | 73.6219 | 60.3276 | 57.6525 | 0.8 | 1 | 22.75 | 140.7301 | 0.3 | 4.6978 | 1.0711 | 0.1236
2016-04-07 07:00 | 156.5333 | 90.3833 | 66.15 | 291.8999 | 6.732 | -59.8725 | 76.9019 | 13.0981 | -61.8714 | 59.2711 | 149.1542 | 67.7875 | 0.8 | 1 | 31.3067 | 248.2483 | 0 | 7.7578 | 1.0603 | 0.21585
2016-04-07 08:00 | 199.3167 | 103.8967 | 95.42 | 349.2795 | 6.7476 | -44.8694 | 74.1458 | 15.8542 | -46.7451 | 44.9713 | 247.1017 | 77.9225 | 0.8 | 1 | 39.8633 | 364.8876 | 0.1 | 11.5027 | 1.0472 | 0.31334
2016-04-07 09:00 | 242.1 | 117.41 | 124.69 | 403.6068 | 6.7633 | -29.8663 | 72.0047 | 17.9953 | -31.3287 | 30.9028 | 346.3105 | 88.0575 | 0.8 | 1 | 48.42 | 482.788 | -0.5 | 14.5871 | 1.0364 | 0.41031
2016-04-07 10:00 | 247.87 | 122.06 | 125.81 | 379.5798 | 6.7789 | -14.8632 | 70.6435 | 19.3565 | -15.663 | 17.739 | 361.5325 | 91.545 | 0.8 | 1 | 49.574 | 502.6515 | -0.9 | 14.8079 | 1.0357 | 0.42688
2016-04-07 11:00 | 253.64 | 126.71 | 126.93 | 374.2108 | 6.7945 | 0.13992 | 70.1722 | 19.8278 | 0.14769 | 10.1731 | 368.3277 | 95.0325 | 0.8 | 1 | 50.728 | 514.0882 | -1.2 | 14.8653 | 1.0355 | 0.43651
2016-04-07 12:00 | 259.41 | 131.36 | 128.05 | 386.0705 | 6.8101 | 15.143 | 70.6295 | 19.3705 | 15.9591 | 17.9452 | 367.2888 | 98.52 | 0.8 | 1 | 51.882 | 517.6908 | -1.5 | 14.6778 | 1.0361 | 0.43984
2016-04-07 13:00 | 222.9167 | 120.1967 | 102.72 | 331.9748 | 6.8257 | 30.1461 | 71.9757 | 18.0243 | 31.6266 | 31.1375 | 284.1467 | 90.1475 | 0.8 | 1 | 44.5833 | 418.8776 | -1.5 | 11.5899 | 1.0469 | 0.3596
2016-04-07 14:00 | 186.4233 | 109.0333 | 77.39 | 282.4788 | 6.8413 | 45.1493 | 74.0995 | 15.9005 | 47.0461 | 45.2089 | 199.013 | 81.775 | 0.8 | 1 | 37.2847 | 318.0727 | -1.6 | 8.3398 | 1.0583 | 0.27603
2016-04-07 15:00 | 149.93 | 97.87 | 52.06 | 228.5838 | 6.8569 | 60.1524 | 76.8353 | 13.1647 | 62.1766 | 59.5047 | 115.9989 | 73.4025 | 0.8 | 1 | 29.986 | 219.3874 | -1.4 | 5.4559 | 1.0684 | 0.1922
2016-04-07 16:00 | 109.2267 | 72.8733 | 36.3533 | 209.0006 | 6.8725 | 75.1555 | 79.9831 | 10.0169 | 77.042 | 73.847 | 58.1448 | 54.655 | 0.8 | 1 | 21.8453 | 134.6451 | -1.8 | 2.4077 | 1.0791 | 0.11914
2016-04-07 17:00 | 68.5233 | 47.8767 | 20.6467 | 177.6509 | 6.888 | 90.1586 | 83.326 | 6.674 | 91.7149 | 88.1451 | 5.7504 | 35.9075 | 0.8 | 1 | 13.7047 | 55.3626 | -1.5 | 0.23008 | 1.0867 | 0.049333
2016-04-07 18:00 | 27.82 | 22.88 | 4.94 | 84.3752 | 6.9036 | 105.1617 | 86.6435 | 3.3565 | 106.2929 | 102.3141 | 0 | 17.16 | 0.8 | 1 | 5.564 | 22.724 | -1.5 | -0.78987 | 1.0903 | 0.020316
2016-04-07 19:00 | 18.5467 | 15.2533 | 3.2933 | 0 | 6.9192 | 120.1648 | 89.7209 | 0.2791 | 120.8741 | 116.2292 | 0 | 11.44 | 0.8 | 1 | 3.7093 | 15.1493 | -1.5 | -1.0266 | 1.0911 | 0.013554
2016-04-07 20:00 | 9.2733 | 7.6267 | 1.6467 | 0 | 6.9348 | 135.1679 | 92.3574 | -2.3574 | 135.5355 | 129.6512 | 0 | 5.72 | 0.8 | 1 | 1.8547 | 7.5747 | -1.6 | -1.3633 | 1.0923 | 0.0067843
2016-04-07 21:00 | 0 | 0 | 0 | 0 | 6.9503 | 150.171 | 94.3765 | -4.3765 | 150.3169 | 142.0311 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-04-07 22:00 | 0 | 0 | 0 | 0 | 6.9659 | 165.1741 | 95.6382 | -5.6382 | 165.2128 | 151.9351 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-04-07 23:00 | 0 | 0 | 0 | 0 | 6.9815 | 180.1772 | 96.0518 | -6.0518 | -179.8232 | 156.0512 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-04-08 | 0 | 0 | 0 | 0 | 6.997 | -164.8197 | 95.5865 | -5.5865 | -164.8619 | 151.7241 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-04-08 01:00 | 2.01 | 2 | 0.01 | 0 | 7.0126 | -149.8167 | 94.2749 | -4.2749 | -149.9735 | 141.7193 | 0 | 1.5 | 0.8 | 1 | 0.402 | 1.902 | -1.6 | -1.5406 | 1.0929 | 0.0017045
2016-04-08 02:00 | 4.02 | 4 | 0.02 | 0 | 7.0282 | -134.8136 | 92.2091 | -2.2091 | -135.203 | 129.2981 | 0 | 3 | 0.8 | 1 | 0.804 | 3.804 | -1.8 | -1.6811 | 1.0934 | 0.0034106
2016-04-08 03:00 | 6.03 | 6 | 0.03 | 0 | 7.0437 | -119.8105 | 89.5301 | 0.46991 | -120.5535 | 115.8567 | 0 | 4.5 | 0.8 | 1 | 1.206 | 5.706 | -2.1 | -1.9217 | 1.0942 | 0.0051198
2016-04-08 04:00 | 22.4433 | 22.4233 | 0.02 | 0.31984 | 7.0593 | -104.8074 | 86.4149 | 3.5851 | -105.9831 | 101.9308 | 0 | 16.8175 | 0.8 | 1 | 4.4887 | 21.3062 | -1.7 | -1.0342 | 1.0911 | 0.019063
2016-04-08 05:00 | 38.8567 | 38.8467 | 0.01 | 0.082811 | 7.0748 | -89.8043 | 83.0642 | 6.9358 | -91.4127 | 87.7544 | 0.0032448 | 29.135 | 0.8 | 1 | 7.7713 | 36.9096 | -2.2 | -1.0466 | 1.0912 | 0.033025
2016-04-08 06:00 | 55.27 | 55.27 | 0 | 0 | 7.0903 | -74.8012 | 79.6928 | 10.3072 | -76.7426 | 73.4495 | 0 | 41.4525 | 0.8 | 1 | 11.054 | 52.5065 | -2.3 | -0.65917 | 1.0898 | 0.046922
2016-04-08 07:00 | 75.0567 | 74.91 | 0.14667 | 0.62922 | 7.1059 | -59.7982 | 76.5208 | 13.4792 | -61.874 | 59.0991 | 0.32314 | 56.1825 | 0.8 | 1 | 15.0113 | 71.517 | -2 | 0.23491 | 1.0867 | 0.063727
2016-04-08 08:00 | 94.8433 | 94.55 | 0.29333 | 1.0492 | 7.1214 | -44.7951 | 73.7649 | 16.2351 | -46.7337 | 44.7907 | 0.7446 | 70.9125 | 0.8 | 1 | 18.9687 | 90.6258 | -2.1 | 0.73206 | 1.0849 | 0.080625
2016-04-08 09:00 | 114.63 | 114.19 | 0.44 | 1.3958 | 7.1369 | -29.792 | 71.6249 | 18.3751 | -31.2981 | 30.6962 | 1.2002 | 85.6425 | 0.8 | 1 | 22.926 | 109.7687 | -2.1 | 1.3303 | 1.0828 | 0.097467
2016-04-08 10:00 | 121.97 | 120.0133 | 1.9567 | 5.7949 | 7.1525 | -14.7889 | 70.266 | 19.734 | -15.6092 | 17.46 | 5.5279 | 90.01 | 0.8 | 1 | 24.394 | 119.9319 | -1.8 | 1.9479 | 1.0807 | 0.10628
2016-04-08 11:00 | 129.31 | 125.8367 | 3.4733 | 10.0583 | 7.168 | 0.21415 | 69.7988 | 20.2012 | 0.2264 | 9.8009 | 9.9115 | 94.3775 | 0.8 | 1 | 25.862 | 130.151 | -2.3 | 1.7672 | 1.0813 | 0.1154
2016-04-08 12:00 | 136.65 | 131.66 | 4.99 | 14.7752 | 7.1835 | 15.2172 | 70.2614 | 19.7386 | 16.0619 | 17.7896 | 14.0687 | 98.745 | 0.8 | 1 | 27.33 | 140.1437 | -2.4 | 1.9795 | 1.0806 | 0.12418
2016-04-08 13:00 | 119.22 | 115.12 | 4.1 | 12.9985 | 7.199 | 30.2203 | 71.6137 | 18.3863 | 31.7505 | 31.0697 | 11.1337 | 86.34 | 0.8 | 1 | 23.844 | 121.3177 | -2.4 | 1.3912 | 1.0826 | 0.1077
2016-04-08 14:00 | 101.79 | 98.58 | 3.21 | 11.467 | 7.2145 | 45.2234 | 73.7437 | 16.2563 | 47.1862 | 45.1703 | 8.0842 | 73.935 | 0.8 | 1 | 20.358 | 102.3772 | -2.6 | 0.59929 | 1.0854 | 0.091119
2016-04-08 15:00 | 84.36 | 82.04 | 2.32 | 9.9269 | 7.2301 | 60.2264 | 76.4846 | 13.5154 | 62.3277 | 59.4753 | 5.042 | 61.53 | 0.8 | 1 | 16.872 | 83.444 | -3.1 | -0.49238 | 1.0892 | 0.074529
2016-04-08 16:00 | 61.5933 | 60.03 | 1.5633 | 8.6896 | 7.2456 | 75.2295 | 79.6355 | 10.3645 | 77.1988 | 73.8169 | 2.4219 | 45.0225 | 0.8 | 1 | 12.3187 | 59.763 | -3.1 | -1.2324 | 1.0918 | 0.053505
2016-04-08 17:00 | 38.8267 | 38.02 | 0.80667 | 6.5998 | 7.2611 | 90.2326 | 82.9794 | 7.0206 | 91.8722 | 88.1071 | 0.218 | 28.515 | 0.8 | 1 | 7.7653 | 36.4983 | -3.5 | -2.3594 | 1.0958 | 0.032795
2016-04-08 18:00 | 16.06 | 16.01 | 0.05 | 0.77388 | 7.2766 | 105.2356 | 86.2956 | 3.7044 | 106.4461 | 102.261 | 0 | 12.0075 | 0.8 | 1 | 3.212 | 15.2195 | -3.6 | -3.1244 | 1.0984 | 0.013708
2016-04-08 19:00 | 10.7067 | 10.6733 | 0.033333 | 0 | 7.2921 | 120.2387 | 89.3695 | 0.63052 | 121.0187 | 116.1517 | 0 | 8.005 | 0.8 | 1 | 2.1413 | 10.1463 | -3.6 | -3.2829 | 1.099 | 0.0091436
2016-04-08 20:00 | 5.3533 | 5.3367 | 0.016667 | 0 | 7.3076 | 135.2417 | 92.001 | -2.001 | 135.6672 | 129.5345 | 0 | 4.0025 | 0.8 | 1 | 1.0707 | 5.0732 | -3.7 | -3.5415 | 1.0999 | 0.0045756
2016-04-08 21:00 | 0 | 0 | 0 | 0 | 7.323 | 150.2448 | 94.0144 | -4.0144 | 150.4319 | 141.8502 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.1033 | 0
2016-04-08 22:00 | 0 | 0 | 0 | 0 | 7.3385 | 165.2478 | 95.2704 | -5.2704 | 165.3079 | 151.6539 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4 | -4 | 1.1015 | 0
2016-04-08 23:00 | 0 | 0 | 0 | 0 | 7.354 | 180.2509 | 95.6792 | -5.6792 | -179.7499 | 155.6781 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.6 | -4.6 | 1.1036 | 0
2016-04-09 | 0 | 0 | 0 | 0 | 7.3695 | -164.7461 | 95.2103 | -5.2103 | -164.8108 | 151.3691 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.1033 | 0
2016-04-09 01:00 | 2.4233 | 2.3967 | 0.026667 | 0 | 7.385 | -149.743 | 93.8966 | -3.8966 | -149.9433 | 141.4272 | 0 | 1.7975 | 0.8 | 1 | 0.48467 | 2.2822 | -4.5 | -4.4287 | 1.103 | 0.0020641
2016-04-09 02:00 | 4.8467 | 4.7933 | 0.053333 | 0 | 7.4004 | -134.74 | 91.8299 | -1.8299 | -135.1905 | 129.0544 | 0 | 3.595 | 0.8 | 1 | 0.96933 | 4.5643 | -5 | -4.8574 | 1.1045 | 0.0041339
2016-04-09 03:00 | 7.27 | 7.19 | 0.08 | 0 | 7.4159 | -119.7369 | 89.1508 | 0.84918 | -120.5548 | 115.6451 | 0 | 5.3925 | 0.8 | 1 | 1.454 | 6.8465 | -5.7 | -5.486 | 1.1067 | 0.0062132
2016-04-09 04:00 | 23.8933 | 23.6933 | 0.2 | 2.893 | 7.4314 | -104.7339 | 86.0358 | 3.9642 | -105.9933 | 101.7402 | 0 | 17.77 | 0.8 | 1 | 4.7787 | 22.5487 | -5.4 | -4.6954 | 1.1039 | 0.020412
2016-04-09 05:00 | 40.5167 | 40.1967 | 0.32 | 2.5134 | 7.4468 | -89.7308 | 82.6854 | 7.3146 | -91.4264 | 87.577 | 0.10626 | 30.1475 | 0.8 | 1 | 8.1033 | 38.3571 | -5.5 | -4.3013 | 1.1026 | 0.034678
2016-04-09 06:00 | 57.14 | 56.7 | 0.44 | 2.3729 | 7.4623 | -74.7278 | 79.314 | 10.686 | -76.7541 | 73.2794 | 0.6827 | 42.525 | 0.8 | 1 | 11.428 | 54.6357 | -4.9 | -3.1926 | 1.0987 | 0.049222
2016-04-09 07:00 | 67.1233 | 66.83 | 0.29333 | 1.2247 | 7.4777 | -59.7248 | 76.1419 | 13.8581 | -61.8773 | 58.9299 | 0.63204 | 50.1225 | 0.8 | 1 | 13.4247 | 64.1792 | -4.4 | -2.3944 | 1.0959 | 0.057673
2016-04-09 08:00 | 77.1067 | 76.96 | 0.14667 | 0.51297 | 7.4932 | -44.7217 | 73.3863 | 16.6137 | -46.723 | 44.6137 | 0.36516 | 57.72 | 0.8 | 1 | 15.4213 | 73.5065 | -4.2 | -1.9029 | 1.0942 | 0.065951
2016-04-09 09:00 | 87.09 | 87.09 | 0 | 0 | 7.5086 | -29.7187 | 71.2472 | 18.7528 | -31.2682 | 30.4943 | 0 | 65.3175 | 0.8 | 1 | 17.418 | 82.7355 | -4.2 | -1.6145 | 1.0932 | 0.074163
2016-04-09 10:00 | 88.8333 | 88.8333 | 0 | 0 | 7.5241 | -14.7157 | 69.8907 | 20.1093 | -15.5563 | 17.1868 | 0 | 66.625 | 0.8 | 1 | 17.7667 | 84.3917 | -3.9 | -1.2628 | 1.0919 | 0.075562
2016-04-09 11:00 | 90.5767 | 90.5767 | 0 | 0 | 7.5395 | 0.28736 | 69.4273 | 20.5727 | 0.30428 | 9.4313 | 0 | 67.9325 | 0.8 | 1 | 18.1153 | 86.0478 | -4.1 | -1.411 | 1.0924 | 0.077082
2016-04-09 12:00 | 92.32 | 92.32 | 0 | 0 | 7.5549 | 15.2904 | 69.8953 | 20.1047 | 16.1638 | 17.6408 | 0 | 69.24 | 0.8 | 1 | 18.464 | 87.704 | -4.1 | -1.3593 | 1.0923 | 0.078552
2016-04-09 13:00 | 96.9467 | 95.81 | 1.1367 | 3.5369 | 7.5704 | 30.2934 | 71.2538 | 18.7462 | 31.8734 | 31.0055 | 3.0315 | 71.8575 | 0.8 | 1 | 19.3893 | 94.2783 | -3.6 | -0.6538 | 1.0898 | 0.08425
2016-04-09 14:00 | 101.5733 | 99.3 | 2.2733 | 7.9526 | 7.5858 | 45.2964 | 73.3897 | 16.6103 | 47.3254 | 45.1336 | 5.6102 | 74.475 | 0.8 | 1 | 20.3147 | 100.3999 | -3.9 | -0.7625 | 1.0902 | 0.089751
2016-04-09 15:00 | 106.2 | 102.79 | 3.41 | 14.2306 | 7.6012 | 60.2994 | 76.1356 | 13.8644 | 62.4777 | 59.4468 | 7.2339 | 77.0925 | 0.8 | 1 | 21.24 | 105.5664 | -3.4 | -0.10105 | 1.0879 | 0.094169
2016-04-09 16:00 | 79.5567 | 76.2133 | 3.3433 | 17.9901 | 7.6166 | 75.3025 | 79.2897 | 10.7103 | 77.3543 | 73.7869 | 5.023 | 57.16 | 0.8 | 1 | 15.9113 | 78.0944 | -3.5 | -1.0596 | 1.0912 | 0.069878
2016-04-09 17:00 | 52.9133 | 49.6367 | 3.2767 | 25.5594 | 7.6321 | 90.3055 | 82.6345 | 7.3655 | 92.0282 | 88.0687 | 0.8614 | 37.2275 | 0.8 | 1 | 10.5827 | 48.6716 | -3.4 | -1.879 | 1.0941 | 0.043665
2016-04-09 18:00 | 26.27 | 23.06 | 3.21 | 45.4425 | 7.6475 | 105.3085 | 85.9493 | 4.0507 | 106.5978 | 102.207 | 0 | 17.295 | 0.8 | 1 | 5.254 | 22.549 | -3.5 | -2.7953 | 1.0973 | 0.020289
2016-04-09 19:00 | 17.5133 | 15.3733 | 2.14 | 0 | 7.6629 | 120.3115 | 89.0198 | 0.98018 | 121.1617 | 116.0727 | 0 | 11.53 | 0.8 | 1 | 3.5027 | 15.0327 | -3.6 | -3.1302 | 1.0985 | 0.01354
2016-04-09 20:00 | 8.7567 | 7.6867 | 1.07 | 0 | 7.6783 | 135.3145 | 91.6464 | -1.6464 | 135.7974 | 129.4159 | 0 | 5.765 | 0.8 | 1 | 1.7513 | 7.5163 | -3.3 | -3.0651 | 1.0982 | 0.0067688
2016-04-09 21:00 | 0 | 0 | 0 | 0 | 7.6937 | 150.3175 | 93.6542 | -3.6542 | 150.5453 | 141.6672 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-04-09 22:00 | 0 | 0 | 0 | 0 | 7.7091 | 165.3205 | 94.9046 | -4.9046 | 165.4015 | 151.3717 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.0991 | 0
2016-04-09 23:00 | 0 | 0 | 0 | 0 | 7.7245 | 180.3235 | 95.3086 | -5.3086 | -179.678 | 155.3068 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-04-10 | 0 | 0 | 0 | 0 | 7.7399 | -164.6735 | 94.8363 | -4.8363 | -164.7609 | 151.0158 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-04-10 01:00 | 4.12 | 3.9 | 0.22 | 0 | 7.7553 | -149.6705 | 93.5205 | -3.5205 | -149.9139 | 141.136 | 0 | 2.925 | 0.8 | 1 | 0.824 | 3.749 | -3.5 | -3.3828 | 1.0993 | 0.0033796
2016-04-10 02:00 | 8.24 | 7.8 | 0.44 | 0 | 7.7706 | -134.6675 | 91.453 | -1.453 | -135.179 | 128.8117 | 0 | 5.85 | 0.8 | 1 | 1.648 | 7.498 | -3.7 | -3.4657 | 1.0996 | 0.0067609
2016-04-10 03:00 | 12.36 | 11.7 | 0.66 | 0 | 7.786 | -119.6645 | 88.7738 | 1.2262 | -120.5569 | 115.4346 | 0 | 8.775 | 0.8 | 1 | 2.472 | 11.247 | -3.7 | -3.3485 | 1.0992 | 0.010138
2016-04-10 04:00 | 37.6433 | 35.6167 | 2.0267 | 26.7755 | 7.8014 | -104.6615 | 85.6591 | 4.3409 | -106.0042 | 101.5509 | 0 | 26.7125 | 0.8 | 1 | 7.5287 | 34.2412 | -4.4 | -3.33 | 1.0992 | 0.030862
2016-04-10 05:00 | 62.9267 | 59.5333 | 3.3933 | 25.3548 | 7.8168 | -89.6585 | 82.3088 | 7.6912 | -91.4408 | 87.4015 | 1.1495 | 44.65 | 0.8 | 1 | 12.5853 | 58.3848 | -4.5 | -2.6755 | 1.0969 | 0.052513
2016-04-10 06:00 | 88.21 | 83.45 | 4.76 | 24.807 | 7.8321 | -74.6555 | 78.9374 | 11.0626 | -76.7663 | 73.1115 | 7.2067 | 62.5875 | 0.8 | 1 | 17.642 | 87.4362 | -4.9 | -2.1676 | 1.0951 | 0.078515
2016-04-10 07:00 | 121.18 | 109.0867 | 12.0933 | 49.1811 | 7.8475 | -59.6525 | 75.7653 | 14.2347 | -61.8815 | 58.7636 | 25.5039 | 81.815 | 0.8 | 1 | 24.236 | 131.5549 | -4.9 | -0.78891 | 1.0903 | 0.11761
2016-04-10 08:00 | 154.15 | 134.7233 | 19.4267 | 66.4824 | 7.8629 | -44.6495 | 73.0098 | 16.9902 | -46.7133 | 44.4405 | 47.467 | 101.0425 | 0.8 | 1 | 30.83 | 179.3395 | -5.4 | 0.20436 | 1.0868 | 0.15982
2016-04-10 09:00 | 187.12 | 160.36 | 26.76 | 81.6642 | 7.8782 | -29.6465 | 70.8718 | 19.1282 | -31.2392 | 30.2974 | 70.5104 | 120.27 | 0.8 | 1 | 37.424 | 228.2044 | -5.2 | 1.9314 | 1.0807 | 0.20224
2016-04-10 10:00 | 184.46 | 161.55 | 22.91 | 65.472 | 7.8936 | -14.6435 | 69.5175 | 20.4825 | -15.5042 | 16.9197 | 62.6379 | 121.1625 | 0.8 | 1 | 36.892 | 220.6924 | -5.4 | 1.4966 | 1.0823 | 0.19585
2016-04-10 11:00 | 181.8 | 162.74 | 19.06 | 53.3262 | 7.9089 | 0.35945 | 69.058 | 20.942 | 0.38121 | 9.0645 | 52.6603 | 122.055 | 0.8 | 1 | 36.36 | 211.0753 | -5.4 | 1.1961 | 1.0833 | 0.1875
2016-04-10 12:00 | 179.14 | 163.93 | 15.21 | 43.4949 | 7.9243 | 15.3624 | 69.5313 | 20.4687 | 16.2648 | 17.4988 | 41.4821 | 122.9475 | 0.8 | 1 | 35.828 | 200.2576 | -5.6 | 0.65805 | 1.0852 | 0.1782
2016-04-10 13:00 | 156 | 140.2667 | 15.7333 | 48.072 | 7.9396 | 30.3654 | 70.8958 | 19.1042 | 31.9952 | 30.9449 | 41.2295 | 105.2 | 0.8 | 1 | 31.2 | 177.6295 | -5.6 | -0.049077 | 1.0877 | 0.15843
2016-04-10 14:00 | 132.86 | 116.6033 | 16.2567 | 55.7229 | 7.9549 | 45.3684 | 73.0378 | 16.9622 | 47.4634 | 45.0988 | 39.3341 | 87.4525 | 0.8 | 1 | 26.572 | 153.3586 | -5.7 | -0.90755 | 1.0907 | 0.13716
2016-04-10 15:00 | 109.72 | 92.94 | 16.78 | 68.35 | 7.9703 | 60.3713 | 75.7885 | 14.2115 | 62.6265 | 59.4191 | 34.7733 | 69.705 | 0.8 | 1 | 21.944 | 126.4223 | -5.6 | -1.6493 | 1.0933 | 0.11334
2016-04-10 16:00 | 81.74 | 70.0933 | 11.6467 | 60.7428 | 7.9856 | 75.3743 | 78.9458 | 11.0542 | 77.5084 | 73.757 | 16.9904 | 52.57 | 0.8 | 1 | 16.348 | 85.9084 | -5.7 | -3.0154 | 1.0981 | 0.077352
2016-04-10 17:00 | 53.76 | 47.2467 | 6.5133 | 48.5587 | 8.0009 | 90.3773 | 82.2915 | 7.7085 | 92.1827 | 88.0297 | 1.6695 | 35.435 | 0.8 | 1 | 10.752 | 47.8565 | -6.3 | -4.8045 | 1.1043 | 0.043336
2016-04-10 18:00 | 25.78 | 24.4 | 1.38 | 18.0078 | 8.0163 | 105.3803 | 85.6049 | 4.3951 | 106.748 | 102.152 | 0 | 18.3 | 0.8 | 1 | 5.156 | 23.456 | -6.2 | -5.467 | 1.1066 | 0.021285
2016-04-10 19:00 | 17.1867 | 16.2667 | 0.92 | 0 | 8.0316 | 120.3832 | 88.672 | 1.328 | 121.3032 | 115.9922 | 0 | 12.2 | 0.8 | 1 | 3.4373 | 15.6373 | -6.3 | -5.8113 | 1.1078 | 0.014205
2016-04-10 20:00 | 8.5933 | 8.1333 | 0.46 | 0 | 8.0469 | 135.3862 | 91.2938 | -1.2938 | 135.926 | 129.2955 | 0 | 6.1 | 0.8 | 1 | 1.7187 | 7.8187 | -8 | -7.7557 | 1.1146 | 0.0071463
2016-04-10 21:00 | 0 | 0 | 0 | 0 | 8.0622 | 150.3891 | 93.2959 | -3.2959 | 150.6572 | 141.4822 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.7 | -8.7 | 1.1179 | 0
2016-04-10 22:00 | 0 | 0 | 0 | 0 | 8.0775 | 165.3921 | 94.5409 | -4.5409 | 165.4937 | 151.0888 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.5 | -9.5 | 1.1207 | 0
2016-04-10 23:00 | 0 | 0 | 0 | 0 | 8.0928 | 180.395 | 94.9402 | -4.9402 | -179.6074 | 154.9375 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.5 | -10.5 | 1.1242 | 0
2016-04-11 | 0 | 0 | 0 | 0 | 8.1081 | -164.602 | 94.4645 | -4.4645 | -164.7122 | 150.6645 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.5 | -9.5 | 1.1207 | 0
2016-04-11 01:00 | 4.8433 | 4.2033 | 0.64 | 0 | 8.1234 | -149.599 | 93.1467 | -3.1467 | -149.8857 | 140.846 | 0 | 3.1525 | 0.8 | 1 | 0.96867 | 4.1212 | -10.3 | -10.1712 | 1.1231 | 0.0037954
2016-04-11 02:00 | 9.6867 | 8.4067 | 1.28 | 0 | 8.1387 | -134.5961 | 91.0783 | -1.0783 | -135.1683 | 128.5699 | 0 | 6.305 | 0.8 | 1 | 1.9373 | 8.2423 | -11.2 | -10.9424 | 1.1258 | 0.0076089
2016-04-11 03:00 | 14.53 | 12.61 | 1.92 | 0 | 8.154 | -119.5932 | 88.3991 | 1.6009 | -120.5598 | 115.2253 | 0 | 9.4575 | 0.8 | 1 | 2.906 | 12.3635 | -10.9 | -10.5136 | 1.1243 | 0.011398
2016-04-11 04:00 | 44.3933 | 34.81 | 9.5833 | 116.5784 | 8.1693 | -104.5902 | 85.2847 | 4.7153 | -106.0159 | 101.3632 | 0 | 26.1075 | 0.8 | 1 | 8.8787 | 34.9862 | -12.7 | -11.6067 | 1.1281 | 0.032364
2016-04-11 05:00 | 74.2567 | 57.01 | 17.2467 | 122.9248 | 8.1845 | -89.5873 | 81.9346 | 8.0654 | -91.456 | 87.2279 | 5.945 | 42.7575 | 0.8 | 1 | 14.8513 | 63.5539 | -10.7 | -8.7139 | 1.118 | 0.058264
2016-04-11 06:00 | 104.12 | 79.21 | 24.91 | 125.6267 | 8.1998 | -74.5843 | 78.5633 | 11.4367 | -76.7794 | 72.9461 | 36.8427 | 59.4075 | 0.8 | 1 | 20.824 | 117.0742 | -10.6 | -6.9414 | 1.1118 | 0.10673
2016-04-11 07:00 | 129.9467 | 99.09 | 30.8567 | 122.3404 | 8.2151 | -59.5814 | 75.3911 | 14.6089 | -61.8865 | 58.6003 | 63.7399 | 74.3175 | 0.8 | 1 | 25.9893 | 164.0467 | -11.2 | -6.0735 | 1.1088 | 0.14915
2016-04-11 08:00 | 155.7733 | 118.97 | 36.8033 | 123.3168 | 8.2304 | -44.5785 | 72.6358 | 17.3642 | -46.7044 | 44.2711 | 88.3004 | 89.2275 | 0.8 | 1 | 31.1547 | 208.6826 | -10.6 | -4.0787 | 1.1018 | 0.18854
2016-04-11 09:00 | 181.6 | 138.85 | 42.75 | 128.0595 | 8.2456 | -29.5755 | 70.4986 | 19.5014 | -31.2112 | 30.1055 | 110.7848 | 104.1375 | 0.8 | 1 | 36.32 | 251.2423 | -10.9 | -3.0487 | 1.0982 | 0.22624
2016-04-11 10:00 | 193.7133 | 140.4967 | 53.2167 | 149.4945 | 8.2609 | -14.5726 | 69.1466 | 20.8534 | -15.4531 | 16.659 | 143.2199 | 105.3725 | 0.8 | 1 | 38.7427 | 287.335 | -10.7 | -1.7208 | 1.0935 | 0.25765
2016-04-11 11:00 | 205.8267 | 142.1433 | 63.6833 | 175.2436 | 8.2761 | 0.43034 | 68.6909 | 21.3091 | 0.45711 | 8.7006 | 173.2269 | 106.6075 | 0.8 | 1 | 41.1653 | 320.9997 | -11.1 | -1.0688 | 1.0912 | 0.28724
2016-04-11 12:00 | 217.94 | 143.79 | 74.15 | 208.5171 | 8.2914 | 15.4333 | 69.1694 | 20.8306 | 16.3647 | 17.3636 | 199.015 | 107.8425 | 0.8 | 1 | 43.588 | 350.4455 | -11.5 | -0.54858 | 1.0894 | 0.31306
2016-04-11 13:00 | 198.7033 | 127.53 | 71.1733 | 213.6379 | 8.3066 | 30.4362 | 70.54 | 19.46 | 32.1159 | 30.8878 | 183.3384 | 95.6475 | 0.8 | 1 | 39.7407 | 318.7266 | -11.6 | -1.6398 | 1.0932 | 0.28572
2016-04-11 14:00 | 179.4667 | 111.27 | 68.1967 | 229.1725 | 8.3219 | 45.4391 | 72.6878 | 17.3122 | 47.6001 | 45.0657 | 161.8635 | 83.4525 | 0.8 | 1 | 35.8933 | 281.2094 | -11 | -2.2122 | 1.0952 | 0.25255
2016-04-11 15:00 | 160.23 | 95.01 | 65.22 | 259.4941 | 8.3371 | 60.442 | 75.4435 | 14.5565 | 62.7739 | 59.3922 | 132.1237 | 71.2575 | 0.8 | 1 | 32.046 | 235.4272 | -11.2 | -3.8429 | 1.101 | 0.21254
2016-04-11 16:00 | 117.2433 | 73.18 | 44.0633 | 223.0015 | 8.3524 | 75.445 | 78.6038 | 11.3962 | 77.6611 | 73.7272 | 62.4875 | 54.885 | 0.8 | 1 | 23.4487 | 140.8212 | -11.6 | -7.1993 | 1.1127 | 0.12849
2016-04-11 17:00 | 74.2567 | 51.35 | 22.9067 | 163.5834 | 8.3676 | 90.4479 | 81.9504 | 8.0496 | 92.3357 | 87.9903 | 5.7367 | 38.5125 | 0.8 | 1 | 14.8513 | 59.1005 | -10.6 | -8.7531 | 1.1181 | 0.054188
2016-04-11 18:00 | 31.27 | 29.52 | 1.75 | 21.1884 | 8.3828 | 105.4508 | 85.2624 | 4.7376 | 106.8966 | 102.096 | 0 | 22.14 | 0.8 | 1 | 6.254 | 28.394 | -11.7 | -10.8127 | 1.1253 | 0.026201
2016-04-11 19:00 | 20.8567 | 19.69 | 1.1667 | 0 | 8.398 | 120.4537 | 88.3261 | 1.6739 | 121.443 | 115.9103 | 0 | 14.7675 | 0.8 | 1 | 4.1713 | 18.9388 | -11.9 | -11.3082 | 1.1271 | 0.017503
2016-04-11 20:00 | 10.4433 | 9.86 | 0.58333 | 0 | 8.4133 | 135.4566 | 90.943 | -0.94304 | 136.0528 | 129.1731 | 0 | 7.395 | 0.8 | 1 | 2.0887 | 9.4837 | -12.9 | -12.6036 | 1.1316 | 0.0088001
2016-04-11 21:00 | 0.03 | 0.03 | 0 | 0 | 8.4285 | 150.4595 | 92.9397 | -2.9397 | 150.7674 | 141.2954 | 0 | 0.0225 | 0.8 | 1 | 0.006 | 0.0285 | -13.7 | -13.6991 | 1.1354 | 2.6535e-05
2016-04-11 22:00 | 0.02 | 0.02 | 0 | 0 | 8.4437 | 165.4624 | 94.1792 | -4.1792 | 165.5842 | 150.8052 | 0 | 0.015 | 0.8 | 1 | 0.004 | 0.019 | -14.4 | -14.3994 | 1.1379 | 1.7728e-05
2016-04-11 23:00 | 0.01 | 0.01 | 0 | 0 | 8.4589 | 180.4653 | 94.574 | -4.574 | -179.5383 | 154.5703 | 0 | 0.0075 | 0.8 | 1 | 0.002 | 0.0095 | -14.6 | -14.5997 | 1.1386 | 8.8697e-06
2016-04-12 | 0 | 0 | 0 | 0 | 8.4741 | -164.5318 | 94.095 | -4.095 | -164.6647 | 150.3152 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.1 | -14.1 | 1.1368 | 0
2016-04-12 01:00 | 5.8333 | 4.29 | 1.5433 | 0 | 8.4893 | -149.5289 | 92.7753 | -2.7753 | -149.8585 | 140.5572 | 0 | 3.2175 | 0.8 | 1 | 1.1667 | 4.3842 | -14 | -13.863 | 1.136 | 0.004084
2016-04-12 02:00 | 11.6667 | 8.58 | 3.0867 | 0 | 8.5045 | -134.526 | 90.7062 | -0.70615 | -135.1586 | 128.3293 | 0 | 6.435 | 0.8 | 1 | 2.3333 | 8.7683 | -13 | -12.726 | 1.132 | 0.0081394
2016-04-12 03:00 | 17.5 | 12.87 | 4.63 | 0 | 8.5197 | -119.5231 | 88.0269 | 1.9731 | -120.5636 | 115.0174 | 0 | 9.6525 | 0.8 | 1 | 3.5 | 13.1525 | -13.8 | -13.389 | 1.1344 | 0.012234
2016-04-12 04:00 | 55.6833 | 31.8867 | 23.7967 | 268.3669 | 8.5349 | -104.5202 | 84.9128 | 5.0872 | -106.0285 | 101.1772 | 0 | 23.915 | 0.8 | 1 | 11.1367 | 35.0517 | -13.7 | -12.6046 | 1.1316 | 0.032525
2016-04-12 05:00 | 93.8667 | 50.9033 | 42.9633 | 292.821 | 8.5501 | -89.5173 | 81.563 | 8.437 | -91.4721 | 87.0564 | 15.0373 | 38.1775 | 0.8 | 1 | 18.7733 | 71.9881 | -13.3 | -11.0504 | 1.1262 | 0.066478
2016-04-12 06:00 | 132.05 | 69.92 | 62.13 | 303.6072 | 8.5652 | -74.5144 | 78.1916 | 11.8084 | -76.7934 | 72.7832 | 89.8641 | 52.44 | 0.8 | 1 | 26.41 | 168.7141 | -12 | -6.7277 | 1.111 | 0.15371
2016-04-12 07:00 | 186.04 | 77.8067 | 108.2333 | 418.709 | 8.5804 | -59.5115 | 75.0193 | 14.9807 | -61.8925 | 58.4402 | 219.1473 | 58.355 | 0.8 | 1 | 37.208 | 314.7103 | -12.4 | -2.5653 | 1.0965 | 0.28296
2016-04-12 08:00 | 240.03 | 85.6933 | 154.3367 | 506.6376 | 8.5956 | -44.5087 | 72.2641 | 17.7359 | -46.6966 | 44.1057 | 363.795 | 64.27 | 0.8 | 1 | 48.006 | 476.071 | -10.3 | 4.5772 | 1.0715 | 0.41828
2016-04-12 09:00 | 294.02 | 93.58 | 200.44 | 589.6662 | 8.6107 | -29.5058 | 70.1279 | 19.8721 | -31.1843 | 29.9187 | 511.0835 | 70.185 | 0.8 | 1 | 58.804 | 640.0725 | -8.4 | 11.6023 | 1.0469 | 0.54947
2016-04-12 10:00 | 301.6633 | 96.76 | 204.9033 | 566.0612 | 8.6259 | -14.5029 | 68.7781 | 21.2219 | -15.4031 | 16.405 | 543.0165 | 72.57 | 0.8 | 1 | 60.3327 | 675.9192 | -9.4 | 11.7225 | 1.0465 | 0.58001
2016-04-12 11:00 | 309.3067 | 99.94 | 209.3667 | 566.8929 | 8.6411 | 0.49996 | 68.3261 | 21.6739 | 0.53189 | 8.3398 | 560.8981 | 74.955 | 0.8 | 1 | 61.8613 | 697.7144 | -9.1 | 12.7036 | 1.043 | 0.59675
2016-04-12 12:00 | 316.95 | 103.12 | 213.83 | 591.5634 | 8.6562 | 15.5028 | 68.8097 | 21.1903 | 16.4635 | 17.2352 | 565.0002 | 77.34 | 0.8 | 1 | 63.39 | 705.7302 | -8.1 | 13.9541 | 1.0387 | 0.60107
2016-04-12 13:00 | 264.6633 | 91.56 | 173.1033 | 510.6844 | 8.6714 | 30.5057 | 70.1863 | 19.8137 | 32.2354 | 30.8342 | 438.5014 | 68.67 | 0.8 | 1 | 52.9327 | 560.1041 | -8.1 | 9.4033 | 1.0546 | 0.48436
2016-04-12 14:00 | 212.3767 | 80 | 132.3767 | 436.3563 | 8.6865 | 45.5086 | 72.34 | 17.66 | 47.7356 | 45.0343 | 308.3658 | 60 | 0.8 | 1 | 42.4753 | 410.8411 | -7.5 | 5.3388 | 1.0688 | 0.36007
2016-04-12 15:00 | 160.09 | 68.44 | 91.65 | 356.4407 | 8.7017 | 60.5114 | 75.1004 | 14.8996 | 62.9199 | 59.3659 | 181.6257 | 51.33 | 0.8 | 1 | 32.018 | 264.9737 | -6.5 | 1.7804 | 1.0813 | 0.23494
2016-04-12 16:00 | 118.57 | 53.1267 | 65.4433 | 321.7379 | 8.7168 | 75.5143 | 78.2638 | 11.7362 | 77.8122 | 73.6973 | 90.3158 | 39.845 | 0.8 | 1 | 23.714 | 153.8748 | -8.5 | -3.6914 | 1.1004 | 0.13885
2016-04-12 17:00 | 77.05 | 37.8133 | 39.2367 | 268.9487 | 8.7319 | 90.5172 | 81.6112 | 8.3888 | 92.487 | 87.9502 | 9.6197 | 28.36 | 0.8 | 1 | 15.41 | 53.3897 | -8.5 | -6.8316 | 1.1114 | 0.048657
2016-04-12 18:00 | 35.53 | 22.5 | 13.03 | 147.2082 | 8.7471 | 105.52 | 84.9219 | 5.0781 | 107.0434 | 102.0389 | 0 | 16.875 | 0.8 | 1 | 7.106 | 23.981 | -9.4 | -8.6506 | 1.1178 | 0.02198
2016-04-12 19:00 | 23.7033 | 15.0167 | 8.6867 | 0 | 8.7622 | 120.5229 | 87.9822 | 2.0178 | 121.581 | 115.8269 | 0 | 11.2625 | 0.8 | 1 | 4.7407 | 16.0032 | -10 | -9.4999 | 1.1207 | 0.014707
2016-04-12 20:00 | 11.8767 | 7.5333 | 4.3433 | 0 | 8.7773 | 135.5257 | 90.5944 | -0.59437 | 136.1779 | 129.049 | 0 | 5.65 | 0.8 | 1 | 2.3753 | 8.0253 | -11.4 | -11.1492 | 1.1265 | 0.0074134
2016-04-12 21:00 | 0.05 | 0.05 | 0 | 0 | 8.7924 | 150.5286 | 92.5856 | -2.5856 | 150.8759 | 141.1067 | 0 | 0.0375 | 0.8 | 1 | 0.01 | 0.0475 | -11.3 | -11.2985 | 1.127 | 4.3898e-05
2016-04-12 22:00 | 0.033333 | 0.033333 | 0 | 0 | 8.8075 | 165.5314 | 93.8198 | -3.8198 | 165.6732 | 150.5212 | 0 | 0.025 | 0.8 | 1 | 0.0066667 | 0.031667 | -11.8 | -11.799 | 1.1288 | 2.9311e-05
2016-04-12 23:00 | 0.016667 | 0.016667 | 0 | 0 | 8.8227 | 180.5343 | 94.2101 | -4.2101 | -179.4706 | 154.2053 | 0 | 0.0125 | 0.8 | 1 | 0.0033333 | 0.015833 | -11.7 | -11.6995 | 1.1284 | 1.4651e-05
2016-04-13 | 0 | 0 | 0 | 0 | 8.8378 | -164.4629 | 93.7279 | -3.7279 | -164.6186 | 149.9682 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.6 | -12.6 | 1.1316 | 0
2016-04-13 01:00 | 5.74 | 4.4 | 1.34 | 0 | 8.8529 | -149.46 | 92.4063 | -2.4063 | -149.8326 | 140.2699 | 0 | 3.3 | 0.8 | 1 | 1.148 | 4.448 | -12.7 | -12.561 | 1.1315 | 0.0041269
2016-04-13 02:00 | 11.48 | 8.8 | 2.68 | 0 | 8.868 | -134.4572 | 90.3365 | -0.33649 | -135.15 | 128.09 | 0 | 6.6 | 0.8 | 1 | 2.296 | 8.896 | -13 | -12.722 | 1.132 | 0.0082578
2016-04-13 03:00 | 17.22 | 13.2 | 4.02 | 0 | 8.883 | -119.4544 | 87.6573 | 2.3427 | -120.5683 | 114.8109 | 0 | 9.9 | 0.8 | 1 | 3.444 | 13.344 | -12.7 | -12.283 | 1.1305 | 0.01237
2016-04-13 04:00 | 58.1367 | 29.4433 | 28.6933 | 301.748 | 8.8981 | -104.4515 | 84.5435 | 5.4565 | -106.0419 | 100.993 | 0 | 22.0825 | 0.8 | 1 | 11.6273 | 33.7098 | -11.3 | -10.2466 | 1.1234 | 0.031052
2016-04-13 05:00 | 99.0533 | 45.6867 | 53.3667 | 348.5954 | 8.9132 | -89.4487 | 81.1939 | 8.8061 | -91.4891 | 86.887 | 18.9305 | 34.265 | 0.8 | 1 | 19.8107 | 73.0062 | -10.8 | -8.5186 | 1.1173 | 0.066888
2016-04-13 06:00 | 139.97 | 61.93 | 78.04 | 369.9635 | 8.9283 | -74.4459 | 77.8226 | 12.1774 | -76.8083 | 72.6229 | 110.4929 | 46.4475 | 0.8 | 1 | 27.994 | 184.9344 | -11.5 | -5.7208 | 1.1075 | 0.16795
2016-04-13 07:00 | 181.7833 | 71.4167 | 110.3667 | 416.9318 | 8.9434 | -59.4431 | 74.6502 | 15.3498 | -61.8995 | 58.2833 | 219.1893 | 53.5625 | 0.8 | 1 | 36.3567 | 309.1084 | -9.1 | 0.55964 | 1.0855 | 0.27515
2016-04-13 08:00 | 223.5967 | 80.9033 | 142.6933 | 459.1784 | 8.9584 | -44.4402 | 71.8951 | 18.1049 | -46.6898 | 43.9442 | 330.6156 | 60.6775 | 0.8 | 1 | 44.7193 | 436.0124 | -10 | 3.6254 | 1.0748 | 0.38428
2016-04-13 09:00 | 265.41 | 90.39 | 175.02 | 505.8999 | 8.9735 | -29.4374 | 69.7597 | 20.2403 | -31.1585 | 29.7373 | 439.2773 | 67.7925 | 0.8 | 1 | 53.082 | 560.1518 | -9.4 | 8.1047 | 1.0591 | 0.48649
2016-04-13 10:00 | 271.47 | 91.2667 | 180.2033 | 489.7768 | 8.9886 | -14.4346 | 68.412 | 21.588 | -15.3543 | 16.1578 | 470.4301 | 68.45 | 0.8 | 1 | 54.294 | 593.1741 | -9.1 | 9.4367 | 1.0545 | 0.5129
2016-04-13 11:00 | 277.53 | 92.1433 | 185.3867 | 494.1093 | 9.0036 | 0.56823 | 67.9637 | 22.0363 | 0.60546 | 7.9822 | 489.3219 | 69.1075 | 0.8 | 1 | 55.506 | 613.9354 | -8.9 | 10.2855 | 1.0515 | 0.52935
2016-04-13 12:00 | 283.59 | 93.02 | 190.57 | 518.8775 | 9.0187 | 15.571 | 68.4524 | 21.5476 | 16.5609 | 17.1135 | 495.9036 | 69.765 | 0.8 | 1 | 56.718 | 622.3866 | -8.8 | 10.6496 | 1.0502 | 0.53599
2016-04-13 13:00 | 243.0567 | 87.8 | 155.2567 | 450.3748 | 9.0337 | 30.5739 | 69.8348 | 20.1652 | 32.3535 | 30.7838 | 386.9193 | 65.85 | 0.8 | 1 | 48.6113 | 501.3806 | -8.7 | 6.9681 | 1.0631 | 0.43708
2016-04-13 14:00 | 202.5233 | 82.58 | 119.9433 | 388.0263 | 9.0488 | 45.5767 | 71.9943 | 18.0057 | 47.8696 | 45.0044 | 274.3548 | 61.935 | 0.8 | 1 | 40.5047 | 376.7944 | -8.7 | 3.0748 | 1.0767 | 0.33268
2016-04-13 15:00 | 161.99 | 77.36 | 84.63 | 321.9451 | 9.0638 | 60.5795 | 74.7595 | 15.2405 | 63.0643 | 59.3402 | 164.1726 | 58.02 | 0.8 | 1 | 32.398 | 254.5906 | -8.7 | -0.74404 | 1.0901 | 0.22757
2016-04-13 16:00 | 121.4233 | 61.2 | 60.2233 | 287.9064 | 9.0789 | 75.5823 | 77.9259 | 12.0741 | 77.9617 | 73.6673 | 80.9637 | 45.9 | 0.8 | 1 | 24.2847 | 151.1483 | -9.8 | -5.0766 | 1.1053 | 0.13699
2016-04-13 17:00 | 80.8567 | 45.04 | 35.8167 | 236.0908 | 9.0939 | 90.5851 | 81.2741 | 8.7259 | 92.6365 | 87.9095 | 8.6121 | 33.78 | 0.8 | 1 | 16.1713 | 58.5635 | -9.3 | -7.4699 | 1.1136 | 0.05348
2016-04-13 18:00 | 40.29 | 28.88 | 11.41 | 120.872 | 9.1089 | 105.5879 | 84.5834 | 5.4166 | 107.1884 | 101.9806 | 0 | 21.66 | 0.8 | 1 | 8.058 | 29.718 | -10.5 | -9.5713 | 1.121 | 0.027317
2016-04-13 19:00 | 26.92 | 19.3133 | 7.6067 | 0 | 9.1239 | 120.5907 | 87.6404 | 2.3596 | 121.717 | 115.742 | 0 | 14.485 | 0.8 | 1 | 5.384 | 19.869 | -10.6 | -9.9791 | 1.1224 | 0.018287
2016-04-13 20:00 | 13.55 | 9.7467 | 3.8033 | 0 | 9.139 | 135.5935 | 90.2478 | -0.24783 | 136.3011 | 128.923 | 0 | 7.31 | 0.8 | 1 | 2.71 | 10.02 | -10.4 | -10.0869 | 1.1228 | 0.0092254
2016-04-13 21:00 | 0.18 | 0.18 | 0 | 0 | 9.154 | 150.5963 | 92.2337 | -2.2337 | 150.9825 | 140.9164 | 0 | 0.135 | 0.8 | 1 | 0.036 | 0.171 | -11.5 | -11.4947 | 1.1277 | 0.00015813
2016-04-13 22:00 | 0.12 | 0.12 | 0 | 0 | 9.169 | 165.599 | 93.4627 | -3.4627 | 165.7604 | 150.2368 | 0 | 0.09 | 0.8 | 1 | 0.024 | 0.114 | -10.4 | -10.3964 | 1.1239 | 0.00010506
2016-04-13 23:00 | 0.06 | 0.06 | 0 | 0 | 9.184 | 180.6018 | 93.8486 | -3.8486 | -179.4045 | 153.8426 | 0 | 0.045 | 0.8 | 1 | 0.012 | 0.057 | -10.8 | -10.7982 | 1.1253 | 5.2596e-05
2016-04-14 | 0 | 0 | 0 | 0 | 9.199 | -164.3954 | 93.3633 | -3.3633 | -164.5739 | 149.6235 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.5 | -10.5 | 1.1242 | 0
2016-04-14 01:00 | 8.7033 | 6.0333 | 2.67 | 0 | 9.214 | -149.3926 | 92.0399 | -2.0399 | -149.8078 | 139.9842 | 0 | 4.525 | 0.8 | 1 | 1.7407 | 6.2657 | -11.6 | -11.4042 | 1.1274 | 0.0057925
2016-04-14 02:00 | 17.4067 | 12.0667 | 5.34 | 0 | 9.229 | -134.3898 | 89.9695 | 0.030538 | -135.1424 | 127.8522 | 0 | 9.05 | 0.8 | 1 | 3.4813 | 12.5313 | -11.1 | -10.7084 | 1.125 | 0.01156
2016-04-14 03:00 | 26.11 | 18.1 | 8.01 | 0 | 9.244 | -119.3871 | 87.2904 | 2.7096 | -120.5741 | 114.606 | 0 | 13.575 | 0.8 | 1 | 5.222 | 18.797 | -10.8 | -10.2126 | 1.1232 | 0.017313
2016-04-14 04:00 | 64.6367 | 40.4 | 24.2367 | 238.8844 | 9.2589 | -104.3843 | 84.1769 | 5.8231 | -106.0564 | 100.8106 | 0 | 30.3 | 0.8 | 1 | 12.9273 | 43.2273 | -10.2 | -8.8491 | 1.1185 | 0.039646
2016-04-14 05:00 | 103.1633 | 62.7 | 40.4633 | 253.8385 | 9.2739 | -89.3815 | 80.8276 | 9.1724 | -91.5071 | 86.7199 | 14.5239 | 47.025 | 0.8 | 1 | 20.6327 | 82.1816 | -10.2 | -7.6318 | 1.1142 | 0.075085
2016-04-14 06:00 | 141.69 | 85 | 56.69 | 261.0216 | 9.2889 | -74.3787 | 77.4562 | 12.5438 | -76.8242 | 72.4654 | 78.6412 | 63.75 | 0.8 | 1 | 28.338 | 170.7292 | -9.4 | -4.0647 | 1.1017 | 0.15424
2016-04-14 07:00 | 188.1767 | 102.5567 | 85.62 | 316.0881 | 9.3039 | -59.376 | 74.2837 | 15.7163 | -61.9075 | 58.1297 | 166.8941 | 76.9175 | 0.8 | 1 | 37.6353 | 281.4469 | -9 | -0.20478 | 1.0882 | 0.25115
2016-04-14 08:00 | 234.6633 | 120.1133 | 114.55 | 361.5508 | 9.3188 | -44.3732 | 71.5287 | 18.4713 | -46.6842 | 43.7869 | 261.01 | 90.085 | 0.8 | 1 | 46.9327 | 398.0277 | -9.1 | 3.3384 | 1.0758 | 0.35113
2016-04-14 09:00 | 281.15 | 137.67 | 143.48 | 407.6862 | 9.3338 | -29.3705 | 69.3941 | 20.6059 | -31.1339 | 29.5613 | 354.6171 | 103.2525 | 0.8 | 1 | 56.23 | 514.0996 | -8.8 | 7.2656 | 1.0621 | 0.44773
2016-04-14 10:00 | 281.41 | 145.8333 | 135.5767 | 362.6774 | 9.3488 | -14.3677 | 68.0485 | 21.9515 | -15.3068 | 15.9178 | 348.7709 | 109.375 | 0.8 | 1 | 56.282 | 514.4279 | -8.5 | 7.5759 | 1.061 | 0.44756
2016-04-14 11:00 | 281.67 | 153.9967 | 127.6733 | 335.0926 | 9.3637 | 0.63506 | 67.6038 | 22.3962 | 0.67772 | 7.628 | 332.1273 | 115.4975 | 0.8 | 1 | 56.334 | 503.9588 | -8.4 | 7.3487 | 1.0618 | 0.43878
2016-04-14 12:00 | 281.93 | 162.16 | 119.77 | 321.0751 | 9.3787 | 15.6378 | 68.0975 | 21.9025 | 16.657 | 16.9985 | 307.0481 | 121.62 | 0.8 | 1 | 56.386 | 485.0541 | -8.3 | 6.8579 | 1.0635 | 0.423
2016-04-14 13:00 | 246.6033 | 144.9467 | 101.6567 | 290.0823 | 9.3936 | 30.6406 | 69.4857 | 20.5143 | 32.4702 | 30.7365 | 249.3335 | 108.71 | 0.8 | 1 | 49.3207 | 407.3641 | -8.1 | 4.6301 | 1.0713 | 0.35785
2016-04-14 14:00 | 211.2767 | 127.7333 | 83.5433 | 265.3806 | 9.4085 | 45.6433 | 71.6509 | 18.3491 | 48.002 | 44.9761 | 187.7308 | 95.8 | 0.8 | 1 | 42.2553 | 325.7861 | -8 | 2.1808 | 1.0799 | 0.28848
2016-04-14 15:00 | 175.95 | 110.52 | 65.43 | 243.6234 | 9.4235 | 60.6461 | 74.4208 | 15.5792 | 63.2071 | 59.3149 | 124.3256 | 82.89 | 0.8 | 1 | 35.19 | 242.4056 | -8.1 | -0.52482 | 1.0893 | 0.21653
2016-04-14 16:00 | 133.4467 | 84.69 | 48.7567 | 226.8763 | 9.4384 | 75.6488 | 77.5901 | 12.4099 | 78.1095 | 73.637 | 63.9158 | 63.5175 | 0.8 | 1 | 26.6893 | 154.1227 | -8.2 | -3.3837 | 1.0993 | 0.13894
2016-04-14 17:00 | 90.9433 | 58.86 | 32.0833 | 203.7248 | 9.4533 | 90.6515 | 80.9391 | 9.0609 | 92.7842 | 87.8681 | 7.5787 | 44.145 | 0.8 | 1 | 18.1887 | 69.9123 | -8.7 | -6.5152 | 1.1103 | 0.063652
2016-04-14 18:00 | 48.44 | 33.03 | 15.41 | 153.7301 | 9.4683 | 105.6543 | 84.247 | 5.753 | 107.3314 | 101.9213 | 0 | 24.7725 | 0.8 | 1 | 9.688 | 34.4605 | -9.5 | -8.4231 | 1.117 | 0.031563
2016-04-14 19:00 | 32.4533 | 22.13 | 10.3233 | 0 | 9.4832 | 120.657 | 87.3007 | 2.6993 | 121.8512 | 115.6556 | 0 | 16.5975 | 0.8 | 1 | 6.4907 | 23.0882 | -9.5 | -8.7785 | 1.1182 | 0.021171
2016-04-14 20:00 | 16.4667 | 11.23 | 5.2367 | 0 | 9.4981 | 135.6597 | 89.9035 | 0.096497 | 136.4223 | 128.7954 | 0 | 8.4225 | 0.8 | 1 | 3.2933 | 11.7158 | -10.1 | -9.7339 | 1.1216 | 0.010775
2016-04-14 21:00 | 0.48 | 0.33 | 0.15 | 0 | 9.513 | 150.6625 | 91.8841 | -1.8841 | 151.0872 | 140.7244 | 0 | 0.2475 | 0.8 | 1 | 0.096 | 0.3435 | -9.4 | -9.3893 | 1.1204 | 0.00031557
2016-04-14 22:00 | 0.32 | 0.22 | 0.1 | 0 | 9.5279 | 165.6652 | 93.108 | -3.108 | 165.8458 | 149.9522 | 0 | 0.165 | 0.8 | 1 | 0.064 | 0.229 | -9.6 | -9.5928 | 1.1211 | 0.00021052
2016-04-14 23:00 | 0.16 | 0.11 | 0.05 | 0 | 9.5428 | 180.6679 | 93.4897 | -3.4897 | -179.3401 | 153.4823 | 0 | 0.0825 | 0.8 | 1 | 0.032 | 0.1145 | -9.6 | -9.5964 | 1.1211 | 0.00010526
2016-04-15 | 0 | 0 | 0 | 0 | 9.5577 | -164.3294 | 93.0013 | -3.0013 | -164.5306 | 149.2814 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.8 | -9.8 | 1.1218 | 0
2016-04-15 01:00 | 8.2567 | 6.2367 | 2.02 | 0 | 9.5726 | -149.3266 | 91.6762 | -1.6762 | -149.7844 | 139.7002 | 0 | 4.6775 | 0.8 | 1 | 1.6513 | 6.3288 | -9.4 | -9.2022 | 1.1197 | 0.0058109
2016-04-15 02:00 | 16.5133 | 12.4733 | 4.04 | 0 | 9.5875 | -134.3239 | 89.6052 | 0.39483 | -135.1361 | 127.6159 | 0 | 9.355 | 0.8 | 1 | 3.3027 | 12.6577 | -10 | -9.6044 | 1.1211 | 0.011636
2016-04-15 03:00 | 24.77 | 18.71 | 6.06 | 113.0129 | 9.6024 | -119.3212 | 86.9262 | 3.0738 | -120.581 | 114.4029 | 0 | 14.0325 | 0.8 | 1 | 4.954 | 18.9865 | -9.7 | -9.1067 | 1.1194 | 0.017427
2016-04-15 04:00 | 55.91 | 42.2267 | 13.6833 | 126.9654 | 9.6172 | -104.3185 | 83.8131 | 6.1869 | -106.0719 | 100.6303 | 0 | 31.67 | 0.8 | 1 | 11.182 | 42.852 | -10.2 | -8.8609 | 1.1185 | 0.039303
2016-04-15 05:00 | 87.05 | 65.7433 | 21.3067 | 128.6122 | 9.6321 | -89.3158 | 80.4641 | 9.5359 | -91.5261 | 86.5552 | 7.728 | 49.3075 | 0.8 | 1 | 17.41 | 74.4455 | -9.1 | -6.7736 | 1.1112 | 0.067834
2016-04-15 06:00 | 118.19 | 89.26 | 28.93 | 129.514 | 9.647 | -74.3131 | 77.0927 | 12.9073 | -76.8412 | 72.3106 | 39.3537 | 66.945 | 0.8 | 1 | 23.638 | 129.9367 | -9.2 | -5.1395 | 1.1055 | 0.11779
2016-04-15 07:00 | 159.2033 | 109.45 | 49.7533 | 179.6292 | 9.6618 | -59.3104 | 73.9201 | 16.0799 | -61.9167 | 57.9794 | 95.2437 | 82.0875 | 0.8 | 1 | 31.8407 | 209.1718 | -8.7 | -2.1634 | 1.0951 | 0.18783
2016-04-15 08:00 | 200.2167 | 129.64 | 70.5767 | 218.6101 | 9.6767 | -44.3077 | 71.1651 | 18.8349 | -46.6797 | 43.6338 | 158.2223 | 97.23 | 0.8 | 1 | 40.0433 | 295.4956 | -8.7 | 0.53424 | 1.0856 | 0.26306
2016-04-15 09:00 | 241.23 | 149.83 | 91.4 | 255.4083 | 9.6916 | -29.305 | 69.0313 | 20.9687 | -31.1105 | 29.3907 | 222.5355 | 112.3725 | 0.8 | 1 | 48.246 | 383.154 | -8.6 | 3.3736 | 1.0757 | 0.33797
2016-04-15 10:00 | 241.54 | 158.1567 | 83.3833 | 219.6286 | 9.7064 | -14.3023 | 67.6876 | 22.3124 | -15.2605 | 15.6852 | 211.45 | 118.6175 | 0.8 | 1 | 48.308 | 378.3755 | -8.5 | 3.3242 | 1.0759 | 0.33381
2016-04-15 11:00 | 241.85 | 166.4833 | 75.3667 | 194.8627 | 9.7212 | 0.70039 | 67.2464 | 22.7536 | 0.74859 | 7.2773 | 193.293 | 124.8625 | 0.8 | 1 | 48.37 | 366.5255 | -8.5 | 2.9539 | 1.0772 | 0.32374
2016-04-15 12:00 | 242.16 | 174.81 | 67.35 | 177.8322 | 9.7361 | 15.7031 | 67.7451 | 22.2549 | 16.7517 | 16.8902 | 170.1611 | 131.1075 | 0.8 | 1 | 48.432 | 349.7006 | -8.5 | 2.4281 | 1.079 | 0.30941
2016-04-15 13:00 | 207.7167 | 151 | 56.7167 | 159.271 | 9.7509 | 30.7058 | 69.139 | 20.861 | 32.5854 | 30.6923 | 136.9604 | 113.25 | 0.8 | 1 | 41.5433 | 291.7537 | -8.2 | 0.9173 | 1.0843 | 0.2594
2016-04-15 14:00 | 173.2733 | 127.19 | 46.0833 | 143.8081 | 9.7658 | 45.7084 | 71.3098 | 18.6902 | 48.1329 | 44.9491 | 101.778 | 95.3925 | 0.8 | 1 | 34.6547 | 231.8252 | -8.2 | -0.95546 | 1.0908 | 0.20737
2016-04-15 15:00 | 138.83 | 103.38 | 35.45 | 129.2747 | 9.7806 | 60.7111 | 74.0843 | 15.9157 | 63.3481 | 59.2901 | 66.0195 | 77.535 | 0.8 | 1 | 27.766 | 171.3205 | -8.5 | -3.1462 | 1.0985 | 0.15432
2016-04-15 16:00 | 107.7 | 80.38 | 27.32 | 123.8516 | 9.7954 | 75.7138 | 77.2565 | 12.7435 | 78.2553 | 73.6066 | 34.9548 | 60.285 | 0.8 | 1 | 21.54 | 116.7798 | -8.6 | -4.9506 | 1.1048 | 0.1058
2016-04-15 17:00 | 76.57 | 57.38 | 19.19 | 117.5734 | 9.8102 | 90.7165 | 80.6063 | 9.3937 | 92.9299 | 87.8259 | 4.4602 | 43.035 | 0.8 | 1 | 15.314 | 62.8092 | -9 | -7.0372 | 1.1121 | 0.057279
2016-04-15 18:00 | 45.44 | 34.38 | 11.06 | 104.2978 | 9.825 | 105.7191 | 83.9128 | 6.0872 | 107.4724 | 101.8608 | 0 | 25.785 | 0.8 | 1 | 9.088 | 34.873 | -9.6 | -8.5102 | 1.1173 | 0.03195
2016-04-15 19:00 | 30.5167 | 23.1233 | 7.3933 | 139.5582 | 9.8398 | 120.7218 | 86.9632 | 3.0368 | 121.9833 | 115.5677 | 0 | 17.3425 | 0.8 | 1 | 6.1033 | 23.4458 | -11 | -10.2673 | 1.1234 | 0.021599
2016-04-15 20:00 | 15.5933 | 11.8667 | 3.7267 | 0 | 9.8546 | 135.7245 | 89.5615 | 0.43854 | 136.5415 | 128.666 | 0 | 8.9 | 0.8 | 1 | 3.1187 | 12.0187 | -11.1 | -10.7244 | 1.125 | 0.011088
2016-04-15 21:00 | 0.67 | 0.61 | 0.06 | 0 | 9.8694 | 150.7271 | 91.5369 | -1.5369 | 151.19 | 140.531 | 0 | 0.4575 | 0.8 | 1 | 0.134 | 0.5915 | -9.8 | -9.7815 | 1.1217 | 0.00054408
2016-04-15 22:00 | 0.44667 | 0.40667 | 0.04 | 0 | 9.8842 | 165.7298 | 92.7558 | -2.7558 | 165.9294 | 149.6676 | 0 | 0.305 | 0.8 | 1 | 0.089333 | 0.39433 | -9.8 | -9.7877 | 1.1218 | 0.00036272
2016-04-15 23:00 | 0.22333 | 0.20333 | 0.02 | 0 | 9.899 | 180.7325 | 93.1333 | -3.1333 | -179.2774 | 153.1245 | 0 | 0.1525 | 0.8 | 1 | 0.044667 | 0.19717 | -9.7 | -9.6938 | 1.1214 | 0.00018131
2016-04-16 | 0 | 0 | 0 | 0 | 9.9138 | -164.2649 | 92.6419 | -2.6419 | -164.4889 | 148.9418 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.1 | -10.1 | 1.1228 | 0
2016-04-16 01:00 | 6.9133 | 5.79 | 1.1233 | 0 | 9.9286 | -149.2622 | 91.3153 | -1.3153 | -149.7624 | 139.4182 | 0 | 4.3425 | 0.8 | 1 | 1.3827 | 5.7252 | -10 | -9.8211 | 1.1219 | 0.0052668
2016-04-16 02:00 | 13.8267 | 11.58 | 2.2467 | 0 | 9.9434 | -134.2596 | 89.2437 | 0.75629 | -135.131 | 127.3814 | 0 | 8.685 | 0.8 | 1 | 2.7653 | 11.4503 | -9.9 | -9.5422 | 1.1209 | 0.010524
2016-04-16 03:00 | 20.74 | 17.37 | 3.37 | 56.2439 | 9.9581 | -119.2569 | 86.5649 | 3.4351 | -120.589 | 114.2016 | 0 | 13.0275 | 0.8 | 1 | 4.148 | 17.1755 | -9.4 | -8.8633 | 1.1185 | 0.015753
2016-04-16 04:00 | 41.9233 | 35.0633 | 6.86 | 60.1587 | 9.9729 | -104.2543 | 83.4522 | 6.5478 | -106.0885 | 100.4521 | 0 | 26.2975 | 0.8 | 1 | 8.3847 | 34.6822 | -9 | -7.9162 | 1.1152 | 0.031716
2016-04-16 05:00 | 63.1067 | 52.7567 | 10.35 | 60.2203 | 9.9877 | -89.2516 | 80.1035 | 9.8965 | -91.5462 | 86.3929 | 3.7887 | 39.5675 | 0.8 | 1 | 12.6213 | 55.9776 | -8.6 | -6.8507 | 1.1115 | 0.051019
2016-04-16 06:00 | 84.29 | 70.45 | 13.84 | 60.3041 | 10.0024 | -74.249 | 76.7322 | 13.2678 | -76.8593 | 72.1588 | 18.476 | 52.8375 | 0.8 | 1 | 16.858 | 88.1715 | -8.3 | -5.5446 | 1.1069 | 0.08003
2016-04-16 07:00 | 113.6833 | 93.8533 | 19.83 | 70.0651 | 10.0172 | -59.2464 | 73.5593 | 16.4407 | -61.9271 | 57.8326 | 37.3023 | 70.39 | 0.8 | 1 | 22.7367 | 130.4289 | -7.9 | -3.8241 | 1.1009 | 0.11774
2016-04-16 08:00 | 143.0767 | 117.2567 | 25.82 | 78.5291 | 10.0319 | -44.2437 | 70.8043 | 19.1957 | -46.6766 | 43.485 | 56.9772 | 87.9425 | 0.8 | 1 | 28.6153 | 173.535 | -8.1 | -2.677 | 1.0969 | 0.15608
2016-04-16 09:00 | 172.47 | 140.66 | 31.81 | 87.4576 | 10.0467 | -29.2411 | 68.6712 | 21.3288 | -31.0885 | 29.2258 | 76.3244 | 105.495 | 0.8 | 1 | 34.494 | 216.3134 | -7.8 | -1.0402 | 1.0911 | 0.19354
2016-04-16 10:00 | 176.54 | 144.1567 | 32.3833 | 84.0184 | 10.0614 | -14.2385 | 67.3295 | 22.6705 | -15.2157 | 15.4603 | 80.9783 | 108.1175 | 0.8 | 1 | 35.308 | 224.4038 | -7.6 | -0.58738 | 1.0896 | 0.20049
2016-04-16 11:00 | 180.61 | 147.6533 | 32.9567 | 83.9726 | 10.0761 | 0.76414 | 66.8918 | 23.1082 | 0.81798 | 6.9304 | 83.359 | 110.74 | 0.8 | 1 | 36.122 | 230.221 | -7.6 | -0.40559 | 1.0889 | 0.20557
2016-04-16 12:00 | 184.68 | 151.15 | 33.53 | 87.2332 | 10.0909 | 15.7668 | 67.3953 | 22.6047 | 16.8448 | 16.7884 | 83.5152 | 113.3625 | 0.8 | 1 | 36.936 | 233.8137 | -7.6 | -0.29332 | 1.0885 | 0.2087
2016-04-16 13:00 | 166.99 | 140.88 | 26.11 | 72.1851 | 10.1056 | 30.7694 | 68.7948 | 21.2052 | 32.699 | 30.6511 | 62.1 | 105.66 | 0.8 | 1 | 33.398 | 201.158 | -7.4 | -1.1138 | 1.0914 | 0.18003
2016-04-16 14:00 | 149.3 | 130.61 | 18.69 | 57.3236 | 10.1203 | 45.772 | 70.9712 | 19.0288 | 48.262 | 44.9233 | 40.5881 | 97.9575 | 0.8 | 1 | 29.86 | 168.4056 | -7.3 | -2.0373 | 1.0946 | 0.15116
2016-04-16 15:00 | 131.61 | 120.34 | 11.27 | 40.2751 | 10.135 | 60.7746 | 73.7502 | 16.2498 | 63.4873 | 59.2656 | 20.5829 | 90.255 | 0.8 | 1 | 26.322 | 137.1599 | -7.5 | -3.2138 | 1.0987 | 0.12358
2016-04-16 16:00 | 101.12 | 92.66 | 8.46 | 37.3968 | 10.1497 | 75.7772 | 76.9252 | 13.0748 | 78.3993 | 73.5759 | 10.5738 | 69.495 | 0.8 | 1 | 20.224 | 100.2928 | -7.9 | -4.7659 | 1.1042 | 0.090808
2016-04-16 17:00 | 70.63 | 64.98 | 5.65 | 33.4505 | 10.1644 | 90.7798 | 80.2758 | 9.7242 | 93.0737 | 87.783 | 1.294 | 48.735 | 0.8 | 1 | 14.126 | 64.155 | -8 | -5.9952 | 1.1085 | 0.058314
2016-04-16 18:00 | 40.14 | 37.3 | 2.84 | 25.4022 | 10.1791 | 105.7824 | 83.5808 | 6.4192 | 107.6114 | 101.7991 | 0 | 27.975 | 0.8 | 1 | 8.028 | 36.003 | -8 | -6.8749 | 1.1116 | 0.032816
2016-04-16 19:00 | 27.0767 | 25.1733 | 1.9033 | 32.3601 | 10.1938 | 120.785 | 86.6281 | 3.3719 | 122.1132 | 115.4783 | 0 | 18.88 | 0.8 | 1 | 5.4153 | 24.2953 | -8.1 | -7.3408 | 1.1132 | 0.022177
2016-04-16 20:00 | 14.0133 | 13.0467 | 0.96667 | 0 | 10.2085 | 135.7876 | 89.2218 | 0.77822 | 136.6586 | 128.5349 | 0 | 9.785 | 0.8 | 1 | 2.8027 | 12.5877 | -8.4 | -8.0066 | 1.1155 | 0.011514
2016-04-16 21:00 | 0.95 | 0.92 | 0.03 | 0 | 10.2232 | 150.7902 | 91.1921 | -1.1921 | 151.2908 | 140.3361 | 0 | 0.69 | 0.8 | 1 | 0.19 | 0.88 | -8.4 | -8.3725 | 1.1168 | 0.00080589
2016-04-16 22:00 | 0.63333 | 0.61333 | 0.02 | 0 | 10.2379 | 165.7928 | 92.4061 | -2.4061 | 166.0111 | 149.3831 | 0 | 0.46 | 0.8 | 1 | 0.12667 | 0.58667 | -8.1 | -8.0817 | 1.1158 | 0.00053677
2016-04-16 23:00 | 0.31667 | 0.30667 | 0.01 | 0 | 10.2526 | 180.7954 | 92.7796 | -2.7796 | -179.2164 | 152.7694 | 0 | 0.23 | 0.8 | 1 | 0.063333 | 0.29333 | -8.2 | -8.1908 | 1.1162 | 0.00026848
2016-04-17 | 0 | 0 | 0 | 0 | 10.2672 | -164.202 | 92.2854 | -2.2854 | -164.4488 | 148.605 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.6 | -8.6 | 1.1176 | 0
2016-04-17 01:00 | 7.9633 | 7.1133 | 0.85 | 0 | 10.2819 | -149.1994 | 90.9572 | -0.95722 | -149.7417 | 139.1381 | 0 | 5.335 | 0.8 | 1 | 1.5927 | 6.9277 | -8.8 | -8.5835 | 1.1175 | 0.0063484
2016-04-17 02:00 | 15.9267 | 14.2267 | 1.7 | 0 | 10.2966 | -134.1969 | 88.8852 | 1.1148 | -135.1271 | 127.1487 | 0 | 10.67 | 0.8 | 1 | 3.1853 | 13.8553 | -9.2 | -8.767 | 1.1182 | 0.012704
2016-04-17 03:00 | 23.89 | 21.34 | 2.55 | 38.5437 | 10.3112 | -119.1943 | 86.2066 | 3.7934 | -120.5982 | 114.0023 | 0 | 16.005 | 0.8 | 1 | 4.778 | 20.783 | -9.3 | -8.6505 | 1.1178 | 0.019049
2016-04-17 04:00 | 52.3933 | 44.96 | 7.4333 | 61.8236 | 10.3259 | -104.1917 | 83.0944 | 6.9056 | -106.1062 | 100.2761 | 0 | 33.72 | 0.8 | 1 | 10.4787 | 44.1987 | -9.1 | -7.7188 | 1.1145 | 0.040393
2016-04-17 05:00 | 80.8967 | 68.58 | 12.3167 | 69.1896 | 10.3405 | -89.1891 | 79.7459 | 10.2541 | -91.5674 | 86.2332 | 4.5455 | 51.435 | 0.8 | 1 | 16.1793 | 72.1598 | -8.7 | -6.445 | 1.1101 | 0.065683
2016-04-17 06:00 | 109.4 | 92.2 | 17.2 | 73.0136 | 10.3551 | -74.1866 | 76.3746 | 13.6254 | -76.8787 | 72.0099 | 22.5505 | 69.15 | 0.8 | 1 | 21.88 | 113.5805 | -8.6 | -5.0506 | 1.1052 | 0.10293
2016-04-17 07:00 | 139.65 | 114.54 | 25.11 | 86.8842 | 10.3698 | -59.184 | 73.2016 | 16.7984 | -61.9388 | 57.6894 | 46.4404 | 85.905 | 0.8 | 1 | 27.93 | 160.2754 | -8.5 | -3.4914 | 1.0997 | 0.14453
2016-04-17 08:00 | 169.9 | 136.88 | 33.02 | 98.6596 | 10.3844 | -44.1814 | 70.4465 | 19.5535 | -46.6748 | 43.3405 | 71.7539 | 102.66 | 0.8 | 1 | 33.98 | 208.3939 | -8.5 | -1.9877 | 1.0945 | 0.18702
2016-04-17 09:00 | 200.15 | 159.22 | 40.93 | 110.7657 | 10.399 | -29.1789 | 68.3141 | 21.6859 | -31.068 | 29.0665 | 96.8155 | 119.415 | 0.8 | 1 | 40.03 | 256.2605 | -8.1 | -0.09186 | 1.0878 | 0.22859
2016-04-17 10:00 | 210.0267 | 162.74 | 47.2867 | 120.8927 | 10.4137 | -14.1763 | 66.9742 | 23.0258 | -15.1724 | 15.2432 | 116.6395 | 122.055 | 0.8 | 1 | 42.0053 | 280.6998 | -8.3 | 0.47187 | 1.0858 | 0.24993
2016-04-17 11:00 | 219.9033 | 166.26 | 53.6433 | 134.7445 | 10.4283 | 0.82623 | 66.5398 | 23.4602 | 0.88582 | 6.5874 | 133.8549 | 124.695 | 0.8 | 1 | 43.9807 | 302.5306 | -8.3 | 1.1541 | 1.0835 | 0.26878
2016-04-17 12:00 | 229.78 | 169.78 | 60 | 153.8624 | 10.4429 | 15.8288 | 67.0481 | 22.9519 | 16.9363 | 16.6931 | 147.3782 | 127.335 | 0.8 | 1 | 45.956 | 320.6692 | -8.1 | 1.9209 | 1.0808 | 0.28419
2016-04-17 13:00 | 205.4067 | 155.5233 | 49.8833 | 135.8251 | 10.4575 | 30.8313 | 68.4532 | 21.5468 | 32.8108 | 30.6126 | 116.8951 | 116.6425 | 0.8 | 1 | 41.0813 | 274.619 | -8 | 0.58184 | 1.0855 | 0.24443
2016-04-17 14:00 | 181.0333 | 141.2667 | 39.7667 | 119.9291 | 10.4721 | 45.8339 | 70.635 | 19.365 | 48.3893 | 44.8988 | 84.9523 | 105.95 | 0.8 | 1 | 36.2067 | 227.109 | -8.4 | -1.3028 | 1.0921 | 0.20337
2016-04-17 15:00 | 156.66 | 127.01 | 29.65 | 103.8969 | 10.4867 | 60.8364 | 73.4185 | 16.5815 | 63.6246 | 59.2414 | 53.1352 | 95.2575 | 0.8 | 1 | 31.332 | 179.7247 | -8.1 | -2.4836 | 1.0962 | 0.16155
2016-04-17 16:00 | 122.02 | 97.04 | 24.98 | 107.7602 | 10.5013 | 75.839 | 76.5963 | 13.4037 | 78.5412 | 73.5448 | 30.5248 | 72.78 | 0.8 | 1 | 24.404 | 127.7088 | -8.7 | -4.7091 | 1.104 | 0.11561
2016-04-17 17:00 | 87.38 | 67.07 | 20.31 | 116.3563 | 10.5159 | 90.8415 | 79.9475 | 10.0525 | 93.2153 | 87.7392 | 4.59 | 50.3025 | 0.8 | 1 | 17.476 | 72.3685 | -8.6 | -6.3385 | 1.1097 | 0.065851
2016-04-17 18:00 | 52.74 | 37.1 | 15.64 | 133.0878 | 10.5305 | 105.844 | 83.2512 | 6.7488 | 107.7482 | 101.7362 | 0 | 27.825 | 0.8 | 1 | 10.548 | 38.373 | -9.4 | -8.2008 | 1.1162 | 0.035122
2016-04-17 19:00 | 35.6667 | 25.15 | 10.5167 | 162.7599 | 10.545 | 120.8466 | 86.2953 | 3.7047 | 122.241 | 115.3874 | 0 | 18.8625 | 0.8 | 1 | 7.1333 | 25.9958 | -8.8 | -7.9876 | 1.1155 | 0.023778
2016-04-17 20:00 | 18.5933 | 13.2 | 5.3933 | 0 | 10.5596 | 135.8491 | 88.8846 | 1.1154 | 136.7735 | 128.4022 | 0 | 9.9 | 0.8 | 1 | 3.7187 | 13.6187 | -8.5 | -8.0744 | 1.1158 | 0.01246
2016-04-17 21:00 | 1.52 | 1.25 | 0.27 | 0 | 10.5742 | 150.8516 | 90.8499 | -0.84989 | 151.3894 | 140.1399 | 0 | 0.9375 | 0.8 | 1 | 0.304 | 1.2415 | -9.2 | -9.1612 | 1.1196 | 0.0011397
2016-04-17 22:00 | 1.06 | 0.88 | 0.18 | 0 | 10.5887 | 165.8541 | 92.0592 | -2.0592 | 166.0907 | 149.0988 | 0 | 0.66 | 0.8 | 1 | 0.212 | 0.872 | -9.5 | -9.4727 | 1.1207 | 0.00080131
2016-04-17 23:00 | 0.6 | 0.51 | 0.09 | 0 | 10.6033 | 180.8566 | 92.4286 | -2.4286 | -179.1572 | 152.417 | 0 | 0.3825 | 0.8 | 1 | 0.12 | 0.5025 | -9.7 | -9.6843 | 1.1214 | 0.00046207
2016-04-18 | 0.14 | 0.14 | 0 | 0 | 10.6179 | -164.1408 | 91.9317 | -1.9317 | -164.4103 | 148.271 | 0 | 0.105 | 0.8 | 1 | 0.028 | 0.133 | -9 | -8.9958 | 1.119 | 0.00012204
2016-04-18 01:00 | 12.1967 | 8.0267 | 4.17 | 0 | 10.6324 | -149.1383 | 90.6021 | -0.60212 | -149.7225 | 138.8603 | 0 | 6.02 | 0.8 | 1 | 2.4393 | 8.4593 | -9.3 | -9.0356 | 1.1191 | 0.007763
2016-04-18 02:00 | 24.2533 | 15.9133 | 8.34 | 0 | 10.6469 | -134.1358 | 88.5297 | 1.4703 | -135.1246 | 126.918 | 0 | 11.935 | 0.8 | 1 | 4.8507 | 16.7857 | -9.4 | -8.8754 | 1.1186 | 0.015396
2016-04-18 03:00 | 36.31 | 23.8 | 12.51 | 172.9252 | 10.6615 | -119.1333 | 85.8514 | 4.1486 | -120.6086 | 113.8051 | 0 | 17.85 | 0.8 | 1 | 7.262 | 25.112 | -9.4 | -8.6152 | 1.1177 | 0.023015
2016-04-18 04:00 | 79.9167 | 42.4733 | 37.4433 | 296.2788 | 10.676 | -104.1308 | 82.7396 | 7.2604 | -106.1251 | 100.1024 | 0 | 31.855 | 0.8 | 1 | 15.9833 | 47.8383 | -9.2 | -7.7051 | 1.1145 | 0.043718
2016-04-18 05:00 | 123.5233 | 61.1467 | 62.3767 | 338.8252 | 10.6905 | -89.1283 | 79.3915 | 10.6085 | -91.5899 | 86.0761 | 23.1863 | 45.86 | 0.8 | 1 | 24.7047 | 93.751 | -8.6 | -5.6703 | 1.1073 | 0.085128
2016-04-18 06:00 | 167.13 | 79.82 | 87.31 | 361.4129 | 10.7051 | -74.1258 | 76.0202 | 13.9798 | -76.8992 | 71.864 | 112.4981 | 59.865 | 0.8 | 1 | 33.426 | 205.7891 | -8.7 | -2.2691 | 1.0954 | 0.18485
2016-04-18 07:00 | 209.3333 | 97.2933 | 112.04 | 379.8931 | 10.7196 | -59.1233 | 72.847 | 17.153 | -61.9518 | 57.5497 | 203.8383 | 72.97 | 0.8 | 1 | 41.8667 | 318.675 | -8.6 | 1.3586 | 1.0827 | 0.28294
2016-04-18 08:00 | 251.5367 | 114.7667 | 136.77 | 401.6578 | 10.7341 | -44.1208 | 70.0918 | 19.9082 | -46.6744 | 43.2004 | 292.7941 | 86.075 | 0.8 | 1 | 50.3073 | 429.1764 | -8.3 | 5.1118 | 1.0696 | 0.37642
2016-04-18 09:00 | 293.74 | 132.24 | 161.5 | 430.3739 | 10.7486 | -29.1183 | 67.9599 | 22.0401 | -31.0489 | 28.913 | 376.73 | 99.18 | 0.8 | 1 | 58.748 | 534.658 | -7.9 | 8.8081 | 1.0567 | 0.46327
2016-04-18 10:00 | 308.2833 | 127.19 | 181.0933 | 456.3861 | 10.7631 | -14.1159 | 66.6218 | 23.3782 | -15.1307 | 15.0342 | 440.7645 | 95.3925 | 0.8 | 1 | 61.6567 | 597.8136 | -7.7 | 10.9817 | 1.0491 | 0.51426
2016-04-18 11:00 | 322.8267 | 122.14 | 200.6867 | 497.1265 | 10.7776 | 0.88662 | 66.1907 | 23.8093 | 0.952 | 6.2486 | 494.1731 | 91.605 | 0.8 | 1 | 64.5653 | 650.3434 | -7.4 | 12.9232 | 1.0423 | 0.55582
2016-04-18 12:00 | 337.37 | 117.09 | 220.28 | 556.9836 | 10.7921 | 15.8891 | 66.7036 | 23.2964 | 17.026 | 16.6042 | 533.7582 | 87.8175 | 0.8 | 1 | 67.474 | 689.0497 | -7.5 | 14.0328 | 1.0384 | 0.58671
2016-04-18 13:00 | 296.6667 | 116.3967 | 180.27 | 483.6113 | 10.8066 | 30.8916 | 68.1142 | 21.8858 | 32.9208 | 30.5769 | 416.3638 | 87.2975 | 0.8 | 1 | 59.3333 | 562.9946 | -7.7 | 9.8936 | 1.0529 | 0.48606
2016-04-18 14:00 | 255.9633 | 115.7033 | 140.26 | 416.1121 | 10.8211 | 45.894 | 70.3014 | 19.6986 | 48.5147 | 44.8754 | 294.8751 | 86.7775 | 0.8 | 1 | 51.1927 | 432.8453 | -7.9 | 5.6264 | 1.0678 | 0.379
2016-04-18 15:00 | 215.26 | 115.01 | 100.25 | 344.6422 | 10.8355 | 60.8965 | 73.0893 | 16.9107 | 63.7599 | 59.2174 | 176.3818 | 86.2575 | 0.8 | 1 | 43.052 | 305.6913 | -7.8 | 1.7529 | 1.0814 | 0.27106
2016-04-18 16:00 | 166.37 | 90.8367 | 75.5333 | 318.2352 | 10.85 | 75.899 | 76.2698 | 13.7302 | 78.681 | 73.5133 | 90.313 | 68.1275 | 0.8 | 1 | 33.274 | 191.7145 | -7.2 | -1.2089 | 1.0917 | 0.17163
2016-04-18 17:00 | 117.48 | 66.6633 | 50.8167 | 282.085 | 10.8645 | 90.9014 | 79.6217 | 10.3783 | 93.3547 | 87.6946 | 11.347 | 49.9975 | 0.8 | 1 | 23.496 | 84.8405 | -8.3 | -5.6487 | 1.1073 | 0.077032
2016-04-18 18:00 | 68.59 | 42.49 | 26.1 | 211.8753 | 10.8789 | 105.9039 | 82.924 | 7.076 | 107.8827 | 101.6722 | 0 | 31.8675 | 0.8 | 1 | 13.718 | 45.5855 | -8.9 | -7.4755 | 1.1137 | 0.041629
2016-04-18 19:00 | 46.61 | 28.98 | 17.63 | 250.5437 | 10.8934 | 120.9064 | 85.9649 | 4.0351 | 122.3665 | 115.295 | 0 | 21.735 | 0.8 | 1 | 9.322 | 31.057 | -10.1 | -9.1295 | 1.1195 | 0.028509
2016-04-18 20:00 | 24.63 | 15.47 | 9.16 | 0 | 10.9078 | 135.9088 | 88.5499 | 1.4501 | 136.8862 | 128.268 | 0 | 11.6025 | 0.8 | 1 | 4.926 | 16.5285 | -10.7 | -10.1835 | 1.1231 | 0.015222
2016-04-18 21:00 | 2.65 | 1.96 | 0.69 | 0 | 10.9223 | 150.9113 | 90.5103 | -0.51031 | 151.4858 | 139.9425 | 0 | 1.47 | 0.8 | 1 | 0.53 | 2 | -10.3 | -10.2375 | 1.1233 | 0.0018423
2016-04-18 22:00 | 1.89 | 1.3867 | 0.50333 | 0 | 10.9367 | 165.9137 | 91.7149 | -1.7149 | 166.1684 | 148.8149 | 0 | 1.04 | 0.8 | 1 | 0.378 | 1.418 | -9.5 | -9.4557 | 1.1206 | 0.001303
2016-04-18 23:00 | 1.13 | 0.81333 | 0.31667 | 0 | 10.9512 | 180.9161 | 92.0805 | -2.0805 | -179.0999 | 152.0675 | 0 | 0.61 | 0.8 | 1 | 0.226 | 0.836 | -10.3 | -10.2739 | 1.1235 | 0.00077015
2016-04-19 | 0.37 | 0.24 | 0.13 | 0 | 10.9656 | -164.0814 | 91.581 | -1.581 | -164.3735 | 147.94 | 0 | 0.18 | 0.8 | 1 | 0.074 | 0.254 | -10.2 | -10.1921 | 1.1232 | 0.00023393
2016-04-19 01:00 | 12.1433 | 7.2533 | 4.89 | 0 | 10.98 | -149.079 | 90.2501 | -0.25008 | -149.7049 | 138.5847 | 0 | 5.44 | 0.8 | 1 | 2.4287 | 7.8687 | -9.3 | -9.0541 | 1.1192 | 0.0072214
2016-04-19 02:00 | 23.9167 | 14.2667 | 9.65 | 0 | 10.9944 | -134.0765 | 88.1774 | 1.8226 | -135.1234 | 126.6894 | 0 | 10.7 | 0.8 | 1 | 4.7833 | 15.4833 | -9.4 | -8.9161 | 1.1187 | 0.014203
2016-04-19 03:00 | 35.69 | 21.28 | 14.41 | 183.6373 | 11.0089 | -119.0741 | 85.4994 | 4.5006 | -120.6203 | 113.6101 | 0 | 15.96 | 0.8 | 1 | 7.138 | 23.098 | -9.8 | -9.0782 | 1.1193 | 0.021199
2016-04-19 04:00 | 83.6533 | 35.1333 | 48.52 | 366.2931 | 11.0233 | -104.0717 | 82.3881 | 7.6119 | -106.1452 | 99.9312 | 0 | 26.35 | 0.8 | 1 | 16.7307 | 43.0807 | -8.9 | -7.5537 | 1.1139 | 0.039351
2016-04-19 05:00 | 131.6167 | 48.9867 | 82.63 | 434.625 | 11.0377 | -89.0693 | 79.0403 | 10.9597 | -91.6135 | 85.9218 | 30.9099 | 36.74 | 0.8 | 1 | 26.3233 | 93.9733 | -7.3 | -4.3633 | 1.1028 | 0.084977
2016-04-19 06:00 | 179.58 | 62.84 | 116.74 | 471.6334 | 11.0521 | -74.0668 | 75.669 | 14.331 | -76.921 | 71.7213 | 147.9226 | 47.13 | 0.8 | 1 | 35.916 | 230.9686 | -6.3 | 0.91777 | 1.0843 | 0.20536
2016-04-19 07:00 | 234.3367 | 72.6367 | 161.7 | 537.6021 | 11.0665 | -59.0644 | 72.4955 | 17.5045 | -61.9661 | 57.4137 | 289.5358 | 54.4775 | 0.8 | 1 | 46.8673 | 390.8806 | -5.7 | 6.515 | 1.0647 | 0.34126
2016-04-19 08:00 | 289.0933 | 82.4333 | 206.66 | 596.8068 | 11.0809 | -44.062 | 69.7403 | 20.2597 | -46.6754 | 43.0648 | 436.0165 | 61.825 | 0.8 | 1 | 57.8187 | 555.6602 | -5.9 | 11.4644 | 1.0474 | 0.47723
2016-04-19 09:00 | 343.85 | 92.23 | 251.62 | 660.5464 | 11.0952 | -29.0596 | 67.6089 | 22.3911 | -31.0313 | 28.7653 | 579.0341 | 69.1725 | 0.8 | 1 | 68.77 | 716.9766 | -6 | 16.4055 | 1.0301 | 0.60561
2016-04-19 10:00 | 345.4167 | 91.65 | 253.7667 | 630.6518 | 11.1096 | -14.0572 | 66.2725 | 23.7275 | -15.0906 | 14.8336 | 609.6344 | 68.7375 | 0.8 | 1 | 69.0833 | 747.4552 | -5.7 | 17.658 | 1.0257 | 0.62866
2016-04-19 11:00 | 346.9833 | 91.07 | 255.9133 | 625.3784 | 11.124 | 0.94522 | 65.8446 | 24.1554 | 1.0165 | 5.9141 | 622.0498 | 68.3025 | 0.8 | 1 | 69.3967 | 759.749 | -5.5 | 18.2422 | 1.0237 | 0.63773
2016-04-19 12:00 | 348.55 | 90.49 | 258.06 | 643.6109 | 11.1384 | 15.9476 | 66.362 | 23.638 | 17.114 | 16.5216 | 617.0378 | 67.8675 | 0.8 | 1 | 69.71 | 754.6153 | -5.4 | 18.1817 | 1.0239 | 0.63355
2016-04-19 13:00 | 315.9033 | 85.9567 | 229.9467 | 608.0068 | 11.1527 | 30.95 | 67.7779 | 22.2221 | 33.0289 | 30.5437 | 523.6407 | 64.4675 | 0.8 | 1 | 63.1807 | 651.2889 | -5.5 | 14.8528 | 1.0355 | 0.55302
2016-04-19 14:00 | 283.2567 | 81.4233 | 201.8333 | 589.2846 | 11.1671 | 45.9524 | 69.9704 | 20.0296 | 48.6381 | 44.8529 | 417.7556 | 61.0675 | 0.8 | 1 | 56.6513 | 535.4744 | -5.4 | 11.3336 | 1.0478 | 0.46009
2016-04-19 15:00 | 250.61 | 76.89 | 173.72 | 586.2351 | 11.1814 | 60.9548 | 72.7626 | 17.2374 | 63.8931 | 59.1934 | 300.2351 | 57.6675 | 0.8 | 1 | 50.122 | 408.0246 | -5.5 | 7.2508 | 1.0621 | 0.35537
2016-04-19 16:00 | 191.3367 | 65.1433 | 126.1933 | 519.6557 | 11.1958 | 75.9572 | 75.9458 | 14.0542 | 78.8187 | 73.4813 | 147.7528 | 48.8575 | 0.8 | 1 | 38.2673 | 234.8776 | -5.6 | 1.7399 | 1.0814 | 0.20828
2016-04-19 17:00 | 132.0633 | 53.3967 | 78.6667 | 423.6337 | 11.2101 | 90.9596 | 79.2983 | 10.7017 | 93.4918 | 87.6491 | 17.3769 | 40.0475 | 0.8 | 1 | 26.4127 | 83.8371 | -5.7 | -3.0801 | 1.0983 | 0.075503
2016-04-19 18:00 | 72.79 | 41.65 | 31.14 | 241.7554 | 11.2245 | 105.962 | 82.5993 | 7.4007 | 108.0149 | 101.6069 | 0 | 31.2375 | 0.8 | 1 | 14.558 | 45.7955 | -6 | -4.5689 | 1.1035 | 0.041439
2016-04-19 19:00 | 49.5967 | 28.58 | 21.0167 | 276.2699 | 11.2388 | 120.9643 | 85.6371 | 4.3629 | 122.4897 | 115.2013 | 0 | 21.435 | 0.8 | 1 | 9.9193 | 31.3543 | -6.4 | -5.4202 | 1.1065 | 0.028448
2016-04-19 20:00 | 26.4033 | 15.51 | 10.8933 | 0 | 11.2531 | 135.9667 | 88.2178 | 1.7822 | 136.9965 | 128.1322 | 0 | 11.6325 | 0.8 | 1 | 5.2807 | 16.9132 | -7.8 | -7.2715 | 1.113 | 0.015435
2016-04-19 21:00 | 3.21 | 2.44 | 0.77 | 0 | 11.2675 | 150.9691 | 90.1734 | -0.17345 | 151.5801 | 139.744 | 0 | 1.83 | 0.8 | 1 | 0.642 | 2.472 | -7.3 | -7.2227 | 1.1128 | 0.0022556
2016-04-19 22:00 | 2.4467 | 1.83 | 0.61667 | 0 | 11.2818 | 165.9715 | 91.3735 | -1.3735 | 166.2439 | 148.5316 | 0 | 1.3725 | 0.8 | 1 | 0.48933 | 1.8618 | -7.5 | -7.4418 | 1.1135 | 0.0017001
2016-04-19 23:00 | 1.6833 | 1.22 | 0.46333 | 0 | 11.2961 | 180.9738 | 91.7354 | -1.7354 | -179.0446 | 151.7209 | 0 | 0.915 | 0.8 | 1 | 0.33667 | 1.2517 | -7.1 | -7.0609 | 1.1122 | 0.0011415
2016-04-20 | 0.92 | 0.61 | 0.31 | 0 | 11.3104 | -164.0238 | 91.2334 | -1.2334 | -164.3384 | 147.6122 | 0 | 0.4575 | 0.8 | 1 | 0.184 | 0.6415 | -7 | -6.98 | 1.1119 | 0.00058491
2016-04-20 01:00 | 16.5233 | 8.6433 | 7.88 | 0 | 11.3247 | -149.0214 | 89.9012 | 0.0988 | -149.6888 | 138.3117 | 0 | 6.4825 | 0.8 | 1 | 3.3047 | 9.7872 | -6.4 | -6.0942 | 1.1088 | 0.0088989
2016-04-20 02:00 | 32.1267 | 16.6767 | 15.45 | 0 | 11.339 | -134.0191 | 87.8282 | 2.1718 | -135.1237 | 126.4631 | 0 | 12.5075 | 0.8 | 1 | 6.4253 | 18.9328 | -6.8 | -6.2083 | 1.1092 | 0.017221
2016-04-20 03:00 | 47.73 | 24.71 | 23.02 | 272.3095 | 11.3533 | -119.0167 | 85.1506 | 4.8494 | -120.6333 | 113.4175 | 0 | 18.5325 | 0.8 | 1 | 9.546 | 28.0785 | -7.1 | -6.2225 | 1.1093 | 0.02554
2016-04-20 04:00 | 95.0333 | 37.1367 | 57.8967 | 418.0769 | 11.3676 | -104.0144 | 82.0399 | 7.9601 | -106.1666 | 99.7625 | 0 | 27.8525 | 0.8 | 1 | 19.0067 | 46.8592 | -6.5 | -5.0357 | 1.1051 | 0.042464
2016-04-20 05:00 | 142.3367 | 49.5633 | 92.7733 | 473.1532 | 11.3818 | -89.012 | 78.6925 | 11.3075 | -91.6384 | 85.7702 | 34.898 | 37.1725 | 0.8 | 1 | 28.4673 | 100.5378 | -6.8 | -3.6582 | 1.1003 | 0.09071
2016-04-20 06:00 | 189.64 | 61.99 | 127.65 | 503.7486 | 11.3961 | -74.0097 | 75.3212 | 14.6788 | -76.9442 | 71.5818 | 159.1593 | 46.4925 | 0.8 | 1 | 37.928 | 243.5798 | -5.9 | 1.7119 | 1.0815 | 0.21602
2016-04-20 07:00 | 233.4433 | 77.1933 | 156.25 | 509.6737 | 11.4104 | -59.0074 | 72.1474 | 17.8526 | -61.9818 | 57.2815 | 275.485 | 57.895 | 0.8 | 1 | 46.6887 | 380.0687 | -5.5 | 6.3771 | 1.0652 | 0.33197
2016-04-20 08:00 | 277.2467 | 92.3967 | 184.85 | 525.1833 | 11.4246 | -44.005 | 69.392 | 20.608 | -46.678 | 42.9336 | 384.5093 | 69.2975 | 0.8 | 1 | 55.4493 | 509.2562 | -5.5 | 10.4143 | 1.0511 | 0.43891
2016-04-20 09:00 | 321.05 | 107.6 | 213.45 | 552.2164 | 11.4389 | -29.0027 | 67.261 | 22.739 | -31.0154 | 28.6234 | 484.7286 | 80.7 | 0.8 | 1 | 64.21 | 629.6386 | -5.4 | 14.2762 | 1.0375 | 0.53568
2016-04-20 10:00 | 324.5 | 107.7867 | 216.7133 | 531.2738 | 11.4531 | -14.0004 | 65.9262 | 24.0738 | -15.0522 | 14.6415 | 514.0215 | 80.84 | 0.8 | 1 | 64.9 | 659.7615 | -5.4 | 15.2175 | 1.0342 | 0.55953
2016-04-20 11:00 | 327.95 | 107.9733 | 219.9767 | 530.4849 | 11.4674 | 1.002 | 65.5014 | 24.4986 | 1.0791 | 5.5843 | 527.9672 | 80.98 | 0.8 | 1 | 65.59 | 674.5372 | -5.2 | 15.8793 | 1.0319 | 0.57078
2016-04-20 12:00 | 331.4 | 108.16 | 223.24 | 549.3583 | 11.4816 | 16.0043 | 66.0233 | 23.9767 | 17.2 | 16.4452 | 526.8847 | 81.12 | 0.8 | 1 | 66.28 | 674.2847 | -5 | 16.0714 | 1.0313 | 0.57019
2016-04-20 13:00 | 306.8967 | 100.34 | 206.5567 | 538.4988 | 11.4959 | 31.0066 | 67.4445 | 22.5555 | 33.1351 | 30.513 | 463.9242 | 75.255 | 0.8 | 1 | 61.3793 | 600.5586 | -5 | 13.7675 | 1.0393 | 0.51182
2016-04-20 14:00 | 282.3933 | 92.52 | 189.8733 | 545.7966 | 11.5101 | 46.0089 | 69.6421 | 20.3579 | 48.7594 | 44.8313 | 387.0709 | 69.39 | 0.8 | 1 | 56.4787 | 512.9395 | -5 | 11.0294 | 1.0489 | 0.44118
2016-04-20 15:00 | 257.89 | 84.7 | 173.19 | 573.9929 | 11.5243 | 61.0112 | 72.4386 | 17.5614 | 64.0241 | 59.1696 | 294.1707 | 63.525 | 0.8 | 1 | 51.578 | 409.2737 | -5.2 | 7.5898 | 1.0609 | 0.35605
2016-04-20 16:00 | 198.9567 | 70.6533 | 128.3033 | 516.7716 | 11.5385 | 76.0136 | 75.6243 | 14.3757 | 78.954 | 73.4488 | 147.2136 | 52.99 | 0.8 | 1 | 39.7913 | 239.9949 | -5.8 | 1.6998 | 1.0816 | 0.21284
2016-04-20 17:00 | 140.0233 | 56.6067 | 83.4167 | 436.2939 | 11.5528 | 91.0159 | 78.9775 | 11.0225 | 93.6266 | 87.6027 | 18.2492 | 42.455 | 0.8 | 1 | 28.0047 | 88.7089 | -6 | -3.2278 | 1.0988 | 0.079928
2016-04-20 18:00 | 81.09 | 42.56 | 38.53 | 286.7207 | 11.567 | 106.0182 | 82.2771 | 7.7229 | 108.1447 | 101.5404 | 0 | 31.92 | 0.8 | 1 | 16.218 | 48.138 | -6.3 | -4.7957 | 1.1043 | 0.04359
2016-04-20 19:00 | 55.54 | 29.4267 | 26.1133 | 319.5032 | 11.5812 | 121.0205 | 85.3119 | 4.6881 | 122.6104 | 115.106 | 0 | 22.07 | 0.8 | 1 | 11.108 | 33.178 | -7.4 | -6.3632 | 1.1098 | 0.030192
2016-04-20 20:00 | 29.99 | 16.2933 | 13.6967 | 0 | 11.5954 | 136.0228 | 87.8884 | 2.1116 | 137.1045 | 127.995 | 0 | 12.22 | 0.8 | 1 | 5.998 | 18.218 | -8 | -7.4307 | 1.1135 | 0.016634
2016-04-20 21:00 | 4.44 | 3.16 | 1.28 | 0 | 11.6096 | 151.0251 | 89.8394 | 0.16061 | 151.672 | 139.5445 | 0 | 2.37 | 0.8 | 1 | 0.888 | 3.258 | -8.9 | -8.7982 | 1.1183 | 0.0029876
2016-04-20 22:00 | 3.38 | 2.4033 | 0.97667 | 0 | 11.6237 | 166.0274 | 91.035 | -1.035 | 166.3173 | 148.2489 | 0 | 1.8025 | 0.8 | 1 | 0.676 | 2.4785 | -8.2 | -8.1225 | 1.1159 | 0.002268
2016-04-20 23:00 | 2.32 | 1.6467 | 0.67333 | 0 | 11.6379 | 181.0296 | 91.3934 | -1.3934 | -178.9912 | 151.3773 | 0 | 1.235 | 0.8 | 1 | 0.464 | 1.699 | -10.1 | -10.0469 | 1.1227 | 0.0015641
2016-04-21 | 1.26 | 0.89 | 0.37 | 0 | 11.6521 | -163.9681 | 90.889 | -0.88895 | -164.3051 | 147.2876 | 0 | 0.6675 | 0.8 | 1 | 0.252 | 0.9195 | -9.4 | -9.3713 | 1.1203 | 0.00084469
2016-04-21 01:00 | 12.0067 | 8.5433 | 3.4633 | 0 | 11.6663 | -148.9658 | 89.5556 | 0.44442 | -149.6743 | 138.0412 | 0 | 6.4075 | 0.8 | 1 | 2.4013 | 8.8088 | -10 | -9.7247 | 1.1215 | 0.0081011
2016-04-21 02:00 | 22.7533 | 16.1967 | 6.5567 | 0 | 11.6804 | -133.9635 | 87.4825 | 2.5175 | -135.1254 | 126.2391 | 0 | 12.1475 | 0.8 | 1 | 4.5507 | 16.6982 | -9.5 | -8.9782 | 1.1189 | 0.015321
2016-04-21 03:00 | 33.5 | 23.85 | 9.65 | 106.5822 | 11.6946 | -118.9612 | 84.8053 | 5.1947 | -120.6476 | 113.2272 | 0 | 17.8875 | 0.8 | 1 | 6.7 | 24.5875 | -9.5 | -8.7316 | 1.1181 | 0.022542
2016-04-21 04:00 | 52.2967 | 41.0833 | 11.2133 | 77.6331 | 11.7088 | -103.959 | 81.6951 | 8.3049 | -106.1893 | 99.5964 | 0 | 30.8125 | 0.8 | 1 | 10.4593 | 41.2718 | -9.2 | -7.9103 | 1.1152 | 0.037741
2016-04-21 05:00 | 71.0933 | 58.3167 | 12.7767 | 63.2617 | 11.7229 | -88.9567 | 78.3481 | 11.6519 | -91.6647 | 85.6216 | 4.8296 | 43.7375 | 0.8 | 1 | 14.2187 | 62.7857 | -8.6 | -6.6379 | 1.1107 | 0.057185
2016-04-21 06:00 | 89.89 | 75.55 | 14.34 | 55.3219 | 11.737 | -73.9544 | 74.9768 | 15.0232 | -76.9687 | 71.4456 | 17.6037 | 56.6625 | 0.8 | 1 | 17.978 | 92.2442 | -6.6 | -3.7174 | 1.1005 | 0.083243
2016-04-21 07:00 | 93.6667 | 82.4767 | 11.19 | 35.8322 | 11.7512 | -58.9522 | 71.8027 | 18.1973 | -61.999 | 57.153 | 19.4353 | 61.8575 | 0.8 | 1 | 18.7333 | 100.0261 | -6.6 | -3.4742 | 1.0997 | 0.090196
2016-04-21 08:00 | 97.4433 | 89.4033 | 8.04 | 22.4832 | 11.7653 | -43.9499 | 69.0471 | 20.9529 | -46.6821 | 42.8071 | 16.4947 | 67.0525 | 0.8 | 1 | 19.4887 | 103.0359 | -6.1 | -2.8801 | 1.0976 | 0.092734
2016-04-21 09:00 | 101.22 | 96.33 | 4.89 | 12.4722 | 11.7794 | -28.9477 | 66.9165 | 23.0835 | -31.0012 | 28.4875 | 10.9621 | 72.2475 | 0.8 | 1 | 20.244 | 103.4536 | -6.1 | -2.8671 | 1.0975 | 0.093106
2016-04-21 10:00 | 117.02 | 109.2667 | 7.7533 | 18.7563 | 11.7936 | -13.9454 | 65.5832 | 24.4168 | -15.0156 | 14.4581 | 18.1623 | 81.95 | 0.8 | 1 | 23.404 | 123.5163 | -6.9 | -3.0401 | 1.0981 | 0.11122
2016-04-21 11:00 | 132.82 | 122.2033 | 10.6167 | 25.2739 | 11.8077 | 1.0568 | 65.1614 | 24.8386 | 1.1399 | 5.2595 | 25.1675 | 91.6525 | 0.8 | 1 | 26.564 | 143.384 | -6.4 | -1.9193 | 1.0942 | 0.12865
2016-04-21 12:00 | 148.62 | 135.14 | 13.48 | 32.7414 | 11.8218 | 16.0591 | 65.6876 | 24.3124 | 17.2841 | 16.3747 | 31.4133 | 101.355 | 0.8 | 1 | 29.724 | 162.4923 | -6 | -0.92211 | 1.0907 | 0.14533
2016-04-21 13:00 | 117.65 | 108.49 | 9.16 | 23.5536 | 11.8359 | 31.0613 | 67.1139 | 22.8861 | 33.2391 | 30.4846 | 20.2977 | 81.3675 | 0.8 | 1 | 23.53 | 125.1952 | -5.5 | -1.5877 | 1.0931 | 0.11221
2016-04-21 14:00 | 86.68 | 81.84 | 4.84 | 13.7032 | 11.85 | 46.0635 | 69.3166 | 20.6834 | 48.8785 | 44.8106 | 9.7216 | 61.38 | 0.8 | 1 | 17.336 | 88.4376 | -5.4 | -2.6363 | 1.0967 | 0.079533
2016-04-21 15:00 | 55.71 | 55.19 | 0.52 | 1.6934 | 11.8641 | 61.0658 | 72.1172 | 17.8828 | 64.1528 | 59.1457 | 0.86848 | 41.3925 | 0.8 | 1 | 11.142 | 53.403 | -5 | -3.3312 | 1.0992 | 0.048133
2016-04-21 16:00 | 46.8467 | 45.83 | 1.0167 | 4.0079 | 11.8782 | 76.068 | 75.3055 | 14.6945 | 79.087 | 73.4158 | 1.144 | 34.3725 | 0.8 | 1 | 9.3693 | 44.8858 | -4.3 | -2.8973 | 1.0976 | 0.0404
2016-04-21 17:00 | 37.9833 | 36.47 | 1.5133 | 7.6959 | 11.8923 | 91.0702 | 78.6594 | 11.3406 | 93.759 | 87.5554 | 0.32826 | 27.3525 | 0.8 | 1 | 7.5967 | 35.2774 | -4.6 | -3.4976 | 1.0997 | 0.031813
2016-04-21 18:00 | 29.12 | 27.11 | 2.01 | 14.3668 | 11.9063 | 106.0725 | 81.9576 | 8.0424 | 108.272 | 101.4727 | 0 | 20.3325 | 0.8 | 1 | 5.824 | 26.1565 | -4.3 | -3.4826 | 1.0997 | 0.023586
2016-04-21 19:00 | 20.1 | 18.7567 | 1.3433 | 15.3805 | 11.9204 | 121.0747 | 84.9894 | 5.0106 | 122.7287 | 115.0094 | 0 | 14.0675 | 0.8 | 1 | 4.02 | 18.0875 | -4.3 | -3.7348 | 1.1006 | 0.016323
2016-04-21 20:00 | 11.08 | 10.4033 | 0.67667 | 0 | 11.9345 | 136.0769 | 87.5617 | 2.4383 | 137.21 | 127.8564 | 0 | 7.8025 | 0.8 | 1 | 2.216 | 10.0185 | -3.7 | -3.3869 | 1.0994 | 0.0090314
2016-04-21 21:00 | 2.06 | 2.05 | 0.01 | 0 | 11.9485 | 151.0791 | 89.5082 | 0.49179 | 151.7616 | 139.3442 | 0 | 1.5375 | 0.8 | 1 | 0.412 | 1.9495 | -3.7 | -3.6391 | 1.1002 | 0.0017588
2016-04-21 22:00 | 1.9533 | 1.8967 | 0.056667 | 0 | 11.9626 | 166.0813 | 90.6995 | -0.69954 | 166.3884 | 147.9671 | 0 | 1.4225 | 0.8 | 1 | 0.39067 | 1.8132 | -3.3 | -3.2433 | 1.0989 | 0.0016338
2016-04-21 23:00 | 1.8467 | 1.7433 | 0.10333 | 0 | 11.9766 | 181.0835 | 91.0544 | -1.0544 | -178.9399 | 151.0369 | 0 | 1.3075 | 0.8 | 1 | 0.36933 | 1.6768 | -2.4 | -2.3476 | 1.0957 | 0.0015066
2016-04-22 | 1.74 | 1.59 | 0.15 | 0 | 11.9907 | -163.9143 | 90.5478 | -0.54775 | -164.2737 | 146.9663 | 0 | 1.1925 | 0.8 | 1 | 0.348 | 1.5405 | -2 | -1.9519 | 1.0943 | 0.0013824
2016-04-22 01:00 | 15.5267 | 13.5133 | 2.0133 | 0 | 12.0047 | -148.9121 | 89.2133 | 0.78668 | -149.6615 | 137.7735 | 0 | 10.135 | 0.8 | 1 | 3.1053 | 13.2403 | -1.7 | -1.2862 | 1.092 | 0.011856
2016-04-22 02:00 | 29.3133 | 25.4367 | 3.8767 | 0 | 12.0188 | -133.9099 | 87.1401 | 2.8599 | -135.1286 | 126.0176 | 0 | 19.0775 | 0.8 | 1 | 5.8627 | 24.9402 | -1.6 | -0.82062 | 1.0904 | 0.022299
2016-04-22 03:00 | 43.1 | 37.36 | 5.74 | 59.4937 | 12.0328 | -118.9077 | 84.4634 | 5.5366 | -120.6634 | 113.0395 | 0 | 28.02 | 0.8 | 1 | 8.62 | 36.64 | -0.7 | 0.445 | 1.0859 | 0.032627
2016-04-22 04:00 | 72.3667 | 57.7533 | 14.6133 | 97.2078 | 12.0468 | -103.9055 | 81.3539 | 8.6461 | -106.2134 | 99.433 | 0 | 43.315 | 0.8 | 1 | 14.4733 | 57.7883 | -0.5 | 1.3059 | 1.0829 | 0.051316
2016-04-22 05:00 | 101.6333 | 78.1467 | 23.4867 | 113.0318 | 12.0608 | -88.9033 | 78.0072 | 11.9928 | -91.6923 | 85.476 | 8.9156 | 58.61 | 0.8 | 1 | 20.3267 | 87.8523 | -0.5 | 2.2454 | 1.0796 | 0.077776
2016-04-22 06:00 | 130.9 | 98.54 | 32.36 | 122.1355 | 12.0748 | -73.9011 | 74.6359 | 15.3641 | -76.9947 | 71.3127 | 39.1325 | 73.905 | 0.8 | 1 | 26.18 | 139.2175 | -0.1 | 4.2505 | 1.0726 | 0.12245
2016-04-22 07:00 | 185.39 | 123.3667 | 62.0233 | 195.0784 | 12.0888 | -58.899 | 71.4616 | 18.5384 | -62.0177 | 57.0284 | 106.1663 | 92.525 | 0.8 | 1 | 37.078 | 235.7693 | -0.2 | 7.1678 | 1.0624 | 0.2054
2016-04-22 08:00 | 239.88 | 148.1933 | 91.6867 | 252.4694 | 12.1028 | -43.8968 | 68.7056 | 21.2944 | -46.6879 | 42.6851 | 185.5879 | 111.145 | 0.8 | 1 | 47.976 | 344.7089 | -0.2 | 10.5722 | 1.0505 | 0.29693
2016-04-22 09:00 | 294.37 | 173.02 | 121.35 | 305.2502 | 12.1168 | -28.8946 | 66.5754 | 23.4246 | -30.9887 | 28.3575 | 268.6205 | 129.765 | 0.8 | 1 | 58.874 | 457.2595 | 0.1 | 14.3894 | 1.0371 | 0.38888
2016-04-22 10:00 | 304.7967 | 174.52 | 130.2767 | 311.0985 | 12.1308 | -13.8925 | 65.2435 | 24.7565 | -14.9808 | 14.2836 | 301.4813 | 130.89 | 0.8 | 1 | 60.9593 | 493.3307 | 0 | 15.4166 | 1.0335 | 0.4181
2016-04-22 11:00 | 315.2233 | 176.02 | 139.2033 | 327.2351 | 12.1448 | 1.1097 | 64.8245 | 25.1755 | 1.1988 | 4.94 | 326.0196 | 132.015 | 0.8 | 1 | 63.0447 | 521.0792 | -0.5 | 15.7837 | 1.0323 | 0.44107
2016-04-22 12:00 | 325.65 | 177.52 | 148.13 | 355.2319 | 12.1588 | 16.1119 | 65.355 | 24.645 | 17.3662 | 16.3102 | 340.9357 | 133.14 | 0.8 | 1 | 65.13 | 539.2057 | 0 | 16.8502 | 1.0285 | 0.45476
2016-04-22 13:00 | 280.63 | 153.5967 | 127.0333 | 322.2874 | 12.1727 | 31.114 | 66.7863 | 23.2137 | 33.341 | 30.4584 | 277.8109 | 115.1975 | 0.8 | 1 | 56.126 | 449.1344 | 0.1 | 14.1355 | 1.038 | 0.38229
2016-04-22 14:00 | 235.61 | 129.6733 | 105.9367 | 295.5282 | 12.1867 | 46.1162 | 68.994 | 21.006 | 48.9954 | 44.7906 | 209.7325 | 97.255 | 0.8 | 1 | 47.122 | 354.1095 | -0.2 | 10.8659 | 1.0495 | 0.30473
2016-04-22 15:00 | 190.59 | 105.75 | 84.84 | 271.6121 | 12.2007 | 61.1183 | 71.7987 | 18.2013 | 64.2792 | 59.1217 | 139.3957 | 79.3125 | 0.8 | 1 | 38.118 | 256.8262 | 0.1 | 8.1258 | 1.0591 | 0.22304
2016-04-22 16:00 | 152.7367 | 87.8433 | 64.8933 | 250.5568 | 12.2146 | 76.1205 | 74.9895 | 15.0105 | 79.2175 | 73.3822 | 71.6559 | 65.8825 | 0.8 | 1 | 30.5473 | 168.0857 | -0.2 | 5.0527 | 1.0698 | 0.14745
2016-04-22 17:00 | 114.8833 | 69.9367 | 44.9467 | 222.4672 | 12.2286 | 91.1226 | 78.3439 | 11.6561 | 93.8888 | 87.5071 | 9.6764 | 52.4525 | 0.8 | 1 | 22.9767 | 85.1055 | -0.4 | 2.2595 | 1.0796 | 0.075341
2016-04-22 18:00 | 77.03 | 52.03 | 25 | 171.965 | 12.2425 | 106.1248 | 81.6408 | 8.3592 | 108.3968 | 101.4037 | 0 | 39.0225 | 0.8 | 1 | 15.406 | 54.4285 | -0.2 | 1.5009 | 1.0822 | 0.048302
2016-04-22 19:00 | 53.41 | 36.3767 | 17.0333 | 183.3559 | 12.2564 | 121.1269 | 84.6697 | 5.3303 | 122.8444 | 114.9115 | 0 | 27.2825 | 0.8 | 1 | 10.682 | 37.9645 | -0.5 | 0.68639 | 1.0851 | 0.03378
2016-04-22 20:00 | 29.79 | 20.7233 | 9.0667 | 0 | 12.2704 | 136.129 | 87.238 | 2.762 | 137.313 | 127.7165 | 0 | 15.5425 | 0.8 | 1 | 5.958 | 21.5005 | -0.9 | -0.22811 | 1.0883 | 0.019187
2016-04-22 21:00 | 6.17 | 5.07 | 1.1 | 0 | 12.2843 | 151.1312 | 89.18 | 0.81999 | 151.8488 | 139.1431 | 0 | 3.8025 | 0.8 | 1 | 1.234 | 5.0365 | -0.6 | -0.44261 | 1.089 | 0.0044977
2016-04-22 22:00 | 5.1467 | 4.0633 | 1.0833 | 0 | 12.2982 | 166.1333 | 90.3672 | -0.36718 | 166.4573 | 147.6862 | 0 | 3.0475 | 0.8 | 1 | 1.0293 | 4.0768 | -0.7 | -0.5726 | 1.0895 | 0.0036422
2016-04-22 23:00 | 4.1233 | 3.0567 | 1.0667 | 0 | 12.3121 | 181.1354 | 90.7187 | -0.71874 | -178.8906 | 150.6997 | 0 | 2.2925 | 0.8 | 1 | 0.82467 | 3.1172 | -0.8 | -0.70259 | 1.09 | 0.002786
2016-04-23 | 3.1 | 2.05 | 1.05 | 0 | 12.326 | -163.8625 | 90.2099 | -0.2099 | -164.2442 | 146.6484 | 0 | 1.5375 | 0.8 | 1 | 0.62 | 2.1575 | -0.6 | -0.53258 | 1.0894 | 0.0019272
2016-04-23 01:00 | 16.5567 | 11.8333 | 4.7233 | 0 | 12.3399 | -148.8604 | 88.8745 | 1.1255 | -149.6503 | 137.5086 | 0 | 8.875 | 0.8 | 1 | 3.3113 | 12.1863 | -1 | -0.61918 | 1.0897 | 0.010889
2016-04-23 02:00 | 30.0133 | 21.6167 | 8.3967 | 150.4818 | 12.3538 | -133.8583 | 86.8013 | 3.1987 | -135.1333 | 125.7988 | 0 | 16.2125 | 0.8 | 1 | 6.0027 | 22.2152 | -1 | -0.30578 | 1.0886 | 0.01983
2016-04-23 03:00 | 43.47 | 31.4 | 12.07 | 117.9225 | 12.3677 | -118.8561 | 84.1252 | 5.8748 | -120.6805 | 112.8544 | 0 | 23.55 | 0.8 | 1 | 8.694 | 32.244 | -1.1 | -0.092375 | 1.0878 | 0.028762
2016-04-23 04:00 | 76.7167 | 48.2667 | 28.45 | 182.1923 | 12.3816 | -103.854 | 81.0163 | 8.9837 | -106.2388 | 99.2724 | 0 | 36.2 | 0.8 | 1 | 15.3433 | 51.5433 | -1.1 | 0.51073 | 1.0857 | 0.045888
2016-04-23 05:00 | 109.9633 | 65.1333 | 44.83 | 209.9358 | 12.3955 | -88.8519 | 77.67 | 12.33 | -91.7213 | 85.3334 | 17.0799 | 48.85 | 0.8 | 1 | 21.9927 | 87.9226 | -1 | 1.7476 | 1.0814 | 0.077964
2016-04-23 06:00 | 143.21 | 82 | 61.21 | 226.1825 | 12.4093 | -73.8498 | 74.2987 | 15.7013 | -77.022 | 71.1832 | 72.9535 | 61.5 | 0.8 | 1 | 28.642 | 163.0955 | -1.1 | 3.9967 | 1.0735 | 0.14357
2016-04-23 07:00 | 176.8567 | 111.6633 | 65.1933 | 201.512 | 12.4232 | -58.8478 | 71.124 | 18.876 | -62.0379 | 56.9076 | 110.0237 | 83.7475 | 0.8 | 1 | 35.3713 | 229.1425 | -1 | 6.1607 | 1.0659 | 0.20029
2016-04-23 08:00 | 210.5033 | 141.3267 | 69.1767 | 187.6498 | 12.4371 | -43.8457 | 68.3678 | 21.6322 | -46.6952 | 42.5678 | 138.1998 | 105.995 | 0.8 | 1 | 42.1007 | 286.2955 | -1.6 | 7.3467 | 1.0618 | 0.24927
2016-04-23 09:00 | 244.15 | 170.99 | 73.16 | 181.564 | 12.4509 | -28.8436 | 66.2377 | 23.7623 | -30.978 | 28.2336 | 159.9626 | 128.2425 | 0.8 | 1 | 48.83 | 337.0351 | -2 | 8.5323 | 1.0576 | 0.2923
2016-04-23 10:00 | 235.6767 | 180.7633 | 54.9133 | 129.4861 | 12.4648 | -13.8415 | 64.9071 | 25.0929 | -14.948 | 14.1182 | 125.5749 | 135.5725 | 0.8 | 1 | 47.1353 | 308.2827 | -2.2 | 7.4338 | 1.0615 | 0.26833
2016-04-23 11:00 | 227.2033 | 190.5367 | 36.6667 | 85.1418 | 12.4786 | 1.1606 | 64.4909 | 25.5091 | 1.2556 | 4.6262 | 84.8644 | 142.9025 | 0.8 | 1 | 45.4407 | 273.2076 | -2.2 | 6.3377 | 1.0653 | 0.23866
2016-04-23 12:00 | 218.73 | 200.31 | 18.42 | 43.6271 | 12.4925 | 16.1627 | 65.0255 | 24.9745 | 17.4461 | 16.2514 | 41.8839 | 150.2325 | 0.8 | 1 | 43.746 | 235.8624 | -2.6 | 4.7707 | 1.0708 | 0.2071
2016-04-23 13:00 | 184.5067 | 168.4933 | 16.0133 | 40.0974 | 12.5063 | 31.1647 | 66.4617 | 23.5383 | 33.4407 | 30.4342 | 34.5724 | 126.37 | 0.8 | 1 | 36.9013 | 197.8437 | -2.7 | 3.4826 | 1.0753 | 0.17445
2016-04-23 14:00 | 150.2833 | 136.6767 | 13.6067 | 37.415 | 12.5201 | 46.1668 | 68.6743 | 21.3257 | 49.11 | 44.7712 | 26.5619 | 102.5075 | 0.8 | 1 | 30.0567 | 159.126 | -3 | 1.9727 | 1.0806 | 0.141
2016-04-23 15:00 | 116.06 | 104.86 | 11.2 | 35.266 | 12.5339 | 61.1689 | 71.483 | 18.517 | 64.4032 | 59.0976 | 18.1118 | 78.645 | 0.8 | 1 | 23.212 | 119.9688 | -2.9 | 0.84902 | 1.0845 | 0.10669
2016-04-23 16:00 | 95.0833 | 85.9733 | 9.11 | 34.4719 | 12.5477 | 76.1709 | 74.6762 | 15.3238 | 79.3456 | 73.3479 | 9.8782 | 64.48 | 0.8 | 1 | 19.0167 | 93.3749 | -2.6 | 0.31797 | 1.0864 | 0.083182
2016-04-23 17:00 | 74.1067 | 67.0867 | 7.02 | 33.851 | 12.5615 | 91.173 | 78.0312 | 11.9688 | 94.0161 | 87.4578 | 1.5015 | 50.315 | 0.8 | 1 | 14.8213 | 66.6378 | -2.6 | -0.51757 | 1.0893 | 0.059523
2016-04-23 18:00 | 53.13 | 48.2 | 4.93 | 32.6926 | 12.5753 | 106.175 | 81.3268 | 8.6732 | 108.519 | 101.3336 | 0 | 36.15 | 0.8 | 1 | 10.626 | 46.776 | -2.8 | -1.3382 | 1.0922 | 0.041892
2016-04-23 19:00 | 37.0433 | 33.7467 | 3.2967 | 33.5016 | 12.5891 | 121.1771 | 84.3528 | 5.6472 | 122.9575 | 114.8121 | 0 | 25.31 | 0.8 | 1 | 7.4087 | 32.7187 | -3.1 | -2.0775 | 1.0948 | 0.029372
2016-04-23 20:00 | 20.9567 | 19.2933 | 1.6633 | 30.9286 | 12.6029 | 136.1791 | 86.9172 | 3.0828 | 137.4135 | 127.5754 | 0 | 14.47 | 0.8 | 1 | 4.1913 | 18.6613 | -3.4 | -2.8168 | 1.0974 | 0.016792
2016-04-23 21:00 | 4.87 | 4.84 | 0.03 | 0 | 12.6167 | 151.1812 | 88.8549 | 1.1451 | 151.9335 | 138.9414 | 0 | 3.63 | 0.8 | 1 | 0.974 | 4.604 | -3.3 | -3.1561 | 1.0985 | 0.0041473
2016-04-23 22:00 | 4.0633 | 3.9267 | 0.13667 | 0 | 12.6305 | 166.1832 | 90.038 | -0.037997 | 166.524 | 147.4064 | 0 | 2.945 | 0.8 | 1 | 0.81267 | 3.7577 | -3.1 | -2.9826 | 1.0979 | 0.0033831
2016-04-23 23:00 | 3.2567 | 3.0133 | 0.24333 | 0 | 12.6443 | 181.1852 | 90.3864 | -0.38637 | -178.8435 | 150.3659 | 0 | 2.26 | 0.8 | 1 | 0.65133 | 2.9113 | -2.9 | -2.809 | 1.0973 | 0.0026197
2016-04-24 | 2.45 | 2.1 | 0.35 | 0 | 12.658 | -163.8127 | 89.8755 | 0.12451 | -164.2165 | 146.3341 | 0 | 1.575 | 0.8 | 1 | 0.49 | 2.065 | -3 | -2.9355 | 1.0978 | 0.0018589
2016-04-24 01:00 | 13.33 | 10.67 | 2.66 | 0 | 12.6718 | -148.8107 | 88.5392 | 1.4608 | -149.6409 | 137.2466 | 0 | 8.0025 | 0.8 | 1 | 2.666 | 10.6685 | -3 | -2.6666 | 1.0968 | 0.0095953
2016-04-24 02:00 | 24.21 | 19.24 | 4.97 | 80.6314 | 12.6856 | -133.8087 | 86.4661 | 3.5339 | -135.1397 | 125.5827 | 0 | 14.43 | 0.8 | 1 | 4.842 | 19.272 | -3 | -2.3977 | 1.0959 | 0.017318
2016-04-24 03:00 | 35.09 | 27.81 | 7.28 | 67.3062 | 12.6993 | -118.8066 | 83.7906 | 6.2094 | -120.6991 | 112.6721 | 0 | 20.8575 | 0.8 | 1 | 7.018 | 27.8755 | -3 | -2.1289 | 1.095 | 0.025028
2016-04-24 04:00 | 63.23 | 45.47 | 17.76 | 109.6926 | 12.713 | -103.8046 | 80.6824 | 9.3176 | -106.2656 | 99.1147 | 0 | 34.1025 | 0.8 | 1 | 12.646 | 46.7485 | -3.1 | -1.6391 | 1.0932 | 0.041908
2016-04-24 05:00 | 91.37 | 63.13 | 28.24 | 128.8182 | 12.7268 | -88.8026 | 77.3366 | 12.6634 | -91.7517 | 85.1939 | 10.7929 | 47.3475 | 0.8 | 1 | 18.274 | 76.4144 | -3.2 | -0.81205 | 1.0903 | 0.068321
2016-04-24 06:00 | 119.51 | 80.79 | 38.72 | 140.1777 | 12.7405 | -73.8006 | 73.9652 | 16.0348 | -77.0509 | 71.0572 | 45.5051 | 60.5925 | 0.8 | 1 | 23.902 | 129.9996 | -3.1 | 0.96249 | 1.0841 | 0.11557
2016-04-24 07:00 | 130.3133 | 102.89 | 27.4233 | 83.3463 | 12.7542 | -58.7986 | 70.7902 | 19.2098 | -62.0597 | 56.7908 | 45.6486 | 77.1675 | 0.8 | 1 | 26.0627 | 148.8788 | -2.8 | 1.8525 | 1.081 | 0.13197
2016-04-24 08:00 | 141.1167 | 124.99 | 16.1267 | 43.1121 | 12.768 | -43.7966 | 68.0335 | 21.9665 | -46.7043 | 42.4552 | 31.8083 | 93.7425 | 0.8 | 1 | 28.2233 | 153.7742 | -2.8 | 2.0054 | 1.0805 | 0.13624
2016-04-24 09:00 | 151.92 | 147.09 | 4.83 | 11.8303 | 12.7817 | -28.7946 | 65.9036 | 24.0964 | -30.9691 | 28.1157 | 10.4343 | 110.3175 | 0.8 | 1 | 30.384 | 151.1358 | -2.8 | 1.923 | 1.0808 | 0.13394
2016-04-24 10:00 | 168.4667 | 162.7633 | 5.7033 | 13.2839 | 12.7954 | -13.7926 | 64.5743 | 25.4257 | -14.9171 | 13.962 | 12.8915 | 122.0725 | 0.8 | 1 | 33.6933 | 168.6573 | -2.6 | 2.6705 | 1.0782 | 0.14911
2016-04-24 11:00 | 185.0133 | 178.4367 | 6.5767 | 15.0893 | 12.8091 | 1.2094 | 64.1607 | 25.8393 | 1.3103 | 4.3187 | 15.0465 | 133.8275 | 0.8 | 1 | 37.0027 | 185.8767 | -2.6 | 3.2086 | 1.0763 | 0.16404
2016-04-24 12:00 | 201.56 | 194.11 | 7.45 | 17.4322 | 12.8228 | 16.2114 | 64.6993 | 25.3007 | 17.5238 | 16.1981 | 16.7402 | 145.5825 | 0.8 | 1 | 40.312 | 202.6347 | -2.6 | 3.7323 | 1.0744 | 0.17853
2016-04-24 13:00 | 168.7667 | 163.4767 | 5.29 | 13.0779 | 12.8365 | 31.2134 | 66.1403 | 23.8597 | 33.5381 | 30.4121 | 11.2785 | 122.6075 | 0.8 | 1 | 33.7533 | 167.6393 | -2.4 | 2.8387 | 1.0776 | 0.14813
2016-04-24 14:00 | 135.9733 | 132.8433 | 3.13 | 8.4867 | 12.8501 | 46.2153 | 68.3577 | 21.6423 | 49.2221 | 44.7523 | 6.0269 | 99.6325 | 0.8 | 1 | 27.1947 | 132.8541 | -2.6 | 1.5517 | 1.0821 | 0.11788
2016-04-24 15:00 | 103.18 | 102.21 | 0.97 | 3.0053 | 12.8638 | 61.2173 | 71.1702 | 18.8298 | 64.5246 | 59.0733 | 1.5446 | 76.6575 | 0.8 | 1 | 20.636 | 98.8381 | -3 | 0.08869 | 1.0872 | 0.088114
2016-04-24 16:00 | 85.2867 | 83.7833 | 1.5033 | 5.5783 | 12.8775 | 76.2193 | 74.3658 | 15.6342 | 79.471 | 73.3129 | 1.6018 | 62.8375 | 0.8 | 1 | 17.0573 | 81.4966 | -3.5 | -0.95323 | 1.0908 | 0.072898
2016-04-24 17:00 | 67.3933 | 65.3567 | 2.0367 | 9.5768 | 12.8911 | 91.2213 | 77.7213 | 12.2787 | 94.1407 | 87.4075 | 0.43318 | 49.0175 | 0.8 | 1 | 13.4787 | 62.9293 | -3.7 | -1.7335 | 1.0936 | 0.05643
2016-04-24 18:00 | 49.5 | 46.93 | 2.57 | 16.457 | 12.9048 | 106.2232 | 81.0156 | 8.9844 | 108.6384 | 101.2622 | 0 | 35.1975 | 0.8 | 1 | 9.9 | 45.0975 | -4.3 | -2.8907 | 1.0976 | 0.04059
2016-04-24 19:00 | 34.9233 | 33.1533 | 1.77 | 17.043 | 12.9185 | 121.2252 | 84.0388 | 5.9612 | 123.068 | 114.7115 | 0 | 24.865 | 0.8 | 1 | 6.9847 | 31.8497 | -4.4 | -3.4047 | 1.0994 | 0.028713
2016-04-24 20:00 | 20.3467 | 19.3767 | 0.97 | 16.3526 | 12.9321 | 136.2271 | 86.5994 | 3.4006 | 137.5114 | 127.433 | 0 | 14.5325 | 0.8 | 1 | 4.0693 | 18.6018 | -4.7 | -4.1187 | 1.1019 | 0.016808
2016-04-24 21:00 | 5.77 | 5.6 | 0.17 | 0 | 12.9457 | 151.2291 | 88.5329 | 1.4671 | 152.0158 | 138.7391 | 0 | 4.2 | 0.8 | 1 | 1.154 | 5.354 | -4.8 | -4.6327 | 1.1037 | 0.0048456
2016-04-24 22:00 | 5.0733 | 4.95 | 0.12333 | 0 | 12.9594 | 166.2311 | 89.7121 | 0.2879 | 166.5882 | 147.1279 | 0 | 3.7125 | 0.8 | 1 | 1.0147 | 4.7272 | -5.2 | -5.0523 | 1.1052 | 0.004284
2016-04-24 23:00 | 4.3767 | 4.3 | 0.076667 | 0 | 12.973 | 181.233 | 90.0574 | -0.057409 | -178.7985 | 150.0356 | 0 | 3.225 | 0.8 | 1 | 0.87533 | 4.1003 | -5.3 | -5.1719 | 1.1056 | 0.0037173
2016-04-25 | 3.68 | 3.65 | 0.03 | 0 | 12.9866 | -163.7651 | 89.5446 | 0.45538 | -164.1908 | 146.0235 | 0 | 2.7375 | 0.8 | 1 | 0.736 | 3.4735 | -5.6 | -5.4915 | 1.1067 | 0.0031522
2016-04-25 01:00 | 15.98 | 15.6967 | 0.28333 | 0 | 13.0002 | -148.7631 | 88.2076 | 1.7924 | -149.6332 | 136.9878 | 0 | 11.7725 | 0.8 | 1 | 3.196 | 14.9685 | -5.9 | -5.4322 | 1.1065 | 0.013582
2016-04-25 02:00 | 28.28 | 27.7433 | 0.53667 | 7.961 | 13.0139 | -133.7612 | 86.1347 | 3.8653 | -135.1476 | 125.3694 | 0 | 20.8075 | 0.8 | 1 | 5.656 | 26.4635 | -6.1 | -5.273 | 1.106 | 0.023999
2016-04-25 03:00 | 40.58 | 39.79 | 0.79 | 6.9359 | 13.0275 | -118.7592 | 83.4598 | 6.5402 | -120.7193 | 112.4926 | 0 | 29.8425 | 0.8 | 1 | 8.116 | 37.9585 | -6.4 | -5.2138 | 1.1057 | 0.034417
2016-04-25 04:00 | 68.1533 | 66.2567 | 1.8967 | 11.3174 | 13.0411 | -103.7573 | 80.3523 | 9.6477 | -106.2939 | 98.96 | 0 | 49.6925 | 0.8 | 1 | 13.6307 | 63.3232 | -6.5 | -4.5212 | 1.1033 | 0.05729
2016-04-25 05:00 | 95.7267 | 92.7233 | 3.0033 | 13.358 | 13.0547 | -88.7554 | 77.0069 | 12.9931 | -91.7835 | 85.0576 | 1.1508 | 69.5425 | 0.8 | 1 | 19.1453 | 89.8387 | -6.5 | -3.6925 | 1.1004 | 0.081066
2016-04-25 06:00 | 123.3 | 119.19 | 4.11 | 14.5876 | 13.0682 | -73.7535 | 73.6356 | 16.3644 | -77.0812 | 70.9347 | 4.765 | 89.3925 | 0.8 | 1 | 24.66 | 118.8175 | -6.7 | -2.987 | 1.098 | 0.10697
2016-04-25 07:00 | 150.5067 | 146.9067 | 3.6 | 10.7635 | 13.0818 | -58.7516 | 70.4601 | 19.5399 | -62.0831 | 56.6779 | 5.9129 | 110.18 | 0.8 | 1 | 30.1013 | 146.1942 | -6.6 | -2.0314 | 1.0946 | 0.13122
2016-04-25 08:00 | 177.7133 | 174.6233 | 3.09 | 8.1443 | 13.0954 | -43.7496 | 67.7031 | 22.2969 | -46.7152 | 42.3472 | 6.0193 | 130.9675 | 0.8 | 1 | 35.5427 | 172.5294 | -6.7 | -1.3085 | 1.0921 | 0.1545
2016-04-25 09:00 | 204.92 | 202.34 | 2.58 | 6.239 | 13.109 | -28.7477 | 65.5732 | 24.4268 | -30.9621 | 28.0038 | 5.5085 | 151.755 | 0.8 | 1 | 40.984 | 198.2475 | -6.4 | -0.20477 | 1.0882 | 0.1769
2016-04-25 10:00 | 208.35 | 205.7433 | 2.6067 | 5.9989 | 13.1225 | -13.7458 | 64.245 | 25.755 | -14.8882 | 13.8151 | 5.8254 | 154.3075 | 0.8 | 1 | 41.67 | 201.8029 | -6.5 | -0.19366 | 1.0882 | 0.18007
2016-04-25 11:00 | 211.78 | 209.1467 | 2.6333 | 5.9716 | 13.1361 | 1.2561 | 63.834 | 26.166 | 1.3629 | 4.018 | 5.957 | 156.86 | 0.8 | 1 | 42.356 | 205.173 | -6.6 | -0.18835 | 1.0882 | 0.18307
2016-04-25 12:00 | 215.21 | 212.55 | 2.66 | 6.1509 | 13.1496 | 16.258 | 64.3764 | 25.6236 | 17.5992 | 16.1502 | 5.9082 | 159.4125 | 0.8 | 1 | 43.042 | 208.3627 | -6.5 | 0.011333 | 1.0875 | 0.1858
2016-04-25 13:00 | 188.3133 | 179.7433 | 8.57 | 20.9243 | 13.1632 | 31.2599 | 65.8221 | 24.1779 | 33.6331 | 30.3917 | 18.0491 | 134.8075 | 0.8 | 1 | 37.6627 | 190.5192 | -6.4 | -0.44627 | 1.0891 | 0.17014
2016-04-25 14:00 | 161.4167 | 146.9367 | 14.48 | 38.7277 | 13.1767 | 46.2618 | 68.0441 | 21.9559 | 49.3318 | 44.7339 | 27.5115 | 110.2025 | 0.8 | 1 | 32.2833 | 169.9973 | -6.3 | -0.98758 | 1.091 | 0.15208
2016-04-25 15:00 | 134.52 | 114.13 | 20.39 | 62.1892 | 13.1902 | 61.2637 | 70.8604 | 19.1396 | 64.6434 | 59.0487 | 31.9845 | 85.5975 | 0.8 | 1 | 26.904 | 144.486 | -6.1 | -1.5848 | 1.093 | 0.1295
2016-04-25 16:00 | 113.7067 | 92.2067 | 21.5 | 78.2792 | 13.2038 | 76.2655 | 74.0584 | 15.9416 | 79.5938 | 73.2773 | 22.5241 | 69.155 | 0.8 | 1 | 22.7413 | 114.4204 | -6 | -2.4244 | 1.096 | 0.10283
2016-04-25 17:00 | 92.8933 | 70.2833 | 22.61 | 103.7641 | 13.2173 | 91.2674 | 77.4144 | 12.5856 | 94.2626 | 87.3562 | 4.7863 | 52.7125 | 0.8 | 1 | 18.5787 | 76.0774 | -6.1 | -3.7226 | 1.1005 | 0.068655
2016-04-25 18:00 | 72.08 | 48.36 | 23.72 | 146.8953 | 13.2308 | 106.2693 | 80.7074 | 9.2926 | 108.7552 | 101.1896 | 0 | 36.27 | 0.8 | 1 | 14.416 | 50.686 | -6.2 | -4.6161 | 1.1037 | 0.045871
2016-04-25 19:00 | 50.5633 | 34.6633 | 15.9 | 145.5361 | 13.2443 | 121.2712 | 83.7278 | 6.2722 | 123.1757 | 114.6096 | 0 | 25.9975 | 0.8 | 1 | 10.1127 | 36.1102 | -6.1 | -4.9716 | 1.1049 | 0.032716
2016-04-25 20:00 | 29.0467 | 20.9667 | 8.08 | 124.6921 | 13.2578 | 136.273 | 86.2847 | 3.7153 | 137.6066 | 127.2896 | 0 | 15.725 | 0.8 | 1 | 5.8093 | 21.5343 | -6.3 | -5.6271 | 1.1072 | 0.019551
2016-04-25 21:00 | 7.53 | 7.27 | 0.26 | 0 | 13.2713 | 151.2749 | 88.2141 | 1.7859 | 152.0954 | 138.5364 | 0 | 5.4525 | 0.8 | 1 | 1.506 | 6.9585 | -6.9 | -6.6825 | 1.1109 | 0.0063387
2016-04-25 22:00 | 6.0933 | 5.8233 | 0.27 | 0 | 13.2848 | 166.2768 | 89.3896 | 0.61044 | 166.6501 | 146.8508 | 0 | 4.3675 | 0.8 | 1 | 1.2187 | 5.5862 | -5.9 | -5.7254 | 1.1075 | 0.0050733
2016-04-25 23:00 | 4.6567 | 4.3767 | 0.28 | 0 | 13.2982 | 181.2786 | 89.732 | 0.26804 | -178.7557 | 149.7087 | 0 | 3.2825 | 0.8 | 1 | 0.93133 | 4.2138 | -5.1 | -4.9683 | 1.1049 | 0.0038178
2016-04-26 | 3.22 | 2.93 | 0.29 | 0 | 13.3117 | -163.7195 | 89.2174 | 0.78262 | -164.1671 | 145.7167 | 0 | 2.1975 | 0.8 | 1 | 0.644 | 2.8415 | -5 | -4.9112 | 1.1047 | 0.002574
2016-04-26 01:00 | 10.5533 | 9.9233 | 0.63 | 0 | 13.3252 | -148.7177 | 87.8797 | 2.1203 | -149.6274 | 136.7322 | 0 | 7.4425 | 0.8 | 1 | 2.1107 | 9.5532 | -4.6 | -4.3015 | 1.1026 | 0.008637
2016-04-26 02:00 | 17.8867 | 16.9167 | 0.97 | 13.2666 | 13.3387 | -133.7158 | 85.807 | 4.193 | -135.1571 | 125.159 | 0 | 12.6875 | 0.8 | 1 | 3.5773 | 16.2648 | -4.4 | -3.8917 | 1.1011 | 0.014686
2016-04-26 03:00 | 25.22 | 23.91 | 1.31 | 10.9562 | 13.3521 | -118.714 | 83.1329 | 6.8671 | -120.7409 | 112.316 | 0 | 17.9325 | 0.8 | 1 | 5.044 | 22.9765 | -4.1 | -3.382 | 1.0993 | 0.020712
2016-04-26 04:00 | 40.5167 | 39.28 | 1.2367 | 7.1402 | 13.3656 | -103.7122 | 80.0262 | 9.9738 | -106.3236 | 98.8083 | 0 | 29.46 | 0.8 | 1 | 8.1033 | 37.5633 | -3.8 | -2.6261 | 1.0967 | 0.03378
2016-04-26 05:00 | 55.8133 | 54.65 | 1.1633 | 5.0499 | 13.379 | -88.7103 | 76.6812 | 13.3188 | -91.8168 | 84.9246 | 0.44675 | 40.9875 | 0.8 | 1 | 11.1627 | 52.5969 | -3.3 | -1.6563 | 1.0933 | 0.047153
2016-04-26 06:00 | 71.11 | 70.02 | 1.09 | 3.7953 | 13.3924 | -73.7085 | 73.3099 | 16.6901 | -77.1131 | 70.8157 | 1.2472 | 52.515 | 0.8 | 1 | 14.222 | 67.9842 | -3.1 | -0.97549 | 1.0909 | 0.060815
2016-04-26 07:00 | 79.9867 | 78.5633 | 1.4233 | 4.1885 | 13.4059 | -58.7067 | 70.134 | 19.866 | -62.1082 | 56.5691 | 2.3076 | 58.9225 | 0.8 | 1 | 15.9973 | 77.2274 | -3 | -0.58664 | 1.0896 | 0.068998
2016-04-26 08:00 | 88.8633 | 87.1067 | 1.7567 | 4.5666 | 13.4193 | -43.7048 | 67.3765 | 22.6235 | -46.7278 | 42.2439 | 3.3806 | 65.33 | 0.8 | 1 | 17.7727 | 86.4833 | -3.2 | -0.4974 | 1.0892 | 0.077245
2016-04-26 09:00 | 97.74 | 95.65 | 2.09 | 4.9915 | 13.4327 | -28.703 | 65.2466 | 24.7534 | -30.957 | 27.8979 | 4.4114 | 71.7375 | 0.8 | 1 | 19.548 | 95.6969 | -3.3 | -0.30947 | 1.0886 | 0.085423
2016-04-26 10:00 | 104 | 100.54 | 3.46 | 7.8702 | 13.4461 | -13.7012 | 63.9194 | 26.0806 | -14.8614 | 13.6776 | 7.647 | 75.405 | 0.8 | 1 | 20.8 | 103.852 | -2.8 | 0.44537 | 1.0859 | 0.092477
2016-04-26 11:00 | 110.26 | 105.43 | 4.83 | 10.8289 | 13.4595 | 1.3006 | 63.5108 | 26.4892 | 1.4133 | 3.7249 | 10.806 | 79.0725 | 0.8 | 1 | 22.052 | 111.9305 | -2.8 | 0.69783 | 1.0851 | 0.09959
2016-04-26 12:00 | 116.52 | 110.32 | 6.2 | 14.1721 | 13.4729 | 16.3024 | 64.0569 | 25.9431 | 17.6724 | 16.1074 | 13.6158 | 82.74 | 0.8 | 1 | 23.304 | 119.6598 | -2.9 | 0.83937 | 1.0846 | 0.10642
2016-04-26 13:00 | 115.0433 | 110.79 | 4.2533 | 10.2594 | 13.4863 | 31.3042 | 65.5072 | 24.4928 | 33.7257 | 30.373 | 8.8513 | 83.0925 | 0.8 | 1 | 23.0087 | 114.9525 | -2.9 | 0.69227 | 1.0851 | 0.10228
2016-04-26 14:00 | 113.5667 | 111.26 | 2.3067 | 6.0876 | 13.4997 | 46.306 | 67.7337 | 22.2663 | 49.4389 | 44.7158 | 4.3259 | 83.445 | 0.8 | 1 | 22.7133 | 110.4842 | -3.6 | -0.14737 | 1.088 | 0.098571
2016-04-26 15:00 | 112.09 | 111.73 | 0.36 | 1.0813 | 13.5131 | 61.3078 | 70.5537 | 19.4463 | 64.7596 | 59.0238 | 0.55654 | 83.7975 | 0.8 | 1 | 22.418 | 106.772 | -3.8 | -0.46337 | 1.0891 | 0.095356
2016-04-26 16:00 | 92.8667 | 92.11 | 0.75667 | 2.7047 | 13.5265 | 76.3096 | 73.7539 | 16.2461 | 79.7138 | 73.2409 | 0.77989 | 69.0825 | 0.8 | 1 | 18.5733 | 88.4357 | -3.7 | -0.93638 | 1.0908 | 0.0791
2016-04-26 17:00 | 73.6433 | 72.49 | 1.1533 | 5.1702 | 13.5398 | 91.3114 | 77.1105 | 12.8895 | 94.3817 | 87.3039 | 0.2432 | 54.3675 | 0.8 | 1 | 14.7287 | 69.3394 | -3.7 | -1.5331 | 1.0929 | 0.062138
2016-04-26 18:00 | 54.42 | 52.87 | 1.55 | 9.2965 | 13.5532 | 106.3132 | 80.4023 | 9.5977 | 108.8691 | 101.1159 | 0 | 39.6525 | 0.8 | 1 | 10.884 | 50.5365 | -4 | -2.4207 | 1.096 | 0.045417
2016-04-26 19:00 | 39.12 | 38.0767 | 1.0433 | 9.1049 | 13.5665 | 121.315 | 83.42 | 6.58 | 123.2806 | 114.5065 | 0 | 28.5575 | 0.8 | 1 | 7.824 | 36.3815 | -4.2 | -3.0631 | 1.0982 | 0.032763
2016-04-26 20:00 | 23.82 | 23.2833 | 0.53667 | 7.6422 | 13.5799 | 136.3167 | 85.9731 | 4.0269 | 137.6991 | 127.1452 | 0 | 17.4625 | 0.8 | 1 | 4.764 | 22.2265 | -4.1 | -3.4054 | 1.0994 | 0.020038
2016-04-26 21:00 | 8.52 | 8.49 | 0.03 | 0 | 13.5932 | 151.3185 | 87.8986 | 2.1014 | 152.1726 | 138.3335 | 0 | 6.3675 | 0.8 | 1 | 1.704 | 8.0715 | -4.2 | -3.9478 | 1.1013 | 0.0072892
2016-04-26 22:00 | 7.4 | 7.1967 | 0.20333 | 0 | 13.6066 | 166.3203 | 89.0705 | 0.92951 | 166.7096 | 146.5751 | 0 | 5.3975 | 0.8 | 1 | 1.48 | 6.8775 | -3.8 | -3.5851 | 1.1 | 0.0062038
2016-04-26 23:00 | 6.28 | 5.9033 | 0.37667 | 0 | 13.6199 | 181.322 | 89.4101 | 0.5899 | -178.7151 | 149.3856 | 0 | 4.4275 | 0.8 | 1 | 1.256 | 5.6835 | -3.5 | -3.3224 | 1.0991 | 0.0051225
2016-04-27 | 5.16 | 4.61 | 0.55 | 0 | 13.6332 | -163.6762 | 88.8939 | 1.1061 | -164.1454 | 145.4137 | 0 | 3.4575 | 0.8 | 1 | 1.032 | 4.4895 | -3.2 | -3.0597 | 1.0982 | 0.0040429
2016-04-27 01:00 | 15.8467 | 13.12 | 2.7267 | 0 | 13.6465 | -148.6744 | 87.5557 | 2.4443 | -149.6233 | 136.4799 | 0 | 9.84 | 0.8 | 1 | 3.1693 | 13.0093 | -2.7 | -2.2935 | 1.0955 | 0.011687
2016-04-27 02:00 | 26.5333 | 21.63 | 4.9033 | 62.2648 | 13.6598 | -133.6727 | 85.4833 | 4.5167 | -135.1682 | 124.9517 | 0 | 16.2225 | 0.8 | 1 | 5.3067 | 21.5292 | -2.5 | -1.8272 | 1.0939 | 0.019312
2016-04-27 03:00 | 37.22 | 30.14 | 7.08 | 56.5671 | 13.6731 | -118.6709 | 82.8099 | 7.1901 | -120.764 | 112.1425 | 0 | 22.605 | 0.8 | 1 | 7.444 | 30.049 | -2.8 | -1.861 | 1.094 | 0.026957
2016-04-27 04:00 | 57.6867 | 47.9867 | 9.7 | 54.2709 | 13.6864 | -103.6692 | 79.704 | 10.296 | -106.3548 | 98.6597 | 0 | 35.99 | 0.8 | 1 | 11.5373 | 47.5273 | -2.4 | -0.91477 | 1.0907 | 0.042507
2016-04-27 05:00 | 78.1533 | 65.8333 | 12.32 | 52.2415 | 13.6997 | -88.6674 | 76.3596 | 13.6404 | -91.8515 | 84.7949 | 4.7395 | 49.375 | 0.8 | 1 | 15.6307 | 69.7451 | -2.4 | -0.22047 | 1.0883 | 0.062239
2016-04-27 06:00 | 98.62 | 83.68 | 14.94 | 51.0649 | 13.713 | -73.6657 | 72.9882 | 17.0118 | -77.1465 | 70.7003 | 16.8774 | 62.76 | 0.8 | 1 | 19.724 | 99.3614 | -1.9 | 1.205 | 1.0833 | 0.088262
2016-04-27 07:00 | 129.1867 | 93.07 | 36.1167 | 104.6545 | 13.7263 | -58.664 | 69.8119 | 20.1881 | -62.1349 | 56.4642 | 57.8172 | 69.8025 | 0.8 | 1 | 25.8373 | 153.457 | -2.1 | 2.6955 | 1.0781 | 0.13566
2016-04-27 08:00 | 159.7533 | 102.46 | 57.2933 | 146.9561 | 13.7396 | -43.6622 | 67.0538 | 22.9462 | -46.7422 | 42.1454 | 108.9598 | 76.845 | 0.8 | 1 | 31.9507 | 217.7555 | -1.5 | 5.3049 | 1.0689 | 0.19087
2016-04-27 09:00 | 190.32 | 111.85 | 78.47 | 185.148 | 13.7528 | -28.6605 | 64.9238 | 25.0762 | -30.9539 | 27.7981 | 163.7814 | 83.8875 | 0.8 | 1 | 38.064 | 285.7329 | -1.9 | 7.0292 | 1.0629 | 0.24904
2016-04-27 10:00 | 185.1667 | 106.06 | 79.1067 | 177.8981 | 13.7661 | -13.6588 | 63.5975 | 26.4025 | -14.8368 | 13.5496 | 172.9468 | 79.545 | 0.8 | 1 | 37.0333 | 289.5251 | -2 | 7.0477 | 1.0628 | 0.25233
2016-04-27 11:00 | 180.0133 | 100.27 | 79.7433 | 176.8087 | 13.7793 | 1.3429 | 63.1912 | 26.8088 | 1.4614 | 3.4402 | 176.4901 | 75.2025 | 0.8 | 1 | 36.0027 | 287.6952 | -1.8 | 7.1905 | 1.0623 | 0.25062
2016-04-27 12:00 | 174.86 | 94.48 | 80.38 | 181.6784 | 13.7926 | 16.3446 | 63.741 | 26.259 | 17.7431 | 16.0697 | 174.5795 | 70.86 | 0.8 | 1 | 34.972 | 280.4115 | -1.5 | 7.2629 | 1.0621 | 0.24421
2016-04-27 13:00 | 169.8233 | 106.2 | 63.6233 | 151.6569 | 13.8058 | 31.3463 | 65.1956 | 24.8044 | 33.8157 | 30.3559 | 130.8653 | 79.65 | 0.8 | 1 | 33.9647 | 244.4799 | -1.8 | 5.84 | 1.0671 | 0.21392
2016-04-27 14:00 | 164.7867 | 117.92 | 46.8667 | 122.0909 | 13.8191 | 46.3481 | 67.4266 | 22.5734 | 49.5433 | 44.6981 | 86.785 | 88.44 | 0.8 | 1 | 32.9573 | 208.1823 | -1.4 | 5.1057 | 1.0696 | 0.1826
2016-04-27 15:00 | 159.75 | 129.64 | 30.11 | 89.1057 | 13.8323 | 61.3498 | 70.2502 | 19.7498 | 64.8731 | 58.9985 | 45.8949 | 97.23 | 0.8 | 1 | 31.95 | 175.0749 | -0.5 | 4.9711 | 1.0701 | 0.15363
2016-04-27 16:00 | 118.4567 | 96.1 | 22.3567 | 78.4973 | 13.8455 | 76.3515 | 73.4526 | 16.5474 | 79.831 | 73.2037 | 22.6834 | 72.075 | 0.8 | 1 | 23.6913 | 118.4497 | -1.3 | 2.4016 | 1.0791 | 0.10481
2016-04-27 17:00 | 77.1633 | 62.56 | 14.6033 | 63.9971 | 13.8587 | 91.3532 | 76.8096 | 13.1904 | 94.498 | 87.2505 | 3.0699 | 46.92 | 0.8 | 1 | 15.4327 | 65.4225 | -1.4 | 0.64445 | 1.0852 | 0.05822
2016-04-27 18:00 | 35.87 | 29.02 | 6.85 | 39.8428 | 13.8719 | 106.3548 | 80.1002 | 9.8998 | 108.9802 | 101.041 | 0 | 21.765 | 0.8 | 1 | 7.174 | 28.939 | -1.3 | -0.39566 | 1.0889 | 0.025839
2016-04-27 19:00 | 25.7567 | 21.07 | 4.6867 | 39.0972 | 13.8851 | 121.3565 | 83.1153 | 6.8847 | 123.3828 | 114.4023 | 0 | 15.8025 | 0.8 | 1 | 5.1513 | 20.9538 | -2.1 | -1.4452 | 1.0926 | 0.018772
2016-04-27 20:00 | 15.6433 | 13.12 | 2.5233 | 33.3821 | 13.8983 | 136.3582 | 85.6649 | 4.3351 | 137.7889 | 126.9998 | 0 | 9.84 | 0.8 | 1 | 3.1287 | 12.9687 | -2.5 | -2.0947 | 1.0948 | 0.011643
2016-04-27 21:00 | 5.53 | 5.17 | 0.36 | 0 | 13.9115 | 151.3599 | 87.5866 | 2.4134 | 152.247 | 138.1304 | 0 | 3.8775 | 0.8 | 1 | 1.106 | 4.9835 | -1.7 | -1.5443 | 1.0929 | 0.0044661
2016-04-27 22:00 | 5.4767 | 5.19 | 0.28667 | 0 | 13.9247 | 166.3616 | 88.755 | 1.245 | 166.7666 | 146.3012 | 0 | 3.8925 | 0.8 | 1 | 1.0953 | 4.9878 | -2.5 | -2.3441 | 1.0957 | 0.0044815
2016-04-27 23:00 | 5.4233 | 5.21 | 0.21333 | 0 | 13.9379 | 181.3632 | 89.0919 | 0.90807 | -178.6767 | 149.0662 | 0 | 3.9075 | 0.8 | 1 | 1.0847 | 4.9922 | -2.2 | -2.044 | 1.0947 | 0.004481
2016-04-28 | 5.37 | 5.23 | 0.14 | 0 | 13.951 | -163.6351 | 88.5742 | 1.4258 | -164.1257 | 145.1148 | 0 | 3.9225 | 0.8 | 1 | 1.074 | 4.9965 | -1.9 | -1.7439 | 1.0936 | 0.0044806
2016-04-28 01:00 | 24.57 | 14.3967 | 10.1733 | 0 | 13.9642 | -148.6334 | 87.2355 | 2.7645 | -149.621 | 136.231 | 0 | 10.7975 | 0.8 | 1 | 4.914 | 15.7115 | -2.7 | -2.209 | 1.0952 | 0.01411
2016-04-28 02:00 | 43.77 | 23.5633 | 20.2067 | 239.6674 | 13.9773 | -133.6318 | 85.1636 | 4.8364 | -135.1811 | 124.7476 | 0 | 17.6725 | 0.8 | 1 | 8.754 | 26.4265 | -2.8 | -1.9742 | 1.0944 | 0.023716
2016-04-28 03:00 | 62.97 | 32.73 | 30.24 | 231.4038 | 13.9905 | -118.6301 | 82.4911 | 7.5089 | -120.7887 | 111.972 | 0 | 24.5475 | 0.8 | 1 | 12.594 | 37.1415 | -2.2 | -1.0393 | 1.0911 | 0.033232
2016-04-28 04:00 | 82.5767 | 47.8133 | 34.7633 | 188.735 | 14.0036 | -103.6285 | 79.386 | 10.614 | -106.3875 | 98.5143 | 0 | 35.86 | 0.8 | 1 | 16.5153 | 52.3753 | -2 | -0.36327 | 1.0888 | 0.04676
2016-04-28 05:00 | 102.1833 | 62.8967 | 39.2867 | 162.8734 | 14.0168 | -88.6268 | 76.042 | 13.958 | -91.8878 | 84.6685 | 15.1339 | 47.1725 | 0.8 | 1 | 20.4367 | 82.7431 | -1.8 | 0.78572 | 1.0847 | 0.0736
2016-04-28 06:00 | 121.79 | 77.98 | 43.81 | 147.0804 | 14.0299 | -73.6252 | 72.6706 | 17.3294 | -77.1815 | 70.5885 | 48.8821 | 58.485 | 0.8 | 1 | 24.358 | 131.7251 | -1.5 | 2.6164 | 1.0783 | 0.11648
2016-04-28 07:00 | 182.12 | 94.09 | 88.03 | 251.2931 | 14.043 | -58.6235 | 69.4938 | 20.5062 | -62.1633 | 56.3634 | 139.197 | 70.5675 | 0.8 | 1 | 36.424 | 246.1885 | -1.8 | 5.8934 | 1.0669 | 0.21537
2016-04-28 08:00 | 242.45 | 110.2 | 132.25 | 334.8255 | 14.0561 | -43.6219 | 66.7352 | 23.2648 | -46.7585 | 42.0516 | 248.6221 | 82.65 | 0.8 | 1 | 48.49 | 379.7621 | -1.2 | 10.6676 | 1.0502 | 0.32703
2016-04-28 09:00 | 302.78 | 126.31 | 176.47 | 411.4899 | 14.0692 | -28.6203 | 64.605 | 25.395 | -30.9528 | 27.7042 | 364.3164 | 94.7325 | 0.8 | 1 | 60.556 | 519.6049 | -0.8 | 15.4377 | 1.0335 | 0.44034
2016-04-28 10:00 | 303.25 | 132.8433 | 170.4067 | 378.986 | 14.0823 | -13.6186 | 63.2795 | 26.7205 | -14.8143 | 13.4312 | 368.6206 | 99.6325 | 0.8 | 1 | 60.65 | 528.9031 | -0.8 | 15.7282 | 1.0325 | 0.44777
2016-04-28 11:00 | 303.72 | 139.3767 | 164.3433 | 360.4589 | 14.0954 | 1.383 | 62.8753 | 27.1247 | 1.5071 | 3.1653 | 359.909 | 104.5325 | 0.8 | 1 | 60.744 | 525.1855 | -1 | 15.412 | 1.0336 | 0.4451
2016-04-28 12:00 | 304.19 | 145.91 | 158.28 | 353.8462 | 14.1085 | 16.3846 | 63.4286 | 26.5714 | 17.8113 | 16.0367 | 340.0763 | 109.4325 | 0.8 | 1 | 60.838 | 510.3468 | -0.9 | 15.0483 | 1.0348 | 0.43306
2016-04-28 13:00 | 290.6133 | 125.4 | 165.2133 | 389.2898 | 14.1216 | 31.3862 | 64.8875 | 25.1125 | 33.9031 | 30.3402 | 335.9733 | 94.05 | 0.8 | 1 | 58.1227 | 488.1459 | -1.1 | 14.1546 | 1.038 | 0.41547
2016-04-28 14:00 | 277.0367 | 104.89 | 172.1467 | 442.8122 | 14.1347 | 46.3878 | 67.1228 | 22.8772 | 49.6451 | 44.6806 | 314.8563 | 78.6675 | 0.8 | 1 | 55.4073 | 448.9312 | -1.6 | 12.4291 | 1.044 | 0.38432
2016-04-28 15:00 | 263.46 | 84.38 | 179.08 | 522.3411 | 14.1477 | 61.3895 | 69.9499 | 20.0501 | 64.9838 | 58.9728 | 269.2384 | 63.285 | 0.8 | 1 | 52.692 | 385.2154 | -1.2 | 10.838 | 1.0496 | 0.33153
2016-04-28 16:00 | 223.3367 | 73.2767 | 150.06 | 517.8189 | 14.1608 | 76.3911 | 73.1545 | 16.8455 | 79.9454 | 73.1657 | 149.9628 | 54.9575 | 0.8 | 1 | 44.6673 | 249.5876 | -1.2 | 6.5996 | 1.0644 | 0.21784
2016-04-28 17:00 | 183.2133 | 62.1733 | 121.04 | 518.9438 | 14.1739 | 91.3927 | 76.5119 | 13.4881 | 94.6113 | 87.1962 | 25.3851 | 46.63 | 0.8 | 1 | 36.6427 | 108.6577 | -1.1 | 2.2956 | 1.0795 | 0.09618
2016-04-28 18:00 | 143.09 | 51.07 | 92.02 | 519.7044 | 14.1869 | 106.3943 | 79.8013 | 10.1987 | 109.0884 | 100.9649 | 0 | 38.3025 | 0.8 | 1 | 28.618 | 66.9205 | -2.2 | -0.10873 | 1.0879 | 0.059697
2016-04-28 19:00 | 102.64 | 38.0367 | 64.6033 | 516.439 | 14.2 | 121.3959 | 82.8138 | 7.1862 | 123.482 | 114.2969 | 0 | 28.5275 | 0.8 | 1 | 20.528 | 49.0555 | -2.2 | -0.66702 | 1.0898 | 0.043839
2016-04-28 20:00 | 62.19 | 25.0033 | 37.1867 | 459.6949 | 14.213 | 136.3974 | 85.36 | 4.64 | 137.8758 | 126.8536 | 0 | 18.7525 | 0.8 | 1 | 12.438 | 31.1905 | -2.3 | -1.3253 | 1.0921 | 0.027933
2016-04-28 21:00 | 21.74 | 11.97 | 9.77 | 0 | 14.226 | 151.399 | 87.278 | 2.722 | 152.3188 | 137.9273 | 0 | 8.9775 | 0.8 | 1 | 4.348 | 13.3255 | -3.5 | -3.0836 | 1.0983 | 0.012001
2016-04-28 22:00 | 21.1267 | 11.35 | 9.7767 | 0 | 14.239 | 166.4006 | 88.4431 | 1.5569 | 166.8211 | 146.029 | 0 | 8.5125 | 0.8 | 1 | 4.2253 | 12.7378 | -3.9 | -3.5019 | 1.0998 | 0.011487
2016-04-28 23:00 | 20.5133 | 10.73 | 9.7833 | 0 | 14.2521 | 181.4022 | 88.7775 | 1.2225 | -178.6407 | 148.7506 | 0 | 8.0475 | 0.8 | 1 | 4.1027 | 12.1502 | -3.9 | -3.5203 | 1.0998 | 0.010958
2016-04-29 | 19.9 | 10.11 | 9.79 | 0 | 14.2651 | -163.5962 | 88.2584 | 1.7416 | -164.1081 | 144.8199 | 0 | 7.5825 | 0.8 | 1 | 3.98 | 11.5625 | -3.1 | -2.7387 | 1.0971 | 0.010402
2016-04-29 01:00 | 49.6567 | 19.2533 | 30.4033 | 565.7462 | 14.2781 | -148.5947 | 86.9194 | 3.0806 | -149.6206 | 135.9857 | 0 | 14.44 | 0.8 | 1 | 9.9313 | 24.3713 | -2.5 | -1.7384 | 1.0936 | 0.021855
2016-04-29 02:00 | 79.4133 | 28.3967 | 51.0167 | 568.1209 | 14.2911 | -133.5931 | 84.848 | 5.152 | -135.1956 | 124.5467 | 0 | 21.2975 | 0.8 | 1 | 15.8827 | 37.1802 | -3.1 | -1.9381 | 1.0943 | 0.033362
2016-04-29 03:00 | 109.17 | 37.54 | 71.63 | 526.2105 | 14.304 | -118.5916 | 82.1764 | 7.8236 | -120.8149 | 111.8047 | 0 | 28.155 | 0.8 | 1 | 21.834 | 49.989 | -2.9 | -1.3378 | 1.0922 | 0.04477
2016-04-29 04:00 | 163.9633 | 49.7633 | 114.2 | 602.4098 | 14.317 | -103.59 | 79.0722 | 10.9278 | -106.4216 | 98.3722 | 0 | 37.3225 | 0.8 | 1 | 32.7927 | 70.1152 | -2.4 | -0.2089 | 1.0882 | 0.062567
2016-04-29 05:00 | 218.7567 | 61.9867 | 156.77 | 635.9504 | 14.33 | -88.5884 | 75.7287 | 14.2713 | -91.9256 | 84.5455 | 60.4501 | 46.49 | 0.8 | 1 | 43.7513 | 150.6914 | -2 | 2.7091 | 1.078 | 0.13321
2016-04-29 06:00 | 273.55 | 74.21 | 199.34 | 657.7133 | 14.343 | -73.5869 | 72.3573 | 17.6427 | -77.2181 | 70.4804 | 219.7608 | 55.6575 | 0.8 | 1 | 54.71 | 330.1283 | -1 | 9.3165 | 1.0549 | 0.28556
2016-04-29 07:00 | 329.2367 | 67.6067 | 261.63 | 736.0875 | 14.3559 | -58.5853 | 69.18 | 20.82 | -62.1934 | 56.2667 | 408.77 | 50.705 | 0.8 | 1 | 65.8473 | 525.3223 | -1.3 | 15.1163 | 1.0346 | 0.44567
2016-04-29 08:00 | 384.9233 | 61.0033 | 323.92 | 809.7626 | 14.3689 | -43.5838 | 66.4207 | 23.5793 | -46.7766 | 41.9625 | 602.1258 | 45.7525 | 0.8 | 1 | 76.9847 | 724.863 | -0.2 | 22.452 | 1.0089 | 0.59969
2016-04-29 09:00 | 440.61 | 54.4 | 386.21 | 890.2695 | 14.3818 | -28.5823 | 64.2902 | 25.7098 | -30.9538 | 27.6164 | 788.8419 | 40.8 | 0.8 | 1 | 88.122 | 917.7639 | -1.4 | 27.2801 | 0.99202 | 0.74656
2016-04-29 10:00 | 442.8833 | 59.5567 | 383.3267 | 843.3515 | 14.3948 | -13.5807 | 62.9654 | 27.0346 | -14.794 | 13.3223 | 820.6562 | 44.6675 | 0.8 | 1 | 88.5767 | 953.9004 | -1.4 | 28.4094 | 0.98807 | 0.77286
2016-04-29 11:00 | 445.1567 | 64.7133 | 380.4433 | 825.6713 | 14.4077 | 1.4208 | 62.5633 | 27.4367 | 1.5505 | 2.9015 | 824.6128 | 48.535 | 0.8 | 1 | 89.0313 | 962.1791 | -1 | 29.0681 | 0.98576 | 0.77775
2016-04-29 12:00 | 447.43 | 69.87 | 377.56 | 835.0778 | 14.4206 | 16.4223 | 63.1199 | 26.8801 | 17.877 | 16.0083 | 802.6951 | 52.4025 | 0.8 | 1 | 89.486 | 944.5836 | -1.1 | 28.4182 | 0.98804 | 0.76529
2016-04-29 13:00 | 414.5733 | 61.2333 | 353.34 | 823.2446 | 14.4336 | 31.4238 | 64.5829 | 25.4171 | 33.9879 | 30.3258 | 710.5986 | 45.925 | 0.8 | 1 | 82.9147 | 839.4382 | -0.8 | 25.4324 | 0.99849 | 0.6873
2016-04-29 14:00 | 381.7167 | 52.5967 | 329.12 | 836.2153 | 14.4465 | 46.4254 | 66.8224 | 23.1776 | 49.7441 | 44.6632 | 594.7595 | 39.4475 | 0.8 | 1 | 76.3433 | 710.5503 | 0.3 | 22.5047 | 1.0087 | 0.58774
2016-04-29 15:00 | 348.86 | 43.96 | 304.9 | 876.8916 | 14.4594 | 61.4269 | 69.653 | 20.347 | 65.0916 | 58.9466 | 452.3332 | 32.97 | 0.8 | 1 | 69.772 | 555.0752 | -1.1 | 16.2461 | 1.0306 | 0.46911
2016-04-29 16:00 | 280.84 | 44.9133 | 235.9267 | 800.5259 | 14.4723 | 76.4284 | 72.8596 | 17.1404 | 80.0568 | 73.1269 | 232.3551 | 33.685 | 0.8 | 1 | 56.168 | 322.2081 | -1.1 | 8.969 | 1.0561 | 0.27904
2016-04-29 17:00 | 212.82 | 45.8667 | 166.9533 | 700.7858 | 14.4852 | 91.4299 | 76.2175 | 13.7825 | 94.7217 | 87.1407 | 34.9572 | 34.4 | 0.8 | 1 | 42.564 | 111.9212 | -1.1 | 2.3975 | 1.0791 | 0.099036
2016-04-29 18:00 | 144.8 | 46.82 | 97.98 | 537.9441 | 14.4981 | 106.4314 | 79.5057 | 10.4943 | 109.1936 | 100.8877 | 0 | 35.115 | 0.8 | 1 | 28.96 | 64.075 | -0.7 | 1.3023 | 1.0829 | 0.056899
2016-04-29 19:00 | 105.57 | 36.08 | 69.49 | 533.4947 | 14.5109 | 121.4329 | 82.5157 | 7.4843 | 123.5783 | 114.1904 | 0 | 27.06 | 0.8 | 1 | 21.114 | 48.174 | -0.9 | 0.60544 | 1.0854 | 0.042875
2016-04-29 20:00 | 66.34 | 25.34 | 41 | 475.9864 | 14.5238 | 136.4344 | 85.0586 | 4.9414 | 137.9599 | 126.7066 | 0 | 19.005 | 0.8 | 1 | 13.268 | 32.273 | -1.4 | -0.39147 | 1.0889 | 0.028816
2016-04-29 21:00 | 27.11 | 14.6 | 12.51 | 236.9045 | 14.5367 | 151.4359 | 86.973 | 3.027 | 152.388 | 137.7243 | 0 | 10.95 | 0.8 | 1 | 5.422 | 16.372 | -2.1 | -1.5884 | 1.0931 | 0.014674
2016-04-29 22:00 | 24.88 | 13.4733 | 11.4067 | 0 | 14.5495 | 166.4373 | 88.1349 | 1.8651 | 166.8731 | 145.7587 | 0 | 10.105 | 0.8 | 1 | 4.976 | 15.081 | -1.8 | -1.3287 | 1.0922 | 0.013506
2016-04-29 23:00 | 22.65 | 12.3467 | 10.3033 | 0 | 14.5624 | 181.4388 | 88.467 | 1.533 | -178.6069 | 148.439 | 0 | 9.26 | 0.8 | 1 | 4.53 | 13.79 | -1.6 | -1.1691 | 1.0916 | 0.012344
2016-04-30 | 20.42 | 11.22 | 9.2 | 0 | 14.5752 | -163.5597 | 87.9466 | 2.0534 | -164.0926 | 144.5292 | 0 | 8.415 | 0.8 | 1 | 4.084 | 12.499 | -1.4 | -1.0094 | 1.091 | 0.011182
2016-04-30 01:00 | 52.3433 | 20.1767 | 32.1667 | 543.5655 | 14.5881 | -148.5582 | 86.6074 | 3.3926 | -149.6221 | 135.7441 | 0 | 15.1325 | 0.8 | 1 | 10.4687 | 25.6012 | -0.5 | 0.30004 | 1.0864 | 0.022808
2016-04-30 02:00 | 84.2667 | 29.1333 | 55.1333 | 579.0644 | 14.6009 | -133.5568 | 84.5365 | 5.4635 | -135.2117 | 124.3491 | 0 | 21.85 | 0.8 | 1 | 16.8533 | 38.7033 | -1.1 | 0.10948 | 1.0871 | 0.034502
2016-04-30 03:00 | 116.19 | 38.09 | 78.1 | 551.9819 | 14.6137 | -118.5553 | 81.8659 | 8.1341 | -120.8427 | 111.6407 | 0 | 28.5675 | 0.8 | 1 | 23.238 | 51.8055 | -1 | 0.61892 | 1.0853 | 0.046106
2016-04-30 04:00 | 155.03 | 56.5867 | 98.4433 | 505.1657 | 14.6266 | -103.5538 | 78.7627 | 11.2373 | -106.4573 | 98.2334 | 0 | 42.44 | 0.8 | 1 | 31.006 | 73.446 | -1.6 | 0.69519 | 1.0851 | 0.065349
2016-04-30 05:00 | 193.87 | 75.0833 | 118.7867 | 471.8705 | 14.6394 | -88.5524 | 75.4198 | 14.5802 | -91.9649 | 84.426 | 45.8331 | 56.3125 | 0.8 | 1 | 38.774 | 140.9196 | -1.6 | 2.8037 | 1.0777 | 0.12453
2016-04-30 06:00 | 232.71 | 93.58 | 139.13 | 451.4047 | 14.6522 | -73.5509 | 72.0483 | 17.9517 | -77.2562 | 70.3761 | 151.6021 | 70.185 | 0.8 | 1 | 46.542 | 268.3291 | -1.4 | 6.9853 | 1.0631 | 0.2339
2016-04-30 07:00 | 251.1633 | 120.3733 | 130.79 | 362.8238 | 14.665 | -58.5495 | 68.8704 | 21.1296 | -62.2252 | 56.174 | 201.9739 | 90.28 | 0.8 | 1 | 50.2327 | 342.4866 | -1.3 | 9.4027 | 1.0546 | 0.29617
2016-04-30 08:00 | 269.6167 | 147.1667 | 122.45 | 302.3639 | 14.6778 | -43.548 | 66.1104 | 23.8896 | -46.7966 | 41.878 | 225.1303 | 110.375 | 0.8 | 1 | 53.9233 | 389.4287 | -1.5 | 10.6696 | 1.0502 | 0.33535
2016-04-30 09:00 | 288.07 | 173.96 | 114.11 | 260.1149 | 14.6905 | -28.5466 | 63.9796 | 26.0204 | -30.9568 | 27.5345 | 230.6524 | 130.47 | 0.8 | 1 | 57.614 | 418.7364 | -2.2 | 10.8855 | 1.0494 | 0.36033
2016-04-30 10:00 | 285.7 | 160.5867 | 125.1133 | 272.3757 | 14.7033 | -13.5452 | 62.6554 | 27.3446 | -14.776 | 13.223 | 265.1543 | 120.44 | 0.8 | 1 | 57.14 | 442.7343 | -2.6 | 11.2354 | 1.0482 | 0.38053
2016-04-30 11:00 | 283.33 | 147.2133 | 136.1167 | 292.3875 | 14.7161 | 1.4563 | 62.2551 | 27.7449 | 1.5915 | 2.6509 | 292.0746 | 110.41 | 0.8 | 1 | 56.666 | 459.1506 | -2.5 | 11.8485 | 1.046 | 0.39383
2016-04-30 12:00 | 280.96 | 133.84 | 147.12 | 322.0196 | 14.7288 | 16.4577 | 62.8149 | 27.1851 | 17.9402 | 15.9842 | 309.5695 | 100.38 | 0.8 | 1 | 56.192 | 466.1415 | -2.9 | 11.6669 | 1.0467 | 0.40007
2016-04-30 13:00 | 249.31 | 112.0167 | 137.2933 | 316.386 | 14.7416 | 31.4591 | 64.282 | 25.718 | 34.07 | 30.3126 | 273.131 | 84.0125 | 0.8 | 1 | 49.862 | 407.0055 | -2.1 | 10.6189 | 1.0503 | 0.35054
2016-04-30 14:00 | 217.66 | 90.1933 | 127.4667 | 319.9936 | 14.7544 | 46.4605 | 66.5255 | 23.4745 | 49.8402 | 44.6458 | 227.6641 | 67.645 | 0.8 | 1 | 43.532 | 338.8411 | -2.4 | 8.1888 | 1.0588 | 0.2942
2016-04-30 15:00 | 186.01 | 68.37 | 117.64 | 333.7257 | 14.7671 | 61.462 | 69.3594 | 20.6406 | 65.1965 | 58.9199 | 172.2813 | 51.2775 | 0.8 | 1 | 37.202 | 260.7608 | -1.5 | 6.6488 | 1.0642 | 0.22756
2016-04-30 16:00 | 168.58 | 58.1767 | 110.4033 | 368.5351 | 14.7798 | 76.4634 | 72.568 | 17.432 | 80.1653 | 73.0872 | 107.2126 | 43.6325 | 0.8 | 1 | 33.716 | 184.5611 | -0.4 | 5.3675 | 1.0687 | 0.16174
2016-04-30 17:00 | 151.15 | 47.9833 | 103.1667 | 424.2587 | 14.7926 | 91.4648 | 75.9263 | 14.0737 | 94.8291 | 87.0843 | 21.5808 | 35.9875 | 0.8 | 1 | 30.23 | 87.7983 | -0.2 | 2.5437 | 1.0786 | 0.077653
2016-04-30 18:00 | 133.72 | 37.79 | 95.93 | 512.5796 | 14.8053 | 106.4662 | 79.2134 | 10.7866 | 109.2958 | 100.8094 | 0 | 28.3425 | 0.8 | 1 | 26.744 | 55.0865 | 0.5 | 2.2215 | 1.0797 | 0.048772
2016-04-30 19:00 | 95.76 | 28.67 | 67.09 | 495.6696 | 14.818 | 121.4676 | 82.221 | 7.779 | 123.6717 | 114.0829 | 0 | 21.5025 | 0.8 | 1 | 19.152 | 40.6545 | 0 | 1.2705 | 1.0831 | 0.036105
2016-04-30 20:00 | 57.8 | 19.55 | 38.25 | 418.8754 | 14.8307 | 136.469 | 84.7607 | 5.2393 | 138.0412 | 126.559 | 0 | 14.6625 | 0.8 | 1 | 11.56 | 26.2225 | 0.7 | 1.5195 | 1.0822 | 0.02327
2016-04-30 21:00 | 19.84 | 10.43 | 9.41 | 162.0816 | 14.8434 | 151.4704 | 86.6717 | 3.3283 | 152.4543 | 137.5215 | 0 | 7.8225 | 0.8 | 1 | 3.968 | 11.7905 | 0.5 | 0.86845 | 1.0845 | 0.010485
2016-04-30 22:00 | 18.5567 | 9.7 | 8.8567 | 0 | 14.8561 | 166.4717 | 87.8305 | 2.1695 | 166.9226 | 145.4905 | 0 | 7.275 | 0.8 | 1 | 3.7113 | 10.9863 | 0.5 | 0.84332 | 1.0845 | 0.0097705
2016-04-30 23:00 | 17.2733 | 8.97 | 8.3033 | 0 | 14.8688 | 181.4731 | 88.1604 | 1.8396 | -178.5755 | 148.1314 | 0 | 6.7275 | 0.8 | 1 | 3.4547 | 10.1822 | 0.5 | 0.81819 | 1.0846 | 0.009056
2016-05-01 | 15.99 | 8.24 | 7.75 | 0 | 14.8815 | -163.5255 | 87.6388 | 2.3612 | -164.0791 | 144.2427 | 0 | 6.18 | 0.8 | 1 | 3.198 | 9.378 | 0.6 | 0.89306 | 1.0844 | 0.0083388
2016-05-01 01:00 | 41.5867 | 15.9133 | 25.6733 | 397.7942 | 14.8941 | -148.5241 | 86.2996 | 3.7004 | -149.6254 | 135.5062 | 0 | 11.935 | 0.8 | 1 | 8.3173 | 20.2523 | -0.1 | 0.53289 | 1.0856 | 0.018029
2016-05-01 02:00 | 67.1833 | 23.5867 | 43.5967 | 433.5996 | 14.9068 | -133.5227 | 84.2294 | 5.7706 | -135.2296 | 124.155 | 0 | 17.69 | 0.8 | 1 | 13.4367 | 31.1267 | 0.3 | 1.2727 | 1.083 | 0.027644
2016-05-01 03:00 | 92.78 | 31.26 | 61.52 | 419.1397 | 14.9195 | -118.5214 | 81.5598 | 8.4402 | -120.8721 | 111.48 | 0 | 23.445 | 0.8 | 1 | 18.556 | 42.001 | 2 | 3.3125 | 1.0759 | 0.037055
2016-05-01 04:00 | 118.0133 | 37.9367 | 80.0767 | 400.1952 | 14.9321 | -103.52 | 78.4575 | 11.5425 | -106.4945 | 98.0979 | 0 | 28.4525 | 0.8 | 1 | 23.6027 | 52.0552 | 2 | 3.6267 | 1.0748 | 0.045878
2016-05-01 05:00 | 143.2467 | 44.6133 | 98.6333 | 383.9712 | 14.9448 | -88.5187 | 75.1152 | 14.8848 | -92.0057 | 84.31 | 38.069 | 33.46 | 0.8 | 1 | 28.6493 | 100.1783 | 2.3 | 5.4306 | 1.0685 | 0.087773
2016-05-01 06:00 | 168.48 | 51.29 | 117.19 | 374.0874 | 14.9574 | -73.5173 | 71.7437 | 18.2563 | -77.296 | 70.2754 | 126.2543 | 38.4675 | 0.8 | 1 | 33.696 | 198.4178 | 1.7 | 7.9006 | 1.0598 | 0.17244
2016-05-01 07:00 | 237.7533 | 60.7867 | 176.9667 | 484.2549 | 14.97 | -58.516 | 68.5653 | 21.4347 | -62.2587 | 56.0854 | 270.1929 | 45.59 | 0.8 | 1 | 47.5507 | 363.3336 | 1.5 | 12.8542 | 1.0425 | 0.3106
2016-05-01 08:00 | 307.0267 | 70.2833 | 236.7433 | 577.6313 | 14.9826 | -43.5146 | 65.8045 | 24.1955 | -46.8185 | 41.7983 | 430.6216 | 52.7125 | 0.8 | 1 | 61.4053 | 544.7394 | 0.7 | 17.7231 | 1.0255 | 0.45806
2016-05-01 09:00 | 376.3 | 79.78 | 296.52 | 668.6061 | 14.9953 | -28.5133 | 63.6732 | 26.3268 | -30.9619 | 27.4586 | 593.2841 | 59.835 | 0.8 | 1 | 75.26 | 728.3791 | 0.2 | 22.9618 | 1.0071 | 0.60153
2016-05-01 10:00 | 361.3167 | 83.6167 | 277.7 | 598.3917 | 15.0079 | -13.5119 | 62.3495 | 27.6505 | -14.7602 | 13.1331 | 582.7406 | 62.7125 | 0.8 | 1 | 72.2633 | 717.7164 | 2 | 24.4286 | 1.002 | 0.5897
2016-05-01 11:00 | 346.3333 | 87.4533 | 258.88 | 550.5427 | 15.0205 | 1.4894 | 61.951 | 28.049 | 1.63 | 2.4161 | 550.0533 | 65.59 | 0.8 | 1 | 69.2667 | 684.91 | 1.8 | 23.2034 | 1.0063 | 0.56516
2016-05-01 12:00 | 331.35 | 91.29 | 240.06 | 520.1334 | 15.0331 | 16.4907 | 62.5138 | 27.4862 | 18.0007 | 15.9643 | 500.0735 | 68.4675 | 0.8 | 1 | 66.27 | 634.811 | 0.8 | 20.6378 | 1.0153 | 0.52849
2016-05-01 13:00 | 330.8367 | 87.2967 | 243.54 | 555.2527 | 15.0457 | 31.4921 | 63.9847 | 26.0153 | 34.1492 | 30.3006 | 479.4 | 65.4725 | 0.8 | 1 | 66.1673 | 611.0399 | 1.4 | 20.495 | 1.0158 | 0.50895
2016-05-01 14:00 | 330.3233 | 83.3033 | 247.02 | 612.9041 | 15.0582 | 46.4934 | 66.2321 | 23.7679 | 49.9335 | 44.6285 | 436.1899 | 62.4775 | 0.8 | 1 | 66.0647 | 564.7321 | 1.8 | 19.4479 | 1.0194 | 0.47208
2016-05-01 15:00 | 329.81 | 79.31 | 250.5 | 701.2116 | 15.0708 | 61.4947 | 69.0693 | 20.9307 | 65.2984 | 58.8926 | 362.2765 | 59.4825 | 0.8 | 1 | 65.962 | 487.721 | 2.2 | 17.4413 | 1.0265 | 0.41051
2016-05-01 16:00 | 259.27 | 69.11 | 190.16 | 624.7704 | 15.0834 | 76.496 | 72.2799 | 17.7201 | 80.2707 | 73.0467 | 182.1781 | 51.8325 | 0.8 | 1 | 51.854 | 285.8646 | 1.6 | 10.5333 | 1.0506 | 0.24628
2016-05-01 17:00 | 188.73 | 58.91 | 129.82 | 523.3887 | 15.0959 | 91.4973 | 75.6386 | 14.3614 | 94.9335 | 87.0268 | 27.1476 | 44.1825 | 0.8 | 1 | 37.746 | 109.0761 | 1.7 | 5.1086 | 1.0696 | 0.095669
2016-05-01 18:00 | 118.19 | 48.71 | 69.48 | 361.6839 | 15.1085 | 106.4986 | 78.9246 | 11.0754 | 109.395 | 100.73 | 0 | 36.5325 | 0.8 | 1 | 23.638 | 60.1705 | 0.7 | 2.5803 | 1.0785 | 0.053211
2016-05-01 19:00 | 84.69 | 37.03 | 47.66 | 339.4922 | 15.121 | 121.4999 | 81.9298 | 8.0702 | 123.762 | 113.9745 | 0 | 27.7725 | 0.8 | 1 | 16.938 | 44.7105 | 0.4 | 1.7972 | 1.0812 | 0.03964
2016-05-01 20:00 | 51.19 | 25.35 | 25.84 | 267.967 | 15.1336 | 136.5012 | 84.4664 | 5.5336 | 138.1196 | 126.4108 | 0 | 19.0125 | 0.8 | 1 | 10.238 | 29.2505 | 0.9 | 1.8141 | 1.0812 | 0.025932
2016-05-01 21:00 | 17.69 | 13.67 | 4.02 | 63.5659 | 15.1461 | 151.5025 | 86.3741 | 3.6259 | 152.518 | 137.3191 | 0 | 10.2525 | 0.8 | 1 | 3.538 | 13.7905 | -0.1 | 0.33095 | 1.0863 | 0.012285
2016-05-01 22:00 | 17.73 | 14.59 | 3.14 | 0 | 15.1586 | 166.5038 | 87.53 | 2.47 | 166.9695 | 145.2245 | 0 | 10.9425 | 0.8 | 1 | 3.546 | 14.4885 | -0.3 | 0.15277 | 1.087 | 0.012914
2016-05-01 23:00 | 17.77 | 15.51 | 2.26 | 0 | 15.1711 | 181.5051 | 87.8579 | 2.1421 | -178.5464 | 147.8279 | 0 | 11.6325 | 0.8 | 1 | 3.554 | 15.1865 | -1.2 | -0.72542 | 1.09 | 0.013574
2016-05-02 | 17.81 | 16.43 | 1.38 | 0 | 15.1837 | -163.4936 | 87.3353 | 2.6647 | -164.0678 | 143.9606 | 0 | 12.3225 | 0.8 | 1 | 3.562 | 15.8845 | -1 | -0.50361 | 1.0893 | 0.014188
2016-05-02 01:00 | 50.7167 | 24.8633 | 25.8533 | 370.2602 | 15.1962 | -148.4924 | 85.9961 | 4.0039 | -149.6306 | 135.2721 | 0 | 18.6475 | 0.8 | 1 | 10.1433 | 28.7908 | -0.6 | 0.29971 | 1.0865 | 0.025649
2016-05-02 02:00 | 83.6233 | 33.2967 | 50.3267 | 475.6687 | 15.2086 | -133.4911 | 83.9266 | 6.0734 | -135.2492 | 123.9644 | 0 | 24.9725 | 0.8 | 1 | 16.7247 | 41.6972 | -0.6 | 0.70304 | 1.085 | 0.037099
2016-05-02 03:00 | 116.53 | 41.73 | 74.8 | 492.1611 | 15.2211 | -118.4898 | 81.2582 | 8.7418 | -120.9031 | 111.3228 | 0 | 31.2975 | 0.8 | 1 | 23.306 | 54.6035 | -0.8 | 0.90636 | 1.0843 | 0.048551
2016-05-02 04:00 | 177.6633 | 44.4033 | 133.26 | 649.3125 | 15.2336 | -103.4886 | 78.1569 | 11.8431 | -106.5332 | 97.9659 | 0 | 33.3025 | 0.8 | 1 | 35.5327 | 68.8352 | -0.7 | 1.4511 | 1.0824 | 0.061097
2016-05-02 05:00 | 238.7967 | 47.0767 | 191.72 | 731.9376 | 15.2461 | -88.4873 | 74.8151 | 15.1849 | -92.0481 | 84.1976 | 73.9975 | 35.3075 | 0.8 | 1 | 47.7593 | 157.0643 | -0.7 | 4.2083 | 1.0728 | 0.13817
2016-05-02 06:00 | 299.93 | 49.75 | 250.18 | 786.1386 | 15.2586 | -73.4861 | 71.4435 | 18.5565 | -77.3374 | 70.1785 | 266.5726 | 37.3125 | 0.8 | 1 | 59.986 | 363.8711 | -1.1 | 10.271 | 1.0516 | 0.31376
2016-05-02 07:00 | 340.56 | 61.11 | 279.45 | 754.6148 | 15.271 | -58.4848 | 68.2646 | 21.7354 | -62.294 | 56.001 | 421.9648 | 45.8325 | 0.8 | 1 | 68.112 | 535.9093 | -1.1 | 15.6472 | 1.0327 | 0.45383
2016-05-02 08:00 | 381.19 | 72.47 | 308.72 | 744.5375 | 15.2835 | -43.4836 | 65.5029 | 24.4971 | -46.8424 | 41.7233 | 555.699 | 54.3525 | 0.8 | 1 | 76.238 | 686.2895 | -1.1 | 20.3465 | 1.0163 | 0.57192
2016-05-02 09:00 | 421.82 | 83.83 | 337.99 | 754.0905 | 15.2959 | -28.4823 | 63.3712 | 26.6288 | -30.9691 | 27.3884 | 669.5632 | 62.8725 | 0.8 | 1 | 84.364 | 816.7997 | -1.2 | 24.325 | 1.0024 | 0.67136
2016-05-02 10:00 | 425.4267 | 83.0767 | 342.35 | 730.3694 | 15.3083 | -13.4811 | 62.0478 | 27.9522 | -14.7468 | 13.0528 | 711.4985 | 62.3075 | 0.8 | 1 | 85.0853 | 858.8913 | -1.3 | 25.5404 | 0.99811 | 0.70296
2016-05-02 11:00 | 429.0333 | 82.3233 | 346.71 | 730.1571 | 15.3208 | 1.5202 | 61.6509 | 28.3491 | 1.666 | 2.2002 | 729.6188 | 61.7425 | 0.8 | 1 | 85.8067 | 877.168 | -0.7 | 26.7115 | 0.99401 | 0.71497
2016-05-02 12:00 | 432.64 | 81.57 | 351.07 | 753.1574 | 15.3332 | 16.5214 | 62.2166 | 27.7834 | 18.0585 | 15.9483 | 724.1683 | 61.1775 | 0.8 | 1 | 86.528 | 871.8738 | -1.4 | 25.8461 | 0.99704 | 0.71282
2016-05-02 13:00 | 378.2367 | 101.6067 | 276.63 | 624.1529 | 15.3456 | 31.5226 | 63.6912 | 26.3088 | 34.2257 | 30.2894 | 538.949 | 76.205 | 0.8 | 1 | 75.6473 | 690.8013 | -1.6 | 19.9875 | 1.0175 | 0.57639
2016-05-02 14:00 | 323.8333 | 121.6433 | 202.19 | 495.9842 | 15.358 | 46.5238 | 65.9424 | 24.0576 | 50.0238 | 44.611 | 353.0868 | 91.2325 | 0.8 | 1 | 64.7667 | 509.0859 | -0.7 | 15.2089 | 1.0343 | 0.43176
2016-05-02 15:00 | 269.43 | 141.68 | 127.75 | 352.9925 | 15.3704 | 61.5251 | 68.7827 | 21.2173 | 65.3973 | 58.8648 | 182.5183 | 106.26 | 0.8 | 1 | 53.886 | 342.6643 | -0.6 | 10.1083 | 1.0521 | 0.29563
2016-05-02 16:00 | 224.3067 | 116.4467 | 107.86 | 348.9524 | 15.3828 | 76.5263 | 71.9952 | 18.0048 | 80.3731 | 73.0053 | 101.9929 | 87.335 | 0.8 | 1 | 44.8613 | 234.1893 | -1.2 | 6.1184 | 1.0661 | 0.20473
2016-05-02 17:00 | 179.1833 | 91.2133 | 87.97 | 347.9264 | 15.3952 | 91.5275 | 75.3543 | 14.6457 | 95.0347 | 86.9683 | 18.4013 | 68.41 | 0.8 | 1 | 35.8367 | 122.648 | -1.8 | 2.0327 | 1.0804 | 0.10866
2016-05-02 18:00 | 134.06 | 65.98 | 68.08 | 345.6073 | 15.4076 | 106.5287 | 78.6392 | 11.3608 | 109.491 | 100.6496 | 0 | 49.485 | 0.8 | 1 | 26.812 | 76.297 | -1.7 | 0.68428 | 1.0851 | 0.067888
2016-05-02 19:00 | 101.0167 | 50.8867 | 50.13 | 344.8809 | 15.42 | 121.5299 | 81.6422 | 8.3578 | 123.8494 | 113.8652 | 0 | 38.165 | 0.8 | 1 | 20.2033 | 58.3683 | -1.6 | 0.22401 | 1.0867 | 0.052012
2016-05-02 20:00 | 67.9733 | 35.7933 | 32.18 | 317.1164 | 15.4323 | 136.5311 | 84.1758 | 5.8242 | 138.195 | 126.2621 | 0 | 26.845 | 0.8 | 1 | 13.5947 | 40.4397 | -1.5 | -0.23626 | 1.0883 | 0.036089
2016-05-02 21:00 | 34.93 | 20.7 | 14.23 | 208.1713 | 15.4447 | 151.5323 | 86.0804 | 3.9196 | 152.5788 | 137.1172 | 0 | 15.525 | 0.8 | 1 | 6.986 | 22.511 | -1 | -0.29653 | 1.0885 | 0.020093
2016-05-02 22:00 | 32.51 | 18.0833 | 14.4267 | 0 | 15.457 | 166.5335 | 87.2335 | 2.7665 | 167.0138 | 144.9609 | 0 | 13.5625 | 0.8 | 1 | 6.502 | 20.0645 | -1.2 | -0.57298 | 1.0895 | 0.017926
2016-05-02 23:00 | 30.09 | 15.4667 | 14.6233 | 0 | 15.4694 | 181.5346 | 87.5595 | 2.4405 | -178.5196 | 147.5287 | 0 | 11.6 | 0.8 | 1 | 6.018 | 17.618 | -1.7 | -1.1494 | 1.0915 | 0.015769
2016-05-03 | 27.67 | 12.85 | 14.82 | 0 | 15.4817 | -163.4642 | 87.036 | 2.964 | -164.0585 | 143.683 | 0 | 9.6375 | 0.8 | 1 | 5.534 | 15.1715 | -0.8 | -0.32589 | 1.0886 | 0.013543
2016-05-03 01:00 | 51.4867 | 19.5367 | 31.95 | 425.8175 | 15.494 | -148.463 | 85.6969 | 4.3031 | -149.6378 | 135.042 | 0 | 14.6525 | 0.8 | 1 | 10.2973 | 24.9498 | -1.1 | -0.32032 | 1.0886 | 0.022272
2016-05-03 02:00 | 75.3033 | 26.2233 | 49.08 | 442.2517 | 15.5064 | -133.4618 | 83.6283 | 6.3717 | -135.2705 | 123.7774 | 0 | 19.6675 | 0.8 | 1 | 15.0607 | 34.7282 | -1.1 | -0.014745 | 1.0876 | 0.03097
2016-05-03 03:00 | 99.12 | 32.91 | 66.21 | 421.4343 | 15.5187 | -118.4607 | 80.961 | 9.039 | -120.9356 | 111.169 | 0 | 24.6825 | 0.8 | 1 | 19.824 | 44.5065 | -1.2 | 0.19083 | 1.0868 | 0.039664
2016-05-03 04:00 | 107.4167 | 46.1667 | 61.25 | 291.2683 | 15.531 | -103.4595 | 77.8608 | 12.1392 | -106.5735 | 97.8374 | 0 | 34.625 | 0.8 | 1 | 21.4833 | 56.1083 | -1.1 | 0.65339 | 1.0852 | 0.049929
2016-05-03 05:00 | 115.7133 | 59.4233 | 56.29 | 210.8962 | 15.5433 | -88.4583 | 74.5196 | 15.4804 | -92.092 | 84.0887 | 21.7198 | 44.5675 | 0.8 | 1 | 23.1427 | 89.43 | -1 | 1.7947 | 1.0812 | 0.079289
2016-05-03 06:00 | 124.01 | 72.68 | 51.33 | 158.8551 | 15.5556 | -73.4572 | 71.148 | 18.852 | -77.3803 | 70.0853 | 54.1093 | 54.51 | 0.8 | 1 | 24.802 | 133.4213 | -0.8 | 3.3694 | 1.0757 | 0.11769
2016-05-03 07:00 | 129.98 | 86.7467 | 43.2333 | 115.2527 | 15.5679 | -58.456 | 67.9684 | 22.0316 | -62.3311 | 55.9205 | 64.5809 | 65.06 | 0.8 | 1 | 25.996 | 155.6369 | -0.7 | 4.1637 | 1.0729 | 0.13693
2016-05-03 08:00 | 135.95 | 100.8133 | 35.1367 | 83.7867 | 15.5801 | -43.4549 | 65.2059 | 24.7941 | -46.8681 | 41.6528 | 62.6042 | 75.61 | 0.8 | 1 | 27.19 | 165.4042 | -0.6 | 4.5689 | 1.0715 | 0.14533
2016-05-03 09:00 | 141.92 | 114.88 | 27.04 | 59.7112 | 15.5924 | -28.4537 | 63.0735 | 26.9265 | -30.9785 | 27.3241 | 53.0488 | 86.16 | 0.8 | 1 | 28.384 | 167.5928 | -0.1 | 5.1373 | 1.0695 | 0.14698
2016-05-03 10:00 | 180.7133 | 146.1933 | 34.52 | 72.9325 | 15.6047 | -13.4526 | 61.7503 | 28.2497 | -14.7358 | 12.9818 | 71.0684 | 109.645 | 0.8 | 1 | 36.1427 | 216.8561 | -0.4 | 6.3768 | 1.0652 | 0.18941
2016-05-03 11:00 | 219.5067 | 177.5067 | 42 | 87.6127 | 15.6169 | 1.5485 | 61.3549 | 28.6451 | 1.6994 | 2.0077 | 87.5589 | 133.13 | 0.8 | 1 | 43.9013 | 264.5903 | -0.5 | 7.7684 | 1.0603 | 0.23005
2016-05-03 12:00 | 258.3 | 208.82 | 49.48 | 105.1307 | 15.6292 | 16.5497 | 61.9234 | 28.0766 | 18.1136 | 15.936 | 101.0904 | 156.615 | 0.8 | 1 | 51.66 | 309.3654 | -0.2 | 9.4677 | 1.0544 | 0.26747
2016-05-03 13:00 | 226.7433 | 177.2933 | 49.45 | 110.4449 | 15.6414 | 31.5508 | 63.4016 | 26.5984 | 34.2993 | 30.2791 | 95.3779 | 132.97 | 0.8 | 1 | 45.3487 | 273.6966 | -0.4 | 8.153 | 1.059 | 0.23766
2016-05-03 14:00 | 195.1867 | 145.7667 | 49.42 | 119.8914 | 15.6536 | 46.5519 | 65.6565 | 24.3435 | 50.1112 | 44.5934 | 85.3755 | 109.325 | 0.8 | 1 | 39.0373 | 233.7378 | -0.4 | 6.9043 | 1.0633 | 0.2038
2016-05-03 15:00 | 163.63 | 114.24 | 49.39 | 134.7596 | 15.6659 | 61.553 | 68.4998 | 21.5002 | 65.4931 | 58.8363 | 69.7361 | 85.68 | 0.8 | 1 | 32.726 | 188.1421 | -0.5 | 5.3794 | 1.0687 | 0.16487
2016-05-03 16:00 | 137.02 | 98.06 | 38.96 | 124.1719 | 15.6781 | 76.5541 | 71.7141 | 18.2859 | 80.4723 | 72.963 | 36.381 | 73.545 | 0.8 | 1 | 27.404 | 137.33 | -0.8 | 3.4916 | 1.0753 | 0.12109
2016-05-03 17:00 | 110.41 | 81.88 | 28.53 | 110.7626 | 15.6903 | 91.5552 | 75.0736 | 14.9264 | 95.1327 | 86.9088 | 5.973 | 61.41 | 0.8 | 1 | 22.082 | 89.465 | -0.7 | 2.0958 | 1.0802 | 0.079242
2016-05-03 18:00 | 83.8 | 65.7 | 18.1 | 89.6903 | 15.7025 | 106.5563 | 78.3574 | 11.6426 | 109.5839 | 100.5682 | 0 | 49.275 | 0.8 | 1 | 16.76 | 66.035 | -1 | 1.0636 | 1.0838 | 0.058685
2016-05-03 19:00 | 64.7133 | 50.03 | 14.6833 | 97.7221 | 15.7147 | 121.5574 | 81.3582 | 8.6418 | 123.9336 | 113.755 | 0 | 37.5225 | 0.8 | 1 | 12.9427 | 50.4652 | -1.2 | 0.37704 | 1.0862 | 0.044948
2016-05-03 20:00 | 45.6267 | 34.36 | 11.2667 | 105.8341 | 15.7269 | 136.5585 | 83.8889 | 6.1111 | 138.2674 | 126.113 | 0 | 25.77 | 0.8 | 1 | 9.1253 | 34.8953 | -1.6 | -0.50952 | 1.0893 | 0.031169
2016-05-03 21:00 | 26.54 | 18.69 | 7.85 | 106.944 | 15.7391 | 151.5596 | 85.7905 | 4.2095 | 152.6369 | 136.9158 | 0 | 14.0175 | 0.8 | 1 | 5.308 | 19.3255 | -1.7 | -1.0961 | 1.0913 | 0.017294
2016-05-03 22:00 | 26.1367 | 17.2533 | 8.8833 | 166.4728 | 15.7512 | 166.5607 | 86.9411 | 3.0589 | 167.0555 | 144.6996 | 0 | 12.94 | 0.8 | 1 | 5.2273 | 18.1673 | -1.4 | -0.83227 | 1.0904 | 0.016244
2016-05-03 23:00 | 25.7333 | 15.8167 | 9.9167 | 0 | 15.7634 | 181.5618 | 87.2653 | 2.7347 | -178.4952 | 147.2337 | 0 | 11.8625 | 0.8 | 1 | 5.1467 | 17.0092 | -0.9 | -0.36846 | 1.0888 | 0.015186
2016-05-04 | 25.33 | 14.38 | 10.95 | 192.6207 | 15.7756 | -163.4371 | 86.7411 | 3.2589 | -164.0514 | 143.4099 | 0 | 10.785 | 0.8 | 1 | 5.066 | 15.851 | -1.3 | -0.80466 | 1.0903 | 0.014172
2016-05-04 01:00 | 39.02 | 24.1967 | 14.8233 | 184.9224 | 15.7877 | -148.436 | 85.4023 | 4.5977 | -149.6468 | 134.8159 | 0 | 18.1475 | 0.8 | 1 | 7.804 | 25.9515 | -1.6 | -0.78902 | 1.0903 | 0.023201
2016-05-04 02:00 | 52.71 | 34.0133 | 18.6967 | 161.0793 | 15.7999 | -133.435 | 83.3346 | 6.6654 | -135.2935 | 123.5941 | 0 | 25.51 | 0.8 | 1 | 10.542 | 36.052 | -1.9 | -0.77337 | 1.0902 | 0.032229
2016-05-04 03:00 | 66.4 | 43.83 | 22.57 | 139.1954 | 15.812 | -118.4339 | 80.6685 | 9.3315 | -120.9697 | 111.0188 | 0 | 32.8725 | 0.8 | 1 | 13.28 | 46.1525 | -2 | -0.55773 | 1.0895 | 0.04123
2016-05-04 04:00 | 83 | 62.9633 | 20.0367 | 93.0825 | 15.8241 | -103.4328 | 77.5694 | 12.4306 | -106.6152 | 97.7124 | 0 | 47.2225 | 0.8 | 1 | 16.6 | 63.8225 | -2.4 | -0.40555 | 1.0889 | 0.056988
2016-05-04 05:00 | 99.6 | 82.0967 | 17.5033 | 64.3987 | 15.8362 | -88.4318 | 74.2288 | 15.7712 | -92.1374 | 83.9835 | 6.75 | 61.5725 | 0.8 | 1 | 19.92 | 88.2425 | -2.3 | 0.45758 | 1.0859 | 0.078574
2016-05-04 06:00 | 116.2 | 101.23 | 14.97 | 45.6508 | 15.8484 | -73.4307 | 70.8572 | 19.1428 | -77.4249 | 69.996 | 15.6165 | 75.9225 | 0.8 | 1 | 23.24 | 114.779 | -2.7 | 0.88684 | 1.0844 | 0.10206
2016-05-04 07:00 | 160.23 | 135.01 | 25.22 | 66.3983 | 15.8605 | -58.4297 | 67.6769 | 22.3231 | -62.3698 | 55.8442 | 37.279 | 101.2575 | 0.8 | 1 | 32.046 | 170.5825 | -2.7 | 2.6307 | 1.0783 | 0.15083
2016-05-04 08:00 | 204.26 | 168.79 | 35.47 | 83.6583 | 15.8726 | -43.4286 | 64.9135 | 25.0865 | -46.8958 | 41.587 | 62.5721 | 126.5925 | 0.8 | 1 | 40.852 | 230.0166 | -2.7 | 4.488 | 1.0718 | 0.20215
2016-05-04 09:00 | 248.29 | 202.57 | 45.72 | 99.9557 | 15.8847 | -28.4276 | 62.7804 | 27.2196 | -30.99 | 27.2655 | 88.85 | 151.9275 | 0.8 | 1 | 49.658 | 290.4355 | -2.6 | 6.4761 | 1.0648 | 0.2536
2016-05-04 10:00 | 247.0933 | 204.6733 | 42.42 | 88.7794 | 15.8967 | -13.4266 | 61.4573 | 28.5427 | -14.7271 | 12.92 | 86.5318 | 153.505 | 0.8 | 1 | 49.4187 | 289.4554 | -2.3 | 6.7455 | 1.0639 | 0.25252
2016-05-04 11:00 | 245.8967 | 206.7767 | 39.12 | 80.8525 | 15.9088 | 1.5745 | 61.0632 | 28.9368 | 1.7302 | 1.8437 | 80.8106 | 155.0825 | 0.8 | 1 | 49.1793 | 285.0724 | -1.9 | 7.0085 | 1.063 | 0.24848
2016-05-04 12:00 | 244.7 | 208.88 | 35.82 | 75.3949 | 15.9209 | 16.5755 | 61.6342 | 28.3658 | 18.1659 | 15.9271 | 72.5006 | 156.66 | 0.8 | 1 | 48.94 | 278.1006 | -2.5 | 6.1906 | 1.0658 | 0.24306
2016-05-04 13:00 | 229.79 | 200.2533 | 29.5367 | 65.3195 | 15.9329 | 31.5765 | 63.1159 | 26.8841 | 34.3699 | 30.2696 | 56.4141 | 150.19 | 0.8 | 1 | 45.958 | 252.5621 | -2.3 | 5.5926 | 1.0679 | 0.22117
2016-05-04 14:00 | 214.88 | 191.6267 | 23.2533 | 55.8051 | 15.945 | 46.5775 | 65.3743 | 24.6257 | 50.1954 | 44.5756 | 39.7514 | 143.72 | 0.8 | 1 | 42.976 | 226.4474 | -1.8 | 5.2765 | 1.069 | 0.19851
2016-05-04 15:00 | 199.97 | 183 | 16.97 | 45.737 | 15.957 | 61.5786 | 68.2206 | 21.7794 | 65.5858 | 58.8071 | 23.6881 | 137.25 | 0.8 | 1 | 39.994 | 200.9321 | -2.2 | 4.0791 | 1.0732 | 0.17683
2016-05-04 16:00 | 158.5033 | 147.19 | 11.3133 | 35.5371 | 15.9691 | 76.5796 | 71.4367 | 18.5633 | 80.5683 | 72.9198 | 10.4376 | 110.3925 | 0.8 | 1 | 31.7007 | 152.5308 | -2.3 | 2.4666 | 1.0789 | 0.13494
2016-05-04 17:00 | 117.0367 | 111.38 | 5.6567 | 21.5699 | 15.9811 | 91.5806 | 74.7965 | 15.2035 | 95.2276 | 86.8483 | 1.1859 | 83.535 | 0.8 | 1 | 23.4073 | 108.1283 | -2.4 | 0.97901 | 1.0841 | 0.09612
2016-05-04 18:00 | 75.57 | 75.57 | 0 | 0 | 15.9931 | 106.5816 | 78.0793 | 11.9207 | 109.6737 | 100.4858 | 0 | 56.6775 | 0.8 | 1 | 15.114 | 71.7915 | -2.1 | 0.14348 | 1.087 | 0.063991
2016-05-04 19:00 | 58.2 | 58.2 | 0 | 0 | 16.0051 | 121.5826 | 81.078 | 8.922 | 124.0147 | 113.6441 | 0 | 43.65 | 0.8 | 1 | 11.64 | 55.29 | -2.1 | -0.37219 | 1.0888 | 0.049364
2016-05-04 20:00 | 40.83 | 40.83 | 0 | 0 | 16.0172 | 136.5836 | 83.606 | 6.394 | 138.3369 | 125.9636 | 0 | 30.6225 | 0.8 | 1 | 8.166 | 38.7885 | -1.9 | -0.68786 | 1.0899 | 0.034666
2016-05-04 21:00 | 23.46 | 23.46 | 0 | 0 | 16.0292 | 151.5846 | 85.5047 | 4.4953 | 152.6921 | 136.7152 | 0 | 17.595 | 0.8 | 1 | 4.692 | 22.287 | -1.6 | -0.90353 | 1.0907 | 0.019932
2016-05-04 22:00 | 18.0467 | 18.0467 | 0 | 0 | 16.0411 | 166.5855 | 86.6529 | 3.3471 | 167.0946 | 144.441 | 0 | 13.535 | 0.8 | 1 | 3.6093 | 17.1443 | -1.4 | -0.86424 | 1.0905 | 0.015331
2016-05-04 23:00 | 12.6333 | 12.6333 | 0 | 0 | 16.0531 | 181.5865 | 86.9754 | 3.0246 | -178.4732 | 146.9432 | 0 | 9.475 | 0.8 | 1 | 2.5267 | 12.0017 | -1.3 | -0.92495 | 1.0907 | 0.010734
2016-05-05 | 7.22 | 7.22 | 0 | 0 | 16.0651 | -163.4125 | 86.4506 | 3.5494 | -164.0464 | 143.1415 | 0 | 5.415 | 0.8 | 1 | 1.444 | 6.859 | -0.6 | -0.38566 | 1.0888 | 0.0061241
2016-05-05 01:00 | 13.18 | 12.7767 | 0.40333 | 4.7336 | 16.0771 | -148.4115 | 85.1121 | 4.8879 | -149.6577 | 134.594 | 0 | 9.5825 | 0.8 | 1 | 2.636 | 12.2185 | -0.2 | 0.18183 | 1.0869 | 0.010889
2016-05-05 02:00 | 19.14 | 18.3333 | 0.80667 | 6.6622 | 16.089 | -133.4106 | 83.0455 | 6.9545 | -135.3183 | 123.4146 | 0 | 13.75 | 0.8 | 1 | 3.828 | 17.578 | -0.1 | 0.44931 | 1.0859 | 0.015653
2016-05-05 03:00 | 25.1 | 23.89 | 1.21 | 7.2411 | 16.101 | -118.4096 | 80.3807 | 9.6193 | -121.0054 | 110.8721 | 0 | 17.9175 | 0.8 | 1 | 5.02 | 22.9375 | -0.2 | 0.5168 | 1.0857 | 0.02042
2016-05-05 04:00 | 46.6667 | 44.1067 | 2.56 | 11.6289 | 16.1129 | -103.4086 | 77.2827 | 12.7173 | -106.6585 | 97.591 | 0 | 33.08 | 0.8 | 1 | 9.3333 | 42.4133 | -0.6 | 0.72542 | 1.085 | 0.037734
2016-05-05 05:00 | 68.2333 | 64.3233 | 3.91 | 14.1361 | 16.1249 | -88.4077 | 73.9428 | 16.0572 | -92.1843 | 83.8818 | 1.5066 | 48.2425 | 0.8 | 1 | 13.6467 | 63.3958 | -0.6 | 1.3811 | 1.0827 | 0.056282
2016-05-05 06:00 | 89.8 | 84.54 | 5.26 | 15.813 | 16.1368 | -73.4067 | 70.5711 | 19.4289 | -77.4711 | 69.9104 | 5.4316 | 63.405 | 0.8 | 1 | 17.96 | 86.7966 | -0.6 | 2.1124 | 1.0801 | 0.076875
2016-05-05 07:00 | 111.31 | 100.4033 | 10.9067 | 28.3692 | 16.1487 | -58.4058 | 67.3902 | 22.6098 | -62.4104 | 55.7719 | 15.9574 | 75.3025 | 0.8 | 1 | 22.262 | 113.5219 | -0.6 | 2.9476 | 1.0772 | 0.10027
2016-05-05 08:00 | 132.82 | 116.2667 | 16.5533 | 38.6282 | 16.1607 | -43.4048 | 64.6257 | 25.3743 | -46.9255 | 41.5258 | 28.9193 | 87.2 | 0.8 | 1 | 26.564 | 142.6833 | -0.8 | 3.6589 | 1.0747 | 0.12574
2016-05-05 09:00 | 154.33 | 132.13 | 22.2 | 48.0649 | 16.1726 | -28.4039 | 62.4918 | 27.5082 | -31.0037 | 27.2125 | 42.7449 | 99.0975 | 0.8 | 1 | 30.866 | 172.7084 | -0.9 | 4.4971 | 1.0718 | 0.15178
2016-05-05 10:00 | 157.01 | 128.7467 | 28.2633 | 58.6094 | 16.1845 | -13.403 | 61.1687 | 28.8313 | -14.7209 | 12.8673 | 57.1376 | 96.56 | 0.8 | 1 | 31.402 | 185.0996 | -1.1 | 4.6844 | 1.0711 | 0.16257
2016-05-05 11:00 | 159.69 | 125.3633 | 34.3267 | 70.3087 | 16.1964 | 1.598 | 60.7758 | 29.2242 | 1.7584 | 1.7143 | 70.2772 | 94.0225 | 0.8 | 1 | 31.938 | 196.2377 | -1.2 | 4.9324 | 1.0702 | 0.17222
2016-05-05 12:00 | 162.37 | 121.98 | 40.39 | 84.2391 | 16.2082 | 16.5989 | 61.3493 | 28.6507 | 18.2154 | 15.9215 | 81.0075 | 91.485 | 0.8 | 1 | 32.474 | 204.9665 | -1.1 | 5.3052 | 1.0689 | 0.17966
2016-05-05 13:00 | 150.7267 | 107.5367 | 43.19 | 94.5973 | 16.2201 | 31.5998 | 62.8342 | 27.1658 | 34.4376 | 30.2606 | 81.7077 | 80.6525 | 0.8 | 1 | 30.1453 | 192.5055 | -0.7 | 5.3158 | 1.0689 | 0.16873
2016-05-05 14:00 | 139.0833 | 93.0933 | 45.99 | 109.2144 | 16.232 | 46.6007 | 65.0961 | 24.9039 | 50.2766 | 44.5575 | 77.8204 | 69.82 | 0.8 | 1 | 27.8167 | 175.457 | -0.9 | 4.583 | 1.0715 | 0.15416
2016-05-05 15:00 | 127.44 | 78.65 | 48.79 | 129.9353 | 16.2439 | 61.6017 | 67.9451 | 22.0549 | 65.6752 | 58.7772 | 67.3542 | 58.9875 | 0.8 | 1 | 25.488 | 151.8297 | -1 | 3.7447 | 1.0744 | 0.13376
2016-05-05 16:00 | 113.4867 | 69.25 | 44.2367 | 137.0073 | 16.2557 | 76.6026 | 71.1629 | 18.8371 | 80.6611 | 72.8757 | 40.3412 | 51.9375 | 0.8 | 1 | 22.6973 | 114.9761 | -1.1 | 2.493 | 1.0788 | 0.10171
2016-05-05 17:00 | 99.5333 | 59.85 | 39.6833 | 148.7107 | 16.2676 | 91.6035 | 74.5231 | 15.4769 | 95.3192 | 86.7868 | 8.3355 | 44.8875 | 0.8 | 1 | 19.9067 | 73.1296 | -1.3 | 0.9853 | 1.0841 | 0.065007
2016-05-05 18:00 | 85.58 | 50.45 | 35.13 | 166.3039 | 16.2794 | 106.6044 | 77.805 | 12.195 | 109.7602 | 100.4025 | 0 | 37.8375 | 0.8 | 1 | 17.116 | 54.9535 | -1.6 | 0.1173 | 1.0871 | 0.048986
2016-05-05 19:00 | 69.4233 | 39.5033 | 29.92 | 187.1721 | 16.2912 | 121.6053 | 80.8016 | 9.1984 | 124.0927 | 113.5324 | 0 | 29.6275 | 0.8 | 1 | 13.8847 | 43.5122 | -1.3 | 0.059755 | 1.0873 | 0.038795
2016-05-05 20:00 | 53.2667 | 28.5567 | 24.71 | 212.6445 | 16.3031 | 136.6062 | 83.327 | 6.673 | 138.4034 | 125.8141 | 0 | 21.4175 | 0.8 | 1 | 10.6533 | 32.0708 | -1.4 | -0.39779 | 1.0889 | 0.028636
2016-05-05 21:00 | 37.11 | 17.61 | 19.5 | 234.155 | 16.3149 | 151.607 | 85.223 | 4.777 | 152.7445 | 136.5155 | 0 | 13.2075 | 0.8 | 1 | 7.422 | 20.6295 | -1.3 | -0.65533 | 1.0898 | 0.018435
2016-05-05 22:00 | 37.8 | 17.9533 | 19.8467 | 313.3695 | 16.3267 | 166.6079 | 86.3688 | 3.6312 | 167.1311 | 144.1851 | 0 | 13.465 | 0.8 | 1 | 7.56 | 21.025 | -1.4 | -0.74297 | 1.0901 | 0.018794
2016-05-05 23:00 | 38.49 | 18.2967 | 20.1933 | 349.7345 | 16.3385 | 181.6088 | 86.69 | 3.31 | -178.4536 | 146.6571 | 0 | 13.7225 | 0.8 | 1 | 7.698 | 21.4205 | -1 | -0.33061 | 1.0887 | 0.019122
2016-05-06 | 39.18 | 18.64 | 20.54 | 307.0779 | 16.3503 | -163.3903 | 86.1647 | 3.8353 | -164.0436 | 142.8777 | 0 | 13.98 | 0.8 | 1 | 7.836 | 21.816 | -0.6 | 0.08175 | 1.0872 | 0.019449
2016-05-06 01:00 | 49.5567 | 32.6367 | 16.92 | 187.6467 | 16.3621 | -148.3894 | 84.8266 | 5.1734 | -149.6705 | 134.3763 | 0 | 24.4775 | 0.8 | 1 | 9.9113 | 34.3888 | -0.3 | 0.77465 | 1.0848 | 0.03059
2016-05-06 02:00 | 59.9333 | 46.6333 | 13.3 | 105.5501 | 16.3738 | -133.3886 | 82.7611 | 7.2389 | -135.3447 | 123.2389 | 0 | 34.975 | 0.8 | 1 | 11.9867 | 46.9617 | 0.2 | 1.6676 | 1.0817 | 0.041653
2016-05-06 03:00 | 70.31 | 60.63 | 9.68 | 56.2893 | 16.3856 | -118.3877 | 80.0977 | 9.9023 | -121.0427 | 110.7292 | 0 | 45.4725 | 0.8 | 1 | 14.062 | 59.5345 | -0.5 | 1.3605 | 1.0827 | 0.052857
2016-05-06 04:00 | 90.1867 | 75.6033 | 14.5833 | 64.8333 | 16.3974 | -103.3869 | 77.0009 | 12.9991 | -106.7032 | 97.4732 | 0 | 56.7025 | 0.8 | 1 | 18.0373 | 74.7398 | -0.3 | 2.0356 | 1.0804 | 0.066213
2016-05-06 05:00 | 110.0633 | 90.5767 | 19.4867 | 69.2711 | 16.4091 | -88.386 | 73.6616 | 16.3384 | -92.2327 | 83.7839 | 7.5006 | 67.9325 | 0.8 | 1 | 22.0127 | 97.4458 | -0.4 | 2.6452 | 1.0782 | 0.086157
2016-05-06 06:00 | 129.94 | 105.55 | 24.39 | 72.3176 | 16.4209 | -73.3851 | 70.2898 | 19.7102 | -77.5188 | 69.8286 | 24.9372 | 79.1625 | 0.8 | 1 | 25.988 | 130.0877 | 0.2 | 4.2652 | 1.0726 | 0.11441
2016-05-06 07:00 | 158.7567 | 119.5133 | 39.2433 | 100.8847 | 16.4326 | -58.3843 | 67.1082 | 22.8918 | -62.4526 | 55.7037 | 56.8458 | 89.635 | 0.8 | 1 | 31.7513 | 178.2321 | 0.3 | 5.8698 | 1.067 | 0.15594
2016-05-06 08:00 | 187.5733 | 133.4767 | 54.0967 | 124.9382 | 16.4443 | -43.3835 | 64.3427 | 25.6573 | -46.957 | 41.469 | 93.6179 | 100.1075 | 0.8 | 1 | 37.5147 | 231.2401 | 0.2 | 7.4263 | 1.0615 | 0.20128
2016-05-06 09:00 | 216.39 | 147.44 | 68.95 | 147.8776 | 16.4561 | -28.3826 | 62.2079 | 27.7921 | -31.0196 | 27.1651 | 131.5659 | 110.58 | 0.8 | 1 | 43.278 | 285.4239 | 0.5 | 9.4195 | 1.0545 | 0.24681
2016-05-06 10:00 | 215.0067 | 152.2233 | 62.7833 | 129.0328 | 16.4678 | -13.3818 | 60.8847 | 29.1153 | -14.717 | 12.8235 | 125.8146 | 114.1675 | 0.8 | 1 | 43.0013 | 282.9834 | 0.4 | 9.2432 | 1.0551 | 0.24484
2016-05-06 11:00 | 213.6233 | 157.0067 | 56.6167 | 114.9502 | 16.4795 | 1.619 | 60.4929 | 29.5071 | 1.784 | 1.6253 | 114.904 | 117.755 | 0.8 | 1 | 42.7247 | 275.3837 | 0.8 | 9.4057 | 1.0546 | 0.23814
2016-05-06 12:00 | 212.24 | 161.79 | 50.45 | 104.2868 | 16.4912 | 16.6199 | 61.0686 | 28.9314 | 18.262 | 15.9188 | 100.2875 | 121.3425 | 0.8 | 1 | 42.448 | 264.078 | 0.7 | 8.9524 | 1.0562 | 0.22871
2016-05-06 13:00 | 197.02 | 143.2167 | 53.8033 | 116.7425 | 16.5029 | 31.6207 | 62.5566 | 27.4434 | 34.5022 | 30.2522 | 100.8441 | 107.4125 | 0.8 | 1 | 39.404 | 247.6606 | 0.6 | 8.3394 | 1.0583 | 0.21492
2016-05-06 14:00 | 181.8 | 124.6433 | 57.1567 | 134.3485 | 16.5146 | 46.6215 | 64.8218 | 25.1782 | 50.3546 | 44.5391 | 95.7599 | 93.4825 | 0.8 | 1 | 36.36 | 225.6024 | 0.7 | 7.7501 | 1.0604 | 0.19616
2016-05-06 15:00 | 166.58 | 106.07 | 60.51 | 159.2858 | 16.5262 | 61.6223 | 67.6735 | 22.3265 | 65.7615 | 58.7466 | 82.6412 | 79.5525 | 0.8 | 1 | 33.316 | 195.5097 | 0.5 | 6.6097 | 1.0644 | 0.17064
2016-05-06 16:00 | 136.5267 | 88.6467 | 47.88 | 146.273 | 16.5379 | 76.6231 | 70.893 | 19.107 | 80.7506 | 72.8307 | 43.1793 | 66.485 | 0.8 | 1 | 27.3053 | 136.9696 | 0.9 | 5.1803 | 1.0694 | 0.12011
2016-05-06 17:00 | 106.4733 | 71.2233 | 35.25 | 129.8914 | 16.5496 | 91.6239 | 74.2536 | 15.7464 | 95.4075 | 86.7244 | 7.4219 | 53.4175 | 0.8 | 1 | 21.2947 | 82.1341 | 0.9 | 3.4667 | 1.0754 | 0.072426
2016-05-06 18:00 | 76.42 | 53.8 | 22.62 | 104.7939 | 16.5612 | 106.6247 | 77.5345 | 12.4655 | 109.8435 | 100.3184 | 0 | 40.35 | 0.8 | 1 | 15.284 | 55.634 | 0.7 | 2.4386 | 1.079 | 0.049222
2016-05-06 19:00 | 57.4733 | 41.53 | 15.9433 | 96.8932 | 16.5729 | 121.6255 | 80.5292 | 9.4708 | 124.1676 | 113.4202 | 0 | 31.1475 | 0.8 | 1 | 11.4947 | 42.6422 | 1 | 2.3326 | 1.0793 | 0.037741
2016-05-06 20:00 | 38.5267 | 29.26 | 9.2667 | 76.6037 | 16.5845 | 136.6263 | 83.052 | 6.948 | 138.4668 | 125.6644 | 0 | 21.945 | 0.8 | 1 | 7.7053 | 29.6503 | 0.7 | 1.6266 | 1.0818 | 0.026302
2016-05-06 21:00 | 19.58 | 16.99 | 2.59 | 29.3969 | 16.5961 | 151.6271 | 84.9454 | 5.0546 | 152.7941 | 136.3167 | 0 | 12.7425 | 0.8 | 1 | 3.916 | 16.6585 | 0.5 | 1.0206 | 1.0839 | 0.014806
2016-05-06 22:00 | 27.43 | 18.2 | 9.23 | 135.3294 | 16.6078 | 166.6279 | 86.0892 | 3.9108 | 167.165 | 143.932 | 0 | 13.65 | 0.8 | 1 | 5.486 | 19.136 | 0.4 | 0.998 | 1.084 | 0.01701
2016-05-06 23:00 | 35.28 | 19.41 | 15.87 | 253.3749 | 16.6194 | 181.6286 | 86.409 | 3.591 | -178.4363 | 146.3756 | 0 | 14.5575 | 0.8 | 1 | 7.056 | 21.6135 | 0.7 | 1.3754 | 1.0827 | 0.019189
2016-05-07 | 43.13 | 20.62 | 22.51 | 313.5671 | 16.631 | -163.3706 | 85.8834 | 4.1166 | -164.0429 | 142.6188 | 0 | 15.465 | 0.8 | 1 | 8.626 | 24.091 | 0.8 | 1.5528 | 1.0821 | 0.021376
2016-05-07 01:00 | 72.6933 | 30.7467 | 41.9467 | 441.3185 | 16.6426 | -148.3698 | 84.5459 | 5.4541 | -149.6852 | 134.1629 | 0 | 23.06 | 0.8 | 1 | 14.5387 | 37.5987 | 0.9 | 2.075 | 1.0802 | 0.033305
2016-05-07 02:00 | 102.2567 | 40.8733 | 61.3833 | 469.1293 | 16.6542 | -133.369 | 82.4816 | 7.5184 | -135.3728 | 123.0672 | 0 | 30.655 | 0.8 | 1 | 20.4513 | 51.1063 | 0.9 | 2.4971 | 1.0788 | 0.045208
2016-05-07 03:00 | 131.82 | 51 | 80.82 | 457.2591 | 16.6657 | -118.3683 | 79.8196 | 10.1804 | -121.0815 | 110.59 | 0 | 38.25 | 0.8 | 1 | 26.364 | 64.614 | 0.7 | 2.7192 | 1.078 | 0.057115
2016-05-07 04:00 | 176.8 | 64.4533 | 112.3467 | 489.2243 | 16.6773 | -103.3675 | 76.724 | 13.276 | -106.7495 | 97.359 | 0 | 48.34 | 0.8 | 1 | 35.36 | 83.7 | 1.2 | 3.8156 | 1.0741 | 0.073723
2016-05-07 05:00 | 221.78 | 77.9067 | 143.8733 | 503.1707 | 16.6889 | -88.3668 | 73.3853 | 16.6147 | -92.2826 | 83.6896 | 55.3057 | 58.43 | 0.8 | 1 | 44.356 | 158.0917 | 1.1 | 6.0404 | 1.0664 | 0.13824
2016-05-07 06:00 | 266.76 | 91.36 | 175.4 | 513.1688 | 16.7004 | -73.366 | 70.0136 | 19.9864 | -77.5682 | 69.7506 | 177.6111 | 68.52 | 0.8 | 1 | 53.352 | 299.4831 | 0.8 | 10.1588 | 1.0519 | 0.25833
2016-05-07 07:00 | 312.89 | 100.42 | 212.47 | 540.0295 | 16.712 | -58.3653 | 66.8312 | 23.1688 | -62.4966 | 55.6395 | 304.7915 | 75.315 | 0.8 | 1 | 62.578 | 442.6845 | 0.4 | 14.2339 | 1.0377 | 0.37668
2016-05-07 08:00 | 359.02 | 109.48 | 249.54 | 570.5624 | 16.7235 | -43.3646 | 64.0646 | 25.9354 | -46.9906 | 41.4168 | 427.8745 | 82.11 | 0.8 | 1 | 71.804 | 581.7885 | 0.4 | 18.5809 | 1.0225 | 0.48778
2016-05-07 09:00 | 405.15 | 118.54 | 286.61 | 609.0723 | 16.7351 | -28.3638 | 61.9288 | 28.0712 | -31.0377 | 27.1231 | 542.0921 | 88.905 | 0.8 | 1 | 81.03 | 712.0271 | 0.2 | 22.4508 | 1.0089 | 0.58907
2016-05-07 10:00 | 408.48 | 117.59 | 290.89 | 592.6578 | 16.7466 | -13.3631 | 60.6053 | 29.3947 | -14.7156 | 12.7884 | 577.9566 | 88.1925 | 0.8 | 1 | 81.696 | 747.8451 | 0.6 | 23.9702 | 1.0036 | 0.61544
2016-05-07 11:00 | 411.81 | 116.64 | 295.17 | 594.1951 | 16.7581 | 1.6376 | 60.2144 | 29.7856 | 1.8068 | 1.581 | 593.9689 | 87.48 | 0.8 | 1 | 82.362 | 763.8109 | 0.3 | 24.1691 | 1.0029 | 0.62815
2016-05-07 12:00 | 415.14 | 115.69 | 299.45 | 613.6548 | 16.7696 | 16.6384 | 60.7922 | 29.2078 | 18.3057 | 15.919 | 590.1215 | 86.7675 | 0.8 | 1 | 83.028 | 759.917 | 0.1 | 23.8474 | 1.004 | 0.62565
2016-05-07 13:00 | 313.6833 | 100.75 | 212.9333 | 457.8214 | 16.7811 | 31.6391 | 62.2832 | 27.7168 | 34.5638 | 30.2441 | 395.5061 | 75.5625 | 0.8 | 1 | 62.7367 | 533.8053 | 0.1 | 16.7814 | 1.0288 | 0.45031
2016-05-07 14:00 | 212.2267 | 85.81 | 126.4167 | 294.1977 | 16.7926 | 46.6398 | 64.5515 | 25.4485 | 50.4295 | 44.5202 | 209.7639 | 64.3575 | 0.8 | 1 | 42.4453 | 316.5667 | 0.7 | 10.5927 | 1.0504 | 0.27267
2016-05-07 15:00 | 110.77 | 70.87 | 39.9 | 103.8522 | 16.8041 | 61.6405 | 67.4059 | 22.5941 | 65.8445 | 58.7153 | 53.9295 | 53.1525 | 0.8 | 1 | 22.154 | 129.236 | 0.7 | 4.7386 | 1.0709 | 0.11349
2016-05-07 16:00 | 84.94 | 55.5867 | 29.3533 | 88.4891 | 16.8156 | 76.6412 | 70.627 | 19.373 | 80.8368 | 72.7848 | 26.1894 | 41.69 | 0.8 | 1 | 16.988 | 84.8674 | 0.8 | 3.4521 | 1.0754 | 0.07484
2016-05-07 17:00 | 59.11 | 40.3033 | 18.8067 | 68.1793 | 16.827 | 91.6419 | 73.9879 | 16.0121 | 95.4926 | 86.661 | 3.971 | 30.2275 | 0.8 | 1 | 11.822 | 46.0205 | 0.6 | 2.0381 | 1.0804 | 0.04077
2016-05-07 18:00 | 33.28 | 25.02 | 8.26 | 37.4784 | 16.8385 | 106.6426 | 77.2679 | 12.7321 | 109.9235 | 100.2334 | 0 | 18.765 | 0.8 | 1 | 6.656 | 25.421 | 0.4 | 1.1944 | 1.0833 | 0.022582
2016-05-07 19:00 | 25.1233 | 19.5667 | 5.5567 | 32.8475 | 16.85 | 121.6433 | 80.2607 | 9.7393 | 124.2393 | 113.3074 | 0 | 14.675 | 0.8 | 1 | 5.0247 | 19.6997 | 0.1 | 0.71561 | 1.085 | 0.017527
2016-05-07 20:00 | 16.9667 | 14.1133 | 2.8533 | 22.7067 | 16.8614 | 136.644 | 82.7811 | 7.2189 | 138.5272 | 125.5148 | 0 | 10.585 | 0.8 | 1 | 3.3933 | 13.9783 | -0.2 | 0.23682 | 1.0867 | 0.012456
2016-05-07 21:00 | 8.81 | 8.66 | 0.15 | 1.6154 | 16.8728 | 151.6447 | 84.6721 | 5.3279 | 152.8408 | 136.1191 | 0 | 6.495 | 0.8 | 1 | 1.762 | 8.257 | 0.2 | 0.45803 | 1.0859 | 0.0073523
2016-05-07 22:00 | 12.9133 | 12.09 | 0.82333 | 11.2791 | 16.8843 | 166.6453 | 85.8139 | 4.1861 | 167.1962 | 143.6818 | 0 | 9.0675 | 0.8 | 1 | 2.5827 | 11.6502 | -0.2 | 0.16407 | 1.0869 | 0.010384
2016-05-07 23:00 | 17.0167 | 15.52 | 1.4967 | 22.1897 | 16.8957 | 181.646 | 86.1325 | 3.8675 | -178.4215 | 146.0988 | 0 | 11.64 | 0.8 | 1 | 3.4033 | 15.0433 | -0.1 | 0.3701 | 1.0862 | 0.013399
2016-05-08 | 21.12 | 18.95 | 2.17 | 28.3284 | 16.9071 | -163.3533 | 85.6067 | 4.3933 | -164.0443 | 142.3647 | 0 | 14.2125 | 0.8 | 1 | 4.224 | 18.4365 | -0.3 | 0.27614 | 1.0865 | 0.016426
2016-05-08 01:00 | 38.1167 | 30.8433 | 7.2733 | 72.8487 | 16.9185 | -148.3527 | 84.2699 | 5.7301 | -149.7017 | 133.9538 | 0 | 23.1325 | 0.8 | 1 | 7.6233 | 30.7558 | -0.3 | 0.66112 | 1.0852 | 0.027368
2016-05-08 02:00 | 55.1133 | 42.7367 | 12.3767 | 91.276 | 16.9299 | -133.352 | 82.2069 | 7.7931 | -135.4026 | 122.8994 | 0 | 32.0525 | 0.8 | 1 | 11.0227 | 43.0752 | 0.1 | 1.4461 | 1.0824 | 0.038234
2016-05-08 03:00 | 72.11 | 54.63 | 17.48 | 96.3407 | 16.9413 | -118.3513 | 79.5464 | 10.4536 | -121.1218 | 110.4545 | 0 | 40.9725 | 0.8 | 1 | 14.422 | 55.3945 | -0.2 | 1.5311 | 1.0821 | 0.049155
2016-05-08 04:00 | 96.4367 | 69.54 | 26.8967 | 114.8161 | 16.9527 | -103.3507 | 76.4521 | 13.5479 | -106.7972 | 97.2486 | 0 | 52.155 | 0.8 | 1 | 19.2873 | 71.4423 | -0.1 | 2.1326 | 1.08 | 0.063271
2016-05-08 05:00 | 120.7633 | 84.45 | 36.3133 | 125.0174 | 16.9641 | -88.35 | 73.1141 | 16.8859 | -92.334 | 83.5991 | 13.9376 | 63.3375 | 0.8 | 1 | 24.1527 | 101.4278 | 0.1 | 3.2696 | 1.0761 | 0.089496
2016-05-08 06:00 | 145.09 | 99.36 | 45.73 | 132.0747 | 16.9754 | -73.3494 | 69.7423 | 20.2577 | -77.619 | 69.6764 | 45.8723 | 74.52 | 0.8 | 1 | 29.018 | 149.4103 | -0.1 | 4.5691 | 1.0715 | 0.13128
2016-05-08 07:00 | 167.93 | 125.4 | 42.53 | 106.9125 | 16.9868 | -58.3487 | 66.5592 | 23.4408 | -62.5423 | 55.5793 | 60.4339 | 94.05 | 0.8 | 1 | 33.586 | 188.0699 | -0.1 | 5.7772 | 1.0673 | 0.16459
2016-05-08 08:00 | 190.77 | 151.44 | 39.33 | 89.0542 | 16.9981 | -43.3481 | 63.7914 | 26.2086 | -47.026 | 41.369 | 66.8325 | 113.58 | 0.8 | 1 | 38.154 | 218.5665 | -0.2 | 6.6302 | 1.0643 | 0.19075
2016-05-08 09:00 | 213.61 | 177.48 | 36.13 | 76.0974 | 17.0095 | -28.3475 | 61.6545 | 28.3455 | -31.0579 | 27.0865 | 67.751 | 133.11 | 0.8 | 1 | 42.722 | 243.583 | 0 | 7.612 | 1.0609 | 0.21189
2016-05-08 10:00 | 215.0067 | 178.31 | 36.6967 | 74.1356 | 17.0208 | -13.3469 | 60.3307 | 29.6693 | -14.7167 | 12.7617 | 72.3043 | 133.7325 | 0.8 | 1 | 43.0013 | 249.0381 | 0 | 7.7824 | 1.0603 | 0.21652
2016-05-08 11:00 | 216.4033 | 179.14 | 37.2633 | 74.3929 | 17.0321 | 1.6538 | 59.9405 | 30.0595 | 1.827 | 1.5829 | 74.3645 | 134.355 | 0.8 | 1 | 43.2807 | 252.0002 | 0.2 | 8.075 | 1.0592 | 0.21888
2016-05-08 12:00 | 217.8 | 179.97 | 37.83 | 76.8722 | 17.0434 | 16.6544 | 60.5203 | 29.4797 | 18.3466 | 15.9216 | 73.9233 | 134.9775 | 0.8 | 1 | 43.56 | 252.4608 | 0.6 | 8.4894 | 1.0578 | 0.21898
2016-05-08 13:00 | 183.7467 | 153.1267 | 30.62 | 65.2524 | 17.0547 | 31.655 | 62.0141 | 27.9859 | 34.6223 | 30.2363 | 56.3752 | 114.845 | 0.8 | 1 | 36.7493 | 207.9695 | 0.4 | 6.899 | 1.0634 | 0.18134
2016-05-08 14:00 | 149.6933 | 126.2833 | 23.41 | 53.9539 | 17.066 | 46.6556 | 64.2854 | 25.7146 | 50.5011 | 44.5009 | 38.482 | 94.7125 | 0.8 | 1 | 29.9387 | 163.1332 | 0.9 | 5.9979 | 1.0665 | 0.14267
2016-05-08 15:00 | 115.64 | 99.44 | 16.2 | 41.7049 | 17.0773 | 61.6562 | 67.1423 | 22.8577 | 65.9241 | 58.6831 | 21.677 | 74.58 | 0.8 | 1 | 23.128 | 119.385 | 0.7 | 4.4308 | 1.072 | 0.10494
2016-05-08 16:00 | 106.39 | 83.81 | 22.58 | 67.1967 | 17.0886 | 76.6568 | 70.3649 | 19.6351 | 80.9196 | 72.7379 | 19.9401 | 62.8575 | 0.8 | 1 | 21.278 | 104.0756 | 0.6 | 3.8524 | 1.074 | 0.091659
2016-05-08 17:00 | 97.14 | 68.18 | 28.96 | 103.3439 | 17.0999 | 91.6574 | 73.7261 | 16.2739 | 95.5742 | 86.5967 | 6.1348 | 51.135 | 0.8 | 1 | 19.428 | 76.6978 | 0.4 | 2.7968 | 1.0777 | 0.06778
2016-05-08 18:00 | 87.89 | 52.55 | 35.34 | 157.1631 | 17.1112 | 106.658 | 77.0052 | 12.9948 | 110.0003 | 100.1476 | 0 | 39.4125 | 0.8 | 1 | 17.578 | 56.9905 | 0.5 | 2.281 | 1.0795 | 0.050448
2016-05-08 19:00 | 67.7033 | 41.25 | 26.4533 | 152.2831 | 17.1224 | 121.6586 | 79.9963 | 10.0037 | 124.3077 | 113.1941 | 0 | 30.9375 | 0.8 | 1 | 13.5407 | 44.4782 | 0.7 | 2.0899 | 1.0802 | 0.039397
2016-05-08 20:00 | 47.5167 | 29.95 | 17.5667 | 134.8416 | 17.1337 | 136.6592 | 82.5144 | 7.4856 | 138.5845 | 125.3653 | 0 | 22.4625 | 0.8 | 1 | 9.5033 | 31.9658 | 0.5 | 1.4989 | 1.0823 | 0.028368
2016-05-08 21:00 | 27.33 | 18.65 | 8.68 | 89.0004 | 17.1449 | 151.6598 | 84.4032 | 5.5968 | 152.8846 | 135.9227 | 0 | 13.9875 | 0.8 | 1 | 5.466 | 19.4535 | 0.3 | 0.90792 | 1.0843 | 0.017297
2016-05-08 22:00 | 25.7533 | 19.92 | 5.8333 | 75.0668 | 17.1562 | 166.6603 | 85.5431 | 4.4569 | 167.2248 | 143.4348 | 0 | 14.94 | 0.8 | 1 | 5.1507 | 20.0907 | 0.1 | 0.72783 | 1.085 | 0.017874
2016-05-08 23:00 | 24.1767 | 21.19 | 2.9867 | 41.3776 | 17.1674 | 181.6609 | 85.8608 | 4.1392 | -178.409 | 145.8268 | 0 | 15.8925 | 0.8 | 1 | 4.8353 | 20.7278 | 0.3 | 0.94774 | 1.0842 | 0.018428
2016-05-09 | 22.6 | 22.46 | 0.14 | 1.7214 | 17.1786 | -163.3385 | 85.3349 | 4.6651 | -164.0477 | 142.1156 | 0 | 16.845 | 0.8 | 1 | 4.52 | 21.365 | -0.3 | 0.36766 | 1.0862 | 0.01903
2016-05-09 01:00 | 37.72 | 35.5733 | 2.1467 | 20.5329 | 17.1898 | -148.338 | 83.9989 | 6.0011 | -149.7202 | 133.7493 | 0 | 26.68 | 0.8 | 1 | 7.544 | 34.224 | -0.4 | 0.6695 | 1.0852 | 0.030453
2016-05-09 02:00 | 52.84 | 48.6867 | 4.1533 | 29.6121 | 17.201 | -133.3374 | 81.9372 | 8.0628 | -135.434 | 122.7358 | 0 | 36.515 | 0.8 | 1 | 10.568 | 47.083 | -0.3 | 1.1713 | 1.0834 | 0.041828
2016-05-09 03:00 | 67.96 | 61.8 | 6.16 | 33.1113 | 17.2122 | -118.3368 | 79.2783 | 10.7217 | -121.1637 | 110.323 | 0 | 46.35 | 0.8 | 1 | 13.592 | 59.942 | -0.6 | 1.2732 | 1.083 | 0.053234
2016-05-09 04:00 | 95.2967 | 84.1067 | 11.19 | 46.8625 | 17.2234 | -103.3363 | 76.1852 | 13.8148 | -106.8463 | 97.1419 | 0 | 63.08 | 0.8 | 1 | 19.0593 | 82.1393 | -0.6 | 1.9669 | 1.0806 | 0.072784
2016-05-09 05:00 | 122.6333 | 106.4133 | 16.22 | 55.0003 | 17.2346 | -88.3358 | 72.848 | 17.152 | -92.3868 | 83.5122 | 6.2146 | 79.81 | 0.8 | 1 | 24.5267 | 110.5512 | -0.8 | 2.6547 | 1.0782 | 0.097742
2016-05-09 06:00 | 149.97 | 128.72 | 21.25 | 60.6108 | 17.2457 | -73.3352 | 69.4761 | 20.5239 | -77.6715 | 69.606 | 21.1212 | 96.54 | 0.8 | 1 | 29.994 | 147.6552 | -0.8 | 3.8142 | 1.0742 | 0.13006
2016-05-09 07:00 | 178.2233 | 150.0567 | 28.1667 | 70.0537 | 17.2569 | -58.3347 | 66.2922 | 23.7078 | -62.5897 | 55.5231 | 39.6556 | 112.5425 | 0.8 | 1 | 35.6447 | 187.8428 | -0.6 | 5.2701 | 1.0691 | 0.16467
2016-05-09 08:00 | 206.4767 | 171.3933 | 35.0833 | 78.6912 | 17.2681 | -43.3341 | 63.5232 | 26.4768 | -47.0633 | 41.3255 | 59.0948 | 128.545 | 0.8 | 1 | 41.2953 | 228.9351 | -0.6 | 6.5542 | 1.0646 | 0.19985
2016-05-09 09:00 | 234.73 | 192.73 | 42 | 87.6976 | 17.2792 | -28.3336 | 61.3852 | 28.6148 | -31.0803 | 27.055 | 78.1008 | 144.5475 | 0.8 | 1 | 46.946 | 269.5943 | -0.5 | 7.9248 | 1.0598 | 0.23428
2016-05-09 10:00 | 241.5267 | 198.21 | 43.3167 | 86.793 | 17.2903 | -13.3331 | 60.0608 | 29.9392 | -14.7202 | 12.7433 | 84.6551 | 148.6575 | 0.8 | 1 | 48.3053 | 281.6179 | 0.7 | 9.5006 | 1.0542 | 0.24345
2016-05-09 11:00 | 248.3233 | 203.69 | 44.6333 | 88.3897 | 17.3015 | 1.6674 | 59.6713 | 30.3287 | 1.8445 | 1.6282 | 88.354 | 152.7675 | 0.8 | 1 | 49.6647 | 290.7862 | 0.7 | 9.7871 | 1.0532 | 0.25114
2016-05-09 12:00 | 255.12 | 209.17 | 45.95 | 92.6088 | 17.3126 | 16.6679 | 60.2529 | 29.7471 | 18.3844 | 15.9265 | 89.054 | 156.8775 | 0.8 | 1 | 51.024 | 296.9555 | 0.4 | 9.6799 | 1.0536 | 0.25656
2016-05-09 13:00 | 234.7933 | 195.3 | 39.4933 | 83.4371 | 17.3237 | 31.6685 | 61.7493 | 28.2507 | 34.6777 | 30.2288 | 72.0915 | 146.475 | 0.8 | 1 | 46.9587 | 265.5252 | 0.5 | 8.7977 | 1.0567 | 0.23008
2016-05-09 14:00 | 214.4667 | 181.43 | 33.0367 | 75.4256 | 17.3348 | 46.669 | 64.0234 | 25.9766 | 50.5695 | 44.4811 | 53.8148 | 136.0725 | 0.8 | 1 | 42.8933 | 232.7806 | 1.4 | 8.6744 | 1.0571 | 0.20179
2016-05-09 15:00 | 194.14 | 167.56 | 26.58 | 67.7002 | 17.3459 | 61.6695 | 66.8828 | 23.1172 | 66.0004 | 58.6502 | 35.2218 | 125.67 | 0.8 | 1 | 38.828 | 199.7198 | 0.2 | 6.4412 | 1.065 | 0.17441
2016-05-09 16:00 | 154.83 | 134.3633 | 20.4667 | 60.1489 | 17.357 | 76.67 | 70.1069 | 19.8931 | 80.9991 | 72.6902 | 17.8966 | 100.7725 | 0.8 | 1 | 30.966 | 149.6351 | 0.5 | 5.1761 | 1.0694 | 0.13121
2016-05-09 17:00 | 115.52 | 101.1667 | 14.3533 | 50.4432 | 17.3681 | 91.6705 | 73.4684 | 16.5316 | 95.6526 | 86.5316 | 3.0517 | 75.875 | 0.8 | 1 | 23.104 | 102.0307 | 0.9 | 4.0885 | 1.0732 | 0.089789
2016-05-09 18:00 | 76.21 | 67.97 | 8.24 | 35.9423 | 17.3791 | 106.6709 | 76.7467 | 13.2533 | 110.0737 | 100.0612 | 0 | 50.9775 | 0.8 | 1 | 15.242 | 66.2195 | 0.2 | 2.2694 | 1.0796 | 0.05862
2016-05-09 19:00 | 60.87 | 54.8867 | 5.9833 | 33.5798 | 17.3902 | 121.6714 | 79.7361 | 10.2639 | 124.373 | 113.0804 | 0 | 41.165 | 0.8 | 1 | 12.174 | 53.339 | 0.5 | 2.1668 | 1.0799 | 0.047233
2016-05-09 20:00 | 45.53 | 41.8033 | 3.7267 | 27.6428 | 17.4012 | 136.6719 | 82.2521 | 7.7479 | 138.6388 | 125.216 | 0 | 31.3525 | 0.8 | 1 | 9.106 | 40.4585 | -1 | 0.26433 | 1.0866 | 0.036048
2016-05-09 21:00 | 30.19 | 28.72 | 1.47 | 14.3947 | 17.4123 | 151.6724 | 84.1387 | 5.8613 | 152.9255 | 135.7277 | 0 | 21.54 | 0.8 | 1 | 6.038 | 27.578 | -1.7 | -0.83819 | 1.0904 | 0.024659
2016-05-09 22:00 | 29.8167 | 28.4767 | 1.34 | 16.2741 | 17.4233 | 166.6729 | 85.277 | 4.723 | 167.2508 | 143.1909 | 0 | 21.3575 | 0.8 | 1 | 5.9633 | 27.3208 | -2.2 | -1.3462 | 1.0922 | 0.024469
2016-05-09 23:00 | 29.4433 | 28.2333 | 1.21 | 15.7494 | 17.4344 | 181.6733 | 85.5937 | 4.4063 | -178.3988 | 145.5595 | 0 | 21.175 | 0.8 | 1 | 5.8887 | 27.0637 | -2.4 | -1.5543 | 1.0929 | 0.024255
2016-05-10 | 29.07 | 27.99 | 1.08 | 12.5619 | 17.4454 | -163.3262 | 85.0679 | 4.9321 | -164.0533 | 141.8715 | 0 | 20.9925 | 0.8 | 1 | 5.814 | 26.8065 | -2.1 | -1.2623 | 1.0919 | 0.024002
2016-05-10 01:00 | 42.8333 | 39.49 | 3.3433 | 30.6265 | 17.4564 | -148.3257 | 83.7328 | 6.2672 | -149.7404 | 133.5493 | 0 | 29.6175 | 0.8 | 1 | 8.5667 | 38.1842 | -2 | -0.80674 | 1.0903 | 0.034139
2016-05-10 02:00 | 56.5967 | 50.99 | 5.6067 | 38.7124 | 17.4674 | -133.3253 | 81.6726 | 8.3274 | -135.4671 | 122.5762 | 0 | 38.2425 | 0.8 | 1 | 11.3193 | 49.5618 | -1.6 | -0.051193 | 1.0877 | 0.044204
2016-05-10 03:00 | 70.36 | 62.49 | 7.87 | 41.302 | 17.4784 | -118.3248 | 79.0153 | 10.9847 | -121.207 | 110.1952 | 0 | 46.8675 | 0.8 | 1 | 14.072 | 60.9395 | -1 | 0.90436 | 1.0843 | 0.054185
2016-05-10 04:00 | 104 | 88.7833 | 15.2167 | 62.5645 | 17.4894 | -103.3244 | 75.9236 | 14.0764 | -106.8969 | 97.0389 | 0 | 66.5875 | 0.8 | 1 | 20.8 | 87.3875 | -1.1 | 1.6309 | 1.0818 | 0.077519
2016-05-10 05:00 | 137.64 | 115.0767 | 22.5633 | 75.3982 | 17.5003 | -88.3239 | 72.5871 | 17.4129 | -92.4411 | 83.4291 | 8.628 | 86.3075 | 0.8 | 1 | 27.528 | 122.4635 | -1 | 2.827 | 1.0776 | 0.10821
2016-05-10 06:00 | 171.28 | 141.37 | 29.91 | 84.2868 | 17.5113 | -73.3235 | 69.2151 | 20.7849 | -77.7254 | 69.5394 | 29.4635 | 106.0275 | 0.8 | 1 | 34.256 | 169.747 | -1 | 4.3046 | 1.0724 | 0.14927
2016-05-10 07:00 | 226.3433 | 150.8133 | 75.53 | 185.9193 | 17.5223 | -58.3231 | 66.0304 | 23.9696 | -62.6387 | 55.4708 | 105.3839 | 113.11 | 0.8 | 1 | 45.2687 | 263.7625 | -1.1 | 7.1426 | 1.0625 | 0.2298
2016-05-10 08:00 | 281.4067 | 160.2567 | 121.15 | 269.2577 | 17.5332 | -43.3226 | 63.2601 | 26.7399 | -47.1026 | 41.2863 | 202.3261 | 120.1925 | 0.8 | 1 | 56.2813 | 378.8 | -0.6 | 11.2375 | 1.0482 | 0.32558
2016-05-10 09:00 | 336.47 | 169.7 | 166.77 | 345.3058 | 17.5442 | -28.3222 | 61.1209 | 28.8791 | -31.1049 | 27.0287 | 307.591 | 127.275 | 0.8 | 1 | 67.294 | 502.16 | -0.7 | 14.9925 | 1.035 | 0.42619
2016-05-10 10:00 | 344.96 | 167.4133 | 177.5467 | 352.9179 | 17.5551 | -13.3218 | 59.7959 | 30.2041 | -14.7261 | 12.7328 | 344.2391 | 125.56 | 0.8 | 1 | 68.992 | 538.7911 | 0.4 | 17.2372 | 1.0272 | 0.45381
2016-05-10 11:00 | 353.45 | 165.1267 | 188.3233 | 370.0307 | 17.566 | 1.6786 | 59.4068 | 30.5932 | 1.8592 | 1.7114 | 369.8657 | 123.845 | 0.8 | 1 | 70.69 | 564.4007 | 0.2 | 17.8375 | 1.0251 | 0.47441
2016-05-10 12:00 | 361.94 | 162.84 | 199.1 | 398.0798 | 17.577 | 16.679 | 59.99 | 30.01 | 18.4194 | 15.9335 | 382.7859 | 122.13 | 0.8 | 1 | 72.388 | 577.3039 | 0 | 18.0407 | 1.0244 | 0.48492
2016-05-10 13:00 | 307.4567 | 156.3467 | 151.11 | 316.5745 | 17.5879 | 31.6794 | 61.4889 | 28.5111 | 34.7299 | 30.2213 | 273.5482 | 117.26 | 0.8 | 1 | 61.4913 | 452.2996 | -0.1 | 14.0344 | 1.0384 | 0.38512
2016-05-10 14:00 | 252.9733 | 149.8533 | 103.12 | 233.2814 | 17.5988 | 46.6798 | 63.7658 | 26.2342 | 50.6345 | 44.4608 | 166.5 | 112.39 | 0.8 | 1 | 50.5947 | 329.4847 | -0.3 | 9.9964 | 1.0525 | 0.28437
2016-05-10 15:00 | 198.49 | 143.36 | 55.13 | 138.9688 | 17.6097 | 61.6802 | 66.6275 | 23.3725 | 66.0734 | 58.6165 | 72.37 | 107.52 | 0.8 | 1 | 39.698 | 219.588 | -0.5 | 6.3621 | 1.0652 | 0.19181
2016-05-10 16:00 | 164.7467 | 117.7167 | 47.03 | 136.5442 | 17.6206 | 76.6806 | 69.853 | 20.147 | 81.0751 | 72.6415 | 40.7378 | 88.2875 | 0.8 | 1 | 32.9493 | 161.9746 | 0 | 5.0617 | 1.0698 | 0.14209
2016-05-10 17:00 | 131.0033 | 92.0733 | 38.93 | 134.8062 | 17.6314 | 91.681 | 73.2148 | 16.7852 | 95.7275 | 86.4656 | 8.3106 | 69.055 | 0.8 | 1 | 26.2007 | 103.5662 | 0.3 | 3.5364 | 1.0751 | 0.091304
2016-05-10 18:00 | 97.26 | 66.43 | 30.83 | 131.9914 | 17.6423 | 106.6814 | 76.4923 | 13.5077 | 110.1437 | 99.974 | 0 | 49.8225 | 0.8 | 1 | 19.452 | 69.2745 | -0.4 | 1.7648 | 1.0813 | 0.061425
2016-05-10 19:00 | 76.7533 | 52.3167 | 24.4367 | 133.8429 | 17.6532 | 121.6818 | 79.4801 | 10.5199 | 124.435 | 112.9665 | 0 | 39.2375 | 0.8 | 1 | 15.3507 | 54.5882 | -0.7 | 1.0059 | 1.084 | 0.048521
2016-05-10 20:00 | 56.2467 | 38.2033 | 18.0433 | 129.5509 | 17.664 | 136.6822 | 81.994 | 8.006 | 138.69 | 125.0671 | 0 | 28.6525 | 0.8 | 1 | 11.2493 | 39.9018 | -0.3 | 0.94693 | 1.0842 | 0.035474
2016-05-10 21:00 | 35.74 | 24.09 | 11.65 | 109.2518 | 17.6749 | 151.6826 | 83.8787 | 6.1213 | 152.9636 | 135.5342 | 0 | 18.0675 | 0.8 | 1 | 7.148 | 25.2155 | -0.2 | 0.58798 | 1.0854 | 0.022443
2016-05-10 22:00 | 29.4333 | 21.6667 | 7.7667 | 89.3879 | 17.6857 | 166.6829 | 85.0154 | 4.9846 | 167.2741 | 142.9503 | 0 | 16.25 | 0.8 | 1 | 5.8867 | 22.1367 | -0.4 | 0.29177 | 1.0865 | 0.019722
2016-05-10 23:00 | 23.1267 | 19.2433 | 3.8833 | 47.7122 | 17.6965 | 181.6833 | 85.3315 | 4.6685 | -178.391 | 145.2972 | 0 | 14.4325 | 0.8 | 1 | 4.6253 | 19.0578 | -0.3 | 0.29556 | 1.0865 | 0.016979
2016-05-11 | 16.82 | 16.82 | 0 | 0 | 17.7073 | -163.3164 | 84.8059 | 5.1941 | -164.061 | 141.6326 | 0 | 12.615 | 0.8 | 1 | 3.364 | 15.979 | -0.2 | 0.29934 | 1.0865 | 0.014236
2016-05-11 01:00 | 25.3367 | 25.3367 | 0 | 0 | 17.7181 | -148.316 | 83.4718 | 6.5282 | -149.7625 | 133.3538 | 0 | 19.0025 | 0.8 | 1 | 5.0673 | 24.0698 | 0.4 | 1.1522 | 1.0835 | 0.021385
2016-05-11 02:00 | 33.8533 | 33.8533 | 0 | 0 | 17.7289 | -133.3156 | 81.4132 | 8.5868 | -135.5018 | 122.4208 | 0 | 25.39 | 0.8 | 1 | 6.7707 | 32.1607 | 1.3 | 2.305 | 1.0794 | 0.028467
2016-05-11 03:00 | 42.37 | 42.37 | 0 | 0 | 17.7397 | -118.3153 | 78.7575 | 11.2425 | -121.2518 | 110.0714 | 0 | 31.7775 | 0.8 | 1 | 8.474 | 40.2515 | 1.2 | 2.4579 | 1.0789 | 0.03561
2016-05-11 04:00 | 50.05 | 49.56 | 0.49 | 1.9794 | 17.7505 | -103.315 | 75.6672 | 14.3328 | -106.9488 | 96.9398 | 0 | 37.17 | 0.8 | 1 | 10.01 | 47.18 | 1.4 | 2.8744 | 1.0774 | 0.041684
2016-05-11 05:00 | 57.73 | 56.75 | 0.98 | 3.2289 | 17.7613 | -88.3146 | 72.3314 | 17.6686 | -92.4967 | 83.3497 | 0.37393 | 42.5625 | 0.8 | 1 | 11.546 | 54.4824 | 1.5 | 3.2026 | 1.0763 | 0.048084
2016-05-11 06:00 | 65.41 | 63.94 | 1.47 | 4.0944 | 17.7721 | -73.3143 | 68.9594 | 21.0406 | -77.7808 | 69.4766 | 1.4354 | 47.955 | 0.8 | 1 | 13.082 | 62.4724 | 1.6 | 3.5523 | 1.0751 | 0.055073
2016-05-11 07:00 | 67.7 | 66.72 | 0.98 | 2.3883 | 17.7828 | -58.3139 | 65.7739 | 24.2261 | -62.6894 | 55.4224 | 1.3554 | 50.04 | 0.8 | 1 | 13.54 | 64.9354 | 1.5 | 3.5292 | 1.0751 | 0.057248
2016-05-11 08:00 | 69.99 | 69.5 | 0.49 | 1.0794 | 17.7936 | -43.3136 | 63.0022 | 26.9978 | -47.1437 | 41.2513 | 0.81152 | 52.125 | 0.8 | 1 | 13.998 | 66.9345 | 1.3 | 3.3917 | 1.0756 | 0.059037
2016-05-11 09:00 | 72.28 | 72.28 | 0 | 0 | 17.8043 | -28.3133 | 60.8617 | 29.1383 | -31.1316 | 27.0074 | 0 | 54.21 | 0.8 | 1 | 14.456 | 68.666 | 1 | 3.1458 | 1.0765 | 0.060613
2016-05-11 10:00 | 75.1567 | 75.1567 | 0 | 0 | 17.815 | -13.313 | 59.5359 | 30.4641 | -14.7345 | 12.73 | 0 | 56.3675 | 0.8 | 1 | 15.0313 | 71.3988 | 1 | 3.2312 | 1.0762 | 0.063008
2016-05-11 11:00 | 78.0333 | 78.0333 | 0 | 0 | 17.8258 | 1.6873 | 59.1471 | 30.8529 | 1.8712 | 1.825 | 0 | 58.525 | 0.8 | 1 | 15.6067 | 74.1317 | 0.9 | 3.2166 | 1.0762 | 0.065423
2016-05-11 12:00 | 80.91 | 80.91 | 0 | 0 | 17.8365 | 16.6876 | 59.7318 | 30.2682 | 18.4513 | 15.9424 | 0 | 60.6825 | 0.8 | 1 | 16.182 | 76.8645 | 1.5 | 3.902 | 1.0738 | 0.067683
2016-05-11 13:00 | 88.7667 | 88.7667 | 0 | 0 | 17.8472 | 31.688 | 61.2331 | 28.7669 | 34.7789 | 30.2138 | 0 | 66.575 | 0.8 | 1 | 17.7533 | 84.3283 | 1.4 | 4.0353 | 1.0734 | 0.074223
2016-05-11 14:00 | 96.6233 | 96.6233 | 0 | 0 | 17.8579 | 46.6883 | 63.5125 | 26.4875 | 50.6963 | 44.4398 | 0 | 72.4675 | 0.8 | 1 | 19.3247 | 91.7922 | 1.8 | 4.6685 | 1.0712 | 0.080626
2016-05-11 15:00 | 104.48 | 104.48 | 0 | 0 | 17.8686 | 61.6886 | 66.3764 | 23.6236 | 66.1429 | 58.5819 | 0 | 78.36 | 0.8 | 1 | 20.896 | 99.256 | 1.8 | 4.9017 | 1.0703 | 0.087115
2016-05-11 16:00 | 70.8467 | 70.8467 | 0 | 0 | 17.8793 | 76.6888 | 69.6033 | 20.3967 | 81.1478 | 72.592 | 0 | 53.135 | 0.8 | 1 | 14.1693 | 67.3043 | 2 | 4.1033 | 1.0731 | 0.059226
2016-05-11 17:00 | 37.2133 | 37.2133 | 0 | 0 | 17.8899 | 91.6891 | 72.9654 | 17.0346 | 95.799 | 86.3988 | 0 | 27.91 | 0.8 | 1 | 7.4427 | 35.3527 | 1 | 2.1048 | 1.0801 | 0.031312
2016-05-11 18:00 | 3.58 | 3.58 | 0 | 0 | 17.9006 | 106.6894 | 76.2422 | 13.7578 | 110.2105 | 99.8862 | 0 | 2.685 | 0.8 | 1 | 0.716 | 3.401 | 0.8 | 0.90628 | 1.0843 | 0.003024
2016-05-11 19:00 | 3.1233 | 3.1233 | 0 | 0 | 17.9113 | 121.6897 | 79.2284 | 10.7716 | 124.4938 | 112.8523 | 0 | 2.3425 | 0.8 | 1 | 0.62467 | 2.9672 | 0.9 | 0.99272 | 1.084 | 0.0026375
2016-05-11 20:00 | 2.6667 | 2.6667 | 0 | 0 | 17.9219 | 136.69 | 81.7405 | 8.2595 | 138.7381 | 124.9186 | 0 | 2 | 0.8 | 1 | 0.53333 | 2.5333 | 0.6 | 0.67917 | 1.0851 | 0.0022542
2016-05-11 21:00 | 2.21 | 2.21 | 0 | 0 | 17.9325 | 151.6902 | 83.6233 | 6.3767 | 152.9988 | 135.3424 | 0 | 1.6575 | 0.8 | 1 | 0.442 | 2.0995 | 0.8 | 0.86561 | 1.0845 | 0.001867
2016-05-11 22:00 | 11.8133 | 11.8133 | 0 | 0 | 17.9432 | 166.6905 | 84.7587 | 5.2413 | 167.2949 | 142.7132 | 0 | 8.86 | 0.8 | 1 | 2.3627 | 11.2227 | 1.1 | 1.4507 | 1.0824 | 0.0099611
2016-05-11 23:00 | 21.4167 | 21.4167 | 0 | 0 | 17.9538 | 181.6908 | 85.0742 | 4.9258 | -178.3856 | 145.0399 | 0 | 16.0625 | 0.8 | 1 | 4.2833 | 20.3458 | 1.5 | 2.1358 | 1.08 | 0.018019
2016-05-12 | 31.02 | 31.02 | 0 | 0 | 17.9644 | -163.309 | 84.5489 | 5.4511 | -164.0708 | 141.3988 | 0 | 23.265 | 0.8 | 1 | 6.204 | 29.469 | 1.8 | 2.7209 | 1.078 | 0.026049
2016-05-12 01:00 | 45.3633 | 43.1367 | 2.2267 | 18.8498 | 17.975 | -148.3087 | 83.216 | 6.784 | -149.7865 | 133.1631 | 0 | 32.3525 | 0.8 | 1 | 9.0727 | 41.4252 | 1.8 | 3.0945 | 1.0767 | 0.036573
2016-05-12 02:00 | 59.7067 | 55.2533 | 4.4533 | 28.9753 | 17.9856 | -133.3085 | 81.1589 | 8.8411 | -135.5381 | 122.2697 | 0 | 41.44 | 0.8 | 1 | 11.9413 | 53.3813 | 2.4 | 4.0682 | 1.0733 | 0.04698
2016-05-12 03:00 | 74.05 | 67.37 | 6.68 | 33.5202 | 17.9962 | -118.3082 | 78.505 | 11.495 | -121.2981 | 109.9516 | 0 | 50.5275 | 0.8 | 1 | 14.81 | 65.3375 | 2.7 | 4.7418 | 1.0709 | 0.057376
2016-05-12 04:00 | 96.0567 | 89.6133 | 6.4433 | 25.5893 | 18.0068 | -103.308 | 75.4161 | 14.5839 | -107.0021 | 96.8444 | 0 | 67.21 | 0.8 | 1 | 19.2113 | 86.4213 | 2.7 | 5.4007 | 1.0686 | 0.075727
2016-05-12 05:00 | 118.0633 | 111.8567 | 6.2067 | 20.1731 | 18.0173 | -88.3077 | 72.0811 | 17.9189 | -92.5537 | 83.274 | 2.3627 | 83.8925 | 0.8 | 1 | 23.6127 | 109.8679 | 3 | 6.4334 | 1.065 | 0.095946
2016-05-12 06:00 | 140.07 | 134.1 | 5.97 | 16.4416 | 18.0279 | -73.3075 | 68.7091 | 21.2909 | -77.8376 | 69.4175 | 5.7801 | 100.575 | 0.8 | 1 | 28.014 | 134.3691 | 3.1 | 7.299 | 1.062 | 0.11701
2016-05-12 07:00 | 163.6733 | 157.36 | 6.3133 | 15.2373 | 18.0385 | -58.3073 | 65.5226 | 24.4774 | -62.7417 | 55.3779 | 8.6572 | 118.02 | 0.8 | 1 | 32.7347 | 159.4119 | 3 | 7.9816 | 1.0596 | 0.1385
2016-05-12 08:00 | 187.2767 | 180.62 | 6.6567 | 14.538 | 18.049 | -43.3071 | 62.7496 | 27.2504 | -47.1867 | 41.2205 | 10.9352 | 135.465 | 0.8 | 1 | 37.4553 | 183.8555 | 2.8 | 8.5455 | 1.0576 | 0.15944
2016-05-12 09:00 | 210.88 | 203.88 | 7 | 14.2628 | 18.0595 | -28.3068 | 60.6076 | 29.3924 | -31.1605 | 26.9909 | 12.7093 | 152.91 | 0.8 | 1 | 42.176 | 207.7953 | 3.5 | 9.9936 | 1.0525 | 0.17934
2016-05-12 10:00 | 227.5367 | 214.8033 | 12.7333 | 24.9269 | 18.0701 | -13.3066 | 59.281 | 30.719 | -14.7454 | 12.7345 | 24.3137 | 161.1025 | 0.8 | 1 | 45.5073 | 230.9235 | 3.2 | 10.4164 | 1.051 | 0.19902
2016-05-12 11:00 | 244.1933 | 225.7267 | 18.4667 | 35.7433 | 18.0806 | 1.6936 | 58.8924 | 31.1076 | 1.8804 | 1.9619 | 35.7223 | 169.295 | 0.8 | 1 | 48.8387 | 253.856 | 3.1 | 11.033 | 1.0489 | 0.21834
2016-05-12 12:00 | 260.85 | 236.65 | 24.2 | 47.6506 | 18.0911 | 16.6938 | 59.4784 | 30.5216 | 18.4802 | 15.9528 | 45.8155 | 177.4875 | 0.8 | 1 | 52.17 | 275.473 | 2.6 | 11.2085 | 1.0483 | 0.23679
2016-05-12 13:00 | 221.79 | 203.5767 | 18.2133 | 37.5465 | 18.1016 | 31.694 | 60.9818 | 29.0182 | 34.8248 | 30.2061 | 32.4485 | 152.6825 | 0.8 | 1 | 44.358 | 229.489 | 3.7 | 10.8715 | 1.0494 | 0.19749
2016-05-12 14:00 | 182.73 | 170.5033 | 12.2267 | 27.1773 | 18.1121 | 46.6942 | 63.2637 | 26.7363 | 50.7547 | 44.4182 | 19.4114 | 127.8775 | 0.8 | 1 | 36.546 | 183.8349 | 3.2 | 8.9448 | 1.0562 | 0.15922
2016-05-12 15:00 | 143.67 | 137.43 | 6.24 | 15.4201 | 18.1226 | 61.6944 | 66.1297 | 23.8703 | 66.209 | 58.5465 | 8.0463 | 103.0725 | 0.8 | 1 | 28.734 | 139.8528 | 3.1 | 7.4704 | 1.0614 | 0.12172
2016-05-12 16:00 | 124.9333 | 118.2267 | 6.7067 | 19.0244 | 18.133 | 76.6946 | 69.3578 | 20.6422 | 81.2169 | 72.5416 | 5.7075 | 88.67 | 0.8 | 1 | 24.9867 | 119.3642 | 2.8 | 6.5301 | 1.0646 | 0.10421
2016-05-12 17:00 | 106.1967 | 99.0233 | 7.1733 | 24.1496 | 18.1435 | 91.6948 | 72.7202 | 17.2798 | 95.867 | 86.3312 | 1.5453 | 74.2675 | 0.8 | 1 | 21.2393 | 97.0521 | 2 | 5.0329 | 1.0699 | 0.085144
2016-05-12 18:00 | 87.46 | 79.82 | 7.64 | 31.5723 | 18.154 | 106.695 | 75.9963 | 14.0037 | 110.2738 | 99.7979 | 0 | 59.865 | 0.8 | 1 | 17.492 | 77.357 | 2 | 4.4174 | 1.072 | 0.068002
2016-05-12 19:00 | 70.39 | 63.9467 | 6.4433 | 33.7115 | 18.1644 | 121.6951 | 78.9812 | 11.0188 | 124.5493 | 112.7379 | 0 | 47.96 | 0.8 | 1 | 14.078 | 62.038 | 1.5 | 3.4387 | 1.0755 | 0.05471
2016-05-12 20:00 | 53.32 | 48.0733 | 5.2467 | 35.4607 | 18.1748 | 136.6953 | 81.4914 | 8.5086 | 138.7831 | 124.7707 | 0 | 36.055 | 0.8 | 1 | 10.664 | 46.719 | 1.6 | 3.06 | 1.0768 | 0.041251
2016-05-12 21:00 | 36.25 | 32.2 | 4.05 | 35.0913 | 18.1853 | 151.6955 | 83.3725 | 6.6275 | 153.0312 | 135.1523 | 0 | 24.15 | 0.8 | 1 | 7.25 | 31.4 | 0.9 | 1.8813 | 1.0809 | 0.027831
2016-05-12 22:00 | 44.8467 | 28.81 | 16.0367 | 167.5229 | 18.1957 | 166.6956 | 84.5068 | 5.4932 | 167.313 | 142.4796 | 0 | 21.6075 | 0.8 | 1 | 8.9693 | 30.5768 | 1 | 1.9555 | 1.0807 | 0.027095
2016-05-12 23:00 | 53.4433 | 25.42 | 28.0233 | 310.4973 | 18.2061 | 181.6958 | 84.8218 | 5.1782 | -178.3825 | 144.7877 | 0 | 19.065 | 0.8 | 1 | 10.6887 | 29.7537 | 1.2 | 2.1298 | 1.08 | 0.026351
2016-05-13 | 62.04 | 22.03 | 40.01 | 402.6333 | 18.2165 | -163.304 | 84.2971 | 5.7029 | -164.0826 | 141.1703 | 0 | 16.5225 | 0.8 | 1 | 12.408 | 28.9305 | 0.9 | 1.8041 | 1.0812 | 0.025649
2016-05-13 01:00 | 94.88 | 27.9733 | 66.9067 | 546.3117 | 18.2269 | -148.3039 | 82.9653 | 7.0347 | -149.8122 | 132.9771 | 0 | 20.98 | 0.8 | 1 | 18.976 | 39.956 | 1.1 | 2.3486 | 1.0793 | 0.035361
2016-05-13 02:00 | 127.72 | 33.9167 | 93.8033 | 593.746 | 18.2373 | -133.3037 | 80.91 | 9.09 | -135.5759 | 122.1229 | 0 | 25.4375 | 0.8 | 1 | 25.544 | 50.9815 | 1.4 | 2.9932 | 1.077 | 0.045025
2016-05-13 03:00 | 160.56 | 39.86 | 120.7 | 593.097 | 18.2477 | -118.3036 | 78.2578 | 11.7422 | -121.3457 | 109.8358 | 0 | 29.895 | 0.8 | 1 | 32.112 | 62.007 | 1.2 | 3.1377 | 1.0765 | 0.054736
2016-05-13 04:00 | 209.05 | 50.6033 | 158.4467 | 619.065 | 18.258 | -103.3035 | 75.1704 | 14.8296 | -107.0567 | 96.7529 | 0 | 37.9525 | 0.8 | 1 | 41.81 | 79.7625 | 1.2 | 3.6926 | 1.0746 | 0.070283
2016-05-13 05:00 | 257.54 | 61.3467 | 196.1933 | 629.3613 | 18.2684 | -88.3033 | 71.8362 | 18.1638 | -92.612 | 83.2021 | 74.4956 | 46.01 | 0.8 | 1 | 51.508 | 172.0136 | 1.1 | 6.4754 | 1.0648 | 0.1502
2016-05-13 06:00 | 306.03 | 72.09 | 233.94 | 637.2926 | 18.2787 | -73.3032 | 68.4641 | 21.5359 | -77.8958 | 69.3621 | 224.6208 | 54.0675 | 0.8 | 1 | 61.206 | 339.8943 | 0.8 | 11.4217 | 1.0475 | 0.29196
2016-05-13 07:00 | 246.1467 | 89.0867 | 157.06 | 375.5306 | 18.2891 | -58.3031 | 65.2768 | 24.7232 | -62.7956 | 55.3372 | 213.5812 | 66.815 | 0.8 | 1 | 49.2293 | 329.6256 | 0.8 | 11.1008 | 1.0486 | 0.28344
2016-05-13 08:00 | 186.2633 | 106.0833 | 80.18 | 173.6578 | 18.2994 | -43.303 | 62.5023 | 27.4977 | -47.2315 | 41.1938 | 130.6752 | 79.5625 | 0.8 | 1 | 37.2527 | 247.4904 | 1.4 | 9.1341 | 1.0555 | 0.21421
2016-05-13 09:00 | 126.38 | 123.08 | 3.3 | 6.6725 | 18.3097 | -28.3028 | 60.3588 | 29.6412 | -31.1915 | 26.9792 | 5.9463 | 92.31 | 0.8 | 1 | 25.276 | 123.5323 | 1.1 | 4.9604 | 1.0701 | 0.1084
2016-05-13 10:00 | 126.4467 | 124.1867 | 2.26 | 4.392 | 18.3201 | -13.3027 | 59.0312 | 30.9688 | -14.7587 | 12.746 | 4.2838 | 93.14 | 0.8 | 1 | 25.2893 | 122.7131 | 1.2 | 5.0348 | 1.0699 | 0.10766
2016-05-13 11:00 | 126.5133 | 125.2933 | 1.22 | 2.3445 | 18.3304 | 1.6974 | 58.6426 | 31.3574 | 1.8869 | 2.1156 | 2.3429 | 93.97 | 0.8 | 1 | 25.3027 | 121.6155 | 0.9 | 4.7005 | 1.071 | 0.10681
2016-05-13 12:00 | 126.58 | 126.4 | 0.18 | 0.35184 | 18.3407 | 16.6975 | 59.2298 | 30.7702 | 18.5061 | 15.9647 | 0.33827 | 94.8 | 0.8 | 1 | 25.316 | 120.4543 | 0.8 | 4.5642 | 1.0715 | 0.10584
2016-05-13 13:00 | 126.88 | 115.8033 | 11.0767 | 22.6588 | 18.351 | 31.6976 | 60.7352 | 29.2648 | 34.8674 | 30.1983 | 19.5837 | 86.8525 | 0.8 | 1 | 25.376 | 131.8122 | 1.4 | 5.5191 | 1.0682 | 0.11546
2016-05-13 14:00 | 127.18 | 105.2067 | 21.9733 | 48.4326 | 18.3612 | 46.6977 | 63.0194 | 26.9806 | 50.8097 | 44.3959 | 34.6062 | 78.905 | 0.8 | 1 | 25.436 | 138.9472 | 1.6 | 5.9421 | 1.0667 | 0.12154
2016-05-13 15:00 | 127.48 | 94.61 | 32.87 | 80.4589 | 18.3715 | 61.6978 | 65.8874 | 24.1126 | 66.2717 | 58.5102 | 42.0274 | 70.9575 | 0.8 | 1 | 25.496 | 138.4809 | 2 | 6.3275 | 1.0654 | 0.12098
2016-05-13 16:00 | 99.12 | 74.3 | 24.82 | 69.6283 | 18.3818 | 76.6979 | 69.1168 | 20.8832 | 81.2826 | 72.4904 | 20.9487 | 55.725 | 0.8 | 1 | 19.824 | 96.4977 | 1.7 | 4.7156 | 1.071 | 0.084746
2016-05-13 17:00 | 70.76 | 53.99 | 16.77 | 55.7054 | 18.392 | 91.698 | 72.4794 | 17.5206 | 95.9316 | 86.2628 | 3.6308 | 40.4925 | 0.8 | 1 | 14.152 | 58.2753 | 1.6 | 3.4211 | 1.0755 | 0.051395
2016-05-13 18:00 | 42.4 | 33.68 | 8.72 | 35.437 | 18.4023 | 106.698 | 75.7549 | 14.2451 | 110.3338 | 99.7091 | 0 | 25.26 | 0.8 | 1 | 8.48 | 33.74 | 1.7 | 2.7544 | 1.0779 | 0.029821
2016-05-13 19:00 | 33.1867 | 26.6167 | 6.57 | 33.6425 | 18.4125 | 121.6981 | 78.7384 | 11.2616 | 124.6016 | 112.6235 | 0 | 19.9625 | 0.8 | 1 | 6.6373 | 26.5998 | 1.5 | 2.3312 | 1.0793 | 0.023542
2016-05-13 20:00 | 23.9733 | 19.5533 | 4.42 | 29.0456 | 18.4227 | 136.6982 | 81.247 | 8.753 | 138.8251 | 124.6235 | 0 | 14.665 | 0.8 | 1 | 4.7947 | 19.4597 | 1.5 | 2.1081 | 1.0801 | 0.017235
2016-05-13 21:00 | 14.76 | 12.49 | 2.27 | 18.9678 | 18.433 | 151.6983 | 83.1266 | 6.8734 | 153.0607 | 134.9641 | 0 | 9.3675 | 0.8 | 1 | 2.952 | 12.3195 | 1.6 | 1.985 | 1.0806 | 0.010916
2016-05-13 22:00 | 18.59 | 16.7 | 1.89 | 18.8965 | 18.4432 | 166.6983 | 84.2598 | 5.7402 | 167.3285 | 142.2497 | 0 | 12.525 | 0.8 | 1 | 3.718 | 16.243 | 1.3 | 1.8076 | 1.0812 | 0.0144
2016-05-13 23:00 | 22.42 | 20.91 | 1.51 | 15.9703 | 18.4534 | 181.6984 | 84.5746 | 5.4254 | -178.3817 | 144.5406 | 0 | 15.6825 | 0.8 | 1 | 4.484 | 20.1665 | 1.5 | 2.1302 | 1.08 | 0.01786
2016-05-14 | 26.25 | 25.12 | 1.13 | 10.9017 | 18.4636 | -163.3016 | 84.0504 | 5.9496 | -164.0964 | 140.9471 | 0 | 18.84 | 0.8 | 1 | 5.25 | 24.09 | 1.2 | 1.9528 | 1.0807 | 0.021347
2016-05-14 01:00 | 39.9933 | 37.67 | 2.3233 | 18.3346 | 18.4737 | -148.3015 | 82.72 | 7.28 | -149.8396 | 132.796 | 0 | 28.2525 | 0.8 | 1 | 7.9987 | 36.2512 | 1.5 | 2.6328 | 1.0783 | 0.032053
2016-05-14 02:00 | 53.7367 | 50.22 | 3.5167 | 21.6835 | 18.4839 | -133.3015 | 80.6665 | 9.3335 | -135.6153 | 121.9804 | 0 | 37.665 | 0.8 | 1 | 10.7473 | 48.4123 | 1.4 | 2.9129 | 1.0773 | 0.042767
2016-05-14 03:00 | 67.48 | 62.77 | 4.71 | 22.6839 | 18.4941 | -118.3014 | 78.0161 | 11.9839 | -121.3948 | 109.724 | 0 | 47.0775 | 0.8 | 1 | 13.496 | 60.5735 | 1.4 | 3.2929 | 1.076 | 0.053444
2016-05-14 04:00 | 96.1967 | 82.03 | 14.1667 | 54.4881 | 18.5042 | -103.3014 | 74.9302 | 15.0698 | -107.1126 | 96.6652 | 0 | 61.5225 | 0.8 | 1 | 19.2393 | 80.7618 | 1.3 | 3.8238 | 1.0741 | 0.071133
2016-05-14 05:00 | 124.9133 | 101.29 | 23.6233 | 74.8281 | 18.5144 | -88.3014 | 71.5968 | 18.4032 | -92.6716 | 83.1339 | 8.9456 | 75.9675 | 0.8 | 1 | 24.9827 | 109.8958 | 1.4 | 4.8342 | 1.0706 | 0.096475
2016-05-14 06:00 | 153.63 | 120.55 | 33.08 | 89.172 | 18.5245 | -73.3013 | 68.2246 | 21.7754 | -77.9554 | 69.3104 | 31.5049 | 90.4125 | 0.8 | 1 | 30.726 | 152.6434 | 1.5 | 6.2701 | 1.0656 | 0.13337
2016-05-14 07:00 | 171.25 | 146.1467 | 25.1033 | 59.4807 | 18.5346 | -58.3013 | 65.0364 | 24.9636 | -62.851 | 55.3003 | 33.8609 | 109.61 | 0.8 | 1 | 34.25 | 177.7209 | 1.9 | 7.4538 | 1.0614 | 0.15468
2016-05-14 08:00 | 188.87 | 171.7433 | 17.1267 | 36.7957 | 18.5448 | -43.3013 | 62.2605 | 27.7395 | -47.2781 | 41.171 | 27.6979 | 128.8075 | 0.8 | 1 | 37.774 | 194.2794 | 1.7 | 7.7712 | 1.0603 | 0.16892
2016-05-14 09:00 | 206.49 | 197.34 | 9.15 | 18.3641 | 18.5549 | -28.3013 | 60.1154 | 29.8846 | -31.2246 | 26.972 | 16.3666 | 148.005 | 0.8 | 1 | 41.298 | 205.6696 | 1.9 | 8.3272 | 1.0584 | 0.17849
2016-05-14 10:00 | 197.1367 | 188.6467 | 8.49 | 16.3828 | 18.565 | -13.3013 | 58.7867 | 31.2133 | -14.7744 | 12.7642 | 15.978 | 141.485 | 0.8 | 1 | 39.4273 | 196.8903 | 2.1 | 8.2528 | 1.0586 | 0.17091
2016-05-14 11:00 | 187.7833 | 179.9533 | 7.83 | 14.9423 | 18.5751 | 1.6987 | 58.3979 | 31.6021 | 1.8907 | 2.2812 | 14.9304 | 134.965 | 0.8 | 1 | 37.5567 | 187.4521 | 2.4 | 8.2579 | 1.0586 | 0.16272
2016-05-14 12:00 | 178.43 | 171.26 | 7.17 | 13.9157 | 18.5852 | 16.6987 | 58.9861 | 31.0139 | 18.529 | 15.9777 | 13.3781 | 128.445 | 0.8 | 1 | 35.686 | 177.5091 | 2.5 | 8.0472 | 1.0593 | 0.15419
2016-05-14 13:00 | 156.5833 | 149.8733 | 6.71 | 13.6237 | 18.5952 | 31.6987 | 60.4933 | 29.5067 | 34.9067 | 30.1902 | 11.7758 | 112.405 | 0.8 | 1 | 31.3167 | 155.4974 | 2.8 | 7.6593 | 1.0607 | 0.13525
2016-05-14 14:00 | 134.7367 | 128.4867 | 6.25 | 13.6638 | 18.6053 | 46.6987 | 62.7797 | 27.2203 | 50.8614 | 44.3729 | 9.7669 | 96.365 | 0.8 | 1 | 26.9473 | 133.0793 | 1.9 | 6.0587 | 1.0663 | 0.11636
2016-05-14 15:00 | 112.89 | 107.1 | 5.79 | 14.0426 | 18.6154 | 61.6987 | 65.6496 | 24.3504 | 66.3309 | 58.4731 | 7.3429 | 80.325 | 0.8 | 1 | 22.578 | 110.2459 | 2.2 | 5.6452 | 1.0677 | 0.096526
2016-05-14 16:00 | 105.3433 | 90.1967 | 15.1467 | 42.0367 | 18.6254 | 76.6987 | 68.8802 | 21.1198 | 81.3448 | 72.4383 | 12.6838 | 67.6475 | 0.8 | 1 | 21.0687 | 101.4 | 0.9 | 4.0688 | 1.0733 | 0.089239
2016-05-14 17:00 | 97.7967 | 73.2933 | 24.5033 | 80.3443 | 18.6354 | 91.6987 | 72.2431 | 17.7569 | 95.9928 | 86.1938 | 5.3334 | 54.97 | 0.8 | 1 | 19.5593 | 79.8627 | 0.8 | 3.2957 | 1.076 | 0.070462
2016-05-14 18:00 | 90.25 | 56.39 | 33.86 | 135.3986 | 18.6455 | 106.6987 | 75.518 | 14.482 | 110.3904 | 99.6199 | 0 | 42.2925 | 0.8 | 1 | 18.05 | 60.3425 | 0.7 | 2.5857 | 1.0785 | 0.053363
2016-05-14 19:00 | 71.09 | 46.12 | 24.97 | 125.2482 | 18.6555 | 121.6987 | 78.5002 | 11.4998 | 124.6506 | 112.5091 | 0 | 34.59 | 0.8 | 1 | 14.218 | 48.808 | 0.3 | 1.8253 | 1.0811 | 0.043269
2016-05-14 20:00 | 51.93 | 35.85 | 16.08 | 102.8736 | 18.6655 | 136.6986 | 81.0073 | 8.9927 | 138.864 | 124.477 | 0 | 26.8875 | 0.8 | 1 | 10.386 | 37.2735 | 0 | 1.1648 | 1.0834 | 0.033114
2016-05-14 21:00 | 32.77 | 25.58 | 7.19 | 58.0526 | 18.6755 | 151.6986 | 82.8855 | 7.1145 | 153.0873 | 134.7779 | 0 | 19.185 | 0.8 | 1 | 6.554 | 25.739 | -0.5 | 0.30434 | 1.0864 | 0.02293
2016-05-14 22:00 | 36.4033 | 30.6233 | 5.78 | 55.4595 | 18.6855 | 166.6986 | 84.0178 | 5.9822 | 167.3414 | 142.0235 | 0 | 22.9675 | 0.8 | 1 | 7.2807 | 30.2482 | -0.7 | 0.24526 | 1.0866 | 0.026953
2016-05-14 23:00 | 40.0367 | 35.6667 | 4.37 | 44.2503 | 18.6955 | 181.6985 | 84.3324 | 5.6676 | -178.3832 | 144.2987 | 0 | 26.75 | 0.8 | 1 | 8.0073 | 34.7573 | -0.7 | 0.38617 | 1.0861 | 0.030956
2016-05-15 | 43.67 | 40.71 | 2.96 | 27.4472 | 18.7055 | -163.3015 | 83.809 | 6.191 | -164.1122 | 140.7292 | 0 | 30.5325 | 0.8 | 1 | 8.734 | 39.2665 | -0.8 | 0.42708 | 1.086 | 0.034968
2016-05-15 01:00 | 66.01 | 58.3267 | 7.6833 | 58.7089 | 18.7154 | -148.3016 | 82.48 | 7.52 | -149.8688 | 132.6197 | 0 | 43.745 | 0.8 | 1 | 13.202 | 56.947 | -0.8 | 0.97959 | 1.0841 | 0.050622
2016-05-15 02:00 | 88.35 | 75.9433 | 12.4067 | 74.6128 | 18.7254 | -133.3016 | 80.4284 | 9.5716 | -135.6562 | 121.8423 | 0 | 56.9575 | 0.8 | 1 | 17.67 | 74.6275 | -0.9 | 1.4321 | 1.0825 | 0.066242
2016-05-15 03:00 | 110.69 | 93.56 | 17.13 | 80.929 | 18.7353 | -118.3017 | 77.7799 | 12.2201 | -121.4451 | 109.6163 | 0 | 70.17 | 0.8 | 1 | 22.138 | 92.308 | -0.7 | 2.1846 | 1.0799 | 0.081737
2016-05-15 04:00 | 159.6067 | 114.1033 | 45.5033 | 172.395 | 18.7453 | -103.3018 | 74.6955 | 15.3045 | -107.1698 | 96.5814 | 0 | 85.5775 | 0.8 | 1 | 31.9213 | 117.4988 | -0.3 | 3.3718 | 1.0757 | 0.10364
2016-05-15 05:00 | 208.5233 | 134.6467 | 73.8767 | 231.1745 | 18.7552 | -88.3018 | 71.363 | 18.637 | -92.7324 | 83.0695 | 27.8948 | 100.985 | 0.8 | 1 | 41.7047 | 170.5844 | -0.4 | 4.9308 | 1.0702 | 0.1497
2016-05-15 06:00 | 257.44 | 155.19 | 102.25 | 272.8442 | 18.7651 | -73.3019 | 67.9908 | 22.0092 | -78.0164 | 69.2624 | 96.611 | 116.3925 | 0.8 | 1 | 51.488 | 264.4915 | -0.1 | 8.1654 | 1.0589 | 0.22966
2016-05-15 07:00 | 293.17 | 198.7667 | 94.4033 | 221.7323 | 18.7751 | -58.302 | 64.8016 | 25.1984 | -62.9079 | 55.2671 | 126.3324 | 149.075 | 0.8 | 1 | 58.634 | 334.0414 | -0.1 | 10.3388 | 1.0513 | 0.28797
2016-05-15 08:00 | 328.9 | 242.3433 | 86.5567 | 184.5165 | 18.785 | -43.3021 | 62.0241 | 27.9759 | -47.3264 | 41.1521 | 138.9345 | 181.7575 | 0.8 | 1 | 65.78 | 386.472 | -0.2 | 11.8772 | 1.0459 | 0.33146
2016-05-15 09:00 | 364.63 | 285.92 | 78.71 | 156.8388 | 18.7948 | -28.3021 | 59.8773 | 30.1227 | -31.2597 | 26.9692 | 139.7827 | 214.44 | 0.8 | 1 | 72.926 | 427.1487 | 0 | 13.3484 | 1.0408 | 0.36455
2016-05-15 10:00 | 378.19 | 283.3033 | 94.8867 | 181.8474 | 18.8047 | -13.3022 | 58.5474 | 31.4526 | -14.7925 | 12.7887 | 177.3364 | 212.4775 | 0.8 | 1 | 75.638 | 465.4519 | 0.3 | 14.8454 | 1.0355 | 0.39524
2016-05-15 11:00 | 391.75 | 280.6867 | 111.0633 | 210.5174 | 18.8146 | 1.6977 | 58.1584 | 31.8416 | 1.8917 | 2.4545 | 210.3243 | 210.515 | 0.8 | 1 | 78.35 | 499.1893 | -0.2 | 15.3997 | 1.0336 | 0.42309
2016-05-15 12:00 | 405.31 | 278.07 | 127.24 | 245.2523 | 18.8245 | 16.6976 | 58.7474 | 31.2526 | 18.5489 | 15.9917 | 235.7614 | 208.5525 | 0.8 | 1 | 81.062 | 525.3759 | 0.3 | 16.718 | 1.029 | 0.4433
2016-05-15 13:00 | 361.42 | 254.93 | 106.49 | 214.6453 | 18.8343 | 31.6975 | 60.2563 | 29.7437 | 34.9429 | 30.1818 | 185.5468 | 191.1975 | 0.8 | 1 | 72.284 | 449.0283 | 0.5 | 14.5321 | 1.0366 | 0.38169
2016-05-15 14:00 | 317.53 | 231.79 | 85.74 | 185.9642 | 18.8442 | 46.6974 | 62.5447 | 27.4553 | 50.9096 | 44.3491 | 132.9818 | 173.8425 | 0.8 | 1 | 63.506 | 370.3303 | 0.4 | 11.9728 | 1.0456 | 0.31752
2016-05-15 15:00 | 273.64 | 208.65 | 64.99 | 156.218 | 18.854 | 61.6973 | 65.4164 | 24.5836 | 66.3866 | 58.4351 | 81.7745 | 156.4875 | 0.8 | 1 | 54.728 | 292.99 | 0.8 | 9.9559 | 1.0527 | 0.2529
2016-05-15 16:00 | 219.1 | 168.4833 | 50.6167 | 139.0202 | 18.8639 | 76.6971 | 68.6481 | 21.3519 | 81.4035 | 72.3854 | 42.0692 | 126.3625 | 0.8 | 1 | 43.82 | 212.2517 | 0.5 | 7.1329 | 1.0625 | 0.18493
2016-05-15 17:00 | 164.56 | 128.3167 | 36.2433 | 117.3569 | 18.8737 | 91.697 | 72.0113 | 17.9887 | 96.0504 | 86.1242 | 7.9327 | 96.2375 | 0.8 | 1 | 32.912 | 137.0822 | 0.5 | 4.7838 | 1.0708 | 0.12036
2016-05-15 18:00 | 110.02 | 88.15 | 21.87 | 86.1019 | 18.8835 | 106.6969 | 75.2856 | 14.7144 | 110.4436 | 99.5303 | 0 | 66.1125 | 0.8 | 1 | 22.004 | 88.1165 | 0.1 | 2.8536 | 1.0775 | 0.077856
2016-05-15 19:00 | 91.2833 | 71.5867 | 19.6967 | 96.8578 | 18.8933 | 121.6968 | 78.2667 | 11.7333 | 124.6964 | 112.3948 | 0 | 53.69 | 0.8 | 1 | 18.2567 | 71.9467 | 0.1 | 2.3483 | 1.0793 | 0.063674
2016-05-15 20:00 | 72.5467 | 55.0233 | 17.5233 | 109.2769 | 18.9031 | 136.6967 | 80.7724 | 9.2276 | 138.8998 | 124.3314 | 0 | 41.2675 | 0.8 | 1 | 14.5093 | 55.7768 | 0.1 | 1.843 | 1.081 | 0.049444
2016-05-15 21:00 | 53.81 | 38.46 | 15.35 | 119.9755 | 18.9129 | 151.6965 | 82.6493 | 7.3507 | 153.1112 | 134.5938 | 0 | 28.845 | 0.8 | 1 | 10.762 | 39.607 | 0.1 | 1.3377 | 1.0828 | 0.035167
2016-05-15 22:00 | 48.0233 | 36.6933 | 11.33 | 104.586 | 18.9227 | 166.6964 | 83.7808 | 6.2192 | 167.3518 | 141.8013 | 0 | 27.52 | 0.8 | 1 | 9.6047 | 37.1247 | 0 | 1.1601 | 1.0834 | 0.032982
2016-05-15 23:00 | 42.2367 | 34.9267 | 7.31 | 71.0605 | 18.9324 | 181.6962 | 84.0955 | 5.9045 | -178.387 | 144.0622 | 0 | 26.195 | 0.8 | 1 | 8.4473 | 34.6423 | -0.1 | 0.98257 | 1.0841 | 0.030795
2016-05-16 | 36.45 | 33.16 | 3.29 | 29.3911 | 18.9422 | -163.3039 | 83.5729 | 6.4271 | -164.13 | 140.5169 | 0 | 24.87 | 0.8 | 1 | 7.29 | 32.16 | -0.1 | 0.905 | 1.0843 | 0.028595
2016-05-16 01:00 | 51.4333 | 48.0867 | 3.3467 | 24.8033 | 18.9519 | -148.3041 | 82.2455 | 7.7545 | -149.8997 | 132.4483 | 0 | 36.065 | 0.8 | 1 | 10.2867 | 46.3517 | -0.1 | 1.3485 | 1.0828 | 0.041155
2016-05-16 02:00 | 66.4167 | 63.0133 | 3.4033 | 19.9865 | 18.9617 | -133.3042 | 80.1958 | 9.8042 | -135.6985 | 121.7086 | 0 | 47.26 | 0.8 | 1 | 13.2833 | 60.5433 | -0.2 | 1.692 | 1.0816 | 0.053696
2016-05-16 03:00 | 81.4 | 77.94 | 3.46 | 16.0483 | 18.9714 | -118.3044 | 77.5493 | 12.4507 | -121.4968 | 109.5127 | 0 | 58.455 | 0.8 | 1 | 16.28 | 74.735 | 0 | 2.3355 | 1.0793 | 0.066144
2016-05-16 04:00 | 107.1867 | 103.2533 | 3.9333 | 14.6875 | 18.9811 | -103.3045 | 74.4665 | 15.5335 | -107.2281 | 96.5014 | 0 | 77.44 | 0.8 | 1 | 21.4373 | 98.8773 | -0.2 | 2.8899 | 1.0774 | 0.087354
2016-05-16 05:00 | 132.9733 | 128.5667 | 4.4067 | 13.6285 | 18.9908 | -88.3047 | 71.1348 | 18.8652 | -92.7945 | 83.0087 | 1.6588 | 96.425 | 0.8 | 1 | 26.5947 | 124.6785 | -0.3 | 3.5962 | 1.0749 | 0.1099
2016-05-16 06:00 | 158.76 | 153.88 | 4.88 | 12.8948 | 19.0005 | -73.3049 | 67.7625 | 22.2375 | -78.0786 | 69.2181 | 4.5752 | 115.41 | 0.8 | 1 | 31.752 | 151.7372 | 0 | 4.7418 | 1.0709 | 0.13325
2016-05-16 07:00 | 210.3767 | 201.9067 | 8.47 | 19.7266 | 19.0102 | -58.3051 | 64.5724 | 25.4276 | -62.9663 | 55.2375 | 11.2476 | 151.43 | 0.8 | 1 | 42.0753 | 204.753 | 0.2 | 6.5985 | 1.0644 | 0.17871
2016-05-16 08:00 | 261.9933 | 249.9333 | 12.06 | 25.5155 | 19.0199 | -43.3052 | 61.7933 | 28.2067 | -47.3765 | 41.1371 | 19.2167 | 187.45 | 0.8 | 1 | 52.3987 | 259.0654 | 0.3 | 8.3958 | 1.0581 | 0.22478
2016-05-16 09:00 | 313.61 | 297.96 | 15.65 | 30.9681 | 19.0296 | -28.3054 | 59.6448 | 30.3552 | -31.2969 | 26.9707 | 27.5999 | 223.47 | 0.8 | 1 | 62.722 | 313.7919 | -0.5 | 9.306 | 1.0549 | 0.27144
2016-05-16 10:00 | 314.11 | 290.7033 | 23.4067 | 44.5612 | 19.0392 | -13.3056 | 58.3135 | 31.6865 | -14.813 | 12.8192 | 43.4505 | 218.0275 | 0.8 | 1 | 62.822 | 324.3 | 1 | 11.1344 | 1.0485 | 0.27883
2016-05-16 11:00 | 314.61 | 283.4467 | 31.1633 | 58.6833 | 19.0489 | 1.6942 | 57.9241 | 32.0759 | 1.89 | 2.6327 | 58.6213 | 212.585 | 0.8 | 1 | 62.922 | 334.1283 | 0.7 | 11.1415 | 1.0485 | 0.28727
2016-05-16 12:00 | 315.11 | 276.19 | 38.92 | 74.5173 | 19.0585 | 16.694 | 58.5137 | 31.4863 | 18.5657 | 16.0065 | 71.6283 | 207.1425 | 0.8 | 1 | 63.022 | 341.7928 | 1.3 | 11.981 | 1.0456 | 0.29304
2016-05-16 13:00 | 280.0467 | 242.6333 | 37.4133 | 74.8814 | 19.0682 | 31.6938 | 60.0242 | 29.9758 | 34.9757 | 30.1728 | 64.736 | 181.975 | 0.8 | 1 | 56.0093 | 302.7203 | 1 | 10.46 | 1.0509 | 0.26086
2016-05-16 14:00 | 244.9833 | 209.0767 | 35.9067 | 77.282 | 19.0778 | 46.6936 | 62.3144 | 27.6856 | 50.9544 | 44.3246 | 55.287 | 156.8075 | 0.8 | 1 | 48.9967 | 261.0912 | 0.8 | 8.9591 | 1.0561 | 0.22611
2016-05-16 15:00 | 209.92 | 175.52 | 34.4 | 81.974 | 19.0874 | 61.6934 | 65.1878 | 24.8122 | 66.4388 | 58.3963 | 42.9578 | 131.64 | 0.8 | 1 | 41.984 | 216.5818 | 0.9 | 7.6682 | 1.0607 | 0.18837
2016-05-16 16:00 | 188.3033 | 158.4633 | 29.84 | 81.1331 | 19.097 | 76.6932 | 68.4206 | 21.5794 | 81.4586 | 72.3318 | 24.6243 | 118.8475 | 0.8 | 1 | 37.6607 | 181.1325 | 0.6 | 6.2604 | 1.0656 | 0.15827
2016-05-16 17:00 | 166.6867 | 141.4067 | 25.28 | 80.8702 | 19.1066 | 91.6929 | 71.784 | 18.216 | 96.1046 | 86.0539 | 5.5654 | 106.055 | 0.8 | 1 | 33.3373 | 144.9577 | -0.2 | 4.3299 | 1.0723 | 0.12746
2016-05-16 18:00 | 145.07 | 124.35 | 20.72 | 80.3587 | 19.1162 | 106.6927 | 75.0578 | 14.9422 | 110.4934 | 99.4404 | 0 | 93.2625 | 0.8 | 1 | 29.014 | 122.2765 | 0.6 | 4.4211 | 1.072 | 0.10749
2016-05-16 19:00 | 116.3433 | 97.1567 | 19.1867 | 92.5707 | 19.1258 | 121.6925 | 78.0379 | 11.9621 | 124.7389 | 112.2808 | 0 | 72.8675 | 0.8 | 1 | 23.2687 | 96.1362 | 0.5 | 3.5043 | 1.0752 | 0.084763
2016-05-16 20:00 | 87.6167 | 69.9633 | 17.6533 | 107.433 | 19.1354 | 136.6923 | 80.5423 | 9.4577 | 138.9325 | 124.1868 | 0 | 52.4725 | 0.8 | 1 | 17.5233 | 69.9958 | 0.4 | 2.5874 | 1.0784 | 0.061899
2016-05-16 21:00 | 58.89 | 42.77 | 16.12 | 122.1735 | 19.145 | 151.692 | 82.4181 | 7.5819 | 153.1322 | 134.412 | 0 | 32.0775 | 0.8 | 1 | 11.778 | 43.8555 | 0.7 | 2.0705 | 1.0803 | 0.038848
2016-05-16 22:00 | 58.7967 | 41.6433 | 17.1533 | 152.6744 | 19.1545 | 166.6918 | 83.5491 | 6.4509 | 167.3596 | 141.583 | 0 | 31.2325 | 0.8 | 1 | 11.7593 | 42.9918 | 0.5 | 1.8435 | 1.081 | 0.038111
2016-05-16 23:00 | 58.7033 | 40.5167 | 18.1867 | 170.1437 | 19.1641 | 181.6916 | 83.8639 | 6.1361 | -178.393 | 143.831 | 0 | 30.3875 | 0.8 | 1 | 11.7407 | 42.1282 | 0.2 | 1.5165 | 1.0822 | 0.037384
2016-05-17 | 58.61 | 39.39 | 19.22 | 165.7789 | 19.1736 | -163.3087 | 83.3423 | 6.6577 | -164.1497 | 140.31 | 0 | 29.5425 | 0.74 | 0.9 | 10.8429 | 40.3854 | 0.4 | 1.662 | 1.0817 | 0.035821
2016-05-17 01:00 | 69.59 | 55.9733 | 13.6167 | 98.0413 | 19.1831 | -148.3089 | 82.0165 | 7.9835 | -149.9322 | 132.282 | 0 | 41.98 | 0.73984 | 0.89974 | 12.8714 | 54.8514 | 0.5 | 2.2141 | 1.0798 | 0.048565
2016-05-17 02:00 | 80.57 | 72.5567 | 8.0133 | 46.0051 | 19.1926 | -133.3092 | 79.9688 | 10.0312 | -135.7423 | 121.5795 | 0 | 54.4175 | 0.73969 | 0.89948 | 14.8992 | 69.3167 | 0.9 | 3.0661 | 1.0768 | 0.061203
2016-05-17 03:00 | 91.55 | 89.14 | 2.41 | 10.9829 | 19.2021 | -118.3095 | 77.3244 | 12.6756 | -121.5497 | 109.4132 | 0 | 66.855 | 0.73953 | 0.89922 | 16.926 | 83.781 | 0.5 | 3.1182 | 1.0766 | 0.073962
2016-05-17 04:00 | 104.6467 | 102.0433 | 2.6033 | 9.5867 | 19.2116 | -103.3097 | 74.2432 | 15.7568 | -107.2877 | 96.4253 | 0 | 76.5325 | 0.73938 | 0.89896 | 19.3433 | 95.8758 | 0.2 | 3.1961 | 1.0763 | 0.084618
2016-05-17 05:00 | 117.7433 | 114.9467 | 2.7967 | 8.5521 | 19.2211 | -88.31 | 70.9123 | 19.0877 | -92.8576 | 82.9517 | 1.0494 | 86.21 | 0.73922 | 0.8987 | 21.7595 | 109.0189 | 0.3 | 3.7068 | 1.0745 | 0.096058
2016-05-17 06:00 | 130.84 | 127.85 | 2.99 | 7.8264 | 19.2306 | -73.3103 | 67.54 | 22.46 | -78.142 | 69.1773 | 2.7821 | 95.8875 | 0.73906 | 0.89844 | 24.1747 | 122.8444 | 0.6 | 4.4389 | 1.072 | 0.10798
2016-05-17 07:00 | 142.77 | 140.7333 | 2.0367 | 4.7048 | 19.2401 | -58.3105 | 64.3489 | 25.6511 | -63.026 | 55.2116 | 2.6843 | 105.55 | 0.73891 | 0.89818 | 26.3734 | 134.6077 | 0.6 | 4.8065 | 1.0707 | 0.11818
2016-05-17 08:00 | 154.7 | 153.6167 | 1.0833 | 2.2754 | 19.2495 | -43.3108 | 61.5682 | 28.4318 | -47.4282 | 41.1257 | 1.714 | 115.2125 | 0.73875 | 0.89792 | 28.5712 | 145.4976 | 0.6 | 5.1468 | 1.0695 | 0.1276
2016-05-17 09:00 | 166.63 | 166.5 | 0.13 | 0.25552 | 19.259 | -28.3111 | 59.4178 | 30.5822 | -31.3361 | 26.9763 | 0.22771 | 124.875 | 0.73859 | 0.89766 | 30.768 | 155.8707 | 0.6 | 5.471 | 1.0684 | 0.13655
2016-05-17 10:00 | 156.06 | 155.9633 | 0.096667 | 0.18285 | 19.2684 | -13.3114 | 58.0851 | 31.9149 | -14.8359 | 12.8553 | 0.17827 | 116.9725 | 0.73844 | 0.8974 | 28.8101 | 145.9609 | 0.5 | 5.0613 | 1.0698 | 0.12804
2016-05-17 11:00 | 145.49 | 145.4267 | 0.063333 | 0.11851 | 19.2779 | 1.6883 | 57.6951 | 32.3049 | 1.8856 | 2.8135 | 0.11836 | 109.07 | 0.73828 | 0.89714 | 26.8531 | 136.0415 | 0.4 | 4.6513 | 1.0712 | 0.1195
2016-05-17 12:00 | 134.92 | 134.89 | 0.03 | 0.057068 | 19.2873 | 16.688 | 58.2852 | 31.7148 | 18.5796 | 16.0218 | 0.054851 | 101.1675 | 0.73813 | 0.89687 | 24.897 | 126.1193 | 0.5 | 4.4412 | 1.072 | 0.11086
2016-05-17 13:00 | 121.1533 | 121.1267 | 0.026667 | 0.053008 | 19.2967 | 31.6877 | 59.797 | 30.203 | 35.0053 | 30.1634 | 0.045831 | 90.845 | 0.73797 | 0.89661 | 22.3518 | 113.2427 | 0.3 | 3.8388 | 1.0741 | 0.099737
2016-05-17 14:00 | 107.3867 | 107.3633 | 0.023333 | 0.049847 | 19.3061 | 46.6874 | 62.089 | 27.911 | 50.9958 | 44.2992 | 0.035676 | 80.5225 | 0.73781 | 0.89635 | 19.8078 | 100.366 | 0.2 | 3.3364 | 1.0758 | 0.08854
2016-05-17 15:00 | 93.62 | 93.6 | 0.02 | 0.04726 | 19.3155 | 61.6871 | 64.964 | 25.036 | 66.4875 | 58.3566 | 0.024794 | 70.2 | 0.73766 | 0.89609 | 17.2648 | 87.4896 | 0.2 | 2.9341 | 1.0772 | 0.077282
2016-05-17 16:00 | 66.6167 | 66.5967 | 0.02 | 0.05385 | 19.3249 | 76.6868 | 68.1977 | 21.8023 | 81.5103 | 72.2773 | 0.016392 | 49.9475 | 0.7375 | 0.89583 | 12.2824 | 62.2463 | 0.2 | 2.1452 | 1.08 | 0.055125
2016-05-17 17:00 | 39.6133 | 39.5933 | 0.02 | 0.063234 | 19.3343 | 91.6865 | 71.5615 | 18.4385 | 96.1553 | 85.983 | 0.0044296 | 29.695 | 0.73734 | 0.89557 | 7.3022 | 37.0016 | -0.1 | 1.0563 | 1.0838 | 0.032884
2016-05-17 18:00 | 12.61 | 12.59 | 0.02 | 0.076452 | 19.3436 | 106.6862 | 74.8348 | 15.1652 | 110.5399 | 99.3503 | 0 | 9.4425 | 0.73719 | 0.89531 | 2.324 | 11.7665 | 0 | 0.3677 | 1.0862 | 0.01048
2016-05-17 19:00 | 10.81 | 10.7433 | 0.066667 | 0.31582 | 19.353 | 121.6858 | 77.8139 | 12.1861 | 124.7782 | 112.167 | 0 | 8.0575 | 0.73703 | 0.89505 | 1.9918 | 10.0493 | 0 | 0.31404 | 1.0864 | 0.0089524
2016-05-17 20:00 | 9.01 | 8.8967 | 0.11333 | 0.67382 | 19.3623 | 136.6855 | 80.3172 | 9.6828 | 138.9623 | 124.0434 | 0 | 6.6725 | 0.73688 | 0.89479 | 1.6598 | 8.3323 | -0.2 | 0.060385 | 1.0873 | 0.0074289
2016-05-17 21:00 | 7.21 | 7.05 | 0.16 | 1.1777 | 19.3717 | 151.6852 | 82.192 | 7.808 | 153.1504 | 134.2326 | 0 | 5.2875 | 0.73672 | 0.89453 | 1.3279 | 6.6154 | -0.8 | -0.59327 | 1.0896 | 0.0059106
2016-05-17 22:00 | 8.37 | 8.0967 | 0.27333 | 2.3506 | 19.381 | 166.6848 | 83.3225 | 6.6775 | 167.365 | 141.3688 | 0 | 6.0725 | 0.73656 | 0.89427 | 1.5413 | 7.6138 | -1.1 | -0.86207 | 1.0905 | 0.0068084
2016-05-17 23:00 | 9.53 | 9.1433 | 0.38667 | 3.4893 | 19.3903 | 181.6845 | 83.6377 | 6.3623 | -178.4012 | 143.6053 | 0 | 6.8575 | 0.73641 | 0.89401 | 1.7545 | 8.612 | -0.7 | -0.43088 | 1.089 | 0.0076904
2016-05-18 | 10.69 | 10.19 | 0.5 | 4.1723 | 19.3996 | -163.3158 | 83.1172 | 6.8828 | -164.1713 | 140.1087 | 0 | 7.6425 | 0.73625 | 0.89375 | 1.9676 | 9.6101 | -0.5 | -0.19968 | 1.0882 | 0.0085753
2016-05-18 01:00 | 15.0633 | 14.0667 | 0.99667 | 6.982 | 19.4089 | -148.3162 | 81.7932 | 8.2068 | -149.9664 | 132.1207 | 0 | 10.55 | 0.73609 | 0.89349 | 2.772 | 13.322 | -1.3 | -0.88369 | 1.0906 | 0.011914
2016-05-18 02:00 | 19.4367 | 17.9433 | 1.4933 | 8.3902 | 19.4182 | -133.3165 | 79.7476 | 10.2524 | -135.7875 | 121.4549 | 0 | 13.4575 | 0.73594 | 0.89323 | 3.576 | 17.0335 | -1 | -0.4677 | 1.0891 | 0.015213
2016-05-18 03:00 | 23.81 | 21.82 | 1.99 | 8.9173 | 19.4275 | -118.3169 | 77.1052 | 12.8948 | -121.6038 | 109.3178 | 0 | 16.365 | 0.73578 | 0.89297 | 4.3797 | 20.7447 | -1.1 | -0.45173 | 1.0891 | 0.018526
2016-05-18 04:00 | 55.3633 | 40.01 | 15.3533 | 55.788 | 19.4368 | -103.3173 | 74.0256 | 15.9744 | -107.3483 | 96.3531 | 0 | 30.0075 | 0.73563 | 0.89271 | 10.1817 | 40.1892 | -1 | 0.25591 | 1.0866 | 0.035809
2016-05-18 05:00 | 86.9167 | 58.2 | 28.7167 | 86.8659 | 19.4461 | -88.3176 | 70.6956 | 19.3044 | -92.9219 | 82.8984 | 10.7392 | 43.65 | 0.73547 | 0.89245 | 15.9811 | 70.3704 | -0.7 | 1.4991 | 1.0823 | 0.06245
2016-05-18 06:00 | 118.47 | 76.39 | 42.08 | 109.1479 | 19.4553 | -73.318 | 67.3232 | 22.6768 | -78.2066 | 69.1401 | 38.8658 | 57.2925 | 0.73531 | 0.89219 | 21.7781 | 117.9364 | -0.8 | 2.8855 | 1.0774 | 0.10419
2016-05-18 07:00 | 157.0667 | 120.3267 | 36.74 | 84.2058 | 19.4646 | -58.3184 | 64.1312 | 25.8688 | -63.0872 | 55.1891 | 48.0705 | 90.245 | 0.73516 | 0.89193 | 28.8671 | 167.1827 | 0 | 5.2245 | 1.0692 | 0.14658
2016-05-18 08:00 | 195.6633 | 164.2633 | 31.4 | 65.4881 | 19.4738 | -43.3187 | 61.3488 | 28.6512 | -47.4815 | 41.118 | 49.3359 | 123.1975 | 0.735 | 0.89167 | 35.9531 | 208.4865 | 1.3 | 7.8152 | 1.0601 | 0.18124
2016-05-18 09:00 | 234.26 | 208.2 | 26.06 | 50.889 | 19.483 | -28.3191 | 59.1965 | 30.8035 | -31.3773 | 26.9859 | 45.3481 | 156.15 | 0.73484 | 0.89141 | 43.0361 | 244.5342 | 1.5 | 9.1417 | 1.0555 | 0.21165
2016-05-18 10:00 | 238.1567 | 198.55 | 39.6067 | 74.4546 | 19.4922 | -13.3195 | 57.8622 | 32.1378 | -14.8611 | 12.8966 | 72.5765 | 148.9125 | 0.73469 | 0.89115 | 43.7427 | 265.2316 | 1.3 | 9.5885 | 1.0539 | 0.22922
2016-05-18 11:00 | 242.0533 | 188.9 | 53.1533 | 98.8495 | 19.5014 | 1.6801 | 57.4714 | 32.5286 | 1.8785 | 2.9951 | 98.7144 | 141.675 | 0.73453 | 0.89089 | 44.4489 | 284.8384 | 1.3 | 10.2012 | 1.0518 | 0.24567
2016-05-18 12:00 | 245.95 | 179.25 | 66.7 | 126.0863 | 19.5106 | 16.6797 | 58.0619 | 31.9381 | 18.5904 | 16.0375 | 121.1792 | 134.4375 | 0.73438 | 0.89062 | 45.1549 | 300.7715 | 0.8 | 10.1991 | 1.0518 | 0.25941
2016-05-18 13:00 | 206.0333 | 159.3133 | 46.72 | 92.2571 | 19.5198 | 31.6793 | 59.5749 | 30.4251 | 35.0317 | 30.1533 | 79.7732 | 119.485 | 0.73422 | 0.89036 | 37.8184 | 237.0766 | 0.3 | 7.7086 | 1.0605 | 0.20617
2016-05-18 14:00 | 166.1167 | 139.3767 | 26.74 | 56.7131 | 19.529 | 46.6789 | 61.8685 | 28.1315 | 51.0338 | 44.273 | 40.6078 | 104.5325 | 0.73406 | 0.8901 | 30.485 | 175.6253 | 0 | 5.4883 | 1.0683 | 0.15385
2016-05-18 15:00 | 126.2 | 119.44 | 6.76 | 15.8444 | 19.5382 | 61.6785 | 64.7449 | 25.2551 | 66.5327 | 58.316 | 8.322 | 89.58 | 0.73391 | 0.88984 | 23.1547 | 121.0568 | 0.1 | 3.883 | 1.0739 | 0.1066
2016-05-18 16:00 | 100.65 | 95.1 | 5.55 | 14.8025 | 19.5473 | 76.6781 | 67.9797 | 22.0203 | 81.5584 | 72.2221 | 4.5196 | 71.325 | 0.73375 | 0.88958 | 18.463 | 94.3076 | -0.4 | 2.5471 | 1.0786 | 0.083409
2016-05-18 17:00 | 75.1 | 70.76 | 4.34 | 13.5671 | 19.5565 | 91.6777 | 71.3437 | 18.6563 | 96.2025 | 85.9117 | 0.96725 | 53.07 | 0.73359 | 0.88932 | 13.7732 | 67.8105 | -0.8 | 1.3191 | 1.0829 | 0.060213
2016-05-18 18:00 | 49.55 | 46.42 | 3.13 | 11.799 | 19.5656 | 106.6773 | 74.6166 | 15.3834 | 110.5829 | 99.26 | 0 | 34.815 | 0.73344 | 0.88906 | 9.0855 | 43.9005 | -0.5 | 0.87189 | 1.0844 | 0.039038
2016-05-18 19:00 | 41.8733 | 39.7033 | 2.17 | 10.1013 | 19.5747 | 121.6768 | 77.5948 | 12.4052 | 124.8143 | 112.0536 | 0 | 29.7775 | 0.73328 | 0.8888 | 7.6762 | 37.4537 | -0.5 | 0.67043 | 1.0852 | 0.033327
2016-05-18 20:00 | 34.1967 | 32.9867 | 1.21 | 7.0357 | 19.5839 | 136.6764 | 80.097 | 9.903 | 138.989 | 123.9011 | 0 | 24.74 | 0.73313 | 0.88854 | 6.2676 | 31.0076 | -1 | -0.031012 | 1.0876 | 0.027654
2016-05-18 21:00 | 26.52 | 26.27 | 0.25 | 1.7899 | 19.593 | 151.676 | 81.971 | 8.029 | 153.1658 | 134.0557 | 0 | 19.7025 | 0.73297 | 0.88828 | 4.8596 | 24.5621 | -1.3 | -0.53243 | 1.0894 | 0.021941
2016-05-18 22:00 | 28.8067 | 28.6267 | 0.18 | 1.4986 | 19.6021 | 166.6755 | 83.1013 | 6.8987 | 167.3678 | 141.1588 | 0 | 21.47 | 0.73281 | 0.88802 | 5.2775 | 26.7475 | -2.3 | -1.4641 | 1.0926 | 0.023964
2016-05-18 23:00 | 31.0933 | 30.9833 | 0.11 | 0.95949 | 19.6112 | 181.6751 | 83.4169 | 6.5831 | -178.4116 | 143.3852 | 0 | 23.2375 | 0.73266 | 0.88776 | 5.6952 | 28.9327 | -2.3 | -1.3959 | 1.0924 | 0.025917
2016-05-19 | 33.38 | 33.34 | 0.04 | 0.32351 | 19.6203 | -163.3253 | 82.8976 | 7.1024 | -164.1948 | 139.9131 | 0 | 25.005 | 0.7325 | 0.8875 | 6.1127 | 31.1177 | -2.7 | -1.7276 | 1.0935 | 0.027904
2016-05-19 01:00 | 41.0867 | 40.9733 | 0.11333 | 0.77357 | 19.6293 | -148.3258 | 81.5754 | 8.4246 | -150.0021 | 131.9644 | 0 | 30.73 | 0.73234 | 0.88724 | 7.5224 | 38.2524 | -2.4 | -1.2046 | 1.0917 | 0.034244
2016-05-19 02:00 | 48.7933 | 48.6067 | 0.18667 | 1.0274 | 19.6384 | -133.3262 | 79.532 | 10.468 | -135.8339 | 121.3348 | 0 | 36.455 | 0.73219 | 0.88698 | 8.9315 | 45.3865 | -2.8 | -1.3817 | 1.0923 | 0.040653
2016-05-19 03:00 | 56.5 | 56.24 | 0.26 | 1.1464 | 19.6474 | -118.3267 | 76.8917 | 13.1083 | -121.659 | 109.2266 | 0 | 42.18 | 0.73203 | 0.88672 | 10.3399 | 52.5199 | -2.7 | -1.0588 | 1.0912 | 0.046994
2016-05-19 04:00 | 63.5267 | 63.29 | 0.23667 | 0.849 | 19.6565 | -103.3271 | 73.8138 | 16.1862 | -107.4099 | 96.2847 | 0 | 47.4675 | 0.73188 | 0.88646 | 11.6234 | 59.0909 | -2.6 | -0.75341 | 1.0901 | 0.052822
2016-05-19 05:00 | 70.5533 | 70.34 | 0.21333 | 0.63861 | 19.6655 | -88.3276 | 70.4848 | 19.5152 | -92.9872 | 82.8487 | 0.079501 | 52.755 | 0.73172 | 0.8862 | 12.9063 | 65.7408 | -3.2 | -1.1456 | 1.0915 | 0.058841
2016-05-19 06:00 | 77.58 | 77.39 | 0.19 | 0.48853 | 19.6745 | -73.3281 | 67.1123 | 22.8877 | -78.2724 | 69.1065 | 0.17422 | 58.0425 | 0.73156 | 0.88594 | 14.1887 | 72.4054 | -3 | -0.73733 | 1.0901 | 0.064721
2016-05-19 07:00 | 112.6667 | 112.3233 | 0.34333 | 0.78095 | 19.6836 | -58.3285 | 63.9193 | 26.0807 | -63.1496 | 55.1702 | 0.44603 | 84.2425 | 0.73141 | 0.88568 | 20.6013 | 105.2898 | -3 | 0.29031 | 1.0865 | 0.093804
2016-05-19 08:00 | 147.7533 | 147.2567 | 0.49667 | 1.0288 | 19.6926 | -43.329 | 61.1351 | 28.8649 | -47.5364 | 41.1138 | 0.77513 | 110.4425 | 0.73125 | 0.88542 | 27.0112 | 138.2288 | -3 | 1.3196 | 1.0829 | 0.12274
2016-05-19 09:00 | 182.84 | 182.19 | 0.65 | 1.2613 | 19.7016 | -28.3295 | 58.9809 | 31.0191 | -31.4203 | 26.9992 | 1.1239 | 136.6425 | 0.73109 | 0.88516 | 33.4183 | 171.1847 | -2.9 | 2.4495 | 1.0789 | 0.15145
2016-05-19 10:00 | 185.3833 | 183.4467 | 1.9367 | 3.6188 | 19.7106 | -13.33 | 57.6449 | 32.3551 | -14.8886 | 12.9427 | 3.5269 | 137.585 | 0.73094 | 0.8849 | 33.8759 | 174.9878 | -3.1 | 2.3684 | 1.0792 | 0.15486
2016-05-19 11:00 | 187.9267 | 184.7033 | 3.2233 | 5.9589 | 19.7195 | 1.6695 | 57.2533 | 32.7467 | 1.8687 | 3.1763 | 5.9498 | 138.5275 | 0.73078 | 0.88464 | 34.3333 | 178.8106 | -2.9 | 2.6878 | 1.0781 | 0.15807
2016-05-19 12:00 | 190.47 | 185.96 | 4.51 | 8.4738 | 19.7285 | 16.669 | 57.8439 | 32.1561 | 18.5982 | 16.0534 | 8.1434 | 139.47 | 0.73063 | 0.88438 | 34.7905 | 182.4039 | -2.8 | 2.9001 | 1.0773 | 0.16114
2016-05-19 13:00 | 179.11 | 175.3867 | 3.7233 | 7.3053 | 19.7375 | 31.6686 | 59.358 | 30.642 | 35.0548 | 30.1426 | 6.3175 | 131.54 | 0.73047 | 0.88411 | 32.7086 | 170.5661 | -2.9 | 2.4302 | 1.079 | 0.15091
2016-05-19 14:00 | 167.75 | 164.8133 | 2.9367 | 6.1849 | 19.7464 | 46.6681 | 61.653 | 28.347 | 51.0684 | 44.2459 | 4.4306 | 123.61 | 0.73031 | 0.88385 | 30.6275 | 158.6681 | -2.8 | 2.1584 | 1.0799 | 0.14051
2016-05-19 15:00 | 156.39 | 154.24 | 2.15 | 4.9997 | 19.7553 | 61.6676 | 64.5308 | 25.4692 | 66.5744 | 58.2746 | 2.6291 | 115.68 | 0.73016 | 0.88359 | 28.5473 | 146.8564 | -2.9 | 1.6893 | 1.0816 | 0.13025
2016-05-19 16:00 | 123.0267 | 121.41 | 1.6167 | 4.2726 | 19.7643 | 76.667 | 67.7664 | 22.2336 | 81.6029 | 72.1662 | 1.3085 | 91.0575 | 0.73 | 0.88333 | 22.4524 | 114.8184 | -2.6 | 0.98807 | 1.084 | 0.10206
2016-05-19 17:00 | 89.6633 | 88.58 | 1.0833 | 3.3497 | 19.7732 | 91.6665 | 71.1307 | 18.8693 | 96.2463 | 85.8399 | 0.243 | 66.435 | 0.72984 | 0.88307 | 16.3601 | 83.0381 | -2.6 | -0.0050607 | 1.0875 | 0.07405
2016-05-19 18:00 | 56.3 | 55.75 | 0.55 | 2.0456 | 19.7821 | 106.666 | 74.4032 | 15.5968 | 110.6226 | 99.1697 | 0 | 41.8125 | 0.72969 | 0.88281 | 10.2704 | 52.0829 | -2.6 | -0.97241 | 1.0909 | 0.04659
2016-05-19 19:00 | 47.33 | 46.8933 | 0.43667 | 1.9987 | 19.791 | 121.6655 | 77.3807 | 12.6193 | 124.8471 | 111.9407 | 0 | 35.17 | 0.72953 | 0.88255 | 8.6322 | 43.8022 | -2.5 | -1.1312 | 1.0915 | 0.039203
2016-05-19 20:00 | 38.36 | 38.0367 | 0.32333 | 1.8405 | 19.7999 | 136.665 | 79.882 | 10.118 | 139.0126 | 123.7602 | 0 | 28.5275 | 0.72938 | 0.88229 | 6.9947 | 35.5222 | -2.9 | -1.7899 | 1.0938 | 0.031859
2016-05-19 21:00 | 29.39 | 29.18 | 0.21 | 1.4644 | 19.8088 | 151.6645 | 81.7554 | 8.2446 | 153.1785 | 133.8814 | 0 | 21.885 | 0.72922 | 0.88203 | 5.3579 | 27.2429 | -3 | -2.1487 | 1.095 | 0.024462
2016-05-19 22:00 | 42.0067 | 40.6 | 1.4067 | 11.3575 | 19.8176 | 166.6639 | 82.8855 | 7.1145 | 167.3682 | 140.9531 | 0 | 30.45 | 0.72906 | 0.88177 | 7.6564 | 38.1064 | -3.1 | -1.9092 | 1.0942 | 0.03419
2016-05-19 23:00 | 54.6233 | 52.02 | 2.6033 | 21.9923 | 19.8265 | 181.6634 | 83.2017 | 6.7983 | -178.4242 | 143.1706 | 0 | 39.015 | 0.72891 | 0.88151 | 9.9538 | 48.9688 | -3.1 | -1.5697 | 1.093 | 0.043889
2016-05-20 | 67.24 | 63.44 | 3.8 | 29.8398 | 19.8353 | -163.3371 | 82.6837 | 7.3163 | -164.2202 | 139.7231 | 0 | 47.58 | 0.72875 | 0.88125 | 12.2503 | 59.8303 | -3 | -1.1303 | 1.0915 | 0.053548
2016-05-20 01:00 | 89.4067 | 78.13 | 11.2767 | 75.0948 | 19.8442 | -148.3377 | 81.3635 | 8.6365 | -150.0394 | 131.8134 | 0 | 58.5975 | 0.72859 | 0.88099 | 16.2853 | 74.8828 | -3.2 | -0.85991 | 1.0905 | 0.066962
2016-05-20 02:00 | 111.5733 | 92.82 | 18.7533 | 101.2136 | 19.853 | -133.3382 | 79.3223 | 10.6777 | -135.8817 | 121.2193 | 0 | 69.615 | 0.72844 | 0.88073 | 20.3185 | 89.9335 | -3.2 | -0.38958 | 1.0889 | 0.080299
2016-05-20 03:00 | 133.74 | 107.51 | 26.23 | 113.8855 | 19.8618 | -118.3388 | 76.6841 | 13.3159 | -121.7154 | 109.1396 | 0 | 80.6325 | 0.72828 | 0.88047 | 24.3501 | 104.9826 | -3.2 | 0.080706 | 1.0872 | 0.093594
2016-05-20 04:00 | 176.5033 | 132.5367 | 43.9667 | 155.7949 | 19.8707 | -103.3393 | 73.6079 | 16.3921 | -107.4726 | 96.2202 | 0 | 99.4025 | 0.72813 | 0.88021 | 32.1291 | 131.5316 | -2.9 | 1.2104 | 1.0833 | 0.11684
2016-05-20 05:00 | 219.2667 | 157.5633 | 61.7033 | 182.8645 | 19.8795 | -88.3399 | 70.2798 | 19.7202 | -93.0535 | 82.8026 | 22.9107 | 118.1725 | 0.72797 | 0.87995 | 39.9048 | 180.988 | -2.5 | 3.1559 | 1.0765 | 0.15976
2016-05-20 06:00 | 262.03 | 182.59 | 79.44 | 202.5396 | 19.8883 | -73.3405 | 66.9073 | 23.0927 | -78.3392 | 69.0764 | 72.3317 | 136.9425 | 0.72781 | 0.87969 | 47.6772 | 256.9513 | -2.4 | 5.6297 | 1.0678 | 0.22498
2016-05-20 07:00 | 310.8467 | 204.18 | 106.6667 | 240.8566 | 19.897 | -58.341 | 63.7133 | 26.2867 | -63.2133 | 55.1546 | 137.6167 | 153.135 | 0.72766 | 0.87943 | 56.5474 | 347.2991 | -2.2 | 8.6531 | 1.0572 | 0.30108
2016-05-20 08:00 | 359.6633 | 225.77 | 133.8933 | 275.5471 | 19.9058 | -43.3416 | 60.9274 | 29.0726 | -47.5929 | 41.1129 | 207.6013 | 169.3275 | 0.7275 | 0.87917 | 65.4138 | 442.3425 | -1.7 | 12.1232 | 1.0451 | 0.37907
2016-05-20 09:00 | 408.48 | 247.36 | 161.12 | 310.7667 | 19.9146 | -28.3422 | 58.771 | 31.229 | -31.4653 | 27.0161 | 276.8554 | 185.52 | 0.72734 | 0.87891 | 74.2763 | 536.6518 | -1.1 | 15.6704 | 1.0327 | 0.45442
2016-05-20 10:00 | 410.5633 | 253.52 | 157.0433 | 291.7495 | 19.9233 | -13.3427 | 57.4333 | 32.5667 | -14.9184 | 12.9934 | 284.2795 | 190.14 | 0.72719 | 0.87865 | 74.6391 | 549.0586 | -1.4 | 15.7581 | 1.0323 | 0.46479
2016-05-20 11:00 | 412.6467 | 259.68 | 152.9667 | 281.166 | 19.9321 | 1.6567 | 57.0406 | 32.9594 | 1.8562 | 3.356 | 280.6838 | 194.76 | 0.72703 | 0.87839 | 75.0018 | 550.4456 | -0.9 | 16.3014 | 1.0304 | 0.46511
2016-05-20 12:00 | 414.73 | 265.84 | 148.89 | 278.109 | 19.9408 | 16.6561 | 57.6313 | 32.3687 | 18.603 | 16.0693 | 267.2427 | 199.38 | 0.72688 | 0.87813 | 75.3642 | 541.9869 | -1 | 15.9371 | 1.0317 | 0.45853
2016-05-20 13:00 | 352.2933 | 238.0367 | 114.2567 | 222.7882 | 19.9495 | 31.6555 | 59.1462 | 30.8538 | 35.0746 | 30.1311 | 192.6849 | 178.5275 | 0.72672 | 0.87786 | 64.0045 | 435.2169 | -1.2 | 12.4005 | 1.0441 | 0.37262
2016-05-20 14:00 | 289.8567 | 210.2333 | 79.6233 | 166.5625 | 19.9582 | 46.6549 | 61.4426 | 28.5574 | 51.0995 | 44.2179 | 119.3742 | 157.675 | 0.72656 | 0.8776 | 52.6497 | 329.6989 | -0.8 | 9.5031 | 1.0542 | 0.28502
2016-05-20 15:00 | 227.42 | 182.43 | 44.99 | 103.8266 | 19.967 | 61.6543 | 64.3216 | 25.6784 | 66.6125 | 58.2324 | 54.6622 | 136.8225 | 0.72641 | 0.87734 | 41.2998 | 232.7845 | -0.8 | 6.4745 | 1.0648 | 0.20326
2016-05-20 16:00 | 196.6867 | 158.1267 | 38.56 | 101.0096 | 19.9756 | 76.6537 | 67.5581 | 22.4419 | 81.644 | 72.1097 | 31.0297 | 118.595 | 0.72625 | 0.87708 | 35.7109 | 185.3356 | 0.4 | 6.1917 | 1.0658 | 0.16198
2016-05-20 17:00 | 165.9533 | 133.8233 | 32.13 | 98.3035 | 19.9843 | 91.6531 | 70.9226 | 19.0774 | 96.2865 | 85.7677 | 7.2549 | 100.3675 | 0.72609 | 0.87682 | 30.1244 | 137.7468 | -1 | 3.3046 | 1.0759 | 0.12153
2016-05-20 18:00 | 135.22 | 109.52 | 25.7 | 94.3581 | 19.993 | 106.6525 | 74.1949 | 15.8051 | 110.6588 | 99.0793 | 0 | 82.14 | 0.72594 | 0.87656 | 24.5403 | 106.6803 | 0.6 | 3.9338 | 1.0737 | 0.093928
2016-05-20 19:00 | 115.7033 | 86.23 | 29.4733 | 132.7436 | 20.0017 | 121.6519 | 77.1716 | 12.8284 | 124.8767 | 111.8284 | 0 | 64.6725 | 0.72578 | 0.8763 | 20.9938 | 85.6663 | 0.4 | 3.0771 | 1.0767 | 0.075636
2016-05-20 20:00 | 96.1867 | 62.94 | 33.2467 | 185.445 | 20.0103 | 136.6513 | 79.6721 | 10.3279 | 139.0333 | 123.6207 | 0 | 47.205 | 0.72563 | 0.87604 | 17.4489 | 64.6539 | -1.9 | 0.12043 | 1.0871 | 0.057633
2016-05-20 21:00 | 76.67 | 39.65 | 37.02 | 251.78 | 20.019 | 151.6506 | 81.545 | 8.455 | 153.1884 | 133.7098 | 0 | 29.7375 | 0.72547 | 0.87578 | 13.9054 | 43.6429 | -2.6 | -1.2362 | 1.0918 | 0.039073
2016-05-20 22:00 | 71.7067 | 37.9167 | 33.79 | 265.0285 | 20.0276 | 166.65 | 82.6751 | 7.3249 | 167.3661 | 140.7518 | 0 | 28.4375 | 0.72531 | 0.87552 | 13.0024 | 41.4399 | -3.3 | -2.005 | 1.0945 | 0.037193
2016-05-20 23:00 | 66.7433 | 36.1833 | 30.56 | 250.4765 | 20.0362 | 181.6494 | 82.992 | 7.008 | -178.4388 | 142.9617 | 0 | 27.1375 | 0.72516 | 0.87526 | 12.0998 | 39.2373 | -3 | -1.7738 | 1.0937 | 0.03519
2016-05-21 | 61.78 | 34.45 | 27.33 | 208.7053 | 20.0449 | -163.3512 | 82.4755 | 7.5245 | -164.2473 | 139.5389 | 0 | 25.8375 | 0.725 | 0.875 | 11.1976 | 37.0351 | -3 | -1.8427 | 1.0939 | 0.033222
2016-05-21 01:00 | 91.5667 | 40.8067 | 50.76 | 330.2058 | 20.0535 | -148.3519 | 81.1573 | 8.8427 | -150.0781 | 131.6675 | 0 | 30.605 | 0.72484 | 0.87474 | 16.5929 | 47.1979 | -1.8 | -0.32507 | 1.0886 | 0.042133
2016-05-21 02:00 | 121.3533 | 47.1633 | 74.19 | 392.9971 | 20.0621 | -133.3525 | 79.1184 | 10.8816 | -135.9307 | 121.1085 | 0 | 35.3725 | 0.72469 | 0.87448 | 21.9858 | 57.3583 | -0.8 | 0.99245 | 1.084 | 0.050986
2016-05-21 03:00 | 151.14 | 53.52 | 97.62 | 417.639 | 20.0706 | -118.3532 | 76.4825 | 13.5175 | -121.7728 | 109.0567 | 0 | 40.14 | 0.72453 | 0.87422 | 27.3764 | 67.5164 | -0.6 | 1.5099 | 1.0822 | 0.059915
2016-05-21 04:00 | 168.84 | 75.32 | 93.52 | 327.5033 | 20.0792 | -103.3538 | 73.408 | 16.592 | -107.5362 | 96.1596 | 0 | 56.49 | 0.72438 | 0.87396 | 30.5759 | 87.0659 | -0.4 | 2.3208 | 1.0794 | 0.077061
2016-05-21 05:00 | 186.54 | 97.12 | 89.42 | 262.4644 | 20.0878 | -88.3545 | 70.0808 | 19.9192 | -93.1206 | 82.7602 | 33.0763 | 72.84 | 0.72422 | 0.8737 | 33.7739 | 139.6903 | -0.2 | 4.1653 | 1.0729 | 0.1229
2016-05-21 06:00 | 204.24 | 118.92 | 85.32 | 215.7746 | 20.0964 | -73.3551 | 66.7083 | 23.2917 | -78.4069 | 69.0496 | 77.1521 | 89.19 | 0.72406 | 0.87344 | 36.9706 | 203.3127 | 0.2 | 6.5535 | 1.0646 | 0.17748
2016-05-21 07:00 | 214.5667 | 155.1633 | 59.4033 | 133.1938 | 20.1049 | -58.3558 | 63.5132 | 26.4868 | -63.2781 | 55.1424 | 76.1254 | 116.3725 | 0.72391 | 0.87318 | 38.8315 | 231.3295 | 0.3 | 7.529 | 1.0611 | 0.20129
2016-05-21 08:00 | 224.8933 | 191.4067 | 33.4867 | 68.4807 | 20.1134 | -43.3564 | 60.7255 | 29.2745 | -47.6508 | 41.1154 | 51.5924 | 143.555 | 0.72375 | 0.87292 | 40.6916 | 235.839 | 0.4 | 7.77 | 1.0603 | 0.20505
2016-05-21 09:00 | 235.22 | 227.65 | 7.57 | 14.5158 | 20.122 | -28.3571 | 58.567 | 31.433 | -31.512 | 27.0366 | 12.9295 | 170.7375 | 0.72359 | 0.87266 | 42.5509 | 226.2179 | 0.2 | 7.2693 | 1.0621 | 0.19701
2016-05-21 10:00 | 246.1267 | 237.1967 | 8.93 | 16.4971 | 20.1305 | -13.3578 | 57.2274 | 32.7726 | -14.9503 | 13.0482 | 16.0712 | 177.8975 | 0.72344 | 0.8724 | 44.5143 | 238.483 | 0.7 | 8.1526 | 1.059 | 0.20709
2016-05-21 11:00 | 257.0333 | 246.7433 | 10.29 | 18.8092 | 20.139 | 1.6415 | 56.8336 | 33.1664 | 1.8412 | 3.5334 | 18.7735 | 185.0575 | 0.72328 | 0.87214 | 46.4768 | 250.3078 | 0.6 | 8.4221 | 1.058 | 0.21716
2016-05-21 12:00 | 267.94 | 256.29 | 11.65 | 21.6375 | 20.1475 | 16.6409 | 57.4241 | 32.5759 | 18.6049 | 16.0849 | 20.7905 | 192.2175 | 0.72313 | 0.87188 | 48.4385 | 261.4465 | 0.7 | 8.8702 | 1.0565 | 0.22649
2016-05-21 13:00 | 248.34 | 233.17 | 15.17 | 29.4027 | 20.156 | 31.6402 | 58.9398 | 31.0602 | 35.0912 | 30.1188 | 25.433 | 174.8775 | 0.72297 | 0.87161 | 44.8855 | 245.196 | 0.5 | 8.1624 | 1.0589 | 0.21291
2016-05-21 14:00 | 228.74 | 210.05 | 18.69 | 38.8418 | 20.1645 | 46.6395 | 61.2373 | 28.7627 | 51.1272 | 44.189 | 27.8513 | 157.5375 | 0.72281 | 0.87135 | 41.334 | 226.7228 | 0.7 | 7.7851 | 1.0603 | 0.19711
2016-05-21 15:00 | 209.14 | 186.93 | 22.21 | 50.8789 | 20.1729 | 61.6388 | 64.1175 | 25.8825 | 66.6472 | 58.1893 | 26.819 | 140.1975 | 0.72266 | 0.87109 | 37.7841 | 204.8006 | 1 | 7.4 | 1.0616 | 0.17828
2016-05-21 16:00 | 196.6733 | 170.4533 | 26.22 | 68.0997 | 20.1814 | 76.6381 | 67.3548 | 22.6452 | 81.6815 | 72.0525 | 20.9846 | 127.84 | 0.7225 | 0.87083 | 35.5241 | 184.3487 | 1 | 6.7609 | 1.0638 | 0.16082
2016-05-21 17:00 | 184.2067 | 153.9767 | 30.23 | 91.5526 | 20.1898 | 91.6374 | 70.7195 | 19.2805 | 96.3233 | 85.6951 | 6.8723 | 115.4825 | 0.72234 | 0.87057 | 33.2651 | 155.6199 | 0.9 | 5.7631 | 1.0673 | 0.1362
2016-05-21 18:00 | 171.74 | 137.5 | 34.24 | 124.157 | 20.1983 | 106.6367 | 73.9915 | 16.0085 | 110.6918 | 98.989 | 0 | 103.125 | 0.72219 | 0.87031 | 31.0071 | 134.1321 | 1.1 | 5.2916 | 1.069 | 0.11758
2016-05-21 19:00 | 140.3467 | 109.8667 | 30.48 | 135.1654 | 20.2067 | 121.636 | 76.9676 | 13.0324 | 124.9032 | 111.7167 | 0 | 82.4 | 0.72203 | 0.87005 | 25.3337 | 107.7337 | 0.8 | 4.1667 | 1.0729 | 0.094783
2016-05-21 20:00 | 108.9533 | 82.2333 | 26.72 | 146.1767 | 20.2151 | 136.6353 | 79.4675 | 10.5325 | 139.0511 | 123.4828 | 0 | 61.675 | 0.72188 | 0.86979 | 19.6627 | 81.3377 | 0.5 | 3.0418 | 1.0769 | 0.071823
2016-05-21 21:00 | 77.56 | 54.6 | 22.96 | 152.4861 | 20.2235 | 151.6346 | 81.34 | 8.66 | 153.1956 | 133.5411 | 0 | 40.95 | 0.72172 | 0.86953 | 13.9941 | 54.9441 | 0.3 | 2.017 | 1.0804 | 0.048678
2016-05-21 22:00 | 79.6933 | 50.21 | 29.4833 | 224.9935 | 20.2319 | 166.6339 | 82.4703 | 7.5297 | 167.3617 | 140.555 | 0 | 37.6575 | 0.72156 | 0.86927 | 14.3759 | 52.0334 | 0.1 | 1.726 | 1.0815 | 0.046143
2016-05-21 23:00 | 81.8267 | 45.82 | 36.0067 | 286.8136 | 20.2403 | 181.6331 | 82.788 | 7.212 | -178.4555 | 142.7585 | 0 | 34.365 | 0.72141 | 0.86901 | 14.7576 | 49.1226 | -0.4 | 1.1351 | 1.0835 | 0.043645
2016-05-22 | 83.96 | 41.43 | 42.53 | 316.3215 | 20.2487 | -163.3676 | 82.2731 | 7.7269 | -164.2761 | 139.3605 | 0 | 31.0725 | 0.72125 | 0.86875 | 15.139 | 46.2115 | -0.3 | 1.1441 | 1.0835 | 0.041057
2016-05-22 01:00 | 124.8333 | 47.2 | 77.6333 | 493.927 | 20.2571 | -148.3683 | 80.957 | 9.043 | -150.1183 | 131.5269 | 0 | 35.4 | 0.72109 | 0.86849 | 22.5041 | 57.9041 | -0.3 | 1.5095 | 1.0822 | 0.051385
2016-05-22 02:00 | 165.7067 | 52.97 | 112.7367 | 586.6468 | 20.2654 | -133.369 | 78.9205 | 11.0795 | -135.9809 | 121.0023 | 0 | 39.7275 | 0.72094 | 0.86823 | 29.866 | 69.5935 | -0.4 | 1.7748 | 1.0813 | 0.061706
2016-05-22 03:00 | 206.58 | 58.74 | 147.84 | 623.6351 | 20.2738 | -118.3698 | 76.2868 | 13.7132 | -121.8312 | 108.9781 | 0 | 44.055 | 0.72078 | 0.86797 | 37.2247 | 81.2797 | 0 | 2.54 | 1.0786 | 0.071889
2016-05-22 04:00 | 261.9833 | 67.7733 | 194.21 | 672.481 | 20.2821 | -103.3705 | 73.2141 | 16.7859 | -107.6006 | 96.1028 | 0 | 50.83 | 0.72063 | 0.86771 | 47.1979 | 98.0279 | 0 | 3.0634 | 1.0768 | 0.086555
2016-05-22 05:00 | 317.3867 | 76.8067 | 240.58 | 699.6489 | 20.2905 | -88.3713 | 69.8879 | 20.1121 | -93.1887 | 82.7214 | 88.6416 | 57.605 | 0.72047 | 0.86745 | 57.1668 | 203.4134 | 0.9 | 7.2567 | 1.0621 | 0.17716
2016-05-22 06:00 | 372.79 | 85.84 | 286.95 | 720.0674 | 20.2988 | -73.372 | 66.5153 | 23.4847 | -78.4757 | 69.0263 | 257.74 | 64.38 | 0.72031 | 0.86719 | 67.1313 | 389.2513 | 0.6 | 12.7641 | 1.0428 | 0.33286
2016-05-22 07:00 | 390.4233 | 134.26 | 256.1633 | 570.4937 | 20.3071 | -58.3728 | 63.3191 | 26.6809 | -63.3441 | 55.1334 | 326.1324 | 100.695 | 0.72016 | 0.86693 | 70.2915 | 497.1189 | 1.1 | 16.635 | 1.0293 | 0.41957
2016-05-22 08:00 | 408.0567 | 182.68 | 225.3767 | 458.107 | 20.3154 | -43.3735 | 60.5296 | 29.4704 | -47.71 | 41.1211 | 345.1015 | 137.01 | 0.72 | 0.86667 | 73.4502 | 555.5617 | 0.9 | 18.2613 | 1.0236 | 0.46631
2016-05-22 09:00 | 425.69 | 231.1 | 194.59 | 371.038 | 20.3237 | -28.3743 | 58.3689 | 31.6311 | -31.5605 | 27.0602 | 330.42 | 173.325 | 0.71984 | 0.86641 | 76.6076 | 580.3525 | 1.3 | 19.436 | 1.0195 | 0.48516
2016-05-22 10:00 | 400.1233 | 242.4833 | 157.64 | 289.652 | 20.332 | -13.375 | 57.0273 | 32.9727 | -14.9845 | 13.1068 | 282.1064 | 181.8625 | 0.71969 | 0.86615 | 71.9909 | 535.9598 | 2.5 | 19.2487 | 1.0201 | 0.44833
2016-05-22 11:00 | 374.5567 | 253.8667 | 120.69 | 219.4322 | 20.3402 | 1.6242 | 56.6323 | 33.3677 | 1.8236 | 3.7078 | 218.9728 | 190.4 | 0.71953 | 0.86589 | 67.3763 | 476.7492 | 2.5 | 17.3984 | 1.0266 | 0.40134
2016-05-22 12:00 | 348.99 | 265.25 | 83.74 | 154.6792 | 20.3485 | 16.6234 | 57.2225 | 32.7775 | 18.6038 | 16.1002 | 148.6123 | 198.9375 | 0.71938 | 0.86562 | 62.7637 | 410.3135 | 2.6 | 15.4223 | 1.0335 | 0.34774
2016-05-22 13:00 | 275.4533 | 218.2967 | 57.1567 | 110.1407 | 20.3567 | 31.6226 | 58.7387 | 31.2613 | 35.1046 | 30.1056 | 95.2829 | 163.7225 | 0.71922 | 0.86536 | 49.5278 | 308.5332 | 2.7 | 12.3417 | 1.0443 | 0.26421
2016-05-22 14:00 | 201.9167 | 171.3433 | 30.5733 | 63.1366 | 20.365 | 46.6219 | 61.0372 | 28.9628 | 51.1515 | 44.1592 | 45.2947 | 128.5075 | 0.71906 | 0.8651 | 36.2977 | 210.0998 | 2.7 | 9.2656 | 1.0551 | 0.18177
2016-05-22 15:00 | 128.38 | 124.39 | 3.99 | 9.0754 | 20.3732 | 61.6211 | 63.9185 | 26.0815 | 66.6783 | 58.1454 | 4.7897 | 93.2925 | 0.71891 | 0.86484 | 23.0733 | 121.1555 | 2 | 5.7861 | 1.0672 | 0.10603
2016-05-22 16:00 | 92.1867 | 89.2633 | 2.9233 | 7.5302 | 20.3814 | 76.6203 | 67.1565 | 22.8435 | 81.7155 | 71.9947 | 2.3276 | 66.9475 | 0.71875 | 0.86458 | 16.5648 | 85.8399 | 2.8 | 5.4825 | 1.0683 | 0.075197
2016-05-22 17:00 | 55.9933 | 54.1367 | 1.8567 | 5.568 | 20.3896 | 91.6195 | 70.5215 | 19.4785 | 96.3566 | 85.6223 | 0.42501 | 40.6025 | 0.71859 | 0.86432 | 10.0591 | 51.0866 | 2 | 3.5965 | 1.0749 | 0.045029
2016-05-22 18:00 | 19.8 | 19.01 | 0.79 | 2.8305 | 20.3978 | 106.6187 | 73.7933 | 16.2067 | 110.7214 | 98.8989 | 0 | 14.2575 | 0.71844 | 0.86406 | 3.5563 | 17.8138 | 1 | 1.5567 | 1.0821 | 0.015806
2016-05-22 19:00 | 15.9633 | 15.4367 | 0.52667 | 2.3011 | 20.406 | 121.6179 | 76.7689 | 13.2311 | 124.9264 | 111.6058 | 0 | 11.5775 | 0.71828 | 0.8638 | 2.8665 | 14.444 | 1 | 1.4514 | 1.0824 | 0.01282
2016-05-22 20:00 | 12.1267 | 11.8633 | 0.26333 | 1.4142 | 20.4142 | 136.6171 | 79.2683 | 10.7317 | 139.0658 | 123.3465 | 0 | 8.8975 | 0.71813 | 0.86354 | 2.1771 | 11.0746 | 0.8 | 1.1461 | 1.0835 | 0.0098394
2016-05-22 21:00 | 8.29 | 8.29 | 0 | 0 | 20.4224 | 151.6163 | 81.1405 | 8.8595 | 153.2002 | 133.3753 | 0 | 6.2175 | 0.71797 | 0.86328 | 1.488 | 7.7055 | 2.1 | 2.3408 | 1.0793 | 0.0068196
2016-05-22 22:00 | 15.8767 | 15.8767 | 0 | 0 | 20.4305 | 166.6155 | 82.271 | 7.729 | 167.3548 | 140.3628 | 0 | 11.9075 | 0.71781 | 0.86302 | 2.8491 | 14.7566 | 1.3 | 1.7611 | 1.0813 | 0.013085
2016-05-22 23:00 | 23.4633 | 23.4633 | 0 | 0 | 20.4387 | 181.6147 | 82.5898 | 7.4102 | -178.4742 | 142.5611 | 0 | 17.5975 | 0.71766 | 0.86276 | 4.2097 | 21.8072 | 1.4 | 2.0815 | 1.0802 | 0.019316
2016-05-23 | 31.05 | 31.05 | 0 | 0 | 20.4468 | -163.3861 | 82.0765 | 7.9235 | -164.3067 | 139.188 | 0 | 23.2875 | 0.7175 | 0.8625 | 5.5696 | 28.8571 | 1.8 | 2.7018 | 1.078 | 0.02551
2016-05-23 01:00 | 43.1567 | 43.1533 | 0.0033333 | 0.020765 | 20.455 | -148.387 | 80.7626 | 9.2374 | -150.1599 | 131.3915 | 0 | 32.365 | 0.71734 | 0.86224 | 7.7395 | 40.1045 | 2.6 | 3.8533 | 1.074 | 0.03532
2016-05-23 02:00 | 55.2633 | 55.2567 | 0.0066667 | 0.034108 | 20.4631 | -133.3878 | 78.7285 | 11.2715 | -136.0322 | 120.9008 | 0 | 41.4425 | 0.71719 | 0.86198 | 9.9085 | 51.351 | 2.7 | 4.3047 | 1.0724 | 0.045158
2016-05-23 03:00 | 67.37 | 67.36 | 0.01 | 0.041619 | 20.4712 | -118.3886 | 76.0972 | 13.9028 | -121.8905 | 108.9037 | 0 | 50.52 | 0.71703 | 0.86172 | 12.0766 | 62.5966 | 3.2 | 5.1561 | 1.0695 | 0.054894
2016-05-23 04:00 | 88.5433 | 87.17 | 1.3733 | 4.7043 | 20.4793 | -103.3894 | 73.0263 | 16.9737 | -107.6659 | 96.0499 | 0 | 65.3775 | 0.71688 | 0.86146 | 15.8686 | 81.2461 | 3.3 | 5.8389 | 1.0671 | 0.07109
2016-05-23 05:00 | 109.7167 | 106.98 | 2.7367 | 7.8885 | 20.4874 | -88.3903 | 69.701 | 20.299 | -93.2575 | 82.6861 | 1.0042 | 80.235 | 0.71672 | 0.8612 | 19.659 | 100.8982 | 3.4 | 6.5531 | 1.0646 | 0.088078
2016-05-23 06:00 | 130.89 | 126.79 | 4.1 | 10.2119 | 20.4955 | -73.3911 | 66.3284 | 23.6716 | -78.5452 | 69.0064 | 3.6585 | 95.0925 | 0.71656 | 0.86094 | 23.4477 | 122.1988 | 3.3 | 7.1187 | 1.0626 | 0.10647
2016-05-23 07:00 | 152.0767 | 149.22 | 2.8567 | 6.3208 | 20.5035 | -58.392 | 63.1312 | 26.8688 | -63.4111 | 55.1277 | 3.6139 | 111.915 | 0.71641 | 0.86068 | 27.2372 | 142.7661 | 3 | 7.4614 | 1.0614 | 0.12425
2016-05-23 08:00 | 173.2633 | 171.65 | 1.6133 | 3.2602 | 20.5116 | -43.3928 | 60.3398 | 29.6602 | -47.7706 | 41.1299 | 2.4557 | 128.7375 | 0.71625 | 0.86042 | 31.025 | 162.2181 | 3 | 8.0693 | 1.0593 | 0.1409
2016-05-23 09:00 | 194.45 | 194.08 | 0.37 | 0.70169 | 20.5196 | -28.3937 | 58.1768 | 31.8232 | -31.6107 | 27.0871 | 0.62472 | 145.56 | 0.71609 | 0.86016 | 34.8111 | 180.9958 | 3 | 8.6561 | 1.0572 | 0.15691
2016-05-23 10:00 | 207.66 | 192.62 | 15.04 | 27.4914 | 20.5277 | -13.3945 | 56.8331 | 33.1669 | -15.0208 | 13.1687 | 26.7685 | 144.465 | 0.71594 | 0.8599 | 37.1679 | 208.4014 | 3.2 | 9.7125 | 1.0535 | 0.18003
2016-05-23 11:00 | 220.87 | 191.16 | 29.71 | 53.7389 | 20.5357 | 1.6046 | 56.4367 | 33.5633 | 1.8034 | 3.8789 | 53.6158 | 143.37 | 0.71578 | 0.85964 | 39.5237 | 236.5094 | 2.8 | 10.1909 | 1.0518 | 0.20399
2016-05-23 12:00 | 234.08 | 189.7 | 44.38 | 81.543 | 20.5437 | 16.6038 | 57.0264 | 32.9736 | 18.5998 | 16.115 | 78.3389 | 142.275 | 0.71563 | 0.85938 | 41.8784 | 262.4923 | 3 | 11.2029 | 1.0483 | 0.22564
2016-05-23 13:00 | 208.91 | 177.7233 | 31.1867 | 59.7607 | 20.5517 | 31.6029 | 58.543 | 31.457 | 35.1148 | 30.0915 | 51.7065 | 133.2925 | 0.71547 | 0.85911 | 37.3671 | 222.3662 | 3.1 | 10.0489 | 1.0523 | 0.19188
2016-05-23 14:00 | 183.74 | 165.7467 | 17.9933 | 36.9312 | 20.5597 | 46.602 | 60.8425 | 29.1575 | 51.1724 | 44.1284 | 26.5085 | 124.31 | 0.71531 | 0.85885 | 32.8579 | 183.6764 | 3.5 | 9.2399 | 1.0552 | 0.15892
2016-05-23 15:00 | 158.57 | 153.77 | 4.8 | 10.8429 | 20.5677 | 61.6012 | 63.7247 | 26.2753 | 66.7059 | 58.1007 | 5.7297 | 115.3275 | 0.71516 | 0.85859 | 28.3506 | 149.4078 | 2.5 | 7.169 | 1.0624 | 0.13016
2016-05-23 16:00 | 155.2967 | 128.67 | 26.6267 | 68.0433 | 20.5757 | 76.6003 | 66.9634 | 23.0366 | 81.746 | 71.9363 | 21.0984 | 96.5025 | 0.715 | 0.85833 | 27.7593 | 145.3602 | 1.6 | 6.1425 | 1.066 | 0.12706
2016-05-23 17:00 | 152.0233 | 103.57 | 48.4533 | 143.9385 | 20.5837 | 91.5994 | 70.3286 | 19.6714 | 96.3865 | 85.5492 | 11.17 | 77.6775 | 0.71484 | 0.85807 | 27.1682 | 116.0157 | 1.9 | 5.5255 | 1.0682 | 0.10162
2016-05-23 18:00 | 148.75 | 78.47 | 70.28 | 248.9214 | 20.5916 | 106.5985 | 73.6002 | 16.3998 | 110.7476 | 98.809 | 0 | 58.8525 | 0.71469 | 0.85781 | 26.5774 | 85.4299 | 1.1 | 3.7697 | 1.0743 | 0.075258
2016-05-23 19:00 | 117.5233 | 67.8533 | 49.67 | 213.9421 | 20.5996 | 121.5976 | 76.5754 | 13.4246 | 124.9466 | 111.4958 | 0 | 50.89 | 0.71453 | 0.85755 | 20.9935 | 71.8835 | 1.4 | 3.6464 | 1.0747 | 0.06335
2016-05-23 20:00 | 86.2967 | 57.2367 | 29.06 | 153.323 | 20.6075 | 136.5967 | 79.0744 | 10.9256 | 139.0777 | 123.2121 | 0 | 42.9275 | 0.71437 | 0.85729 | 15.412 | 58.3395 | 1 | 2.8231 | 1.0776 | 0.051552
2016-05-23 21:00 | 55.07 | 46.62 | 8.45 | 53.6994 | 20.6154 | 151.5959 | 80.9465 | 9.0535 | 153.2022 | 133.2126 | 0 | 34.965 | 0.71422 | 0.85703 | 9.833 | 44.798 | 1.5 | 2.8999 | 1.0774 | 0.039576
2016-05-23 22:00 | 54.0333 | 45.9333 | 8.1 | 58.7663 | 20.6234 | 166.595 | 82.0775 | 7.9225 | 167.3457 | 140.1753 | 0 | 34.45 | 0.71406 | 0.85677 | 9.6458 | 44.0958 | 1.4 | 2.778 | 1.0778 | 0.038971
2016-05-23 23:00 | 52.9967 | 45.2467 | 7.75 | 58.578 | 20.6313 | 181.5941 | 82.3974 | 7.6026 | -178.495 | 142.3696 | 0 | 33.935 | 0.71391 | 0.85651 | 9.4587 | 43.3937 | 1.7 | 3.0561 | 1.0768 | 0.038316
2016-05-24 | 51.96 | 44.56 | 7.4 | 52.4281 | 20.6392 | -163.4069 | 81.8859 | 8.1141 | -164.3388 | 139.0213 | 0 | 33.42 | 0.71375 | 0.85625 | 9.2716 | 42.6916 | 1.5 | 2.8341 | 1.0776 | 0.037723
2016-05-24 01:00 | 69.7367 | 63.0967 | 6.64 | 40.5449 | 20.647 | -148.4078 | 80.5743 | 9.4257 | -150.2028 | 131.2615 | 0 | 47.3225 | 0.71359 | 0.85599 | 12.4409 | 59.7634 | 1.2 | 3.0676 | 1.0768 | 0.052768
2016-05-24 02:00 | 87.5133 | 81.6333 | 5.88 | 29.6016 | 20.6549 | -133.4087 | 78.5427 | 11.4573 | -136.0846 | 120.804 | 0 | 61.225 | 0.71344 | 0.85573 | 15.6088 | 76.8338 | 1.2 | 3.6011 | 1.0749 | 0.067722
2016-05-24 03:00 | 105.29 | 100.17 | 5.12 | 21.0367 | 20.6628 | -118.4096 | 75.9137 | 14.0863 | -121.9507 | 108.8335 | 0 | 75.1275 | 0.71328 | 0.85547 | 18.7753 | 93.9028 | 1.3 | 4.2345 | 1.0727 | 0.082597
2016-05-24 04:00 | 151.4067 | 139.2 | 12.2067 | 41.3834 | 20.6706 | -103.4105 | 72.8445 | 17.1555 | -107.7319 | 96.0008 | 0 | 104.4 | 0.71313 | 0.85521 | 26.993 | 131.393 | 1.2 | 5.306 | 1.0689 | 0.11517
2016-05-24 05:00 | 197.5233 | 178.23 | 19.2933 | 55.1434 | 20.6785 | -88.4114 | 69.5203 | 20.4797 | -93.3271 | 82.6544 | 7.0503 | 133.6725 | 0.71297 | 0.85495 | 35.207 | 175.9298 | 1.8 | 7.2978 | 1.062 | 0.1532
2016-05-24 06:00 | 243.64 | 217.26 | 26.38 | 65.2354 | 20.6863 | -73.4124 | 66.1476 | 23.8524 | -78.6156 | 68.9897 | 23.3892 | 162.945 | 0.71281 | 0.85469 | 43.4174 | 229.7516 | 1.9 | 9.0797 | 1.0557 | 0.19889
2016-05-24 07:00 | 298.2333 | 248.3467 | 49.8867 | 109.6945 | 20.6941 | -58.4133 | 62.9493 | 27.0507 | -63.479 | 55.125 | 62.722 | 186.26 | 0.71266 | 0.85443 | 53.1345 | 302.1164 | 2.2 | 11.6411 | 1.0468 | 0.25932
2016-05-24 08:00 | 352.8267 | 279.4333 | 73.3933 | 147.4828 | 20.702 | -43.4142 | 60.156 | 29.844 | -47.8325 | 41.1417 | 111.067 | 209.575 | 0.7125 | 0.85417 | 62.8473 | 383.4893 | 2.1 | 14.084 | 1.0382 | 0.32648
2016-05-24 09:00 | 407.42 | 310.52 | 96.9 | 182.8109 | 20.7098 | -28.4152 | 57.9908 | 32.0092 | -31.6626 | 27.1168 | 162.7162 | 232.89 | 0.71234 | 0.85391 | 72.5558 | 468.1619 | 2.1 | 16.7301 | 1.0289 | 0.395
2016-05-24 10:00 | 400.88 | 299.8567 | 101.0233 | 183.7366 | 20.7176 | -13.4161 | 56.6449 | 33.3551 | -15.0591 | 13.2338 | 178.8573 | 224.8925 | 0.71219 | 0.85365 | 71.3754 | 475.1252 | 1.8 | 16.6477 | 1.0292 | 0.40099
2016-05-24 11:00 | 394.34 | 289.1933 | 105.1467 | 189.2435 | 20.7253 | 1.5829 | 56.2469 | 33.7531 | 1.7807 | 4.0461 | 188.7718 | 216.895 | 0.71203 | 0.85339 | 70.1956 | 475.8624 | 1.7 | 16.5707 | 1.0295 | 0.40172
2016-05-24 12:00 | 387.8 | 278.53 | 109.27 | 199.7486 | 20.7331 | 16.582 | 56.836 | 33.164 | 18.5929 | 16.129 | 191.8862 | 208.8975 | 0.71188 | 0.85313 | 69.0163 | 469.8 | 2.6 | 17.2812 | 1.027 | 0.39564
2016-05-24 13:00 | 347.8767 | 249.7733 | 98.1033 | 186.9749 | 20.7409 | 31.581 | 58.3528 | 31.6472 | 35.1217 | 30.0764 | 161.8002 | 187.33 | 0.71172 | 0.85286 | 61.8976 | 411.0278 | 1.9 | 14.7446 | 1.0359 | 0.34914
2016-05-24 14:00 | 307.9533 | 221.0167 | 86.9367 | 177.3867 | 20.7486 | 46.5801 | 60.6531 | 29.3469 | 51.19 | 44.0967 | 127.3932 | 165.7625 | 0.71156 | 0.8526 | 54.782 | 347.9377 | 1.4 | 12.2731 | 1.0445 | 0.29802
2016-05-24 15:00 | 268.03 | 192.26 | 75.77 | 170.0277 | 20.7564 | 61.5791 | 63.5361 | 26.4639 | 66.7301 | 58.0553 | 89.9618 | 144.195 | 0.71141 | 0.85234 | 47.6696 | 281.8263 | 1.2 | 10.0071 | 1.0525 | 0.24322
2016-05-24 16:00 | 224.2767 | 155.67 | 68.6067 | 173.9804 | 20.7641 | 76.5782 | 66.7755 | 23.2245 | 81.773 | 71.8775 | 54.1166 | 116.7525 | 0.71125 | 0.85208 | 39.8792 | 210.7483 | 2.1 | 8.6859 | 1.0571 | 0.18268
2016-05-24 17:00 | 180.5233 | 119.08 | 61.4433 | 180.8711 | 20.7718 | 91.5772 | 70.1409 | 19.8591 | 96.4129 | 85.476 | 14.2666 | 89.31 | 0.71109 | 0.85182 | 32.0923 | 135.6688 | 1.9 | 6.1397 | 1.066 | 0.11859
2016-05-24 18:00 | 136.77 | 82.49 | 54.28 | 190.1353 | 20.7796 | 106.5762 | 73.4124 | 16.5876 | 110.7706 | 98.7194 | 0 | 61.8675 | 0.71094 | 0.85156 | 24.3087 | 86.1762 | 1.7 | 4.393 | 1.0721 | 0.075761
2016-05-24 19:00 | 117.6133 | 68.6633 | 48.95 | 207.9809 | 20.7873 | 121.5752 | 76.3873 | 13.6127 | 124.9636 | 111.3867 | 0 | 51.4975 | 0.71078 | 0.8513 | 20.8993 | 72.3968 | 1.9 | 4.1624 | 1.0729 | 0.063695
2016-05-24 20:00 | 98.4567 | 54.8367 | 43.62 | 226.289 | 20.7949 | 136.5743 | 78.886 | 11.114 | 139.0867 | 123.0795 | 0 | 41.1275 | 0.71063 | 0.85104 | 17.4914 | 58.6189 | 1.4 | 3.2318 | 1.0762 | 0.05173
2016-05-24 21:00 | 79.3 | 41.01 | 38.29 | 238.4133 | 20.8026 | 151.5733 | 80.7581 | 9.2419 | 153.2015 | 133.0531 | 0 | 30.7575 | 0.71047 | 0.85078 | 14.085 | 44.8425 | 1.6 | 3.0013 | 1.077 | 0.039602
2016-05-24 22:00 | 75.0367 | 43.0367 | 32 | 226.8217 | 20.8103 | 166.5723 | 81.8897 | 8.1103 | 167.3343 | 139.9925 | 0 | 32.2775 | 0.71031 | 0.85052 | 13.3249 | 45.6024 | 1.8 | 3.2251 | 1.0762 | 0.040244
2016-05-24 23:00 | 70.7733 | 45.0633 | 25.71 | 189.701 | 20.818 | 181.5713 | 82.2108 | 7.7892 | -178.5176 | 142.1839 | 0 | 33.7975 | 0.71016 | 0.85026 | 12.565 | 46.3625 | 2.1 | 3.5488 | 1.0751 | 0.040872
2016-05-25 | 66.51 | 47.09 | 19.42 | 134.5473 | 20.8256 | -163.4297 | 81.7012 | 8.2988 | -164.3726 | 138.8606 | 0 | 35.3175 | 0.71 | 0.85 | 11.8055 | 47.123 | 1.3 | 2.7726 | 1.0778 | 0.041647
2016-05-25 01:00 | 91.33 | 64.2133 | 27.1167 | 162.4656 | 20.8333 | -148.4307 | 80.392 | 9.608 | -150.247 | 131.1368 | 0 | 48.16 | 0.70984 | 0.84974 | 16.2075 | 64.3675 | 1.7 | 3.7115 | 1.0745 | 0.056714
2016-05-25 02:00 | 116.15 | 81.3367 | 34.8133 | 172.5895 | 20.8409 | -133.4317 | 78.3629 | 11.6371 | -136.138 | 120.712 | 0 | 61.0025 | 0.70969 | 0.84948 | 20.6076 | 81.6101 | 1.8 | 4.3503 | 1.0723 | 0.071757
2016-05-25 03:00 | 140.97 | 98.46 | 42.51 | 172.5345 | 20.8485 | -118.4327 | 75.7363 | 14.2637 | -122.0117 | 108.7675 | 0 | 73.845 | 0.70953 | 0.84922 | 25.0057 | 98.8507 | 1.7 | 4.7891 | 1.0707 | 0.086791
2016-05-25 04:00 | 169.4867 | 129.0033 | 40.4833 | 135.8996 | 20.8561 | -103.4337 | 72.669 | 17.331 | -107.7986 | 95.9555 | 0 | 96.7525 | 0.70938 | 0.84896 | 30.0574 | 126.8099 | 1.6 | 5.5628 | 1.068 | 0.11106
2016-05-25 05:00 | 198.0033 | 159.5467 | 38.4567 | 109.0264 | 20.8637 | -88.4347 | 69.3457 | 20.6543 | -93.3973 | 82.6262 | 13.9928 | 119.66 | 0.70922 | 0.8487 | 35.1069 | 168.7597 | 1.3 | 6.5737 | 1.0645 | 0.14731
2016-05-25 06:00 | 226.52 | 190.09 | 36.43 | 89.472 | 20.8713 | -73.4357 | 65.973 | 24.027 | -78.6867 | 68.9763 | 32.0985 | 142.5675 | 0.70906 | 0.84844 | 40.1542 | 214.8202 | 1.4 | 8.1131 | 1.0591 | 0.18656
2016-05-25 07:00 | 266.3067 | 216.9533 | 49.3533 | 107.8746 | 20.8789 | -58.4367 | 62.7737 | 27.2263 | -63.5479 | 55.1254 | 61.6809 | 162.715 | 0.70891 | 0.84818 | 47.1966 | 271.5925 | 1.7 | 10.1873 | 1.0518 | 0.23425
2016-05-25 08:00 | 306.0933 | 243.8167 | 62.2767 | 124.4722 | 20.8865 | -43.4378 | 59.9784 | 30.0216 | -47.8956 | 41.1563 | 93.7172 | 182.8625 | 0.70875 | 0.84792 | 54.2359 | 330.8156 | 1.9 | 12.238 | 1.0447 | 0.28339
2016-05-25 09:00 | 345.88 | 270.68 | 75.2 | 141.1632 | 20.894 | -28.4388 | 57.8108 | 32.1892 | -31.716 | 27.1493 | 125.6099 | 203.01 | 0.70859 | 0.84766 | 61.2721 | 389.892 | 1.9 | 14.0841 | 1.0382 | 0.33193
2016-05-25 10:00 | 342 | 277.5033 | 64.4967 | 116.7401 | 20.9016 | -13.4398 | 56.4626 | 33.5374 | -15.0994 | 13.3015 | 113.6083 | 208.1275 | 0.70844 | 0.8474 | 60.5714 | 382.3072 | 2.3 | 14.2471 | 1.0376 | 0.32529
2016-05-25 11:00 | 338.12 | 284.3267 | 53.7933 | 96.3552 | 20.9091 | 1.5591 | 56.063 | 33.937 | 1.7556 | 4.2091 | 96.0953 | 213.245 | 0.70828 | 0.84714 | 59.871 | 369.2113 | 1.9 | 13.4379 | 1.0405 | 0.315
2016-05-25 12:00 | 334.24 | 291.15 | 43.09 | 78.3835 | 20.9166 | 16.5581 | 56.6513 | 33.3487 | 18.5832 | 16.1422 | 75.2932 | 218.3625 | 0.70813 | 0.84688 | 59.1709 | 352.8266 | 1.9 | 12.9258 | 1.0423 | 0.30154
2016-05-25 13:00 | 318.45 | 264.7 | 53.75 | 101.9098 | 20.9241 | 31.5571 | 58.1682 | 31.8318 | 35.1256 | 30.0603 | 88.2029 | 198.525 | 0.70797 | 0.84661 | 56.3632 | 343.091 | 2.2 | 12.9216 | 1.0423 | 0.29323
2016-05-25 14:00 | 302.66 | 238.25 | 64.41 | 130.6774 | 20.9317 | 46.556 | 60.4691 | 29.5309 | 51.2041 | 44.0641 | 93.8999 | 178.6875 | 0.70781 | 0.84635 | 53.5566 | 326.1441 | 2 | 12.192 | 1.0448 | 0.27943
2016-05-25 15:00 | 286.87 | 211.8 | 75.07 | 167.3825 | 20.9391 | 61.555 | 63.3529 | 26.6471 | 66.7508 | 58.0091 | 88.6767 | 158.85 | 0.70766 | 0.84609 | 50.7513 | 298.2781 | 2.1 | 11.4212 | 1.0475 | 0.25621
2016-05-25 16:00 | 259.47 | 178.47 | 81 | 203.8952 | 20.9466 | 76.5539 | 66.5928 | 23.4072 | 81.7965 | 71.8181 | 63.6223 | 133.8525 | 0.7075 | 0.84583 | 45.8938 | 243.3686 | 1.8 | 9.4053 | 1.0546 | 0.21045
2016-05-25 17:00 | 232.07 | 145.14 | 86.93 | 253.662 | 20.9541 | 91.5529 | 69.9585 | 20.0415 | 96.436 | 85.4026 | 20.3318 | 108.855 | 0.70734 | 0.84557 | 41.0383 | 170.2251 | 1.9 | 7.2195 | 1.0622 | 0.14827
2016-05-25 18:00 | 204.67 | 111.81 | 92.86 | 321.8364 | 20.9616 | 106.5518 | 73.2299 | 16.7701 | 110.7903 | 98.6301 | 0 | 83.8575 | 0.70719 | 0.84531 | 36.185 | 120.0425 | 2.1 | 5.8513 | 1.067 | 0.10503
2016-05-25 19:00 | 163.4967 | 91.92 | 71.5767 | 300.167 | 20.969 | 121.5508 | 76.2046 | 13.7954 | 124.9775 | 111.2787 | 0 | 68.94 | 0.70703 | 0.84505 | 28.8993 | 97.8393 | 2.2 | 5.2575 | 1.0691 | 0.085772
2016-05-25 20:00 | 122.3233 | 72.03 | 50.2933 | 256.7386 | 20.9765 | 136.5497 | 78.7031 | 11.2969 | 139.0928 | 122.9488 | 0 | 54.0225 | 0.70688 | 0.84479 | 21.6168 | 75.6393 | 1 | 3.3637 | 1.0757 | 0.066721
2016-05-25 21:00 | 81.15 | 52.14 | 29.01 | 177.1602 | 20.9839 | 151.5486 | 80.5754 | 9.4246 | 153.1983 | 132.8969 | 0 | 39.105 | 0.70672 | 0.84453 | 14.3376 | 53.4426 | 0.5 | 2.1701 | 1.0799 | 0.047325
2016-05-25 22:00 | 65.0667 | 43.55 | 21.5167 | 149.1893 | 20.9913 | 166.5476 | 81.7077 | 8.2923 | 167.3207 | 139.8146 | 0 | 32.6625 | 0.70656 | 0.84427 | 11.4934 | 44.1559 | 0.8 | 2.1799 | 1.0799 | 0.0391
2016-05-25 23:00 | 48.9833 | 34.96 | 14.0233 | 101.1406 | 20.9987 | 181.5465 | 82.0302 | 7.9698 | -178.5422 | 142.0043 | 0 | 26.22 | 0.70641 | 0.84401 | 8.6505 | 34.8705 | 0.8 | 1.8897 | 1.0809 | 0.030907
2016-05-26 | 32.9 | 26.37 | 6.53 | 44.2951 | 21.0061 | -163.4546 | 81.5225 | 8.4775 | -164.408 | 138.7058 | 0 | 19.7775 | 0.70625 | 0.84375 | 5.8089 | 25.5864 | 1.3 | 2.0996 | 1.0802 | 0.022662
2016-05-26 01:00 | 39.5367 | 34.78 | 4.7567 | 27.9906 | 21.0135 | -148.4557 | 80.2158 | 9.7842 | -150.2924 | 131.0175 | 0 | 26.085 | 0.70609 | 0.84349 | 6.9791 | 33.0641 | 1 | 2.0333 | 1.0804 | 0.029292
2016-05-26 02:00 | 46.1733 | 43.19 | 2.9833 | 14.5757 | 21.0209 | -133.4568 | 78.1893 | 11.8107 | -136.1923 | 120.6247 | 0 | 32.3925 | 0.70594 | 0.84323 | 8.1489 | 40.5414 | 1.4 | 2.6669 | 1.0782 | 0.035842
2016-05-26 03:00 | 52.81 | 51.6 | 1.21 | 4.854 | 21.0283 | -118.4579 | 75.5651 | 14.4349 | -122.0734 | 108.7057 | 0 | 38.7 | 0.70578 | 0.84297 | 9.3181 | 48.0181 | 0.7 | 2.2006 | 1.0798 | 0.042517
2016-05-26 04:00 | 65.39 | 63.5167 | 1.8733 | 6.2297 | 21.0357 | -103.459 | 72.4997 | 17.5003 | -107.8659 | 95.914 | 0 | 47.6375 | 0.70563 | 0.84271 | 11.5352 | 59.1727 | 0.7 | 2.5491 | 1.0786 | 0.052334
2016-05-26 05:00 | 77.97 | 75.4333 | 2.5367 | 7.136 | 21.043 | -88.46 | 69.1774 | 20.8226 | -93.468 | 82.6014 | 0.91891 | 56.575 | 0.70547 | 0.84245 | 13.7513 | 71.2453 | 1.4 | 3.6264 | 1.0748 | 0.062791
2016-05-26 06:00 | 90.55 | 87.35 | 3.2 | 7.8078 | 21.0503 | -73.4611 | 65.8047 | 24.1953 | -78.7584 | 68.966 | 2.8024 | 65.5125 | 0.70531 | 0.84219 | 15.9665 | 84.2814 | 1 | 3.6338 | 1.0748 | 0.074279
2016-05-26 07:00 | 135.4133 | 127.6467 | 7.7667 | 16.8792 | 21.0577 | -58.4623 | 62.6043 | 27.3957 | -63.6176 | 55.1287 | 9.6504 | 95.735 | 0.70516 | 0.84193 | 23.8719 | 129.2573 | 0.9 | 4.9393 | 1.0702 | 0.11343
2016-05-26 08:00 | 180.2767 | 167.9433 | 12.3333 | 24.5238 | 21.065 | -43.4634 | 59.8071 | 30.1929 | -47.9598 | 41.1737 | 18.4595 | 125.9575 | 0.705 | 0.84167 | 31.7738 | 176.1907 | 0.6 | 6.106 | 1.0661 | 0.15403
2016-05-26 09:00 | 225.14 | 208.24 | 16.9 | 31.5722 | 21.0723 | -28.4645 | 57.637 | 32.363 | -31.7709 | 27.1844 | 28.0847 | 156.18 | 0.70484 | 0.84141 | 39.6721 | 223.9369 | 2.9 | 9.898 | 1.0529 | 0.19333
2016-05-26 10:00 | 226.8533 | 210.9133 | 15.94 | 28.7186 | 21.0796 | -13.4656 | 56.2864 | 33.7136 | -15.1417 | 13.3716 | 27.94 | 158.185 | 0.70469 | 0.84115 | 39.9652 | 226.0902 | 1.4 | 8.4653 | 1.0579 | 0.19612
2016-05-26 11:00 | 228.5667 | 213.5867 | 14.98 | 26.7092 | 21.0869 | 1.5333 | 55.885 | 34.115 | 1.728 | 4.3676 | 26.6316 | 160.19 | 0.70453 | 0.84089 | 40.2581 | 227.0797 | 2.1 | 9.1962 | 1.0553 | 0.1965
2016-05-26 12:00 | 230.28 | 216.26 | 14.02 | 25.383 | 21.0942 | 16.5322 | 56.4724 | 33.5276 | 18.5706 | 16.1544 | 24.3808 | 162.195 | 0.70438 | 0.84063 | 40.5509 | 227.1266 | 2.6 | 9.6977 | 1.0536 | 0.19622
2016-05-26 13:00 | 235.97 | 189.1767 | 46.7933 | 88.2763 | 21.1014 | 31.5311 | 57.9893 | 32.0107 | 35.1263 | 30.043 | 76.4164 | 141.8825 | 0.70422 | 0.84036 | 41.5436 | 259.8425 | 3.3 | 11.4201 | 1.0475 | 0.2232
2016-05-26 14:00 | 241.66 | 162.0933 | 79.5667 | 160.5459 | 21.1087 | 46.5299 | 60.2906 | 29.7094 | 51.215 | 44.0305 | 115.4277 | 121.57 | 0.70406 | 0.8401 | 42.5359 | 279.5337 | 3.5 | 12.2354 | 1.0447 | 0.23946
2016-05-26 15:00 | 247.35 | 135.01 | 112.34 | 248.9445 | 21.1159 | 61.5288 | 63.1751 | 26.8249 | 66.7681 | 57.9622 | 132.0599 | 101.2575 | 0.70391 | 0.83984 | 43.5278 | 276.8452 | 3 | 11.6514 | 1.0467 | 0.23762
2016-05-26 16:00 | 211.6033 | 114.7833 | 96.82 | 241.9892 | 21.1232 | 76.5277 | 66.4155 | 23.5845 | 81.8166 | 71.7584 | 75.7488 | 86.0875 | 0.70375 | 0.83958 | 37.229 | 199.0652 | 3.3 | 9.5208 | 1.0542 | 0.17208
2016-05-26 17:00 | 175.8567 | 94.5567 | 81.3 | 235.2421 | 21.1304 | 91.5265 | 69.7815 | 20.2185 | 96.4556 | 85.3292 | 19.1558 | 70.9175 | 0.70359 | 0.83932 | 30.9329 | 121.0062 | 3.3 | 7.0814 | 1.0627 | 0.10545
2016-05-26 18:00 | 140.11 | 74.33 | 65.78 | 225.6687 | 21.1376 | 106.5254 | 73.0529 | 16.9471 | 110.8068 | 98.5414 | 0 | 55.7475 | 0.70344 | 0.83906 | 24.6397 | 80.3872 | 2.2 | 4.7121 | 1.071 | 0.070598
2016-05-26 19:00 | 130.1667 | 62.62 | 67.5467 | 279.7442 | 21.1448 | 121.5242 | 76.0273 | 13.9727 | 124.9884 | 111.1718 | 0 | 46.965 | 0.70328 | 0.8388 | 22.8859 | 69.8509 | 2.5 | 4.6828 | 1.0711 | 0.061351
2016-05-26 20:00 | 120.2233 | 50.91 | 69.3133 | 348.4377 | 21.152 | 136.5231 | 78.5258 | 11.4742 | 139.0962 | 122.8203 | 0 | 38.1825 | 0.70312 | 0.83854 | 21.133 | 59.3155 | 2.1 | 3.9536 | 1.0737 | 0.052222
2016-05-26 21:00 | 110.28 | 39.2 | 71.08 | 426.1489 | 21.1592 | 151.5219 | 80.3984 | 9.6016 | 153.1926 | 132.7441 | 0 | 29.4 | 0.70297 | 0.83828 | 19.3808 | 48.7808 | 2.6 | 4.1244 | 1.0731 | 0.042923
2016-05-26 22:00 | 101.9567 | 35.0333 | 66.9233 | 454.4416 | 21.1664 | 166.5208 | 81.5315 | 8.4685 | 167.3049 | 139.6417 | 0 | 26.275 | 0.70281 | 0.83802 | 17.9141 | 44.1891 | 1.9 | 3.2809 | 1.076 | 0.03899
2016-05-26 23:00 | 93.6333 | 30.8667 | 62.7667 | 443.049 | 21.1735 | 181.5196 | 81.8555 | 8.1445 | -178.5685 | 141.8307 | 0 | 23.15 | 0.70266 | 0.83776 | 16.448 | 39.598 | 2.9 | 4.1374 | 1.073 | 0.034841
2016-05-27 | 85.31 | 26.7 | 58.61 | 389.6989 | 21.1807 | -163.4815 | 81.35 | 8.65 | -164.4448 | 138.5571 | 0 | 20.025 | 0.7025 | 0.8375 | 14.9826 | 35.0076 | 3 | 4.094 | 1.0732 | 0.030807
2016-05-27 01:00 | 66.5567 | 26.7533 | 39.8033 | 230.2611 | 21.1878 | -148.4827 | 80.0458 | 9.9542 | -150.339 | 130.9037 | 0 | 20.065 | 0.70234 | 0.83724 | 11.6864 | 31.7514 | 3.2 | 4.1922 | 1.0728 | 0.027932
2016-05-27 02:00 | 47.8033 | 26.8067 | 20.9967 | 101.171 | 21.195 | -133.4839 | 78.022 | 11.978 | -136.2475 | 120.5421 | 0 | 20.105 | 0.70219 | 0.83698 | 8.3917 | 28.4967 | 2.9 | 3.7905 | 1.0742 | 0.025102
2016-05-27 03:00 | 29.05 | 26.86 | 2.19 | 8.6882 | 21.2021 | -118.485 | 75.4002 | 14.5998 | -122.1358 | 108.6481 | 0 | 20.145 | 0.70203 | 0.83672 | 5.0985 | 25.2435 | 3.9 | 4.6889 | 1.0711 | 0.022171
2016-05-27 04:00 | 21.6367 | 20.1767 | 1.46 | 4.8118 | 21.2092 | -103.4862 | 72.3367 | 17.6633 | -107.9338 | 95.8763 | 0 | 15.1325 | 0.70188 | 0.83646 | 3.7966 | 18.9291 | 3.6 | 4.1915 | 1.0728 | 0.016652
2016-05-27 05:00 | 14.2233 | 13.4933 | 0.73 | 2.0384 | 21.2163 | -88.4874 | 69.0154 | 20.9846 | -93.5393 | 82.58 | 0.26325 | 10.12 | 0.70172 | 0.8362 | 2.4952 | 12.8784 | 3.7 | 4.1025 | 1.0731 | 0.011333
2016-05-27 06:00 | 6.81 | 6.81 | 0 | 0 | 21.2234 | -73.4886 | 65.6427 | 24.3573 | -78.8307 | 68.9589 | 0 | 5.1075 | 0.70156 | 0.83594 | 1.1944 | 6.3019 | 3.9 | 4.0969 | 1.0732 | 0.0055456
2016-05-27 07:00 | 79.04 | 68.52 | 10.52 | 22.7381 | 21.2305 | -58.4898 | 62.4412 | 27.5588 | -63.688 | 55.1349 | 12.9982 | 51.39 | 0.70141 | 0.83568 | 13.8598 | 78.248 | 3.7 | 6.1452 | 1.066 | 0.068398
2016-05-27 08:00 | 151.27 | 130.23 | 21.04 | 41.6302 | 21.2375 | -43.491 | 59.642 | 30.358 | -48.025 | 41.1938 | 31.3262 | 97.6725 | 0.70125 | 0.83542 | 26.5195 | 155.5182 | 3.8 | 8.6599 | 1.0572 | 0.13482
2016-05-27 09:00 | 223.5 | 191.94 | 31.56 | 58.689 | 21.2446 | -28.4921 | 57.4694 | 32.5306 | -31.8273 | 27.222 | 52.1887 | 143.955 | 0.70109 | 0.83516 | 39.1736 | 235.3173 | 3.6 | 10.9537 | 1.0492 | 0.20245
2016-05-27 10:00 | 241.4533 | 209.23 | 32.2233 | 57.7989 | 21.2516 | -13.4933 | 56.1164 | 33.8836 | -15.1859 | 13.4438 | 56.2151 | 156.9225 | 0.70094 | 0.8349 | 42.3109 | 255.4486 | 2.4 | 10.3828 | 1.0512 | 0.22018
2016-05-27 11:00 | 259.4067 | 226.52 | 32.8867 | 58.3782 | 21.2587 | 1.5055 | 55.713 | 34.287 | 1.6982 | 4.5214 | 58.1965 | 169.89 | 0.70078 | 0.83464 | 45.4468 | 273.5334 | 3.7 | 12.2479 | 1.0446 | 0.23431
2016-05-27 12:00 | 277.36 | 243.81 | 33.55 | 60.4665 | 21.2657 | 16.5043 | 56.2994 | 33.7006 | 18.5553 | 16.1655 | 58.0757 | 182.8575 | 0.70063 | 0.83437 | 48.5813 | 289.5146 | 3.9 | 12.9473 | 1.0422 | 0.24742
2016-05-27 13:00 | 318.8033 | 216.6167 | 102.1867 | 191.8497 | 21.2727 | 31.5031 | 57.816 | 32.184 | 35.1239 | 30.0247 | 166.1053 | 162.4625 | 0.70047 | 0.83411 | 55.8279 | 384.3958 | 3.5 | 15.5124 | 1.0332 | 0.32567
2016-05-27 14:00 | 360.2467 | 189.4233 | 170.8233 | 342.8677 | 21.2797 | 46.5018 | 60.1177 | 29.8823 | 51.2225 | 43.9959 | 246.6554 | 142.0675 | 0.70031 | 0.83385 | 63.0713 | 451.7942 | 2.7 | 16.8186 | 1.0286 | 0.38108
2016-05-27 15:00 | 401.69 | 162.23 | 239.46 | 527.5063 | 21.2867 | 61.5006 | 63.0028 | 26.9972 | 66.7819 | 57.9145 | 280.2028 | 121.6725 | 0.70016 | 0.83359 | 70.3114 | 472.1868 | 2.9 | 17.6558 | 1.0257 | 0.39715
2016-05-27 16:00 | 330.1667 | 141.34 | 188.8267 | 468.7297 | 21.2937 | 76.4994 | 66.2437 | 23.7563 | 81.8333 | 71.6982 | 147.1917 | 106.005 | 0.7 | 0.83333 | 57.7792 | 310.9758 | 1.5 | 11.218 | 1.0482 | 0.2673
2016-05-27 17:00 | 258.6433 | 120.45 | 138.1933 | 396.6394 | 21.3007 | 91.4982 | 69.6099 | 20.3901 | 96.4719 | 85.2559 | 32.8046 | 90.3375 | 0.69984 | 0.83307 | 45.2525 | 168.3946 | 1.6 | 6.8623 | 1.0635 | 0.14685
2016-05-27 18:00 | 187.12 | 99.56 | 87.56 | 297.4663 | 21.3076 | 106.497 | 72.8813 | 17.1187 | 110.82 | 98.4531 | 0 | 74.67 | 0.69969 | 0.83281 | 32.7314 | 107.4014 | 0.9 | 4.2563 | 1.0726 | 0.094463
2016-05-27 19:00 | 156.6833 | 81.7667 | 74.9167 | 306.5771 | 21.3146 | 121.4957 | 75.8557 | 14.1443 | 124.9962 | 111.0661 | 0 | 61.325 | 0.69953 | 0.83255 | 27.4012 | 88.7262 | 1.4 | 4.1727 | 1.0729 | 0.078059
2016-05-27 20:00 | 126.2467 | 63.9733 | 62.2733 | 308.4978 | 21.3215 | 136.4945 | 78.3543 | 11.6457 | 139.0967 | 122.694 | 0 | 47.98 | 0.69938 | 0.83229 | 22.0734 | 70.0534 | 1.3 | 3.4892 | 1.0753 | 0.061769
2016-05-27 21:00 | 95.81 | 46.18 | 49.63 | 292.3872 | 21.3284 | 151.4933 | 80.2273 | 9.7727 | 153.1844 | 132.5948 | 0 | 34.635 | 0.69922 | 0.83203 | 16.748 | 51.383 | 1.1 | 2.7057 | 1.078 | 0.045422
2016-05-27 22:00 | 98.2967 | 42.7833 | 55.5133 | 369.5909 | 21.3354 | 166.492 | 81.3614 | 8.6386 | 167.2869 | 139.4738 | 0 | 32.0875 | 0.69906 | 0.83177 | 17.1789 | 49.2664 | 1.1 | 2.6396 | 1.0783 | 0.04356
2016-05-27 23:00 | 100.7833 | 39.3867 | 61.3967 | 424.6504 | 21.3423 | 181.4908 | 81.6869 | 8.3131 | -178.5967 | 141.6632 | 0 | 29.54 | 0.69891 | 0.83151 | 17.6095 | 47.1495 | 1.5 | 2.9734 | 1.0771 | 0.041643
2016-05-28 | 103.27 | 35.99 | 67.28 | 438.9683 | 21.3492 | -163.5104 | 81.1836 | 8.8164 | -164.483 | 138.4145 | 0 | 26.9925 | 0.69875 | 0.83125 | 18.04 | 45.0325 | 1.4 | 2.8073 | 1.0777 | 0.039795
2016-05-28 01:00 | 108.5467 | 48.52 | 60.0267 | 341.6883 | 21.3561 | -148.5117 | 79.882 | 10.118 | -150.3867 | 130.7952 | 0 | 36.39 | 0.69859 | 0.83099 | 18.9575 | 55.3475 | 0.9 | 2.6296 | 1.0783 | 0.048938
2016-05-28 02:00 | 113.8233 | 61.05 | 52.7733 | 250.9601 | 21.3629 | -133.5129 | 77.8609 | 12.1391 | -136.3036 | 120.4643 | 0 | 45.7875 | 0.69844 | 0.83073 | 19.8746 | 65.6621 | 0.8 | 2.8519 | 1.0775 | 0.058017
2016-05-28 03:00 | 119.1 | 73.58 | 45.52 | 178.6893 | 21.3698 | -118.5142 | 75.2416 | 14.7584 | -122.1988 | 108.5948 | 0 | 55.185 | 0.69828 | 0.83047 | 20.7913 | 75.9763 | 1.2 | 3.5743 | 1.075 | 0.066973
2016-05-28 04:00 | 148.23 | 87.36 | 60.87 | 198.9031 | 21.3767 | -103.5154 | 72.18 | 17.82 | -108.0021 | 95.8423 | 0 | 65.52 | 0.69813 | 0.83021 | 25.8708 | 91.3908 | 0.7 | 3.556 | 1.0751 | 0.080565
2016-05-28 05:00 | 177.36 | 101.14 | 76.22 | 211.3396 | 21.3835 | -88.5167 | 68.8598 | 21.1402 | -93.611 | 82.562 | 27.3585 | 75.855 | 0.69797 | 0.82995 | 30.9479 | 134.1614 | 0.6 | 4.7925 | 1.0707 | 0.11779
2016-05-28 06:00 | 206.49 | 114.92 | 91.57 | 220.7039 | 21.3903 | -73.518 | 65.487 | 24.513 | -78.9035 | 68.9548 | 79.2557 | 86.19 | 0.69781 | 0.82969 | 36.0228 | 201.4686 | 0.7 | 6.9959 | 1.063 | 0.17561
2016-05-28 07:00 | 275.71 | 120.23 | 155.48 | 334.3058 | 21.3972 | -58.5192 | 62.2844 | 27.7156 | -63.7591 | 55.1438 | 191.062 | 90.1725 | 0.69766 | 0.82943 | 48.0877 | 329.3222 | 1.9 | 12.1913 | 1.0448 | 0.28215
2016-05-28 08:00 | 344.93 | 125.54 | 219.39 | 432.0478 | 21.404 | -43.5205 | 59.4832 | 30.5168 | -48.0911 | 41.2163 | 324.9981 | 94.155 | 0.6975 | 0.82917 | 60.1472 | 479.3003 | 2.3 | 17.2781 | 1.027 | 0.40365
2016-05-28 09:00 | 414.15 | 130.85 | 283.3 | 524.5119 | 21.4108 | -28.5218 | 57.3081 | 32.6919 | -31.885 | 27.2618 | 466.2505 | 98.1375 | 0.69734 | 0.82891 | 72.2012 | 636.5893 | 2.9 | 22.7934 | 1.0077 | 0.52603
2016-05-28 10:00 | 402.76 | 138.2067 | 264.5533 | 472.5184 | 21.4176 | -13.523 | 55.9525 | 34.0475 | -15.2319 | 13.5176 | 459.4287 | 103.655 | 0.69719 | 0.82865 | 70.1998 | 633.2836 | 2.6 | 22.3901 | 1.0091 | 0.52404
2016-05-28 11:00 | 391.37 | 145.5633 | 245.8067 | 434.4963 | 21.4244 | 1.4757 | 55.5471 | 34.4529 | 1.666 | 4.6703 | 433.0537 | 109.1725 | 0.69703 | 0.82839 | 68.1993 | 610.4254 | 2.1 | 21.1758 | 1.0134 | 0.50725
2016-05-28 12:00 | 379.98 | 152.92 | 227.06 | 407.4456 | 21.4311 | 16.4744 | 56.1323 | 33.8677 | 18.5373 | 16.1752 | 391.3166 | 114.69 | 0.69688 | 0.82812 | 66.1996 | 572.2062 | 3.5 | 21.3814 | 1.0127 | 0.47515
2016-05-28 13:00 | 361.7433 | 144.1967 | 217.5467 | 406.5453 | 21.4379 | 31.4731 | 57.6486 | 32.3514 | 35.1184 | 30.0052 | 352.0602 | 108.1475 | 0.69672 | 0.82786 | 63.0083 | 523.2161 | 3.1 | 19.4505 | 1.0194 | 0.43737
2016-05-28 14:00 | 343.5067 | 135.4733 | 208.0333 | 415.4451 | 21.4446 | 46.4718 | 59.9505 | 30.0495 | 51.2267 | 43.9604 | 299.0456 | 101.605 | 0.69656 | 0.8276 | 59.8185 | 460.4691 | 3 | 17.3897 | 1.0266 | 0.38764
2016-05-28 15:00 | 325.27 | 126.75 | 198.52 | 434.837 | 21.4514 | 61.4705 | 62.836 | 27.164 | 66.7924 | 57.8662 | 231.2889 | 95.0625 | 0.69641 | 0.82734 | 56.63 | 382.9814 | 2.4 | 14.3682 | 1.0372 | 0.32573
2016-05-28 16:00 | 285.7367 | 123.67 | 162.0667 | 399.6678 | 21.4581 | 76.4692 | 66.0773 | 23.9227 | 81.8465 | 71.6377 | 125.9052 | 92.7525 | 0.69625 | 0.82708 | 49.736 | 268.3937 | 2.2 | 10.5873 | 1.0504 | 0.23118
2016-05-28 17:00 | 246.2033 | 120.59 | 125.6133 | 357.7436 | 21.4648 | 91.4679 | 69.4438 | 20.5562 | 96.4849 | 85.1826 | 30.0437 | 90.4425 | 0.69609 | 0.82682 | 42.8452 | 163.3313 | 2.2 | 7.3041 | 1.0619 | 0.14223
2016-05-28 18:00 | 206.67 | 117.51 | 89.16 | 300.0797 | 21.4715 | 106.4666 | 72.7152 | 17.2848 | 110.83 | 98.3655 | 0 | 88.1325 | 0.69594 | 0.82656 | 35.9574 | 124.0899 | 2.3 | 6.1778 | 1.0659 | 0.10846
2016-05-28 19:00 | 180.85 | 90.9467 | 89.9033 | 363.7257 | 21.4782 | 121.4653 | 75.6897 | 14.3103 | 125.0011 | 110.9618 | 0 | 68.21 | 0.69578 | 0.8263 | 31.458 | 99.668 | 2.2 | 5.3146 | 1.0689 | 0.087359
2016-05-28 20:00 | 155.03 | 64.3833 | 90.6467 | 442.8405 | 21.4849 | 136.464 | 78.1884 | 11.8116 | 139.0946 | 122.5699 | 0 | 48.2875 | 0.69563 | 0.82604 | 26.9607 | 75.2482 | 2.1 | 4.4515 | 1.0719 | 0.066141
2016-05-28 21:00 | 129.21 | 37.82 | 91.39 | 529.5433 | 21.4916 | 151.4627 | 80.062 | 9.938 | 153.1738 | 132.4491 | 0 | 28.365 | 0.69547 | 0.82578 | 22.4654 | 50.8304 | 1.6 | 3.1884 | 1.0763 | 0.044863
2016-05-28 22:00 | 119.8933 | 41.7467 | 78.1467 | 510.6479 | 21.4982 | 166.4614 | 81.1972 | 8.8028 | 167.2669 | 139.3111 | 0 | 31.31 | 0.69531 | 0.82552 | 20.8408 | 52.1508 | 1 | 2.6297 | 1.0783 | 0.046112
2016-05-28 23:00 | 110.5767 | 45.6733 | 64.9033 | 440.3608 | 21.5049 | 181.4601 | 81.5245 | 8.4755 | -178.6266 | 141.5018 | 0 | 34.255 | 0.69516 | 0.82526 | 19.217 | 53.472 | 1 | 2.671 | 1.0782 | 0.047274
2016-05-29 | 101.26 | 49.6 | 51.66 | 331.0893 | 21.5115 | -163.5413 | 81.0234 | 8.9766 | -164.5226 | 138.278 | 0 | 37.2 | 0.695 | 0.825 | 17.5939 | 54.7939 | 1.4 | 3.1123 | 1.0766 | 0.048373
2016-05-29 01:00 | 141.95 | 48.7633 | 93.1867 | 522.3985 | 21.5182 | -148.5426 | 79.7244 | 10.2756 | -150.4354 | 130.6923 | 0 | 36.5725 | 0.69484 | 0.82474 | 24.6583 | 61.2308 | 1.8 | 3.7135 | 1.0745 | 0.05395
2016-05-29 02:00 | 182.64 | 47.9267 | 134.7133 | 632.6781 | 21.5248 | -133.5439 | 77.7061 | 12.2939 | -136.3603 | 120.3913 | 0 | 35.945 | 0.69469 | 0.82448 | 31.7194 | 67.6644 | 1.7 | 3.8145 | 1.0741 | 0.059599
2016-05-29 03:00 | 223.33 | 47.09 | 176.24 | 684.9259 | 21.5314 | -118.5452 | 75.0893 | 14.9107 | -122.2624 | 108.5456 | 0 | 35.3175 | 0.69453 | 0.82422 | 38.7774 | 74.0949 | 1.5 | 3.8155 | 1.0741 | 0.065263
2016-05-29 04:00 | 276.3333 | 58.35 | 217.9833 | 706.5334 | 21.538 | -103.5466 | 72.0296 | 17.9704 | -108.0708 | 95.8121 | 0 | 43.7625 | 0.69438 | 0.82396 | 47.9697 | 91.7322 | 1.6 | 4.4666 | 1.0719 | 0.080626
2016-05-29 05:00 | 329.3367 | 69.61 | 259.7267 | 715.3413 | 21.5446 | -88.5479 | 68.7105 | 21.2895 | -93.683 | 82.5474 | 92.7844 | 52.2075 | 0.69422 | 0.8237 | 57.1579 | 202.1499 | 1.8 | 8.1172 | 1.0591 | 0.17556
2016-05-29 06:00 | 382.34 | 80.87 | 301.47 | 722.4834 | 21.5512 | -73.5493 | 65.3377 | 24.6623 | -78.9766 | 68.9537 | 259.4597 | 60.6525 | 0.69406 | 0.82344 | 66.342 | 386.4541 | 2.3 | 14.3767 | 1.0372 | 0.32867
2016-05-29 07:00 | 408.94 | 123.5767 | 285.3633 | 610.5266 | 21.5577 | -58.5506 | 62.134 | 27.866 | -63.8308 | 55.1555 | 348.8255 | 92.6825 | 0.69391 | 0.82318 | 70.9415 | 512.4495 | 3.2 | 19.214 | 1.0203 | 0.42872
2016-05-29 08:00 | 435.54 | 166.2833 | 269.2567 | 527.8707 | 21.5643 | -43.5519 | 59.3308 | 30.6692 | -48.1582 | 41.2413 | 396.9271 | 124.7125 | 0.69375 | 0.82292 | 75.539 | 597.1785 | 2.8 | 21.4618 | 1.0124 | 0.49575
2016-05-29 09:00 | 462.14 | 208.99 | 253.15 | 466.7257 | 21.5708 | -28.5533 | 57.1531 | 32.8469 | -31.944 | 27.3037 | 414.7265 | 156.7425 | 0.69359 | 0.82266 | 80.1344 | 651.6034 | 2.9 | 23.2626 | 1.0061 | 0.53756
2016-05-29 10:00 | 482.6067 | 185.7933 | 296.8133 | 527.9906 | 21.5774 | -13.5546 | 55.7949 | 34.2051 | -15.2797 | 13.5929 | 513.2016 | 139.345 | 0.69344 | 0.8224 | 83.6644 | 736.211 | 4 | 27.0066 | 0.99298 | 0.59945
2016-05-29 11:00 | 503.0733 | 162.5967 | 340.4767 | 599.4046 | 21.5839 | 1.444 | 55.3874 | 34.6126 | 1.6315 | 4.8141 | 597.2901 | 121.9475 | 0.69328 | 0.82214 | 87.1928 | 806.4304 | 3.5 | 28.701 | 0.98705 | 0.65271
2016-05-29 12:00 | 523.54 | 139.4 | 384.14 | 686.4434 | 21.5904 | 16.4426 | 55.9712 | 34.0288 | 18.5166 | 16.1836 | 659.2422 | 104.55 | 0.69313 | 0.82188 | 90.7197 | 854.5118 | 3.1 | 29.8035 | 0.98319 | 0.68892
2016-05-29 13:00 | 452.2533 | 161.5433 | 290.71 | 540.8646 | 21.5969 | 31.4413 | 57.487 | 32.513 | 35.11 | 29.9844 | 468.476 | 121.1575 | 0.69297 | 0.82161 | 78.3494 | 667.9828 | 3.4 | 24.2745 | 1.0025 | 0.54914
2016-05-29 14:00 | 380.9667 | 183.6867 | 197.28 | 392.0615 | 21.6034 | 46.4399 | 59.789 | 30.211 | 51.2277 | 43.9239 | 282.3868 | 137.765 | 0.69281 | 0.82135 | 65.9846 | 486.1364 | 4.2 | 19.3918 | 1.0196 | 0.40646
2016-05-29 15:00 | 309.68 | 205.83 | 103.85 | 226.2332 | 21.6099 | 61.4385 | 62.6748 | 27.3252 | 66.7995 | 57.8173 | 120.4966 | 154.3725 | 0.69266 | 0.82109 | 53.6254 | 328.4945 | 4 | 14.2655 | 1.0376 | 0.27949
2016-05-29 16:00 | 276.07 | 176.7533 | 99.3167 | 243.3832 | 21.6164 | 76.4372 | 65.9165 | 24.0835 | 81.8564 | 71.5769 | 76.9167 | 132.565 | 0.6925 | 0.82083 | 47.7946 | 257.2763 | 3.3 | 11.3399 | 1.0478 | 0.22105
2016-05-29 17:00 | 242.46 | 147.6767 | 94.7833 | 267.9395 | 21.6228 | 91.4358 | 69.2832 | 20.7168 | 96.4946 | 85.1094 | 22.8426 | 110.7575 | 0.69234 | 0.82057 | 41.9664 | 175.5665 | 2.9 | 8.3865 | 1.0581 | 0.15234
2016-05-29 18:00 | 208.85 | 118.6 | 90.25 | 301.0405 | 21.6293 | 106.4344 | 72.5548 | 17.4452 | 110.8369 | 98.2786 | 0 | 88.95 | 0.69219 | 0.82031 | 36.1408 | 125.0908 | 3.9 | 7.8091 | 1.0602 | 0.10875
2016-05-29 19:00 | 177.71 | 95.4833 | 82.2267 | 329.0597 | 21.6357 | 121.433 | 75.5294 | 14.4706 | 125.003 | 110.8589 | 0 | 71.6125 | 0.69203 | 0.82005 | 30.7452 | 102.3577 | 3.3 | 6.4987 | 1.0648 | 0.089368
2016-05-29 20:00 | 146.57 | 72.3667 | 74.2033 | 357.733 | 21.6421 | 136.4316 | 78.0284 | 11.9716 | 139.0897 | 122.4483 | 0 | 54.275 | 0.69188 | 0.81979 | 25.352 | 79.627 | 3.4 | 5.8883 | 1.0669 | 0.069662
2016-05-29 21:00 | 115.43 | 49.25 | 66.18 | 377.4787 | 21.6486 | 151.4303 | 79.9027 | 10.0973 | 153.1607 | 132.3072 | 0 | 36.9375 | 0.69172 | 0.81953 | 19.9613 | 56.8988 | 2.6 | 4.3781 | 1.0722 | 0.050025
2016-05-29 22:00 | 94.0333 | 45.08 | 48.9533 | 314.2854 | 21.655 | 166.4289 | 81.0391 | 8.9609 | 167.2448 | 139.1535 | 0 | 33.81 | 0.69156 | 0.81927 | 16.2575 | 50.0675 | 2.1 | 3.6646 | 1.0747 | 0.044121
2016-05-29 23:00 | 72.6367 | 40.91 | 31.7267 | 211.3928 | 21.6614 | 181.4275 | 81.3682 | 8.6318 | -178.6582 | 141.3467 | 0 | 30.6825 | 0.69141 | 0.81901 | 12.5554 | 43.2379 | 2.4 | 3.7512 | 1.0744 | 0.038092
2016-05-30 | 51.24 | 36.74 | 14.5 | 91.3771 | 21.6677 | -163.5739 | 80.8695 | 9.1305 | -164.5635 | 138.1476 | 0 | 27.555 | 0.69125 | 0.81875 | 8.8549 | 36.4099 | 2.5 | 3.6378 | 1.0748 | 0.032088
2016-05-30 01:00 | 66.5167 | 50.5633 | 15.9533 | 88.1507 | 21.6741 | -148.5753 | 79.5733 | 10.4267 | -150.4851 | 130.5948 | 0 | 37.9225 | 0.69109 | 0.81849 | 11.4923 | 49.4148 | 2.2 | 3.7442 | 1.0744 | 0.043535
2016-05-30 02:00 | 81.7933 | 64.3867 | 17.4067 | 80.7902 | 21.6805 | -133.5767 | 77.5578 | 12.4422 | -136.4178 | 120.3231 | 0 | 48.29 | 0.69094 | 0.81823 | 14.1285 | 62.4185 | 2.4 | 4.3506 | 1.0723 | 0.054882
2016-05-30 03:00 | 97.07 | 78.21 | 18.86 | 72.6023 | 21.6868 | -118.5781 | 74.9435 | 15.0565 | -122.3263 | 108.5006 | 0 | 58.6575 | 0.69078 | 0.81797 | 16.7635 | 75.421 | 2.4 | 4.7569 | 1.0709 | 0.066227
2016-05-30 04:00 | 124.6967 | 102.67 | 22.0267 | 70.845 | 21.6932 | -103.5795 | 71.8857 | 18.1143 | -108.1398 | 95.7855 | 0 | 77.0025 | 0.69063 | 0.81771 | 21.5297 | 98.5322 | 2.8 | 5.8791 | 1.0669 | 0.086204
2016-05-30 05:00 | 152.3233 | 127.13 | 25.1933 | 68.9467 | 21.6995 | -88.581 | 68.5676 | 21.4324 | -93.7553 | 82.536 | 8.9564 | 95.3475 | 0.69047 | 0.81745 | 26.2936 | 130.5975 | 3.4 | 7.4812 | 1.0613 | 0.11366
2016-05-30 06:00 | 179.95 | 151.59 | 28.36 | 67.5988 | 21.7058 | -73.5824 | 65.1948 | 24.8052 | -79.0501 | 68.9556 | 24.2742 | 113.6925 | 0.69031 | 0.81719 | 31.0554 | 169.0221 | 2.9 | 8.1819 | 1.0589 | 0.14676
2016-05-30 07:00 | 209.41 | 186.0633 | 23.3467 | 49.7134 | 21.7121 | -58.5838 | 61.99 | 28.01 | -63.903 | 55.1697 | 28.3937 | 139.5475 | 0.69016 | 0.81693 | 36.1314 | 204.0726 | 3.6 | 9.9773 | 1.0526 | 0.17614
2016-05-30 08:00 | 238.87 | 220.5367 | 18.3333 | 35.7884 | 21.7184 | -43.5852 | 59.1848 | 30.8152 | -48.226 | 41.2686 | 26.8995 | 165.4025 | 0.69 | 0.81667 | 41.2051 | 233.507 | 2.8 | 10.0971 | 1.0522 | 0.20146
2016-05-30 09:00 | 268.33 | 255.01 | 13.32 | 24.4595 | 21.7247 | -28.5866 | 57.0045 | 32.9955 | -32.0041 | 27.3476 | 21.7258 | 191.2575 | 0.68984 | 0.81641 | 46.2764 | 259.2598 | 3.1 | 11.2019 | 1.0483 | 0.22286
2016-05-30 10:00 | 291.1233 | 256.9633 | 34.16 | 60.531 | 21.731 | -13.5881 | 55.6436 | 34.3564 | -15.3291 | 13.6694 | 58.8165 | 192.7225 | 0.68969 | 0.81615 | 50.196 | 301.7351 | 3.6 | 13.0292 | 1.0419 | 0.25779
2016-05-30 11:00 | 313.9167 | 258.9167 | 55 | 96.4526 | 21.7373 | 1.4105 | 55.2338 | 34.7662 | 1.595 | 4.9526 | 96.0925 | 194.1875 | 0.68953 | 0.81589 | 54.1138 | 344.3938 | 3.4 | 14.1623 | 1.0379 | 0.29311
2016-05-30 12:00 | 336.71 | 260.87 | 75.84 | 134.9827 | 21.7435 | 16.4091 | 55.8162 | 34.1838 | 18.4932 | 16.1904 | 129.6294 | 195.6525 | 0.68938 | 0.81563 | 58.0299 | 383.3117 | 3.3 | 15.2785 | 1.034 | 0.32501
2016-05-30 13:00 | 320.6567 | 212.4867 | 108.17 | 200.3961 | 21.7498 | 31.4076 | 57.3313 | 32.6687 | 35.0985 | 29.9625 | 173.6138 | 159.365 | 0.68922 | 0.81536 | 55.2506 | 388.2294 | 3.9 | 16.0322 | 1.0314 | 0.32834
2016-05-30 14:00 | 304.6033 | 164.1033 | 140.5 | 277.9242 | 21.756 | 46.4062 | 59.6332 | 30.3668 | 51.2255 | 43.8866 | 200.3038 | 123.0775 | 0.68906 | 0.8151 | 52.4727 | 375.854 | 4.2 | 15.9454 | 1.0317 | 0.31797
2016-05-30 15:00 | 288.55 | 115.72 | 172.83 | 374.5377 | 21.7622 | 61.4047 | 62.5194 | 27.4806 | 66.8033 | 57.7677 | 199.7608 | 86.79 | 0.68891 | 0.81484 | 49.696 | 336.2468 | 3.6 | 14.1077 | 1.0381 | 0.28623
2016-05-30 16:00 | 238.8767 | 99.6167 | 139.26 | 339.2135 | 21.7684 | 76.4033 | 65.7614 | 24.2386 | 81.863 | 71.5159 | 107.5447 | 74.7125 | 0.68875 | 0.81458 | 41.1316 | 223.3887 | 4.1 | 11.0809 | 1.0487 | 0.1921
2016-05-30 17:00 | 189.2033 | 83.5133 | 105.69 | 296.6514 | 21.7746 | 91.4018 | 69.1283 | 20.8717 | 96.501 | 85.0365 | 25.6665 | 62.635 | 0.68859 | 0.81432 | 32.5711 | 120.8726 | 3.5 | 7.2773 | 1.062 | 0.10526
2016-05-30 18:00 | 139.53 | 67.41 | 72.12 | 238.5164 | 21.7808 | 106.4004 | 72.4 | 17.6 | 110.8407 | 98.1925 | 0 | 50.5575 | 0.68844 | 0.81406 | 24.0144 | 74.5719 | 3.4 | 5.7304 | 1.0674 | 0.065273
2016-05-30 19:00 | 124.12 | 58.4767 | 65.6433 | 259.9791 | 21.787 | 121.3989 | 75.3748 | 14.6252 | 125.002 | 110.7575 | 0 | 43.8575 | 0.68828 | 0.8138 | 21.3574 | 65.2149 | 3.1 | 5.138 | 1.0695 | 0.057194
2016-05-30 20:00 | 108.71 | 49.5433 | 59.1667 | 281.6688 | 21.7932 | 136.3975 | 77.8743 | 12.1257 | 139.0822 | 122.3292 | 0 | 37.1575 | 0.68813 | 0.81354 | 18.7015 | 55.859 | 3 | 4.7456 | 1.0709 | 0.049051
2016-05-30 21:00 | 93.3 | 40.61 | 52.69 | 296.0858 | 21.7993 | 151.396 | 79.7493 | 10.2507 | 153.1454 | 132.169 | 0 | 30.4575 | 0.68797 | 0.81328 | 16.0469 | 46.5044 | 3.3 | 4.7533 | 1.0709 | 0.040836
2016-05-30 22:00 | 90.0233 | 40.5433 | 49.48 | 312.4122 | 21.8055 | 166.3945 | 80.8871 | 9.1129 | 167.2207 | 139.0012 | 0 | 30.4075 | 0.68781 | 0.81302 | 15.4798 | 45.8873 | 3.3 | 4.734 | 1.0709 | 0.040297
2016-05-30 23:00 | 86.7467 | 40.4767 | 46.27 | 303.0668 | 21.8116 | 181.3931 | 81.2182 | 8.7818 | -178.6913 | 141.1977 | 0 | 30.3575 | 0.68766 | 0.81276 | 14.913 | 45.2705 | 3.4 | 4.8147 | 1.0706 | 0.039744
2016-05-31 | 83.47 | 40.41 | 43.06 | 267.0787 | 21.8177 | -163.6084 | 80.7219 | 9.2781 | -164.6057 | 138.0234 | 0 | 30.3075 | 0.6875 | 0.8125 | 14.3464 | 44.6539 | 2.9 | 4.2954 | 1.0725 | 0.03927
2016-05-31 01:00 | 98.8167 | 52.3467 | 46.47 | 253.2937 | 21.8238 | -148.6099 | 79.4285 | 10.5715 | -150.5356 | 130.5028 | 0 | 39.26 | 0.68734 | 0.81224 | 16.9803 | 56.2403 | 2.8 | 4.5575 | 1.0715 | 0.049417
2016-05-31 02:00 | 114.1633 | 64.2833 | 49.88 | 228.9396 | 21.8299 | -133.6113 | 77.4158 | 12.5842 | -136.4759 | 120.2597 | 0 | 48.2125 | 0.68719 | 0.81198 | 19.6129 | 67.8254 | 2.6 | 4.7195 | 1.071 | 0.059565
2016-05-31 03:00 | 129.51 | 76.22 | 53.29 | 203.3036 | 21.836 | -118.6128 | 74.8041 | 15.1959 | -122.3907 | 108.4598 | 0 | 57.165 | 0.68703 | 0.81172 | 22.2444 | 79.4094 | 2.8 | 5.2815 | 1.069 | 0.06961
2016-05-31 04:00 | 135.2333 | 90.4 | 44.8333 | 143.1493 | 21.8421 | -103.6143 | 71.7483 | 18.2517 | -108.209 | 95.7626 | 0 | 67.8 | 0.68688 | 0.81146 | 23.2221 | 91.0221 | 3.5 | 6.3444 | 1.0653 | 0.079512
2016-05-31 05:00 | 140.9567 | 104.58 | 36.3767 | 98.9524 | 21.8482 | -88.6158 | 68.4312 | 21.5688 | -93.8277 | 82.5279 | 12.8682 | 78.435 | 0.68672 | 0.8112 | 24.1994 | 115.5026 | 3.7 | 7.3095 | 1.0619 | 0.10058
2016-05-31 06:00 | 146.68 | 118.76 | 27.92 | 66.2092 | 21.8542 | -73.6173 | 65.0584 | 24.9416 | -79.1238 | 68.9603 | 23.7701 | 89.07 | 0.68656 | 0.81094 | 25.1762 | 138.0164 | 3.3 | 7.613 | 1.0609 | 0.12006
2016-05-31 07:00 | 155.3667 | 136.0467 | 19.32 | 40.9546 | 21.8603 | -58.6188 | 61.8526 | 28.1474 | -63.9755 | 55.1865 | 23.3813 | 102.035 | 0.68641 | 0.81068 | 26.6612 | 152.0774 | 2.6 | 7.3524 | 1.0618 | 0.13241
2016-05-31 08:00 | 164.0533 | 153.3333 | 10.72 | 20.8414 | 21.8663 | -43.6203 | 59.0453 | 30.9547 | -48.2945 | 41.298 | 15.6579 | 115 | 0.68625 | 0.81042 | 28.1454 | 158.8033 | 2.7 | 7.6626 | 1.0607 | 0.13812
2016-05-31 09:00 | 172.74 | 170.62 | 2.12 | 3.8781 | 21.8723 | -28.6218 | 56.8623 | 33.1377 | -32.0654 | 27.3932 | 3.4433 | 127.965 | 0.68609 | 0.81016 | 29.629 | 161.0373 | 3.5 | 8.5324 | 1.0576 | 0.13966
2016-05-31 10:00 | 161.4067 | 158.1833 | 3.2233 | 5.6907 | 21.8783 | -13.6233 | 55.4987 | 34.5013 | -15.3801 | 13.7466 | 5.5277 | 118.6375 | 0.68594 | 0.8099 | 27.6787 | 151.8439 | 3.2 | 7.9451 | 1.0597 | 0.13194
2016-05-31 11:00 | 150.0733 | 145.7467 | 4.3267 | 7.5596 | 21.8844 | 1.3752 | 55.0865 | 34.9135 | 1.5563 | 5.0857 | 7.5299 | 109.31 | 0.68578 | 0.80964 | 25.7294 | 142.5692 | 2.4 | 6.8553 | 1.0635 | 0.12433
2016-05-31 12:00 | 138.74 | 133.31 | 5.43 | 9.6277 | 21.8903 | 16.3737 | 55.6673 | 34.3327 | 18.4673 | 16.1955 | 9.2456 | 99.9825 | 0.68563 | 0.80937 | 23.7809 | 133.009 | 2.9 | 7.0565 | 1.0628 | 0.11592
2016-05-31 13:00 | 144.71 | 125.6667 | 19.0433 | 35.1367 | 21.8963 | 31.3722 | 57.1816 | 32.8184 | 35.0842 | 29.9392 | 30.4479 | 94.25 | 0.68547 | 0.80911 | 24.7985 | 149.4964 | 2.7 | 7.3718 | 1.0617 | 0.13015
2016-05-31 14:00 | 150.68 | 118.0233 | 32.6567 | 64.3115 | 21.9023 | 46.3707 | 59.4833 | 30.5167 | 51.2201 | 43.8482 | 46.38 | 88.5175 | 0.68531 | 0.80885 | 25.8157 | 160.7132 | 2.1 | 7.1223 | 1.0626 | 0.14003
2016-05-31 15:00 | 156.65 | 110.38 | 46.27 | 99.7702 | 21.9083 | 61.3692 | 62.3696 | 27.6304 | 66.8038 | 57.7176 | 53.2866 | 82.785 | 0.68516 | 0.80859 | 26.8324 | 162.904 | 2.1 | 7.1907 | 1.0623 | 0.14191
2016-05-31 16:00 | 142.15 | 104.5267 | 37.6233 | 91.1164 | 21.9142 | 76.3677 | 65.6119 | 24.3881 | 81.8662 | 71.4547 | 28.9799 | 78.395 | 0.685 | 0.80833 | 24.3432 | 131.7181 | 2.4 | 6.5162 | 1.0647 | 0.115
2016-05-31 17:00 | 127.65 | 98.6733 | 28.9767 | 80.7804 | 21.9201 | 91.3661 | 68.9791 | 21.0209 | 96.5042 | 84.9639 | 7.0912 | 74.005 | 0.68484 | 0.80807 | 21.8551 | 102.9513 | 2.3 | 5.5172 | 1.0682 | 0.090177
2016-05-31 18:00 | 113.15 | 92.82 | 20.33 | 66.6892 | 21.9261 | 106.3646 | 72.251 | 17.749 | 110.8413 | 98.1072 | 0 | 69.615 | 0.68469 | 0.80781 | 19.3681 | 88.9831 | 2.4 | 5.1807 | 1.0694 | 0.078028
2016-05-31 19:00 | 108.8133 | 75.82 | 32.9933 | 129.3829 | 21.932 | 121.3631 | 75.2261 | 14.7739 | 124.9981 | 110.6577 | 0 | 56.865 | 0.68453 | 0.80755 | 18.6215 | 75.4865 | 2.3 | 4.659 | 1.0712 | 0.066306
2016-05-31 20:00 | 104.4767 | 58.82 | 45.6567 | 214.7683 | 21.9379 | 136.3616 | 77.7261 | 12.2739 | 139.0721 | 122.2127 | 0 | 44.115 | 0.68438 | 0.80729 | 17.8753 | 61.9903 | 1.7 | 3.6372 | 1.0748 | 0.054633
2016-05-31 21:00 | 100.14 | 41.82 | 58.32 | 323.1313 | 21.9438 | 151.36 | 79.6021 | 10.3979 | 153.1278 | 132.0348 | 0 | 31.365 | 0.68422 | 0.80703 | 17.1294 | 48.4944 | 2.6 | 4.1155 | 1.0731 | 0.042672
2016-05-31 22:00 | 105.7633 | 41.9067 | 63.8567 | 396.89 | 21.9497 | 166.3585 | 80.7413 | 9.2587 | 167.1948 | 138.8542 | 0 | 31.43 | 0.68406 | 0.80677 | 18.0872 | 49.5172 | 2.6 | 4.1474 | 1.073 | 0.043568
2016-05-31 23:00 | 111.3867 | 41.9933 | 69.3933 | 447.2606 | 21.9555 | 181.357 | 81.0744 | 8.9256 | -178.726 | 141.0551 | 0 | 31.495 | 0.68391 | 0.80651 | 19.0445 | 50.5395 | 1.1 | 2.6794 | 1.0781 | 0.04468
2016-06-01 | 117.01 | 42.08 | 74.93 | 457.845 | 21.9614 | -163.6446 | 80.5807 | 9.4193 | -164.6491 | 137.9054 | 0 | 31.56 | 0.68375 | 0.80625 | 20.0014 | 51.5614 | 1.6 | 3.2113 | 1.0763 | 0.045505
2016-06-01 01:00 | 130.3233 | 67.3467 | 62.9767 | 338.882 | 21.9672 | -148.6461 | 79.2901 | 10.7099 | -150.5871 | 130.4164 | 0 | 50.51 | 0.68359 | 0.80599 | 22.2721 | 72.7821 | 2.2 | 4.4744 | 1.0718 | 0.063969
2016-06-01 02:00 | 143.6367 | 92.6133 | 51.0233 | 231.7329 | 21.9731 | -133.6477 | 77.2803 | 12.7197 | -136.5345 | 120.201 | 0 | 69.46 | 0.68344 | 0.80573 | 24.5417 | 94.0017 | 1.1 | 4.0376 | 1.0734 | 0.082737
2016-06-01 03:00 | 156.95 | 117.88 | 39.07 | 147.7917 | 21.9789 | -118.6492 | 74.6712 | 15.3288 | -122.4554 | 108.4232 | 0 | 88.41 | 0.68328 | 0.80547 | 26.8102 | 115.2202 | 1.8 | 5.4006 | 1.0686 | 0.10096
2016-06-01 04:00 | 182.88 | 146.34 | 36.54 | 115.8665 | 21.9847 | -103.6508 | 71.6173 | 18.3827 | -108.2784 | 95.7434 | 0 | 109.755 | 0.68312 | 0.80521 | 31.2325 | 140.9875 | 1.7 | 6.1059 | 1.0661 | 0.12325
2016-06-01 05:00 | 208.81 | 174.8 | 34.01 | 91.9872 | 21.9905 | -88.6523 | 68.3013 | 21.6987 | -93.9003 | 82.5229 | 11.9703 | 131.1 | 0.68297 | 0.80495 | 35.6527 | 178.723 | 2.6 | 8.1851 | 1.0589 | 0.15518
2016-06-01 06:00 | 234.74 | 203.26 | 31.48 | 74.2894 | 21.9963 | -73.6539 | 64.9286 | 25.0714 | -79.1976 | 68.9678 | 26.662 | 152.445 | 0.68281 | 0.80469 | 40.0709 | 219.1778 | 2.8 | 9.6493 | 1.0537 | 0.18938
2016-06-01 07:00 | 268.32 | 234.5133 | 33.8067 | 71.3587 | 22.0021 | -58.6555 | 61.7216 | 28.2784 | -64.0484 | 55.2057 | 40.7196 | 175.885 | 0.68266 | 0.80443 | 45.7926 | 262.3971 | 3.2 | 11.3999 | 1.0476 | 0.22541
2016-06-01 08:00 | 301.9 | 265.7667 | 36.1333 | 69.9783 | 22.0079 | -43.657 | 58.9122 | 31.0878 | -48.3636 | 41.3295 | 52.5484 | 199.325 | 0.6825 | 0.80417 | 51.5117 | 303.3851 | 2.6 | 12.0808 | 1.0452 | 0.26002
2016-06-01 09:00 | 335.48 | 297.02 | 38.46 | 70.1013 | 22.0137 | -28.6586 | 56.7266 | 33.2734 | -32.1277 | 27.4404 | 62.2142 | 222.765 | 0.68234 | 0.80391 | 57.2282 | 342.2074 | 2.9 | 13.594 | 1.0399 | 0.29181
2016-06-01 10:00 | 354.85 | 296.46 | 58.39 | 102.724 | 22.0194 | -13.6602 | 55.3601 | 34.6399 | -15.4327 | 13.8245 | 99.7483 | 222.345 | 0.68219 | 0.80365 | 60.5186 | 382.6119 | 4.3 | 16.2566 | 1.0306 | 0.32334
2016-06-01 11:00 | 374.22 | 295.9 | 78.32 | 136.3616 | 22.0251 | 1.3383 | 54.9455 | 35.0545 | 1.5155 | 5.2133 | 135.7976 | 221.925 | 0.68203 | 0.80339 | 63.8074 | 421.53 | 4.2 | 17.3728 | 1.0267 | 0.35488
2016-06-01 12:00 | 393.59 | 295.34 | 98.25 | 173.5701 | 22.0309 | 16.3367 | 55.5245 | 34.4755 | 18.4389 | 16.1989 | 166.6792 | 221.505 | 0.68188 | 0.80312 | 67.0948 | 455.279 | 4.2 | 18.4275 | 1.023 | 0.38192
2016-06-01 13:00 | 346.79 | 243.89 | 102.9 | 189.1249 | 22.0366 | 31.3351 | 57.0379 | 32.9621 | 35.0669 | 29.9147 | 163.9276 | 182.9175 | 0.68172 | 0.80286 | 59.1033 | 405.9484 | 3.5 | 16.1859 | 1.0308 | 0.34315
2016-06-01 14:00 | 299.99 | 192.44 | 107.55 | 210.902 | 22.0423 | 46.3335 | 59.3393 | 30.6607 | 51.2116 | 43.809 | 152.1977 | 144.33 | 0.68156 | 0.8026 | 51.1155 | 347.6432 | 3.6 | 14.4638 | 1.0369 | 0.29558
2016-06-01 15:00 | 253.19 | 140.99 | 112.2 | 240.7779 | 22.048 | 61.3319 | 62.2257 | 27.7743 | 66.801 | 57.6669 | 128.7777 | 105.7425 | 0.68141 | 0.80234 | 43.1313 | 277.6515 | 4.2 | 12.8766 | 1.0424 | 0.23733
2016-06-01 16:00 | 228.8967 | 122.06 | 106.8367 | 257.3149 | 22.0537 | 76.3304 | 65.4682 | 24.5318 | 81.8662 | 71.3934 | 82.101 | 91.545 | 0.68125 | 0.80208 | 38.984 | 212.63 | 3.8 | 10.4447 | 1.0509 | 0.18324
2016-06-01 17:00 | 204.6033 | 103.13 | 101.4733 | 281.0545 | 22.0593 | 91.3288 | 68.8356 | 21.1644 | 96.5042 | 84.8916 | 25.0251 | 77.3475 | 0.68109 | 0.80182 | 34.8385 | 137.2111 | 3.4 | 7.6878 | 1.0606 | 0.11933
2016-06-01 18:00 | 180.31 | 84.2 | 96.11 | 312.8312 | 22.065 | 106.3272 | 72.1078 | 17.8922 | 110.839 | 98.0229 | 0 | 63.15 | 0.68094 | 0.80156 | 30.695 | 93.845 | 3 | 5.9327 | 1.0667 | 0.082088
2016-06-01 19:00 | 162.1167 | 69.13 | 92.9867 | 361.2326 | 22.0707 | 121.3256 | 75.0833 | 14.9167 | 124.9914 | 110.5597 | 0 | 51.8475 | 0.68078 | 0.8013 | 27.5915 | 79.439 | 2.3 | 4.7825 | 1.0708 | 0.069749
2016-06-01 20:00 | 143.9233 | 54.06 | 89.8633 | 417.9494 | 22.0763 | 136.324 | 77.5839 | 12.4161 | 139.0595 | 122.0989 | 0 | 40.545 | 0.68063 | 0.80104 | 24.4895 | 65.0345 | 2.1 | 4.1323 | 1.073 | 0.057223
2016-06-01 21:00 | 125.73 | 38.99 | 86.74 | 474.2316 | 22.0819 | 151.3224 | 79.4609 | 10.5391 | 153.108 | 131.9045 | 0 | 29.2425 | 0.68047 | 0.80078 | 21.3888 | 50.6313 | 2 | 3.5822 | 1.075 | 0.04463
2016-06-01 22:00 | 124.3367 | 38.6333 | 85.7033 | 524.8332 | 22.0875 | 166.3208 | 80.6017 | 9.3983 | 167.1669 | 138.7127 | 0 | 28.975 | 0.68031 | 0.80052 | 21.1469 | 50.1219 | 1.8 | 3.3663 | 1.0757 | 0.044212
2016-06-01 23:00 | 122.9433 | 38.2767 | 84.6667 | 537.4945 | 22.0932 | 181.3192 | 80.937 | 9.063 | -178.7623 | 140.9188 | 0 | 28.7075 | 0.68016 | 0.80026 | 20.9052 | 49.6127 | 1.7 | 3.2504 | 1.0761 | 0.043779
2016-06-02 | 121.55 | 37.92 | 83.63 | 503.8597 | 22.0988 | -163.6825 | 80.4459 | 9.5541 | -164.6935 | 137.7936 | 0 | 28.44 | 0.68 | 0.8 | 20.6635 | 49.1035 | 1.6 | 3.1345 | 1.0765 | 0.043346
2016-06-02 01:00 | 116.39 | 60.1067 | 56.2833 | 299.2231 | 22.1043 | -148.6841 | 79.1582 | 10.8418 | -150.6393 | 130.3355 | 0 | 45.08 | 0.67984 | 0.79974 | 19.7818 | 64.8618 | 1.6 | 3.6269 | 1.0748 | 0.057165
2016-06-02 02:00 | 111.23 | 82.2933 | 28.9367 | 130.1242 | 22.1099 | -133.6857 | 77.1513 | 12.8487 | -136.5936 | 120.1472 | 0 | 61.72 | 0.67969 | 0.79948 | 18.9004 | 80.6204 | 1.8 | 4.3194 | 1.0724 | 0.070894
2016-06-02 03:00 | 106.07 | 104.48 | 1.59 | 5.9666 | 22.1155 | -118.6873 | 74.5448 | 15.4552 | -122.5202 | 108.3907 | 0 | 78.36 | 0.67953 | 0.79922 | 18.0195 | 96.3795 | 1.7 | 4.7119 | 1.071 | 0.084643
2016-06-02 04:00 | 132.13 | 123.43 | 8.7 | 27.4082 | 22.121 | -103.6889 | 71.4928 | 18.5072 | -108.3478 | 95.7277 | 0 | 92.5725 | 0.67938 | 0.79896 | 22.4415 | 115.014 | 1.5 | 5.0942 | 1.0697 | 0.10088
2016-06-02 05:00 | 158.19 | 142.38 | 15.81 | 42.5315 | 22.1266 | -88.6905 | 68.178 | 21.822 | -93.9728 | 82.5211 | 5.5359 | 106.785 | 0.67922 | 0.7987 | 26.8614 | 139.1824 | 1.5 | 5.8494 | 1.067 | 0.12178
2016-06-02 06:00 | 184.25 | 161.33 | 22.92 | 53.8411 | 22.1321 | -73.6922 | 64.8052 | 25.1948 | -79.2715 | 68.978 | 19.3142 | 120.9975 | 0.67906 | 0.79844 | 31.2793 | 171.591 | 1.5 | 6.8622 | 1.0635 | 0.14964
2016-06-02 07:00 | 171.5933 | 156.1667 | 15.4267 | 32.4316 | 22.1376 | -58.6938 | 61.5971 | 28.4029 | -64.1215 | 55.2272 | 18.4965 | 117.125 | 0.67891 | 0.79818 | 29.1239 | 164.7454 | 1.5 | 6.6483 | 1.0642 | 0.14377
2016-06-02 08:00 | 158.9367 | 151.0033 | 7.9333 | 15.3082 | 22.1431 | -43.6954 | 58.7857 | 31.2143 | -48.4333 | 41.3629 | 11.4894 | 113.2525 | 0.67875 | 0.79792 | 26.9696 | 151.7115 | 1 | 5.741 | 1.0674 | 0.13279
2016-06-02 09:00 | 146.28 | 145.84 | 0.44 | 0.79925 | 22.1486 | -28.6971 | 56.5974 | 33.4026 | -32.191 | 27.4891 | 0.70901 | 109.38 | 0.67859 | 0.79766 | 24.8162 | 134.9052 | 1.9 | 6.1158 | 1.0661 | 0.11793
2016-06-02 10:00 | 136.74 | 136.3667 | 0.37333 | 0.65461 | 22.1541 | -13.6987 | 55.228 | 34.772 | -15.4866 | 13.9026 | 0.63544 | 102.275 | 0.67844 | 0.7974 | 23.1924 | 126.1028 | 2 | 5.9407 | 1.0667 | 0.1103
2016-06-02 11:00 | 127.2 | 126.8933 | 0.30667 | 0.53215 | 22.1596 | 1.2997 | 54.8109 | 35.1891 | 1.4728 | 5.3352 | 0.52985 | 95.17 | 0.67828 | 0.79714 | 21.5693 | 117.2692 | 2.5 | 6.1647 | 1.0659 | 0.1025
2016-06-02 12:00 | 117.66 | 117.42 | 0.24 | 0.42252 | 22.165 | 16.298 | 55.388 | 34.612 | 18.4081 | 16.2005 | 0.40575 | 88.065 | 0.67813 | 0.79688 | 19.947 | 108.4178 | 2.5 | 5.8881 | 1.0669 | 0.094849
2016-06-02 13:00 | 101.2667 | 97.1 | 4.1667 | 7.6299 | 22.1705 | 31.2964 | 56.9003 | 33.0997 | 35.0469 | 29.8889 | 6.6151 | 72.825 | 0.67797 | 0.79661 | 17.1639 | 96.604 | 2.6 | 5.6189 | 1.0678 | 0.084589
2016-06-02 14:00 | 84.8733 | 76.78 | 8.0933 | 15.8066 | 22.1759 | 46.2947 | 59.2013 | 30.7987 | 51.2001 | 43.7689 | 11.4145 | 57.585 | 0.67781 | 0.79635 | 14.3821 | 83.3815 | 2.7 | 5.3057 | 1.0689 | 0.073086
2016-06-02 15:00 | 68.48 | 56.46 | 12.02 | 25.6772 | 22.1814 | 61.2931 | 62.0877 | 27.9123 | 66.7951 | 57.6158 | 13.7526 | 42.345 | 0.67766 | 0.79609 | 11.6015 | 67.699 | 2.9 | 5.0156 | 1.0699 | 0.059396
2016-06-02 16:00 | 75.6233 | 60.9067 | 14.7167 | 35.2591 | 22.1868 | 76.2914 | 65.3303 | 24.6697 | 81.863 | 71.332 | 11.2859 | 45.68 | 0.6775 | 0.79583 | 12.8087 | 69.7746 | 3.5 | 5.6805 | 1.0676 | 0.061084
2016-06-02 17:00 | 82.7667 | 65.3533 | 17.4133 | 47.9331 | 22.1922 | 91.2898 | 68.698 | 21.302 | 96.501 | 84.8198 | 4.3278 | 49.015 | 0.67734 | 0.79557 | 14.0154 | 67.3582 | 2.7 | 4.8049 | 1.0707 | 0.059138
2016-06-02 18:00 | 89.91 | 69.8 | 20.11 | 64.9744 | 22.1976 | 106.2881 | 71.9705 | 18.0295 | 110.8337 | 97.9397 | 0 | 52.35 | 0.67719 | 0.79531 | 15.2215 | 67.5715 | 2.5 | 4.6116 | 1.0714 | 0.059363
2016-06-02 19:00 | 74.5633 | 59.3867 | 15.1767 | 58.4341 | 22.203 | 121.2864 | 74.9464 | 15.0536 | 124.982 | 110.4634 | 0 | 44.54 | 0.67703 | 0.79505 | 12.6204 | 57.1604 | 2.8 | 4.5863 | 1.0714 | 0.05022
2016-06-02 20:00 | 59.2167 | 48.9733 | 10.2433 | 47.1326 | 22.2083 | 136.2848 | 77.4477 | 12.5523 | 139.0444 | 121.9879 | 0 | 36.73 | 0.67688 | 0.79479 | 10.0206 | 46.7506 | 3.1 | 4.561 | 1.0715 | 0.041078
2016-06-02 21:00 | 43.87 | 38.56 | 5.31 | 28.6683 | 22.2137 | 151.2831 | 79.3259 | 10.6741 | 153.086 | 131.7783 | 0 | 28.92 | 0.67672 | 0.79453 | 7.4219 | 36.3419 | 3 | 4.1357 | 1.073 | 0.031977
2016-06-02 22:00 | 50.26 | 45.63 | 4.63 | 27.9605 | 22.219 | 166.2814 | 80.4684 | 9.5316 | 167.1372 | 138.5767 | 0 | 34.2225 | 0.67656 | 0.79427 | 8.501 | 42.7235 | 1.7 | 3.0351 | 1.0769 | 0.037727
2016-06-02 23:00 | 56.65 | 52.7 | 3.95 | 24.7216 | 22.2244 | 181.2798 | 80.8059 | 9.1941 | -178.7999 | 140.7889 | 0 | 39.525 | 0.67641 | 0.79401 | 9.5796 | 49.1046 | 0.5 | 2.0345 | 1.0804 | 0.043502
2016-06-03 | 63.04 | 59.77 | 3.27 | 19.4426 | 22.2297 | -163.7219 | 80.3176 | 9.6824 | -164.739 | 137.6881 | 0 | 44.8275 | 0.67625 | 0.79375 | 10.6577 | 55.4852 | 0.2 | 1.9339 | 1.0807 | 0.049171
2016-06-03 01:00 | 88.7167 | 80.38 | 8.3367 | 43.8201 | 22.235 | -148.7236 | 79.0328 | 10.9672 | -150.6922 | 130.2602 | 0 | 60.285 | 0.67609 | 0.79349 | 14.9952 | 75.2802 | 0.2 | 2.5525 | 1.0786 | 0.06658
2016-06-03 02:00 | 114.3933 | 100.99 | 13.4033 | 59.7135 | 22.2403 | -133.7253 | 77.0288 | 12.9712 | -136.653 | 120.0981 | 0 | 75.7425 | 0.67594 | 0.79323 | 19.3307 | 95.0732 | 0 | 2.971 | 1.0771 | 0.083971
2016-06-03 03:00 | 140.07 | 121.6 | 18.47 | 68.7892 | 22.2456 | -118.727 | 74.4249 | 15.5751 | -122.5853 | 108.3623 | 0 | 91.2 | 0.67578 | 0.79297 | 23.6642 | 114.8642 | 0 | 3.5895 | 1.0749 | 0.10125
2016-06-03 04:00 | 187.1833 | 156.77 | 30.4133 | 95.2281 | 22.2509 | -103.7286 | 71.375 | 18.625 | -108.4172 | 95.7156 | 0 | 117.5775 | 0.67563 | 0.79271 | 31.6164 | 149.1939 | 0.7 | 5.3623 | 1.0687 | 0.13075
2016-06-03 05:00 | 234.2967 | 191.94 | 42.3567 | 113.3694 | 22.2562 | -88.7303 | 68.0612 | 21.9388 | -94.0452 | 82.5223 | 14.7538 | 143.955 | 0.67547 | 0.79245 | 39.565 | 198.2738 | 0.9 | 7.0961 | 1.0627 | 0.17277
2016-06-03 06:00 | 281.41 | 227.11 | 54.3 | 127.0056 | 22.2615 | -73.732 | 64.6884 | 25.3116 | -79.3454 | 68.9909 | 45.5336 | 170.3325 | 0.67531 | 0.79219 | 47.5099 | 263.376 | 1.2 | 9.4305 | 1.0545 | 0.22774
2016-06-03 07:00 | 331.54 | 248.27 | 83.27 | 174.396 | 22.2667 | -58.7337 | 61.4793 | 28.5207 | -64.1947 | 55.2511 | 99.4026 | 186.2025 | 0.67516 | 0.79193 | 55.9603 | 341.5654 | 1.2 | 11.8739 | 1.0459 | 0.29295
2016-06-03 08:00 | 381.67 | 269.43 | 112.24 | 215.8342 | 22.2719 | -43.7354 | 58.6658 | 31.3342 | -48.5034 | 41.3982 | 161.904 | 202.0725 | 0.675 | 0.79167 | 64.4068 | 428.3834 | 1.2 | 14.587 | 1.0364 | 0.36408
2016-06-03 09:00 | 431.8 | 290.59 | 141.21 | 255.6741 | 22.2772 | -28.7371 | 56.4747 | 33.5253 | -32.255 | 27.539 | 226.7053 | 217.9425 | 0.67484 | 0.79141 | 72.8494 | 517.4972 | 1.4 | 17.5718 | 1.026 | 0.43538
2016-06-03 10:00 | 433.7633 | 278.1433 | 155.62 | 272.0101 | 22.2824 | -13.7388 | 55.1024 | 34.8976 | -15.542 | 13.9808 | 263.9523 | 208.6075 | 0.67469 | 0.79115 | 73.1637 | 545.7235 | 1.4 | 18.4539 | 1.0229 | 0.45775
2016-06-03 11:00 | 435.7267 | 265.6967 | 170.03 | 294.1159 | 22.2876 | 1.2595 | 54.6826 | 35.3174 | 1.4283 | 5.4514 | 292.7857 | 199.2725 | 0.67453 | 0.79089 | 73.4778 | 565.536 | 2.9 | 20.573 | 1.0155 | 0.47092
2016-06-03 12:00 | 437.69 | 253.25 | 184.44 | 323.6438 | 22.2928 | 16.2578 | 55.2577 | 34.7423 | 18.3749 | 16.2 | 310.7931 | 189.9375 | 0.67438 | 0.79063 | 73.7918 | 574.5224 | 2.6 | 20.5538 | 1.0156 | 0.47844
2016-06-03 13:00 | 415.9433 | 220.43 | 195.5133 | 356.7639 | 22.298 | 31.2561 | 56.7688 | 33.2312 | 35.0241 | 29.8618 | 309.3961 | 165.3225 | 0.67422 | 0.79036 | 70.1092 | 544.8278 | 2.2 | 19.2259 | 1.0202 | 0.45579
2016-06-03 14:00 | 394.1967 | 187.61 | 206.5867 | 401.9188 | 22.3031 | 46.2544 | 59.0693 | 30.9307 | 51.1855 | 43.7279 | 290.439 | 140.7075 | 0.67406 | 0.7901 | 66.4283 | 497.5747 | 2.6 | 18.1492 | 1.024 | 0.41779
2016-06-03 15:00 | 372.45 | 154.79 | 217.66 | 462.9525 | 22.3083 | 61.2526 | 61.9556 | 28.0444 | 66.786 | 57.5641 | 248.3069 | 116.0925 | 0.67391 | 0.78984 | 62.7491 | 427.1485 | 2.5 | 15.8484 | 1.032 | 0.36148
2016-06-03 16:00 | 319.28 | 149.3933 | 169.8867 | 404.9953 | 22.3135 | 76.2509 | 65.1984 | 24.8016 | 81.8566 | 71.2707 | 130.0432 | 112.045 | 0.67375 | 0.78958 | 53.7787 | 295.8669 | 2.7 | 11.9458 | 1.0457 | 0.2537
2016-06-03 17:00 | 266.11 | 143.9967 | 122.1133 | 334.1677 | 22.3186 | 91.2492 | 68.5662 | 21.4338 | 96.4948 | 84.7484 | 30.5859 | 107.9975 | 0.67359 | 0.78932 | 44.8125 | 183.3959 | 3.1 | 8.8311 | 1.0566 | 0.1589
2016-06-03 18:00 | 212.94 | 138.6 | 74.34 | 238.5091 | 22.3237 | 106.2475 | 71.8391 | 18.1609 | 110.8254 | 97.8575 | 0 | 103.95 | 0.67344 | 0.78906 | 35.8504 | 139.8004 | 3.2 | 7.5688 | 1.061 | 0.12163
2016-06-03 19:00 | 174.8367 | 117.8633 | 56.9733 | 217.5157 | 22.3288 | 121.2458 | 74.8155 | 15.1845 | 124.9698 | 110.369 | 0 | 88.3975 | 0.67328 | 0.7888 | 29.4286 | 117.8261 | 2.4 | 6.0821 | 1.0662 | 0.10301
2016-06-03 20:00 | 136.7333 | 97.1267 | 39.6067 | 180.4039 | 22.3339 | 136.244 | 77.3177 | 12.6823 | 139.0268 | 121.8798 | 0 | 72.845 | 0.67313 | 0.78854 | 23.0097 | 95.8547 | 2.1 | 5.0955 | 1.0697 | 0.084077
2016-06-03 21:00 | 98.63 | 76.39 | 22.24 | 118.6579 | 22.339 | 151.2423 | 79.1972 | 10.8028 | 153.0618 | 131.6563 | 0 | 57.2925 | 0.67297 | 0.78828 | 16.5937 | 73.8862 | 1.9 | 4.2089 | 1.0728 | 0.064996
2016-06-03 22:00 | 88.0767 | 71.9533 | 16.1233 | 96.1007 | 22.3441 | 166.2406 | 80.3415 | 9.6585 | 167.1058 | 138.4463 | 0 | 53.965 | 0.67281 | 0.78802 | 14.8148 | 68.7798 | 1.7 | 3.8494 | 1.074 | 0.060575
2016-06-03 23:00 | 77.5233 | 67.5167 | 10.0067 | 61.7979 | 22.3492 | 181.2388 | 80.6813 | 9.3187 | -178.8389 | 140.6654 | 0 | 50.6375 | 0.67266 | 0.78776 | 13.0366 | 63.6741 | 2 | 3.9898 | 1.0735 | 0.056052
2016-06-04 | 66.97 | 63.08 | 3.89 | 22.8443 | 22.3543 | -163.7629 | 80.1957 | 9.8043 | -164.7855 | 137.5889 | 0 | 47.31 | 0.6725 | 0.7875 | 11.2593 | 58.5693 | 1.5 | 3.3303 | 1.0758 | 0.051669
2016-06-04 01:00 | 102.1033 | 80.1067 | 21.9967 | 114.3971 | 22.3593 | -148.7646 | 78.9139 | 11.0861 | -150.7457 | 130.1905 | 0 | 60.08 | 0.67234 | 0.78724 | 17.1621 | 77.2421 | 1.6 | 4.0138 | 1.0735 | 0.067991
2016-06-04 02:00 | 137.2367 | 97.1333 | 40.1033 | 177.1104 | 22.3643 | -133.7664 | 76.9129 | 13.0871 | -136.7128 | 120.0538 | 0 | 72.85 | 0.67219 | 0.78698 | 23.0622 | 95.9122 | 1.4 | 4.3973 | 1.0721 | 0.084319
2016-06-04 03:00 | 172.37 | 114.16 | 58.21 | 215.2696 | 22.3694 | -118.7681 | 74.3116 | 15.6884 | -122.6504 | 108.338 | 0 | 85.62 | 0.67203 | 0.78672 | 28.9595 | 114.5795 | 2.1 | 5.6806 | 1.0676 | 0.10031
2016-06-04 04:00 | 193.84 | 138.6267 | 55.2133 | 171.8898 | 22.3744 | -103.7699 | 71.2637 | 18.7363 | -108.4865 | 95.707 | 0 | 103.97 | 0.67188 | 0.78646 | 32.5591 | 136.5291 | 1.6 | 5.8665 | 1.067 | 0.11945
2016-06-04 05:00 | 215.31 | 163.0933 | 52.2167 | 139.0961 | 22.3794 | -88.7716 | 67.951 | 22.049 | -94.1175 | 82.5266 | 18.0916 | 122.32 | 0.67172 | 0.7862 | 36.1569 | 176.5685 | 1.7 | 7.2178 | 1.0622 | 0.1538
2016-06-04 06:00 | 236.78 | 187.56 | 49.22 | 114.6577 | 22.3844 | -73.7734 | 64.5783 | 25.4217 | -79.4191 | 69.0064 | 41.0777 | 140.67 | 0.67156 | 0.78594 | 39.7531 | 221.5009 | 2.3 | 9.2219 | 1.0552 | 0.19166
2016-06-04 07:00 | 233.3033 | 197.92 | 35.3833 | 73.8412 | 22.3894 | -58.7751 | 61.368 | 28.632 | -64.2679 | 55.277 | 42.0606 | 148.44 | 0.67141 | 0.78568 | 39.1603 | 229.661 | 1.3 | 8.4769 | 1.0578 | 0.19921
2016-06-04 08:00 | 229.8267 | 208.28 | 21.5467 | 41.2995 | 22.3943 | -43.7769 | 58.5525 | 31.4475 | -48.5737 | 41.4352 | 30.9624 | 156.21 | 0.67125 | 0.78542 | 38.5678 | 225.7402 | 1.4 | 8.4544 | 1.0579 | 0.19583
2016-06-04 09:00 | 226.35 | 218.64 | 7.71 | 13.9172 | 22.3993 | -28.7786 | 56.3587 | 33.6413 | -32.3198 | 27.5901 | 12.3346 | 163.98 | 0.67109 | 0.78516 | 37.9755 | 214.2901 | 1.5 | 8.1966 | 1.0588 | 0.18605
2016-06-04 10:00 | 229.98 | 217.4533 | 12.5267 | 21.8305 | 22.4042 | -13.7804 | 54.9834 | 35.0166 | -15.5985 | 14.0588 | 21.1766 | 163.09 | 0.67094 | 0.7849 | 38.5756 | 222.8422 | 1.6 | 8.5638 | 1.0575 | 0.19324
2016-06-04 11:00 | 233.61 | 216.2667 | 17.3433 | 29.9106 | 22.4092 | 1.2178 | 54.5608 | 35.4392 | 1.3819 | 5.5619 | 29.7698 | 162.2 | 0.67078 | 0.78464 | 39.1753 | 231.1451 | 2.3 | 9.5233 | 1.0542 | 0.19981
2016-06-04 12:00 | 237.24 | 215.08 | 22.16 | 38.7642 | 22.4141 | 16.2161 | 55.1338 | 34.8662 | 18.3394 | 16.1975 | 37.2255 | 161.31 | 0.67063 | 0.78438 | 39.7748 | 238.3103 | 2.4 | 9.8472 | 1.053 | 0.20578
2016-06-04 13:00 | 233.97 | 200.8667 | 33.1033 | 60.2047 | 22.419 | 31.2143 | 56.6436 | 33.3564 | 34.9985 | 29.8333 | 52.2262 | 150.65 | 0.67047 | 0.78411 | 39.2174 | 242.0936 | 2.7 | 10.2654 | 1.0516 | 0.20875
2016-06-04 14:00 | 230.7 | 186.6533 | 44.0467 | 85.3808 | 22.4239 | 46.2125 | 58.9434 | 31.0566 | 51.1679 | 43.686 | 61.7419 | 139.99 | 0.67031 | 0.78385 | 38.6603 | 240.3922 | 2 | 9.5123 | 1.0542 | 0.20781
2016-06-04 15:00 | 227.43 | 172.44 | 54.99 | 116.4801 | 22.4288 | 61.2107 | 61.8294 | 28.1706 | 66.7738 | 57.5121 | 62.564 | 129.33 | 0.67016 | 0.78359 | 38.1034 | 229.9974 | 2.4 | 9.5874 | 1.0539 | 0.19877
2016-06-04 16:00 | 202.78 | 154.2233 | 48.5567 | 115.2068 | 22.4337 | 76.209 | 65.0723 | 24.9277 | 81.8471 | 71.2093 | 37.1094 | 115.6675 | 0.67 | 0.78333 | 33.9656 | 186.7426 | 1.9 | 7.7357 | 1.0604 | 0.16238
2016-06-04 17:00 | 178.13 | 136.0067 | 42.1233 | 114.6313 | 22.4385 | 91.2072 | 68.4404 | 21.5596 | 96.4855 | 84.6777 | 10.633 | 102.005 | 0.66984 | 0.78307 | 29.8298 | 142.4678 | 1.9 | 6.3521 | 1.0653 | 0.12445
2016-06-04 18:00 | 153.48 | 117.79 | 35.69 | 113.7475 | 22.4434 | 106.2054 | 71.7137 | 18.2863 | 110.8142 | 97.7765 | 0 | 88.3425 | 0.66969 | 0.78281 | 25.6959 | 114.0384 | 2.2 | 5.7637 | 1.0673 | 0.099807
2016-06-04 19:00 | 133.0233 | 94.48 | 38.5433 | 145.9815 | 22.4483 | 121.2036 | 74.6907 | 15.3093 | 124.955 | 110.2766 | 0 | 70.86 | 0.66953 | 0.78255 | 22.2658 | 93.1258 | 1.9 | 4.8102 | 1.0707 | 0.081759
2016-06-04 20:00 | 112.5667 | 71.17 | 41.3967 | 186.7636 | 22.4531 | 136.2018 | 77.1939 | 12.8061 | 139.0068 | 121.7746 | 0 | 53.3775 | 0.66938 | 0.78229 | 18.8373 | 72.2148 | 1.8 | 4.0567 | 1.0733 | 0.063557
2016-06-04 21:00 | 92.11 | 47.86 | 44.25 | 233.4741 | 22.4579 | 151.2 | 79.0747 | 10.9253 | 153.0357 | 131.5386 | 0 | 35.895 | 0.66922 | 0.78203 | 15.4104 | 51.3054 | 1.8 | 3.4033 | 1.0756 | 0.04525
2016-06-04 22:00 | 88.64 | 53.87 | 34.77 | 204.7109 | 22.4627 | 166.1983 | 80.2209 | 9.7791 | 167.0728 | 138.3214 | 0 | 40.4025 | 0.66906 | 0.78177 | 14.8264 | 55.2289 | 1.3 | 3.0259 | 1.0769 | 0.048771
2016-06-04 23:00 | 85.17 | 59.88 | 25.29 | 154.2449 | 22.4675 | 181.1965 | 80.5632 | 9.4368 | -178.8792 | 140.5484 | 0 | 44.91 | 0.66891 | 0.78151 | 14.2427 | 59.1527 | 1.1 | 2.9485 | 1.0772 | 0.052249
2016-06-05 | 81.7 | 65.89 | 15.81 | 91.7766 | 22.4723 | -163.8053 | 80.0804 | 9.9196 | -164.8329 | 137.496 | 0 | 49.4175 | 0.66875 | 0.78125 | 13.6592 | 63.0767 | 1 | 2.9711 | 1.0771 | 0.055711
2016-06-05 01:00 | 97.8033 | 80.48 | 17.3233 | 89.2008 | 22.4771 | -148.8071 | 78.8017 | 11.1983 | -150.7997 | 130.1263 | 0 | 60.36 | 0.66859 | 0.78099 | 16.3477 | 76.7077 | 1 | 3.3971 | 1.0756 | 0.067656
2016-06-05 02:00 | 113.9067 | 95.07 | 18.8367 | 82.5125 | 22.4819 | -133.8089 | 76.8037 | 13.1963 | -136.7728 | 120.0143 | 0 | 71.3025 | 0.66844 | 0.78073 | 19.0349 | 90.3374 | 1 | 3.823 | 1.0741 | 0.079567
2016-06-05 03:00 | 130.01 | 109.66 | 20.35 | 74.7621 | 22.4866 | -118.8107 | 74.205 | 15.795 | -122.7154 | 108.3177 | 0 | 82.245 | 0.66828 | 0.78047 | 21.7208 | 103.9658 | 1.1 | 4.3489 | 1.0723 | 0.091414
2016-06-05 04:00 | 152.1467 | 134.7567 | 17.39 | 53.8485 | 22.4914 | -103.8126 | 71.159 | 18.841 | -108.5556 | 95.7019 | 0 | 101.0675 | 0.66813 | 0.78021 | 25.4132 | 126.4807 | 1 | 4.9525 | 1.0702 | 0.11099
2016-06-05 05:00 | 174.2833 | 159.8533 | 14.43 | 38.2683 | 22.4961 | -88.8144 | 67.8474 | 22.1526 | -94.1895 | 82.5339 | 4.9726 | 119.89 | 0.66797 | 0.77995 | 29.104 | 153.9665 | 1 | 5.8115 | 1.0672 | 0.13473
2016-06-05 06:00 | 196.42 | 184.95 | 11.47 | 26.6181 | 22.5008 | -73.8162 | 64.4747 | 25.5253 | -79.4925 | 69.0244 | 9.5285 | 138.7125 | 0.66781 | 0.77969 | 32.7929 | 181.034 | 1 | 6.6573 | 1.0642 | 0.15798
2016-06-05 07:00 | 230.9233 | 222.2867 | 8.6367 | 17.9637 | 22.5055 | -58.818 | 61.2634 | 28.7366 | -64.3411 | 55.3051 | 10.2251 | 166.715 | 0.66766 | 0.77943 | 38.5444 | 215.4844 | 1.2 | 7.9339 | 1.0597 | 0.18725
2016-06-05 08:00 | 265.4267 | 259.6233 | 5.8033 | 11.0898 | 22.5102 | -43.8198 | 58.4458 | 31.5542 | -48.6444 | 41.4738 | 8.3091 | 194.7175 | 0.6675 | 0.77917 | 44.2931 | 247.3197 | 1.4 | 9.1287 | 1.0555 | 0.21407
2016-06-05 09:00 | 299.93 | 296.96 | 2.97 | 5.3458 | 22.5149 | -28.8216 | 56.2492 | 33.7508 | -32.3853 | 27.6421 | 4.7356 | 222.72 | 0.66734 | 0.77891 | 50.0391 | 277.4947 | 1.3 | 9.9717 | 1.0526 | 0.23951
2016-06-05 10:00 | 267.3967 | 261.6133 | 5.7833 | 10.0506 | 22.5196 | -13.8234 | 54.8709 | 35.1291 | -15.6563 | 14.1364 | 9.7463 | 196.21 | 0.66719 | 0.77865 | 44.6009 | 250.5572 | 1.2 | 9.0299 | 1.0559 | 0.21694
2016-06-05 11:00 | 234.8633 | 226.2667 | 8.5967 | 14.7842 | 22.5242 | 1.1747 | 54.4455 | 35.5545 | 1.3338 | 5.6664 | 14.712 | 169.7 | 0.66703 | 0.77839 | 39.1653 | 223.5772 | 1.5 | 8.4868 | 1.0578 | 0.19393
2016-06-05 12:00 | 202.33 | 190.92 | 11.41 | 19.9008 | 22.5289 | 16.1729 | 55.0163 | 34.9837 | 18.3016 | 16.1929 | 19.1113 | 143.19 | 0.66688 | 0.77812 | 33.7322 | 196.0335 | 1.6 | 7.726 | 1.0605 | 0.17047
2016-06-05 13:00 | 186.7233 | 178.71 | 8.0133 | 14.528 | 22.5335 | 31.1711 | 56.5246 | 33.4754 | 34.9704 | 29.8034 | 12.6064 | 134.0325 | 0.66672 | 0.77786 | 31.123 | 177.7619 | 1.6 | 7.1551 | 1.0625 | 0.15487
2016-06-05 14:00 | 171.1167 | 166.5 | 4.6167 | 8.9181 | 22.5382 | 46.1693 | 58.8236 | 31.1764 | 51.1475 | 43.6433 | 6.4536 | 124.875 | 0.66656 | 0.7776 | 28.515 | 159.8436 | 1.9 | 6.8951 | 1.0634 | 0.13938
2016-06-05 15:00 | 155.51 | 154.29 | 1.22 | 2.5741 | 22.5428 | 61.1674 | 61.7094 | 28.2906 | 66.7585 | 57.4597 | 1.3846 | 115.7175 | 0.66641 | 0.77734 | 25.9082 | 143.0103 | 1.9 | 6.3691 | 1.0652 | 0.12492
2016-06-05 16:00 | 140.6867 | 139.3567 | 1.33 | 3.1414 | 22.5474 | 76.1656 | 64.9523 | 25.0477 | 81.8345 | 71.1481 | 1.0151 | 104.5175 | 0.66625 | 0.77708 | 23.4331 | 128.9657 | 1.4 | 5.4302 | 1.0685 | 0.113
2016-06-05 17:00 | 125.8633 | 124.4233 | 1.44 | 3.8981 | 22.552 | 91.1638 | 68.3207 | 21.6793 | 96.4732 | 84.6076 | 0.36633 | 93.3175 | 0.66609 | 0.77682 | 20.9592 | 114.643 | 1.2 | 4.7826 | 1.0708 | 0.10066
2016-06-05 18:00 | 111.04 | 109.49 | 1.55 | 4.9091 | 22.5566 | 106.1619 | 71.5944 | 18.4056 | 110.8002 | 97.6968 | 0 | 82.1175 | 0.66594 | 0.77656 | 18.4864 | 100.6039 | 1.2 | 4.3439 | 1.0723 | 0.088459
2016-06-05 19:00 | 92.0967 | 90.9733 | 1.1233 | 4.2226 | 22.5612 | 121.1601 | 74.5721 | 15.4279 | 124.9375 | 110.1863 | 0 | 68.23 | 0.66578 | 0.7763 | 15.3291 | 83.5591 | 1.1 | 3.7112 | 1.0745 | 0.073624
2016-06-05 20:00 | 73.1533 | 72.4567 | 0.69667 | 3.1149 | 22.5657 | 136.1582 | 77.0763 | 12.9237 | 138.9846 | 121.6726 | 0 | 54.3425 | 0.66563 | 0.77604 | 12.1732 | 66.5157 | 1.1 | 3.1786 | 1.0764 | 0.058709
2016-06-05 21:00 | 54.21 | 53.94 | 0.27 | 1.4098 | 22.5703 | 151.1564 | 78.9586 | 11.0414 | 153.0075 | 131.4252 | 0 | 40.455 | 0.66547 | 0.77578 | 9.0188 | 49.4738 | 1 | 2.5461 | 1.0786 | 0.043757
2016-06-05 22:00 | 55.8567 | 55.0833 | 0.77333 | 4.501 | 22.5748 | 166.1545 | 80.1068 | 9.8932 | 167.0381 | 138.2023 | 0 | 41.3125 | 0.66531 | 0.77552 | 9.2905 | 50.603 | 1.1 | 2.6813 | 1.0781 | 0.044736
2016-06-05 23:00 | 57.5033 | 56.2267 | 1.2767 | 7.6963 | 22.5793 | 181.1527 | 80.4516 | 9.5484 | -178.9207 | 140.4379 | 0 | 42.17 | 0.66516 | 0.77526 | 9.5622 | 51.7322 | 0.7 | 2.3166 | 1.0794 | 0.045788
2016-06-06 | 59.15 | 57.37 | 1.78 | 10.2219 | 22.5838 | -163.8492 | 79.9717 | 10.0283 | -164.8812 | 137.4095 | 0 | 43.0275 | 0.665 | 0.775 | 9.8337 | 52.8612 | 0.6 | 2.2519 | 1.0796 | 0.046797
2016-06-06 01:00 | 75.9767 | 74.57 | 1.4067 | 7.1763 | 22.5884 | -148.851 | 78.696 | 11.304 | -150.8543 | 130.0677 | 0 | 55.9275 | 0.66484 | 0.77474 | 12.6282 | 68.5557 | 0.6 | 2.7424 | 1.0779 | 0.060595
2016-06-06 02:00 | 92.8033 | 91.77 | 1.0333 | 4.4921 | 22.5928 | -133.8529 | 76.701 | 13.299 | -136.833 | 119.9796 | 0 | 68.8275 | 0.66469 | 0.77448 | 15.4213 | 84.2488 | 0.6 | 3.2328 | 1.0762 | 0.074347
2016-06-06 03:00 | 109.63 | 108.97 | 0.66 | 2.4098 | 22.5973 | -118.8547 | 74.105 | 15.895 | -122.7804 | 108.3016 | 0 | 81.7275 | 0.66453 | 0.77422 | 18.2131 | 99.9406 | 0.7 | 3.8231 | 1.0741 | 0.088025
2016-06-06 04:00 | 134.0567 | 132.2467 | 1.81 | 5.5767 | 22.6018 | -103.8566 | 71.061 | 18.939 | -108.6245 | 95.7002 | 0 | 99.185 | 0.66438 | 0.77396 | 22.266 | 121.451 | 0.4 | 4.1953 | 1.0728 | 0.10684
2016-06-06 05:00 | 158.4833 | 155.5233 | 2.96 | 7.8174 | 22.6063 | -88.8585 | 67.7504 | 22.2496 | -94.2612 | 82.5441 | 1.0144 | 116.6425 | 0.66422 | 0.7737 | 26.3169 | 143.9738 | 0.8 | 5.2992 | 1.069 | 0.1262
2016-06-06 06:00 | 182.91 | 178.8 | 4.11 | 9.5043 | 22.6107 | -73.8603 | 64.3778 | 25.6222 | -79.5657 | 69.0448 | 3.3991 | 134.1 | 0.66406 | 0.77344 | 30.3659 | 167.865 | 0.9 | 6.1458 | 1.066 | 0.14673
2016-06-06 07:00 | 194.9 | 191.7067 | 3.1933 | 6.6213 | 22.6151 | -58.8622 | 61.1655 | 28.8345 | -64.414 | 55.3351 | 3.766 | 143.78 | 0.66391 | 0.77318 | 32.3488 | 179.8949 | 1.3 | 6.9217 | 1.0633 | 0.15685
2016-06-06 08:00 | 206.89 | 204.6133 | 2.2767 | 4.3382 | 22.6196 | -43.8641 | 58.3458 | 31.6542 | -48.7151 | 41.5139 | 3.2484 | 153.46 | 0.66375 | 0.77292 | 34.3308 | 191.0393 | 1.2 | 7.17 | 1.0624 | 0.16643
2016-06-06 09:00 | 218.88 | 217.52 | 1.36 | 2.4413 | 22.624 | -28.8659 | 56.1464 | 33.8536 | -32.4513 | 27.6951 | 2.1616 | 163.14 | 0.66359 | 0.77266 | 36.3118 | 201.6135 | 1 | 7.3004 | 1.0619 | 0.17556
2016-06-06 10:00 | 221.7133 | 219.1 | 2.6133 | 4.5297 | 22.6284 | -13.8678 | 54.765 | 35.235 | -15.7151 | 14.2134 | 4.3911 | 164.325 | 0.66344 | 0.7724 | 36.7732 | 205.4893 | 1.6 | 8.0215 | 1.0594 | 0.17851
2016-06-06 11:00 | 224.5467 | 220.68 | 3.8667 | 6.6321 | 22.6328 | 1.1303 | 54.3367 | 35.6633 | 1.2841 | 5.7649 | 6.5986 | 165.51 | 0.66328 | 0.77214 | 37.2344 | 209.343 | 1.4 | 7.942 | 1.0597 | 0.18191
2016-06-06 12:00 | 227.38 | 222.26 | 5.12 | 8.9054 | 22.6372 | 16.1284 | 54.9052 | 35.0948 | 18.2617 | 16.1861 | 8.5524 | 166.695 | 0.66313 | 0.77187 | 37.6953 | 212.9428 | 1.3 | 7.9545 | 1.0597 | 0.18503
2016-06-06 13:00 | 198.75 | 195.3367 | 3.4133 | 6.17 | 22.6415 | 31.1265 | 56.4119 | 33.5881 | 34.9397 | 29.7723 | 5.3556 | 146.5025 | 0.66297 | 0.77161 | 32.9413 | 184.7993 | 1.3 | 7.075 | 1.0627 | 0.16104
2016-06-06 14:00 | 170.12 | 168.4133 | 1.7067 | 3.286 | 22.6459 | 46.1247 | 58.71 | 31.29 | 51.1241 | 43.5999 | 2.3797 | 126.31 | 0.66281 | 0.77135 | 28.1894 | 156.8791 | 1.6 | 6.5025 | 1.0647 | 0.13697
2016-06-06 15:00 | 141.49 | 141.49 | 0 | 0 | 22.6502 | 61.1228 | 61.5954 | 28.4046 | 66.7403 | 57.407 | 0 | 106.1175 | 0.66266 | 0.77109 | 23.4398 | 129.5573 | 1.7 | 5.7487 | 1.0674 | 0.1134
2016-06-06 16:00 | 134.6233 | 134.5733 | 0.05 | 0.1176 | 22.6546 | 76.1209 | 64.8383 | 25.1617 | 81.8189 | 71.0871 | 0.038117 | 100.93 | 0.6625 | 0.77083 | 22.297 | 123.2651 | 1.7 | 5.552 | 1.0681 | 0.10796
2016-06-06 17:00 | 127.7567 | 127.6567 | 0.1 | 0.26936 | 22.6589 | 91.119 | 68.2069 | 21.7931 | 96.458 | 84.5382 | 0.025638 | 95.7425 | 0.66234 | 0.77057 | 21.1547 | 116.9228 | 1.7 | 5.3538 | 1.0688 | 0.10247
2016-06-06 18:00 | 120.89 | 120.74 | 0.15 | 0.47227 | 22.6632 | 106.1171 | 71.4811 | 18.5189 | 110.7834 | 97.6185 | 0 | 90.555 | 0.66219 | 0.77031 | 20.013 | 110.568 | 1.4 | 4.8552 | 1.0705 | 0.097058
2016-06-06 19:00 | 98.1833 | 98.0767 | 0.10667 | 0.39813 | 22.6675 | 121.1152 | 74.4596 | 15.5404 | 124.9175 | 110.0981 | 0 | 73.5575 | 0.66203 | 0.77005 | 16.2501 | 89.8076 | 1.5 | 4.3065 | 1.0724 | 0.078976
2016-06-06 20:00 | 75.4767 | 75.4133 | 0.063333 | 0.2808 | 22.6718 | 136.1133 | 76.9649 | 13.0351 | 138.96 | 121.5737 | 0 | 56.56 | 0.66187 | 0.76979 | 12.489 | 69.049 | 1.4 | 3.5578 | 1.075 | 0.060869
2016-06-06 21:00 | 52.77 | 52.75 | 0.02 | 0.10341 | 22.6761 | 151.1114 | 78.8489 | 11.1511 | 152.9775 | 131.3163 | 0 | 39.5625 | 0.66172 | 0.76953 | 8.7297 | 48.2922 | 1.3 | 2.8091 | 1.0777 | 0.042675
2016-06-06 22:00 | 52.12 | 52.1067 | 0.013333 | 0.076777 | 22.6803 | 166.1095 | 79.9992 | 10.0008 | 167.0018 | 138.0889 | 0 | 39.08 | 0.66156 | 0.76927 | 8.6202 | 47.7002 | 1.3 | 2.7906 | 1.0777 | 0.042155
2016-06-06 23:00 | 51.47 | 51.4633 | 0.0066667 | 0.039756 | 22.6846 | 181.1076 | 80.3465 | 9.6535 | -178.9634 | 140.334 | 0 | 38.5975 | 0.66141 | 0.76901 | 8.5106 | 47.1081 | 1.1 | 2.5721 | 1.0785 | 0.041661
2016-06-07 | 50.82 | 50.82 | 0 | 0 | 22.6888 | -163.8943 | 79.8696 | 10.1304 | -164.9302 | 137.3292 | 0 | 38.115 | 0.66125 | 0.76875 | 8.4012 | 46.5162 | 1.2 | 2.6536 | 1.0782 | 0.041127
2016-06-07 01:00 | 64.6167 | 64.6167 | 0 | 0 | 22.6931 | -148.8962 | 78.597 | 11.403 | -150.9092 | 130.0147 | 0 | 48.4625 | 0.66109 | 0.76849 | 10.6794 | 59.1419 | 1.1 | 2.9482 | 1.0772 | 0.052239
2016-06-07 02:00 | 78.4133 | 78.4133 | 0 | 0 | 22.6973 | -133.8981 | 76.605 | 13.395 | -136.8932 | 119.9496 | 0 | 58.81 | 0.66094 | 0.76823 | 12.9566 | 71.7666 | 1.2 | 3.4427 | 1.0755 | 0.063289
2016-06-07 03:00 | 92.21 | 92.21 | 0 | 0 | 22.7015 | -118.9 | 74.0116 | 15.9884 | -122.8452 | 108.2894 | 0 | 69.1575 | 0.66078 | 0.76797 | 15.2327 | 84.3902 | 1.3 | 3.9372 | 1.0737 | 0.074301
2016-06-07 04:00 | 121.2667 | 118.5167 | 2.75 | 8.4338 | 22.7057 | -103.9019 | 70.9696 | 19.0304 | -108.693 | 95.702 | 0 | 88.8875 | 0.66063 | 0.76771 | 20.0279 | 108.9154 | 1.4 | 4.8036 | 1.0707 | 0.095624
2016-06-07 05:00 | 150.3233 | 144.8233 | 5.5 | 14.4699 | 22.7099 | -88.9039 | 67.6602 | 22.3398 | -94.3324 | 82.5571 | 1.8744 | 108.6175 | 0.66047 | 0.76745 | 24.821 | 135.3129 | 1.8 | 6.0285 | 1.0664 | 0.11832
2016-06-07 06:00 | 179.38 | 171.13 | 8.25 | 19.0156 | 22.714 | -73.9058 | 64.2876 | 25.7124 | -79.6384 | 69.0676 | 6.7937 | 128.3475 | 0.66031 | 0.76719 | 29.6117 | 164.7529 | 1.9 | 7.0485 | 1.0628 | 0.14359
2016-06-07 07:00 | 241.2433 | 214.38 | 26.8633 | 55.5399 | 22.7182 | -58.9077 | 61.0742 | 28.9258 | -64.4868 | 55.367 | 31.5643 | 160.785 | 0.66016 | 0.76693 | 39.8146 | 232.1639 | 2.4 | 9.6551 | 1.0537 | 0.2006
2016-06-07 08:00 | 303.1067 | 257.63 | 45.4767 | 86.4286 | 22.7223 | -43.9096 | 58.2525 | 31.7475 | -48.7858 | 41.5554 | 64.6758 | 193.2225 | 0.66 | 0.76667 | 50.0126 | 307.9109 | 2.9 | 12.5222 | 1.0437 | 0.26351
2016-06-07 09:00 | 364.97 | 300.88 | 64.09 | 114.7612 | 22.7265 | -28.9115 | 56.0504 | 33.9496 | -32.5178 | 27.7487 | 101.5635 | 225.66 | 0.65984 | 0.76641 | 60.2058 | 387.4293 | 3.2 | 15.3072 | 1.0339 | 0.32847
2016-06-07 10:00 | 369.5567 | 301.5167 | 68.04 | 117.6462 | 22.7306 | -13.9135 | 54.6658 | 35.3342 | -15.7749 | 14.2896 | 114.0063 | 226.1375 | 0.65969 | 0.76615 | 60.948 | 401.0918 | 3.3 | 15.8341 | 1.0321 | 0.33945
2016-06-07 11:00 | 374.1433 | 302.1533 | 71.99 | 123.1718 | 22.7347 | 1.0846 | 54.2346 | 35.7654 | 1.2328 | 5.8575 | 122.5287 | 226.615 | 0.65953 | 0.76589 | 61.6898 | 410.8335 | 4 | 16.8385 | 1.0286 | 0.34651
2016-06-07 12:00 | 378.73 | 302.79 | 75.94 | 131.7434 | 22.7388 | 16.0827 | 54.8006 | 35.1994 | 18.2198 | 16.177 | 126.5271 | 227.0925 | 0.65938 | 0.76562 | 62.4313 | 416.0509 | 3.4 | 16.4016 | 1.0301 | 0.35143
2016-06-07 13:00 | 339.28 | 272.3267 | 66.9533 | 120.688 | 22.7429 | 31.0807 | 56.3056 | 33.6944 | 34.9064 | 29.7397 | 104.7919 | 204.245 | 0.65922 | 0.76536 | 55.9149 | 364.9519 | 3.4 | 14.8047 | 1.0357 | 0.30994
2016-06-07 14:00 | 299.83 | 241.8633 | 57.9667 | 111.267 | 22.747 | 46.0788 | 58.6027 | 31.3973 | 51.098 | 43.5556 | 80.6358 | 181.3975 | 0.65906 | 0.7651 | 49.4017 | 311.435 | 3.4 | 13.1323 | 1.0415 | 0.26598
2016-06-07 15:00 | 260.38 | 211.4 | 48.98 | 102.6086 | 22.7511 | 61.0769 | 61.4877 | 28.5123 | 66.7191 | 57.354 | 55.3518 | 158.55 | 0.65891 | 0.76484 | 42.8915 | 256.7933 | 3.4 | 11.4248 | 1.0475 | 0.22058
2016-06-07 16:00 | 225.78 | 184.8 | 40.98 | 95.9996 | 22.7551 | 76.0749 | 64.7305 | 25.2695 | 81.8003 | 71.0263 | 31.2128 | 138.6 | 0.65875 | 0.76458 | 37.1831 | 206.996 | 3.5 | 9.9686 | 1.0526 | 0.17867
2016-06-07 17:00 | 191.18 | 158.2 | 32.98 | 88.4186 | 22.7592 | 91.073 | 68.0993 | 21.9007 | 96.4399 | 84.4695 | 8.5213 | 118.65 | 0.65859 | 0.76432 | 31.4775 | 158.6488 | 3.8 | 8.7578 | 1.0568 | 0.13749
2016-06-07 18:00 | 156.58 | 131.6 | 24.98 | 78.2119 | 22.7632 | 106.071 | 71.374 | 18.626 | 110.7639 | 97.5416 | 0 | 98.7 | 0.65844 | 0.76406 | 25.7745 | 124.4745 | 4 | 7.8898 | 1.0599 | 0.10818
2016-06-07 19:00 | 132.0433 | 108.9 | 23.1433 | 85.8101 | 22.7672 | 121.0691 | 74.3533 | 15.6467 | 124.895 | 110.0122 | 0 | 81.675 | 0.65828 | 0.7638 | 21.7304 | 103.4054 | 3.9 | 7.1314 | 1.0625 | 0.090095
2016-06-07 20:00 | 107.5067 | 86.2 | 21.3067 | 93.7244 | 22.7713 | 136.0672 | 76.8599 | 13.1401 | 138.9333 | 121.4781 | 0 | 64.65 | 0.65813 | 0.76354 | 17.6882 | 82.3382 | 4.2 | 6.7731 | 1.0638 | 0.071825
2016-06-07 21:00 | 82.97 | 63.5 | 19.47 | 99.7608 | 22.7753 | 151.0652 | 78.7455 | 11.2545 | 152.9455 | 131.2119 | 0 | 47.625 | 0.65797 | 0.76328 | 13.6479 | 61.2729 | 4 | 5.9148 | 1.0668 | 0.0536
2016-06-07 22:00 | 81.3967 | 67.9867 | 13.41 | 76.4538 | 22.7792 | 166.0633 | 79.8981 | 10.1019 | 166.9641 | 137.9814 | 0 | 50.99 | 0.65781 | 0.76302 | 13.3859 | 64.3759 | 3.8 | 5.8117 | 1.0672 | 0.056333
2016-06-07 23:00 | 79.8233 | 72.4733 | 7.35 | 43.3927 | 22.7832 | 181.0613 | 80.248 | 9.752 | -179.0072 | 140.2366 | 0 | 54.355 | 0.65766 | 0.76276 | 13.1241 | 67.4791 | 3.6 | 5.7087 | 1.0675 | 0.059069
2016-06-08 | 78.25 | 76.96 | 1.29 | 7.2664 | 22.7872 | -163.9407 | 79.7741 | 10.2259 | -164.9799 | 137.2554 | 0 | 57.72 | 0.6575 | 0.7625 | 12.8623 | 70.5823 | 3.4 | 5.6057 | 1.0679 | 0.061806
2016-06-08 01:00 | 104.2367 | 101.18 | 3.0567 | 15.338 | 22.7911 | -148.9426 | 78.5047 | 11.4953 | -150.9644 | 129.9673 | 0 | 75.885 | 0.65734 | 0.76224 | 17.1298 | 93.0148 | 3.3 | 6.2067 | 1.0658 | 0.081289
2016-06-08 02:00 | 130.2233 | 125.4 | 4.8233 | 20.6852 | 22.7951 | -133.9446 | 76.5157 | 13.4843 | -136.9534 | 119.9243 | 0 | 94.05 | 0.65719 | 0.76198 | 21.3953 | 115.4453 | 3.7 | 7.3077 | 1.0619 | 0.10053
2016-06-08 03:00 | 156.21 | 149.62 | 6.59 | 23.7995 | 22.799 | -118.9465 | 73.925 | 16.075 | -122.9097 | 108.2812 | 0 | 112.215 | 0.65703 | 0.76172 | 25.6587 | 137.8737 | 3.9 | 8.2086 | 1.0588 | 0.1197
2016-06-08 04:00 | 198.1433 | 178.7133 | 19.43 | 59.3343 | 22.8029 | -103.9485 | 70.8849 | 19.1151 | -108.761 | 95.707 | 0 | 134.035 | 0.65688 | 0.76146 | 32.5389 | 166.5739 | 5.1 | 10.3054 | 1.0514 | 0.14362
2016-06-08 05:00 | 240.0767 | 207.8067 | 32.27 | 84.5987 | 22.8069 | -88.9505 | 67.5766 | 22.4234 | -94.403 | 82.5729 | 10.9357 | 155.855 | 0.65672 | 0.7612 | 39.4157 | 206.2064 | 4 | 10.4439 | 1.0509 | 0.1777
2016-06-08 06:00 | 282.01 | 236.9 | 45.11 | 103.6614 | 22.8107 | -73.9524 | 64.2041 | 25.7959 | -79.7106 | 69.0926 | 36.9924 | 177.675 | 0.65656 | 0.76094 | 46.2893 | 260.9567 | 3.9 | 12.0549 | 1.0453 | 0.22368
2016-06-08 07:00 | 338.5967 | 235.45 | 103.1467 | 212.6879 | 22.8146 | -58.9544 | 60.9897 | 29.0103 | -64.5591 | 55.4007 | 120.7713 | 176.5875 | 0.65641 | 0.76068 | 55.5642 | 352.923 | 3.9 | 14.9288 | 1.0352 | 0.2996
2016-06-08 08:00 | 395.1833 | 234 | 161.1833 | 305.5835 | 22.8185 | -43.9564 | 58.1659 | 31.8341 | -48.8565 | 41.5981 | 228.5214 | 175.5 | 0.65625 | 0.76042 | 64.8348 | 468.8561 | 4.4 | 19.0518 | 1.0208 | 0.39247
2016-06-08 09:00 | 451.77 | 232.55 | 219.22 | 391.634 | 22.8224 | -28.9583 | 55.961 | 34.039 | -32.5846 | 27.8028 | 346.423 | 174.4125 | 0.65609 | 0.76016 | 74.1009 | 594.9364 | 4.2 | 22.7918 | 1.0077 | 0.49162
2016-06-08 10:00 | 434.2267 | 243.9033 | 190.3233 | 328.3356 | 22.8262 | -13.9603 | 54.5733 | 35.4267 | -15.8356 | 14.3647 | 318.0706 | 182.9275 | 0.65594 | 0.7599 | 71.2064 | 572.2045 | 5 | 22.8814 | 1.0074 | 0.47269
2016-06-08 11:00 | 416.6833 | 255.2567 | 161.4267 | 275.5565 | 22.8301 | 1.0377 | 54.139 | 35.861 | 1.1801 | 5.9439 | 274.075 | 191.4425 | 0.65578 | 0.75964 | 68.3133 | 533.8308 | 4.5 | 21.1822 | 1.0134 | 0.44359
2016-06-08 12:00 | 399.14 | 266.61 | 132.53 | 229.3615 | 22.8339 | 16.0357 | 54.7025 | 35.2975 | 18.1758 | 16.1656 | 220.2928 | 199.9575 | 0.65563 | 0.75938 | 65.4215 | 485.6718 | 3.2 | 18.3772 | 1.0232 | 0.40748
2016-06-08 13:00 | 343.6233 | 247.3967 | 96.2267 | 173.0031 | 22.8377 | 31.0338 | 56.2057 | 33.7943 | 34.8708 | 29.7059 | 150.2672 | 185.5475 | 0.65547 | 0.75911 | 56.3086 | 392.1233 | 2.7 | 14.9539 | 1.0352 | 0.33285
2016-06-08 14:00 | 288.1067 | 228.1833 | 59.9233 | 114.6916 | 22.8415 | 46.0318 | 58.5017 | 31.4983 | 51.0692 | 43.5106 | 83.1797 | 171.1375 | 0.65531 | 0.75885 | 47.2 | 301.5172 | 2.8 | 12.2224 | 1.0447 | 0.2583
2016-06-08 15:00 | 232.59 | 208.97 | 23.62 | 49.3208 | 22.8453 | 61.0298 | 61.3861 | 28.6139 | 66.6951 | 57.3008 | 26.6445 | 156.7275 | 0.65516 | 0.75859 | 38.0957 | 221.4677 | 2.7 | 9.6209 | 1.0538 | 0.19138
2016-06-08 16:00 | 209.4533 | 189.8567 | 19.5967 | 45.7352 | 22.8491 | 76.0278 | 64.6288 | 25.3712 | 81.7788 | 70.9657 | 14.9158 | 142.3925 | 0.655 | 0.75833 | 34.298 | 191.6063 | 2.6 | 8.5877 | 1.0574 | 0.16614
2016-06-08 17:00 | 186.3167 | 170.7433 | 15.5733 | 41.5687 | 22.8529 | 91.0258 | 67.9979 | 22.0021 | 96.419 | 84.4018 | 4.0551 | 128.0575 | 0.65484 | 0.75807 | 30.5021 | 162.6147 | 2.2 | 7.2817 | 1.062 | 0.14161
2016-06-08 18:00 | 163.18 | 151.63 | 11.55 | 35.9749 | 22.8566 | 106.0238 | 71.2732 | 18.7268 | 110.7417 | 97.4663 | 0 | 113.7225 | 0.65469 | 0.75781 | 26.708 | 140.4305 | 2.5 | 6.8885 | 1.0634 | 0.12245
2016-06-08 19:00 | 139.22 | 126.7367 | 12.4833 | 45.9988 | 22.8604 | 121.0218 | 74.2534 | 15.7466 | 124.8701 | 109.9286 | 0 | 95.0525 | 0.65453 | 0.75755 | 22.781 | 117.8335 | 2.5 | 6.1823 | 1.0659 | 0.10299
2016-06-08 20:00 | 115.26 | 101.8433 | 13.4167 | 58.5856 | 22.8641 | 136.0198 | 76.7612 | 13.2388 | 138.9044 | 121.3859 | 0 | 76.3825 | 0.65438 | 0.75729 | 18.8558 | 95.2383 | 2.1 | 5.0762 | 1.0697 | 0.083541
2016-06-08 21:00 | 91.3 | 76.95 | 14.35 | 72.9076 | 22.8678 | 151.0178 | 78.6487 | 11.3513 | 152.9118 | 131.112 | 0 | 57.7125 | 0.65422 | 0.75703 | 14.9325 | 72.645 | 2.2 | 4.4702 | 1.0719 | 0.063849
2016-06-08 22:00 | 82.7767 | 72.8733 | 9.9033 | 55.9432 | 22.8715 | 166.0158 | 79.8035 | 10.1965 | 166.9249 | 137.8797 | 0 | 54.655 | 0.65406 | 0.75677 | 13.5353 | 68.1903 | 2.1 | 4.2309 | 1.0727 | 0.059981
2016-06-08 23:00 | 74.2533 | 68.7967 | 5.4567 | 31.9173 | 22.8752 | 181.0138 | 80.1562 | 9.8438 | -179.0519 | 140.1458 | 0 | 51.5975 | 0.65391 | 0.75651 | 12.1387 | 63.7362 | 1.9 | 3.8918 | 1.0739 | 0.056125
2016-06-09 | 65.73 | 64.72 | 1.01 | 5.6407 | 22.8789 | -163.9882 | 79.6853 | 10.3147 | -165.0302 | 137.1879 | 0 | 48.54 | 0.65375 | 0.75625 | 10.7427 | 59.2827 | 2 | 3.8526 | 1.074 | 0.05221
2016-06-09 01:00 | 85.1167 | 78.6367 | 6.48 | 32.2787 | 22.8826 | -148.9902 | 78.4191 | 11.5809 | -151.0199 | 129.9254 | 0 | 58.9775 | 0.65359 | 0.75599 | 13.9079 | 72.8854 | 2.3 | 4.5777 | 1.0715 | 0.064038
2016-06-09 02:00 | 104.5033 | 92.5533 | 11.95 | 50.9422 | 22.8863 | -133.9922 | 76.4332 | 13.5668 | -137.0136 | 119.9037 | 0 | 69.415 | 0.65344 | 0.75573 | 17.0716 | 86.4866 | 2.6 | 5.3027 | 1.0689 | 0.075808
2016-06-09 03:00 | 123.89 | 106.47 | 17.42 | 62.6086 | 22.8899 | -118.9942 | 73.845 | 16.155 | -122.9739 | 108.2769 | 0 | 79.8525 | 0.65328 | 0.75547 | 20.2338 | 100.0863 | 2.6 | 5.7277 | 1.0675 | 0.087607
2016-06-09 04:00 | 174.0167 | 141.7533 | 32.2633 | 98.1387 | 22.8936 | -103.9962 | 70.8069 | 19.1931 | -108.8285 | 95.7153 | 0 | 106.315 | 0.65313 | 0.75521 | 28.4137 | 134.7287 | 2.9 | 7.1103 | 1.0626 | 0.11739
2016-06-09 05:00 | 224.1433 | 177.0367 | 47.1067 | 123.0941 | 22.8972 | -88.9982 | 67.4997 | 22.5003 | -94.473 | 82.5914 | 15.8723 | 132.7775 | 0.65297 | 0.75495 | 36.5896 | 185.2395 | 3.1 | 8.8887 | 1.0564 | 0.16046
2016-06-09 06:00 | 274.27 | 212.32 | 61.95 | 141.9656 | 22.9008 | -74.0002 | 64.1273 | 25.8727 | -79.7822 | 69.1199 | 50.5984 | 159.24 | 0.65281 | 0.75469 | 44.7617 | 254.6001 | 3.8 | 11.7563 | 1.0464 | 0.21845
2016-06-09 07:00 | 362.88 | 183.6967 | 179.1833 | 368.5727 | 22.9044 | -59.0022 | 60.9119 | 29.0881 | -64.631 | 55.4362 | 209.1002 | 137.7725 | 0.65266 | 0.75443 | 59.209 | 406.0817 | 4.2 | 16.8901 | 1.0284 | 0.34244
2016-06-09 08:00 | 451.49 | 155.0733 | 296.4167 | 560.711 | 22.908 | -44.0042 | 58.0861 | 31.9139 | -48.927 | 41.642 | 419.0253 | 116.305 | 0.6525 | 0.75417 | 73.6493 | 608.9796 | 4.6 | 23.6306 | 1.0048 | 0.50176
2016-06-09 09:00 | 540.1 | 126.45 | 413.65 | 737.4073 | 22.9116 | -29.0063 | 55.8784 | 34.1216 | -32.6517 | 27.8574 | 651.9517 | 94.8375 | 0.65234 | 0.75391 | 88.0827 | 834.8719 | 5.5 | 31.5897 | 0.97694 | 0.66881
2016-06-09 10:00 | 525.19 | 137.9067 | 387.2833 | 666.7176 | 22.9152 | -14.0083 | 54.4875 | 35.5125 | -15.897 | 14.4386 | 645.6596 | 103.43 | 0.65219 | 0.75365 | 85.6306 | 834.7202 | 5.8 | 31.885 | 0.9759 | 0.66798
2016-06-09 11:00 | 510.28 | 149.3633 | 360.9167 | 614.7685 | 22.9187 | 0.98971 | 54.0501 | 35.9499 | 1.1261 | 6.0243 | 611.3734 | 112.0225 | 0.65203 | 0.75339 | 83.1796 | 806.5756 | 5.9 | 31.1055 | 0.97863 | 0.64726
2016-06-09 12:00 | 495.37 | 160.82 | 334.55 | 577.6823 | 22.9223 | 15.9877 | 54.611 | 35.389 | 18.13 | 16.1517 | 554.8803 | 120.615 | 0.65188 | 0.75313 | 80.7298 | 756.2251 | 5.2 | 28.832 | 0.98659 | 0.61179
2016-06-09 13:00 | 450.29 | 168.17 | 282.12 | 505.9828 | 22.9258 | 30.9857 | 56.1122 | 33.8878 | 34.8328 | 29.6707 | 439.6409 | 126.1275 | 0.65172 | 0.75286 | 73.3656 | 639.134 | 5.2 | 25.1729 | 0.99939 | 0.52377
2016-06-09 14:00 | 405.21 | 175.52 | 229.69 | 438.4385 | 22.9294 | 45.9836 | 58.407 | 31.593 | 51.0378 | 43.4649 | 318.2166 | 131.64 | 0.65156 | 0.7526 | 66.0049 | 515.8615 | 5.4 | 21.5207 | 1.0122 | 0.42816
2016-06-09 15:00 | 360.13 | 182.87 | 177.26 | 369.0113 | 22.9329 | 60.9816 | 61.2908 | 28.7092 | 66.6682 | 57.2475 | 199.6393 | 137.1525 | 0.65141 | 0.75234 | 58.6477 | 395.4396 | 5.7 | 18.0575 | 1.0243 | 0.33214
2016-06-09 16:00 | 308.7433 | 179.2867 | 129.4567 | 301.0721 | 22.9364 | 75.9796 | 64.5334 | 25.4666 | 81.7545 | 70.9056 | 98.4884 | 134.465 | 0.65125 | 0.75208 | 50.2673 | 283.2206 | 6 | 14.8506 | 1.0355 | 0.24049
2016-06-09 17:00 | 257.3567 | 175.7033 | 81.6533 | 217.0586 | 22.9399 | 90.9775 | 67.9027 | 22.0973 | 96.3953 | 84.335 | 21.4263 | 131.7775 | 0.65109 | 0.75182 | 41.8908 | 195.0946 | 5.6 | 11.6967 | 1.0466 | 0.16743
2016-06-09 18:00 | 205.97 | 172.12 | 33.85 | 104.9221 | 22.9434 | 105.9755 | 71.1785 | 18.8215 | 110.7169 | 97.3925 | 0 | 129.09 | 0.65094 | 0.75156 | 33.5184 | 162.6084 | 5.4 | 10.4815 | 1.0508 | 0.14011
2016-06-09 19:00 | 182.8067 | 135.25 | 47.5567 | 174.2281 | 22.9468 | 120.9735 | 74.1597 | 15.8403 | 124.8428 | 109.8474 | 0 | 101.4375 | 0.65078 | 0.7513 | 29.7418 | 131.1793 | 5.1 | 9.1994 | 1.0553 | 0.11352
2016-06-09 20:00 | 159.6433 | 98.38 | 61.2633 | 265.6968 | 22.9503 | 135.9714 | 76.669 | 13.331 | 138.8734 | 121.297 | 0 | 73.785 | 0.65063 | 0.75104 | 25.967 | 99.752 | 4.5 | 7.6172 | 1.0608 | 0.086773
2016-06-09 21:00 | 136.48 | 61.51 | 74.97 | 377.93 | 22.9537 | 150.9694 | 78.5583 | 11.4417 | 152.8763 | 131.0169 | 0 | 46.1325 | 0.65047 | 0.75078 | 22.194 | 68.3265 | 3.9 | 6.0352 | 1.0664 | 0.059747
2016-06-09 22:00 | 134.7533 | 55.5933 | 79.16 | 443.385 | 22.9572 | 165.9674 | 79.7155 | 10.2845 | 166.8844 | 137.7839 | 0 | 41.695 | 0.65031 | 0.75052 | 21.9079 | 63.6029 | 2.7 | 4.6876 | 1.0711 | 0.055862
2016-06-09 23:00 | 133.0267 | 49.6767 | 83.35 | 483.393 | 22.9606 | 180.9653 | 80.071 | 9.929 | -179.0977 | 140.0616 | 0 | 37.2575 | 0.65016 | 0.75026 | 21.622 | 58.8795 | 2.7 | 4.54 | 1.0716 | 0.051739
2016-06-10 | 131.3 | 43.76 | 87.54 | 485.0847 | 22.964 | -164.0367 | 79.6033 | 10.3967 | -165.081 | 137.1268 | 0 | 32.82 | 0.65 | 0.75 | 21.3362 | 54.1562 | 2.3 | 3.9924 | 1.0735 | 0.047673
2016-06-10 01:00 | 143.8967 | 72.75 | 71.1467 | 352.0368 | 22.9674 | -149.0388 | 78.3402 | 11.6598 | -151.0756 | 129.8892 | 0 | 54.5625 | 0.64875 | 0.74792 | 23.3382 | 77.9007 | 2.7 | 5.1344 | 1.0695 | 0.06832
2016-06-10 02:00 | 156.4933 | 101.74 | 54.7533 | 232.1373 | 22.9708 | -134.0408 | 76.3573 | 13.6427 | -137.0736 | 119.8879 | 0 | 76.305 | 0.6475 | 0.74583 | 25.3324 | 101.6374 | 3 | 6.1762 | 1.0659 | 0.088834
2016-06-10 03:00 | 169.09 | 130.73 | 38.36 | 137.2628 | 22.9742 | -119.0429 | 73.7718 | 16.2282 | -123.0376 | 108.2765 | 0 | 98.0475 | 0.64625 | 0.74375 | 27.3186 | 125.3661 | 3.5 | 7.4177 | 1.0615 | 0.10913
2016-06-10 04:00 | 228.0733 | 140.3833 | 87.69 | 265.7864 | 22.9775 | -104.0449 | 70.7357 | 19.2643 | -108.8953 | 95.7269 | 0 | 105.2875 | 0.645 | 0.74167 | 36.7768 | 142.0643 | 3.6 | 8.0395 | 1.0594 | 0.12341
2016-06-10 05:00 | 287.0567 | 150.0367 | 137.02 | 356.9909 | 22.9809 | -89.047 | 67.4295 | 22.5705 | -94.5423 | 82.6126 | 45.9011 | 112.5275 | 0.64375 | 0.73958 | 46.1982 | 204.6268 | 3.3 | 9.6946 | 1.0536 | 0.17678
2016-06-10 06:00 | 346.04 | 159.69 | 186.35 | 425.9683 | 22.9842 | -74.049 | 64.0572 | 25.9428 | -79.853 | 69.1493 | 151.6163 | 119.7675 | 0.6425 | 0.7375 | 55.5827 | 326.9665 | 3.1 | 13.3177 | 1.0409 | 0.27908
2016-06-10 07:00 | 380.6833 | 152.55 | 228.1333 | 468.2169 | 22.9875 | -59.0511 | 60.8408 | 29.1592 | -64.7023 | 55.4732 | 265.3814 | 114.4125 | 0.64125 | 0.73542 | 61.0283 | 440.8222 | 3 | 16.7757 | 1.0288 | 0.37188
2016-06-10 08:00 | 415.3267 | 145.41 | 269.9167 | 509.5395 | 22.9909 | -44.0531 | 58.013 | 31.987 | -48.9972 | 41.687 | 380.5185 | 109.0575 | 0.64 | 0.73333 | 66.4523 | 556.0283 | 2.9 | 20.2759 | 1.0165 | 0.46348
2016-06-10 09:00 | 449.97 | 138.27 | 311.7 | 554.5795 | 22.9942 | -29.0552 | 55.8025 | 34.1975 | -32.7189 | 27.9123 | 490.0627 | 103.7025 | 0.63875 | 0.73125 | 71.8546 | 665.6198 | 3.1 | 23.9006 | 1.0038 | 0.54791
2016-06-10 10:00 | 443.06 | 128.89 | 314.17 | 539.808 | 22.9975 | -14.0573 | 54.4084 | 35.5916 | -15.9591 | 14.5111 | 522.5876 | 96.6675 | 0.6375 | 0.72917 | 70.6127 | 689.8678 | 2.9 | 24.4584 | 1.0019 | 0.56676
2016-06-10 11:00 | 436.15 | 119.51 | 316.64 | 538.2853 | 23.0007 | 0.94067 | 53.9679 | 36.0321 | 1.0707 | 6.0984 | 535.2391 | 89.6325 | 0.63625 | 0.72708 | 69.3751 | 694.2467 | 3.1 | 24.7952 | 1.0007 | 0.56969
2016-06-10 12:00 | 429.24 | 110.13 | 319.11 | 549.8748 | 23.004 | 15.9386 | 54.5261 | 35.4739 | 18.0823 | 16.1355 | 528.2137 | 82.5975 | 0.635 | 0.725 | 68.1418 | 678.9531 | 2.1 | 23.3173 | 1.0059 | 0.56002
2016-06-10 13:00 | 379.6667 | 117.0633 | 262.6033 | 469.9183 | 23.0073 | 30.9365 | 56.0252 | 33.9748 | 34.7926 | 29.6341 | 408.4532 | 87.7975 | 0.63375 | 0.72292 | 60.1534 | 556.4042 | 2.1 | 19.4876 | 1.0193 | 0.46505
2016-06-10 14:00 | 330.0933 | 123.9967 | 206.0967 | 392.4202 | 23.0105 | 45.9345 | 58.3187 | 31.6813 | 51.0037 | 43.4186 | 285.035 | 92.9975 | 0.6325 | 0.72083 | 52.196 | 430.2285 | 2 | 15.4446 | 1.0334 | 0.36459
2016-06-10 15:00 | 280.52 | 130.93 | 149.59 | 310.529 | 23.0138 | 60.9324 | 61.2018 | 28.7982 | 66.6386 | 57.194 | 168.2433 | 98.1975 | 0.63125 | 0.71875 | 44.2696 | 310.7104 | 2.1 | 11.8097 | 1.0462 | 0.26654
2016-06-10 16:00 | 242.87 | 131.8467 | 111.0233 | 257.3616 | 23.017 | 75.9303 | 64.4442 | 25.5558 | 81.7274 | 70.8459 | 84.443 | 98.885 | 0.63 | 0.71667 | 38.252 | 221.58 | 1.4 | 8.3244 | 1.0584 | 0.1923
2016-06-10 17:00 | 205.22 | 132.7633 | 72.4567 | 191.8777 | 23.0202 | 90.9283 | 67.8137 | 22.1863 | 96.3689 | 84.2692 | 19.1599 | 99.5725 | 0.62875 | 0.71458 | 32.258 | 150.9904 | 1.3 | 6.0184 | 1.0664 | 0.13204
2016-06-10 18:00 | 167.57 | 133.68 | 33.89 | 104.5733 | 23.0234 | 105.9262 | 71.0902 | 18.9098 | 110.6896 | 97.3205 | 0 | 100.26 | 0.6275 | 0.7125 | 26.2875 | 126.5475 | 1.4 | 5.3546 | 1.0688 | 0.1109
2016-06-10 19:00 | 149.7233 | 113.59 | 36.1333 | 131.671 | 23.0266 | 120.9241 | 74.0725 | 15.9275 | 124.8132 | 109.7688 | 0 | 85.1925 | 0.62625 | 0.71042 | 23.4411 | 108.6336 | 1.7 | 5.0948 | 1.0697 | 0.095286
2016-06-10 20:00 | 131.8767 | 93.5 | 38.3767 | 165.3935 | 23.0298 | 135.922 | 76.5832 | 13.4168 | 138.8405 | 121.2117 | 0 | 70.125 | 0.625 | 0.70833 | 20.6057 | 90.7307 | 1.9 | 4.7353 | 1.0709 | 0.079676
2016-06-10 21:00 | 114.03 | 73.41 | 40.62 | 203.3 | 23.0329 | 150.92 | 78.4745 | 11.5255 | 152.8392 | 130.9264 | 0 | 55.0575 | 0.62375 | 0.70625 | 17.7816 | 72.8391 | 2.1 | 4.3762 | 1.0722 | 0.064039
2016-06-10 22:00 | 106.32 | 72.86 | 33.46 | 185.959 | 23.0361 | 165.9179 | 79.6342 | 10.3658 | 166.8427 | 137.6941 | 0 | 54.645 | 0.6225 | 0.70417 | 16.5461 | 71.191 | 2 | 4.2247 | 1.0727 | 0.062621
2016-06-10 23:00 | 98.61 | 72.31 | 26.3 | 151.3444 | 23.0392 | 180.9158 | 79.9926 | 10.0074 | -179.1442 | 139.9841 | 0 | 54.2325 | 0.62125 | 0.70208 | 15.3154 | 69.5479 | 2.2 | 4.3734 | 1.0722 | 0.061146
2016-06-11 | 90.9 | 71.76 | 19.14 | 105.3058 | 23.0423 | -164.0863 | 79.5279 | 10.4721 | -165.1323 | 137.0721 | 0 | 53.82 | 0.62 | 0.7 | 14.0895 | 67.9095 | 1.9 | 4.0222 | 1.0734 | 0.059774
2016-06-11 01:00 | 111.3967 | 96.5267 | 14.87 | 73.1313 | 23.0455 | -149.0884 | 78.2681 | 11.7319 | -151.1313 | 129.8585 | 0 | 72.395 | 0.61875 | 0.69792 | 17.2317 | 89.6267 | 2.6 | 5.4008 | 1.0686 | 0.078535
2016-06-11 02:00 | 131.8933 | 121.2933 | 10.6 | 44.7186 | 23.0486 | -134.0905 | 76.2882 | 13.7118 | -137.1333 | 119.8766 | 0 | 90.97 | 0.6175 | 0.69583 | 20.361 | 111.331 | 3.1 | 6.5791 | 1.0645 | 0.097177
2016-06-11 03:00 | 152.39 | 146.06 | 6.33 | 22.5606 | 23.0517 | -119.0926 | 73.7053 | 16.2947 | -123.1008 | 108.28 | 0 | 109.545 | 0.61625 | 0.69375 | 23.4776 | 133.0226 | 2.9 | 7.057 | 1.0628 | 0.11593
2016-06-11 04:00 | 187.1067 | 167.06 | 20.0467 | 60.5658 | 23.0548 | -104.0946 | 70.6711 | 19.3289 | -108.9615 | 95.7417 | 0 | 125.295 | 0.615 | 0.69167 | 28.7676 | 154.0626 | 3.2 | 8.0145 | 1.0594 | 0.13384
2016-06-11 05:00 | 221.8233 | 188.06 | 33.7633 | 87.7331 | 23.0578 | -89.0967 | 67.3661 | 22.6339 | -94.6108 | 82.6364 | 11.2444 | 141.045 | 0.61375 | 0.68958 | 34.036 | 186.3254 | 3.5 | 9.3227 | 1.0549 | 0.16117
2016-06-11 06:00 | 256.54 | 209.06 | 47.48 | 108.2861 | 23.0609 | -74.0988 | 63.9938 | 26.0062 | -79.9231 | 69.1808 | 38.487 | 156.795 | 0.6125 | 0.6875 | 39.2827 | 234.5647 | 2.9 | 10.2301 | 1.0517 | 0.20229
2016-06-11 07:00 | 324.0133 | 218.61 | 105.4033 | 215.8936 | 23.0639 | -59.1009 | 60.7764 | 29.2236 | -64.7729 | 55.5118 | 122.2469 | 163.9575 | 0.61125 | 0.68542 | 49.5133 | 335.7176 | 3 | 13.4912 | 1.0403 | 0.28638
2016-06-11 08:00 | 391.4867 | 228.16 | 163.3267 | 307.7524 | 23.067 | -44.103 | 57.9467 | 32.0533 | -49.067 | 41.7329 | 229.662 | 171.12 | 0.61 | 0.68333 | 59.7017 | 460.4837 | 3.3 | 17.6901 | 1.0256 | 0.38726
2016-06-11 09:00 | 458.96 | 237.71 | 221.25 | 392.9531 | 23.07 | -29.1051 | 55.7334 | 34.2666 | -32.7861 | 27.9673 | 347.0622 | 178.2825 | 0.60875 | 0.68125 | 69.848 | 595.1927 | 3.8 | 22.3998 | 1.0091 | 0.4925
2016-06-11 10:00 | 456.5033 | 232.94 | 223.5633 | 383.4517 | 23.073 | -14.1072 | 54.3362 | 35.6638 | -16.0218 | 14.5821 | 371.0998 | 174.705 | 0.6075 | 0.67917 | 69.3314 | 615.1363 | 3.8 | 23.023 | 1.0069 | 0.5079
2016-06-11 11:00 | 454.0467 | 228.17 | 225.8767 | 383.2945 | 23.076 | 0.89069 | 53.8924 | 36.1076 | 1.0143 | 6.1663 | 381.0769 | 171.1275 | 0.60625 | 0.67708 | 68.8164 | 621.0208 | 4 | 23.4069 | 1.0056 | 0.51208
2016-06-11 12:00 | 451.59 | 223.4 | 228.19 | 392.4538 | 23.079 | 15.8886 | 54.4478 | 35.5522 | 18.0329 | 16.1167 | 377.0297 | 167.55 | 0.605 | 0.675 | 68.303 | 612.8827 | 4.5 | 23.6526 | 1.0047 | 0.50493
2016-06-11 13:00 | 412.6367 | 203.4333 | 209.2033 | 373.5833 | 23.082 | 30.8865 | 55.9448 | 34.0552 | 34.7502 | 29.5963 | 324.8407 | 152.575 | 0.60375 | 0.67292 | 62.2823 | 539.6981 | 5 | 21.8656 | 1.011 | 0.44741
2016-06-11 14:00 | 373.6833 | 183.4667 | 190.2167 | 361.3476 | 23.085 | 45.8844 | 58.2368 | 31.7632 | 50.9672 | 43.3716 | 262.6689 | 137.6 | 0.6025 | 0.67083 | 56.2861 | 456.5549 | 2.2 | 16.4673 | 1.0299 | 0.38556
2016-06-11 15:00 | 334.73 | 163.5 | 171.23 | 354.521 | 23.0879 | 60.8823 | 61.1192 | 28.8808 | 66.6063 | 57.1405 | 192.3563 | 122.625 | 0.60125 | 0.66875 | 50.3141 | 365.2954 | 2.5 | 13.9155 | 1.0388 | 0.31116
2016-06-11 16:00 | 279.6533 | 158.9667 | 120.6867 | 278.9187 | 23.0909 | 75.8802 | 64.3613 | 25.6387 | 81.6976 | 70.7867 | 91.7883 | 119.225 | 0.6 | 0.66667 | 41.948 | 252.9613 | 2.4 | 10.305 | 1.0514 | 0.2181
2016-06-11 17:00 | 224.5767 | 154.4333 | 70.1433 | 185.0973 | 23.0938 | 90.8781 | 67.7311 | 22.2689 | 96.3399 | 84.2045 | 18.6908 | 115.825 | 0.59875 | 0.66458 | 33.6163 | 168.1321 | 3.1 | 8.3541 | 1.0583 | 0.1459
2016-06-11 18:00 | 169.5 | 149.9 | 19.6 | 60.2277 | 23.0967 | 105.8759 | 71.0083 | 18.9917 | 110.6598 | 97.2502 | 0 | 112.425 | 0.5975 | 0.6625 | 25.3191 | 137.7441 | 2.8 | 7.1045 | 1.0626 | 0.12002
2016-06-11 19:00 | 140.19 | 123.4333 | 16.7567 | 60.7614 | 23.0996 | 120.8738 | 73.9916 | 16.0084 | 124.7814 | 109.6927 | 0 | 92.575 | 0.59625 | 0.66042 | 20.8971 | 113.4721 | 2.7 | 6.246 | 1.0656 | 0.099155
2016-06-11 20:00 | 110.88 | 96.9667 | 13.9133 | 59.6171 | 23.1025 | 135.8717 | 76.504 | 13.496 | 138.8056 | 121.13 | 0 | 72.725 | 0.595 | 0.65833 | 16.4934 | 89.2184 | 2.4 | 5.1881 | 1.0693 | 0.078232
2016-06-11 21:00 | 81.57 | 70.5 | 11.07 | 55.0409 | 23.1054 | 150.8696 | 78.3973 | 11.6027 | 152.8005 | 130.8408 | 0 | 52.875 | 0.59375 | 0.65625 | 12.108 | 64.983 | 2.5 | 4.5307 | 1.0716 | 0.057104
2016-06-11 22:00 | 84.8433 | 68.98 | 15.8633 | 87.5392 | 23.1083 | 165.8675 | 79.5595 | 10.4405 | 166.7997 | 137.6103 | 0 | 51.735 | 0.5925 | 0.65417 | 12.5674 | 64.3024 | 2.6 | 4.6095 | 1.0714 | 0.056491
2016-06-11 23:00 | 88.1167 | 67.46 | 20.6567 | 118.0321 | 23.1111 | 180.8654 | 79.9208 | 10.0792 | -179.1916 | 139.9133 | 0 | 50.595 | 0.59125 | 0.65208 | 13.0247 | 63.6197 | 2.2 | 4.1881 | 1.0728 | 0.055968
2016-06-12 | 91.39 | 65.94 | 25.45 | 139.1219 | 23.114 | -164.1368 | 79.4593 | 10.5407 | -165.184 | 137.0238 | 0 | 49.455 | 0.59 | 0.65 | 13.48 | 62.935 | 1.8 | 3.7667 | 1.0743 | 0.055442
2016-06-12 01:00 | 111.97 | 90.24 | 21.73 | 106.2854 | 23.1168 | -149.1389 | 78.2027 | 11.7973 | -151.187 | 129.8333 | 0 | 67.68 | 0.58875 | 0.64792 | 16.4806 | 84.1606 | 1.5 | 4.13 | 1.073 | 0.074053
2016-06-12 02:00 | 132.55 | 114.54 | 18.01 | 75.6423 | 23.1196 | -134.141 | 76.2259 | 13.7741 | -137.1927 | 119.8701 | 0 | 85.905 | 0.5875 | 0.64583 | 19.4683 | 105.3733 | 1.6 | 4.8929 | 1.0704 | 0.092487
2016-06-12 03:00 | 153.13 | 138.84 | 14.29 | 50.7496 | 23.1225 | -119.1431 | 73.6456 | 16.3544 | -123.1634 | 108.2873 | 0 | 104.13 | 0.58625 | 0.64375 | 22.4431 | 126.5731 | 1.7 | 5.6554 | 1.0677 | 0.11082
2016-06-12 04:00 | 192.1867 | 165.7933 | 26.3933 | 79.5121 | 23.1253 | -104.1452 | 70.6134 | 19.3866 | -109.0268 | 95.7596 | 0 | 124.345 | 0.585 | 0.64167 | 28.1073 | 152.4523 | 1.8 | 6.5641 | 1.0645 | 0.13308
2016-06-12 05:00 | 231.2433 | 192.7467 | 38.4967 | 99.7956 | 23.1281 | -89.1474 | 67.3094 | 22.6906 | -94.6783 | 82.6627 | 12.7449 | 144.56 | 0.58375 | 0.63958 | 33.7471 | 191.052 | 2.2 | 8.1704 | 1.0589 | 0.16589
2016-06-12 06:00 | 270.3 | 219.7 | 50.6 | 115.1686 | 23.1308 | -74.1495 | 63.9372 | 26.0628 | -79.9922 | 69.2143 | 40.8703 | 164.775 | 0.5825 | 0.6375 | 39.3624 | 245.0077 | 2.3 | 9.9565 | 1.0527 | 0.21148
2016-06-12 07:00 | 315.3467 | 251.65 | 63.6967 | 130.2336 | 23.1336 | -59.1516 | 60.7188 | 29.2812 | -64.8427 | 55.5518 | 73.668 | 188.7375 | 0.58125 | 0.63542 | 45.8238 | 308.2293 | 2.2 | 11.8322 | 1.0461 | 0.2644
2016-06-12 08:00 | 360.3933 | 283.6 | 76.7933 | 144.4602 | 23.1364 | -44.1538 | 57.8872 | 32.1128 | -49.1363 | 41.7797 | 107.7257 | 212.7 | 0.58 | 0.63333 | 52.257 | 372.6827 | 3 | 14.6463 | 1.0362 | 0.31667
2016-06-12 09:00 | 405.44 | 315.55 | 89.89 | 159.3957 | 23.1391 | -29.1559 | 55.6711 | 34.3289 | -32.8532 | 28.0224 | 140.7088 | 236.6625 | 0.57875 | 0.63125 | 58.6621 | 436.0334 | 2.9 | 16.526 | 1.0297 | 0.36815
2016-06-12 10:00 | 412.31 | 306.1633 | 106.1467 | 181.7714 | 23.1418 | -14.158 | 54.2707 | 35.7293 | -16.085 | 14.6515 | 175.8606 | 229.6225 | 0.5775 | 0.62917 | 59.5273 | 465.0104 | 2.9 | 17.4316 | 1.0265 | 0.39141
2016-06-12 11:00 | 419.18 | 296.7767 | 122.4033 | 207.3677 | 23.1446 | 0.83984 | 53.8237 | 36.1763 | 0.95671 | 6.228 | 206.1438 | 222.5825 | 0.57625 | 0.62708 | 60.3881 | 489.1145 | 2.9 | 18.1848 | 1.0239 | 0.41064
2016-06-12 12:00 | 426.05 | 287.39 | 138.66 | 238.059 | 23.1473 | 15.8377 | 54.3762 | 35.6238 | 17.9819 | 16.0954 | 228.7274 | 215.5425 | 0.575 | 0.625 | 61.2447 | 505.5146 | 2.7 | 18.4973 | 1.0228 | 0.42396
2016-06-12 13:00 | 393.5633 | 269.8 | 123.7633 | 220.589 | 23.15 | 30.8356 | 55.871 | 34.129 | 34.7056 | 29.5572 | 191.8824 | 202.35 | 0.57375 | 0.62292 | 56.4517 | 450.6841 | 2.6 | 16.6839 | 1.0291 | 0.38032
2016-06-12 14:00 | 361.0767 | 252.21 | 108.8667 | 206.3717 | 23.1526 | 45.8334 | 58.1615 | 31.8385 | 50.9282 | 43.3241 | 150.1321 | 189.1575 | 0.5725 | 0.62083 | 51.6791 | 390.9687 | 2.6 | 14.8178 | 1.0356 | 0.33202
2016-06-12 15:00 | 328.59 | 234.62 | 93.97 | 194.091 | 23.1553 | 60.8313 | 61.0429 | 28.9571 | 66.5715 | 57.087 | 105.4622 | 175.965 | 0.57125 | 0.61875 | 46.9268 | 328.354 | 2.5 | 12.7611 | 1.0428 | 0.28078
2016-06-12 16:00 | 291.16 | 204.2633 | 86.8967 | 200.2697 | 23.158 | 75.8291 | 64.2848 | 25.7152 | 81.6652 | 70.728 | 66.0995 | 153.1975 | 0.57 | 0.61667 | 41.4903 | 260.7873 | 2.7 | 10.8496 | 1.0495 | 0.22444
2016-06-12 17:00 | 253.73 | 173.9067 | 79.8233 | 209.9589 | 23.1606 | 90.827 | 67.6548 | 22.3452 | 96.3083 | 84.141 | 21.4329 | 130.43 | 0.56875 | 0.61458 | 36.0772 | 187.9401 | 2.8 | 8.6731 | 1.0571 | 0.16292
2016-06-12 18:00 | 216.3 | 143.55 | 72.75 | 222.6959 | 23.1633 | 105.8249 | 70.9327 | 19.0673 | 110.6276 | 97.1817 | 0 | 107.6625 | 0.5675 | 0.6125 | 30.6876 | 138.3501 | 2.6 | 6.9234 | 1.0633 | 0.12062
2016-06-12 19:00 | 181.0867 | 119.77 | 61.3167 | 221.3392 | 23.1659 | 120.8227 | 73.9172 | 16.0828 | 124.7474 | 109.6192 | 0 | 89.8275 | 0.56625 | 0.61042 | 25.6351 | 115.4626 | 2.5 | 6.1082 | 1.0661 | 0.10094
2016-06-12 20:00 | 145.8733 | 95.99 | 49.8833 | 212.6204 | 23.1685 | 135.8206 | 76.4312 | 13.5688 | 138.7688 | 121.0519 | 0 | 71.9925 | 0.565 | 0.60833 | 20.6046 | 92.5971 | 2.4 | 5.2937 | 1.069 | 0.081167
2016-06-12 21:00 | 110.66 | 72.21 | 38.45 | 190.0362 | 23.1711 | 150.8184 | 78.3268 | 11.6732 | 152.7603 | 130.76 | 0 | 54.1575 | 0.56375 | 0.60625 | 15.5961 | 69.7536 | 2.3 | 4.4798 | 1.0718 | 0.061306
2016-06-12 22:00 | 107.8433 | 81.5933 | 26.25 | 143.9298 | 23.1737 | 165.8163 | 79.4915 | 10.5085 | 166.7556 | 137.5326 | 0 | 61.195 | 0.5625 | 0.60417 | 15.1655 | 76.3605 | 2.5 | 4.8863 | 1.0704 | 0.067024
2016-06-12 23:00 | 105.0267 | 90.9767 | 14.05 | 79.7726 | 23.1763 | 180.8141 | 79.8558 | 10.1442 | -179.2397 | 139.8492 | 0 | 68.2325 | 0.56125 | 0.60208 | 14.7366 | 82.9691 | 2.5 | 5.0928 | 1.0697 | 0.072775
2016-06-13 | 102.21 | 100.36 | 1.85 | 10.0547 | 23.1789 | -164.188 | 79.3976 | 10.6024 | -165.236 | 136.982 | 0 | 75.27 | 0.56 | 0.6 | 14.3094 | 89.5794 | 2.5 | 5.2994 | 1.069 | 0.07852
2016-06-13 01:00 | 129.2833 | 113.0067 | 16.2767 | 79.2245 | 23.1814 | -149.1902 | 78.1442 | 11.8558 | -151.2427 | 129.8137 | 0 | 84.755 | 0.55875 | 0.59792 | 18.0593 | 102.8143 | 2.5 | 5.7129 | 1.0675 | 0.089999
2016-06-13 02:00 | 156.3567 | 125.6533 | 30.7033 | 128.4466 | 23.184 | -134.1923 | 76.1704 | 13.8296 | -137.2516 | 119.8681 | 0 | 94.24 | 0.5575 | 0.59583 | 21.7922 | 116.0322 | 2.6 | 6.226 | 1.0657 | 0.1014
2016-06-13 03:00 | 183.43 | 138.3 | 45.13 | 159.7719 | 23.1865 | -119.1945 | 73.5926 | 16.4074 | -123.2252 | 108.2984 | 0 | 103.725 | 0.55625 | 0.59375 | 25.5082 | 129.2332 | 2.6 | 6.6385 | 1.0643 | 0.11278
2016-06-13 04:00 | 215.0933 | 170.0267 | 45.0667 | 135.4241 | 23.189 | -104.1966 | 70.5623 | 19.4377 | -109.0912 | 95.7805 | 0 | 127.52 | 0.555 | 0.59167 | 29.8442 | 157.3642 | 2.5 | 7.4176 | 1.0615 | 0.13698
2016-06-13 05:00 | 246.7567 | 201.7533 | 45.0033 | 116.4202 | 23.1915 | -89.1988 | 67.2594 | 22.7406 | -94.7448 | 82.6915 | 14.8101 | 151.315 | 0.55375 | 0.58958 | 34.1604 | 200.2854 | 2.9 | 9.1589 | 1.0554 | 0.17334
2016-06-13 06:00 | 278.42 | 233.48 | 44.94 | 102.1044 | 23.194 | -74.201 | 63.8873 | 26.1127 | -80.0603 | 69.2497 | 36.1752 | 175.11 | 0.5525 | 0.5875 | 38.4568 | 249.742 | 3.1 | 10.9044 | 1.0493 | 0.21489
2016-06-13 07:00 | 347.41 | 215.3033 | 132.1067 | 269.6776 | 23.1965 | -59.2031 | 60.668 | 29.332 | -64.9117 | 55.5932 | 152.3853 | 161.4775 | 0.55125 | 0.58542 | 47.8774 | 361.7402 | 3.5 | 14.8044 | 1.0357 | 0.30721
2016-06-13 08:00 | 416.4 | 197.1267 | 219.2733 | 411.8834 | 23.199 | -44.2053 | 57.8344 | 32.1656 | -49.205 | 41.8272 | 306.9186 | 147.845 | 0.55 | 0.58333 | 57.255 | 512.0186 | 3.6 | 19.6006 | 1.0189 | 0.42779
2016-06-13 09:00 | 485.39 | 178.95 | 306.44 | 542.62 | 23.2014 | -29.2075 | 55.6157 | 34.3843 | -32.9202 | 28.0774 | 478.7605 | 134.2125 | 0.54875 | 0.58125 | 66.5894 | 679.5625 | 3.6 | 24.8363 | 1.0006 | 0.55756
2016-06-13 10:00 | 492.5467 | 171.4633 | 321.0833 | 549.0595 | 23.2039 | -14.2096 | 54.212 | 35.788 | -16.1485 | 14.719 | 531.0414 | 128.5975 | 0.5475 | 0.57917 | 67.4173 | 727.0562 | 3.6 | 26.3205 | 0.99538 | 0.59343
2016-06-13 11:00 | 499.7033 | 163.9767 | 335.7267 | 567.9267 | 23.2063 | 0.78822 | 53.7617 | 36.2383 | 0.89819 | 6.2834 | 564.515 | 122.9825 | 0.54625 | 0.57708 | 68.2407 | 755.7383 | 3.8 | 27.4168 | 0.99154 | 0.61446
2016-06-13 12:00 | 506.86 | 156.49 | 350.37 | 600.5853 | 23.2087 | 15.7861 | 54.3113 | 35.6887 | 17.9294 | 16.0716 | 577.1124 | 117.3675 | 0.545 | 0.575 | 69.0597 | 763.5395 | 4.1 | 27.9606 | 0.98964 | 0.61961
2016-06-13 13:00 | 415.68 | 176.19 | 239.49 | 426.1165 | 23.2112 | 30.7839 | 55.8037 | 34.1963 | 34.6591 | 29.5168 | 370.8113 | 132.1425 | 0.54375 | 0.57292 | 56.5065 | 559.4603 | 4 | 21.4831 | 1.0123 | 0.4644
2016-06-13 14:00 | 324.5 | 195.89 | 128.61 | 243.3271 | 23.2136 | 45.7817 | 58.0926 | 31.9074 | 50.8869 | 43.2761 | 177.1566 | 146.9175 | 0.5425 | 0.57083 | 44.0103 | 368.0844 | 4 | 15.5026 | 1.0332 | 0.31186
2016-06-13 15:00 | 233.32 | 215.59 | 17.73 | 36.5402 | 23.216 | 60.7795 | 60.9731 | 29.0269 | 66.5341 | 57.0336 | 19.8832 | 161.6925 | 0.54125 | 0.56875 | 31.5711 | 213.1468 | 4.3 | 10.9608 | 1.0491 | 0.18337
2016-06-13 16:00 | 197.61 | 181.0267 | 16.5833 | 38.1226 | 23.2183 | 75.7774 | 64.2147 | 25.7853 | 81.6302 | 70.67 | 12.6189 | 135.77 | 0.54 | 0.56667 | 26.6774 | 175.0662 | 4.1 | 9.5708 | 1.054 | 0.15131
2016-06-13 17:00 | 161.9 | 146.4633 | 15.4367 | 40.4829 | 23.2207 | 90.7752 | 67.585 | 22.415 | 96.2742 | 84.0787 | 4.1763 | 109.8475 | 0.53875 | 0.56458 | 21.8059 | 135.8297 | 4.1 | 8.3447 | 1.0583 | 0.11787
2016-06-13 18:00 | 126.19 | 111.9 | 14.29 | 43.5911 | 23.2231 | 105.773 | 70.8636 | 19.1364 | 110.5931 | 97.1152 | 0 | 83.925 | 0.5375 | 0.5625 | 16.9568 | 100.8818 | 4.1 | 7.2526 | 1.0621 | 0.087861
2016-06-13 19:00 | 107.8633 | 92.2967 | 15.5667 | 55.9621 | 23.2254 | 120.7709 | 73.8493 | 16.1507 | 124.7112 | 109.5485 | 0 | 69.2225 | 0.53625 | 0.56042 | 14.4604 | 83.6829 | 4.1 | 6.7151 | 1.064 | 0.073011
2016-06-13 20:00 | 89.5367 | 72.6933 | 16.8433 | 71.4504 | 23.2277 | 135.7687 | 76.3651 | 13.6349 | 138.7302 | 120.9776 | 0 | 54.52 | 0.535 | 0.55833 | 11.9755 | 66.4955 | 3.5 | 5.578 | 1.068 | 0.058233
2016-06-13 21:00 | 71.21 | 53.09 | 18.12 | 89.0757 | 23.2301 | 150.7665 | 78.2628 | 11.7372 | 152.7186 | 130.6842 | 0 | 39.8175 | 0.53375 | 0.55625 | 9.5021 | 49.3196 | 3.4 | 4.9412 | 1.0702 | 0.043281
2016-06-13 22:00 | 59.7033 | 46.5867 | 13.1167 | 71.5071 | 23.2324 | 165.7643 | 79.4303 | 10.5697 | 166.7105 | 137.461 | 0 | 34.94 | 0.5325 | 0.55417 | 7.948 | 42.888 | 2.9 | 4.2403 | 1.0727 | 0.037723
2016-06-13 23:00 | 48.1967 | 40.0833 | 8.1133 | 45.8055 | 23.2347 | 180.7621 | 79.7976 | 10.2024 | -179.2884 | 139.7918 | 0 | 30.0625 | 0.53125 | 0.55208 | 6.4011 | 36.4636 | 2.8 | 3.9395 | 1.0737 | 0.032104
2016-06-14 | 36.69 | 33.58 | 3.11 | 16.8166 | 23.2369 | -164.24 | 79.3426 | 10.6574 | -165.2883 | 136.9465 | 0 | 25.185 | 0.53 | 0.55 | 4.8614 | 30.0464 | 3.3 | 4.239 | 1.0727 | 0.026428
2016-06-14 01:00 | 46.0767 | 39.22 | 6.8567 | 33.2309 | 23.2392 | -149.2422 | 78.0924 | 11.9076 | -151.2982 | 129.7997 | 0 | 29.415 | 0.52875 | 0.54792 | 6.0908 | 35.5058 | 2.7 | 3.8096 | 1.0742 | 0.031274
2016-06-14 02:00 | 55.4633 | 44.86 | 10.6033 | 44.206 | 23.2415 | -134.2444 | 76.1216 | 13.8784 | -137.3101 | 119.8707 | 0 | 33.645 | 0.5275 | 0.54583 | 7.3142 | 40.9592 | 2.6 | 3.88 | 1.0739 | 0.036069
2016-06-14 03:00 | 64.85 | 50.5 | 14.35 | 50.664 | 23.2437 | -119.2466 | 73.5464 | 16.4536 | -123.2863 | 108.3133 | 0 | 37.875 | 0.52625 | 0.54375 | 8.5318 | 46.4068 | 3 | 4.4502 | 1.0719 | 0.040791
2016-06-14 04:00 | 80.41 | 60.93 | 19.48 | 58.4089 | 23.246 | -104.2488 | 70.518 | 19.482 | -109.1546 | 95.8045 | 0 | 45.6975 | 0.525 | 0.54167 | 10.5538 | 56.2513 | 2.8 | 4.5579 | 1.0715 | 0.049426
2016-06-14 05:00 | 95.97 | 71.36 | 24.61 | 63.5498 | 23.2482 | -89.251 | 67.2162 | 22.7838 | -94.8103 | 82.7227 | 8.05 | 53.52 | 0.52375 | 0.53958 | 12.5661 | 74.1361 | 2.6 | 4.9168 | 1.0703 | 0.065065
2016-06-14 06:00 | 111.53 | 81.79 | 29.74 | 67.4662 | 23.2504 | -74.2531 | 63.8442 | 26.1558 | -80.1274 | 69.2869 | 23.862 | 61.3425 | 0.5225 | 0.5375 | 14.5686 | 99.7732 | 2.7 | 5.8179 | 1.0671 | 0.087307
2016-06-14 07:00 | 210.8633 | 166.1233 | 44.74 | 91.2058 | 23.2526 | -59.2553 | 60.624 | 29.376 | -64.9797 | 55.6359 | 51.4811 | 124.5925 | 0.52125 | 0.53542 | 27.4781 | 203.5518 | 2.6 | 8.961 | 1.0561 | 0.17628
2016-06-14 08:00 | 310.1967 | 250.4567 | 59.74 | 112.0729 | 23.2548 | -44.2575 | 57.7885 | 32.2115 | -49.273 | 41.8754 | 83.4493 | 187.8425 | 0.52 | 0.53333 | 40.3256 | 311.6173 | 2.9 | 12.638 | 1.0433 | 0.26658
2016-06-14 09:00 | 409.53 | 334.79 | 74.74 | 132.1798 | 23.257 | -29.2597 | 55.567 | 34.433 | -32.9869 | 28.1322 | 116.5644 | 251.0925 | 0.51875 | 0.53125 | 53.1109 | 420.7678 | 3 | 16.149 | 1.031 | 0.35572
2016-06-14 10:00 | 387.4233 | 312.9767 | 74.4467 | 127.1459 | 23.2591 | -14.2619 | 54.1601 | 35.8399 | -16.2123 | 14.7845 | 122.9364 | 234.7325 | 0.5175 | 0.52917 | 50.1229 | 407.7918 | 3.6 | 16.3435 | 1.0303 | 0.34452
2016-06-14 11:00 | 365.3167 | 291.1633 | 74.1533 | 125.2758 | 23.2613 | 0.73591 | 53.7066 | 36.2934 | 0.83883 | 6.3324 | 124.5115 | 218.3725 | 0.51625 | 0.52708 | 47.1487 | 390.0327 | 4.4 | 16.5885 | 1.0294 | 0.32924
2016-06-14 12:00 | 343.21 | 269.35 | 73.86 | 126.4282 | 23.2634 | 15.7337 | 54.2531 | 35.7469 | 17.8754 | 16.0452 | 121.5031 | 202.0125 | 0.515 | 0.525 | 44.1883 | 367.7038 | 3.6 | 15.0907 | 1.0347 | 0.31197
2016-06-14 13:00 | 283.3833 | 233.52 | 49.8633 | 88.5823 | 23.2656 | 30.7315 | 55.7431 | 34.2569 | 34.6106 | 29.4752 | 77.117 | 175.14 | 0.51375 | 0.52292 | 36.397 | 288.6541 | 3.7 | 12.7204 | 1.043 | 0.24687
2016-06-14 14:00 | 223.5567 | 197.69 | 25.8667 | 48.8538 | 23.2677 | 45.7293 | 58.0303 | 31.9697 | 50.8434 | 43.2275 | 35.5968 | 148.2675 | 0.5125 | 0.52083 | 28.6432 | 212.5075 | 3.6 | 10.2409 | 1.0517 | 0.18326
2016-06-14 15:00 | 163.73 | 161.86 | 1.87 | 3.8463 | 23.2698 | 60.7271 | 60.9098 | 29.0902 | 66.4943 | 56.9803 | 2.0959 | 121.395 | 0.51125 | 0.51875 | 20.9267 | 144.4177 | 4.5 | 9.0131 | 1.056 | 0.12505
2016-06-14 16:00 | 144.9333 | 137.3533 | 7.58 | 17.3853 | 23.2719 | 75.7249 | 64.151 | 25.849 | 81.5927 | 70.6127 | 5.7711 | 103.015 | 0.51 | 0.51667 | 18.479 | 127.2651 | 4.3 | 8.277 | 1.0585 | 0.11047
2016-06-14 17:00 | 126.1367 | 112.8467 | 13.29 | 34.76 | 23.274 | 90.7227 | 67.5215 | 22.4785 | 96.2376 | 84.0177 | 3.6227 | 84.635 | 0.50875 | 0.51458 | 16.043 | 104.3007 | 3.7 | 6.9594 | 1.0631 | 0.090927
2016-06-14 18:00 | 107.34 | 88.34 | 19 | 57.7768 | 23.276 | 105.7205 | 70.8009 | 19.1991 | 110.5563 | 97.0506 | 0 | 66.255 | 0.5075 | 0.5125 | 13.6188 | 79.8738 | 3.2 | 5.6961 | 1.0676 | 0.069922
2016-06-14 19:00 | 92.23 | 79.38 | 12.85 | 46.0255 | 23.2781 | 120.7183 | 73.788 | 16.212 | 124.6731 | 109.4807 | 0 | 59.535 | 0.50625 | 0.51042 | 11.6729 | 71.2079 | 2.7 | 4.9252 | 1.0703 | 0.062493
2016-06-14 20:00 | 77.12 | 70.42 | 6.7 | 28.3006 | 23.2802 | 135.7161 | 76.3055 | 13.6945 | 138.6899 | 120.9071 | 0 | 52.815 | 0.505 | 0.50833 | 9.7364 | 62.5514 | 2.5 | 4.4547 | 1.0719 | 0.05498
2016-06-14 21:00 | 62.01 | 61.46 | 0.55 | 2.6908 | 23.2822 | 150.7139 | 78.2056 | 11.7944 | 152.6756 | 130.6134 | 0 | 46.095 | 0.50375 | 0.50625 | 7.8094 | 53.9044 | 2.1 | 3.7845 | 1.0743 | 0.047484
2016-06-14 22:00 | 43.8067 | 43.42 | 0.38667 | 2.0973 | 23.2842 | 165.7117 | 79.3758 | 10.6242 | 166.6644 | 137.3956 | 0 | 32.565 | 0.5025 | 0.50417 | 5.5032 | 38.0682 | 2 | 3.1896 | 1.0763 | 0.033599
2016-06-14 23:00 | 25.6033 | 25.38 | 0.22333 | 1.2546 | 23.2862 | 180.7095 | 79.7462 | 10.2538 | -179.3377 | 139.7411 | 0 | 19.035 | 0.50125 | 0.50208 | 3.2084 | 22.2434 | 2 | 2.6951 | 1.0781 | 0.019664
2016-06-15 | 7.4 | 7.34 | 0.06 | 0.32299 | 23.2882 | -164.2927 | 79.2944 | 10.7056 | -165.3406 | 136.9174 | 0 | 5.505 | 0.5 | 0.5 | 0.925 | 6.43 | 2 | 2.2009 | 1.0798 | 0.0056933
2016-06-15 01:00 | 6.5467 | 6.5067 | 0.04 | 0.19314 | 23.2902 | -149.2949 | 78.0474 | 11.9526 | -151.3535 | 129.7911 | 0 | 4.88 | 0.49875 | 0.49792 | 0.81629 | 5.6963 | 1 | 1.178 | 1.0834 | 0.0050604
2016-06-15 02:00 | 5.6933 | 5.6733 | 0.02 | 0.083135 | 23.2922 | -134.2971 | 76.0796 | 13.9204 | -137.3679 | 119.8778 | 0 | 4.255 | 0.4975 | 0.49583 | 0.70811 | 4.9631 | 3 | 3.1551 | 1.0765 | 0.0043809
2016-06-15 03:00 | 4.84 | 4.84 | 0 | 0 | 23.2942 | -119.2993 | 73.507 | 16.493 | -123.3466 | 108.3318 | 0 | 3.63 | 0.49625 | 0.49375 | 0.60046 | 4.2305 | 3.2 | 3.3322 | 1.0758 | 0.0037321
2016-06-15 04:00 | 6.3267 | 6.0967 | 0.23 | 0.68836 | 23.2961 | -104.3015 | 70.4805 | 19.5195 | -109.217 | 95.8314 | 0 | 4.5725 | 0.495 | 0.49167 | 0.78292 | 5.3554 | 3.1 | 3.2674 | 1.0761 | 0.0047255
2016-06-15 05:00 | 7.8133 | 7.3533 | 0.46 | 1.186 | 23.2981 | -89.3037 | 67.1797 | 22.8203 | -94.8745 | 82.7562 | 0.14955 | 5.515 | 0.49375 | 0.48958 | 0.96446 | 6.629 | 3 | 3.2072 | 1.0763 | 0.0058504
2016-06-15 06:00 | 9.3 | 8.61 | 0.69 | 1.5633 | 23.3 | -74.3059 | 63.8078 | 26.1922 | -80.1932 | 69.3258 | 0.55192 | 6.4575 | 0.4925 | 0.4875 | 1.1451 | 8.1545 | 3.5 | 3.7548 | 1.0744 | 0.0071839
2016-06-15 07:00 | 37.9833 | 37.5 | 0.48333 | 0.98417 | 23.3019 | -59.3082 | 60.5867 | 29.4133 | -65.0465 | 55.6797 | 0.5549 | 28.125 | 0.49125 | 0.48542 | 4.6648 | 33.3447 | 3.9 | 4.942 | 1.0702 | 0.029262
2016-06-15 08:00 | 66.6667 | 66.39 | 0.27667 | 0.51847 | 23.3038 | -44.3104 | 57.7494 | 32.2506 | -49.3402 | 41.9241 | 0.38576 | 49.7925 | 0.49 | 0.48333 | 8.1667 | 58.3449 | 3.9 | 5.7233 | 1.0675 | 0.051071
2016-06-15 09:00 | 95.35 | 95.28 | 0.07 | 0.12367 | 23.3057 | -29.3126 | 55.5252 | 34.4748 | -33.0531 | 28.1867 | 0.109 | 71.46 | 0.48875 | 0.48125 | 11.6506 | 83.2196 | 2.5 | 5.1006 | 1.0696 | 0.072993
2016-06-15 10:00 | 71.0533 | 71.0067 | 0.046667 | 0.079614 | 23.3076 | -14.3148 | 54.1152 | 35.8848 | -16.2762 | 14.848 | 0.076956 | 53.255 | 0.4875 | 0.47917 | 8.6596 | 61.9916 | 4.4 | 6.3372 | 1.0653 | 0.054153
2016-06-15 11:00 | 46.7567 | 46.7333 | 0.023333 | 0.039374 | 23.3095 | 0.68299 | 53.6583 | 36.3417 | 0.77871 | 6.3751 | 0.039131 | 35.05 | 0.48625 | 0.47708 | 5.6839 | 40.773 | 1.8 | 3.0742 | 1.0767 | 0.036
2016-06-15 12:00 | 22.46 | 22.46 | 0 | 0 | 23.3113 | 15.6808 | 54.2017 | 35.7983 | 17.8201 | 16.0163 | 0 | 16.845 | 0.485 | 0.475 | 2.7233 | 19.5683 | 1.7 | 2.3115 | 1.0794 | 0.01732
2016-06-15 13:00 | 39.4133 | 29.5167 | 9.8967 | 17.5572 | 23.3132 | 30.6786 | 55.6892 | 34.3108 | 34.5604 | 29.4324 | 15.2912 | 22.1375 | 0.48375 | 0.47292 | 4.7665 | 42.1953 | 2 | 3.3186 | 1.0759 | 0.037226
2016-06-15 14:00 | 56.3667 | 36.5733 | 19.7933 | 37.3251 | 23.315 | 45.6763 | 57.9746 | 32.0254 | 50.7977 | 43.1786 | 27.2184 | 27.43 | 0.4825 | 0.47083 | 6.7992 | 61.4476 | 1.3 | 3.2202 | 1.0762 | 0.054228
2016-06-15 15:00 | 73.32 | 43.63 | 29.69 | 60.9587 | 23.3168 | 60.6741 | 60.8531 | 29.1469 | 66.4521 | 56.9272 | 33.2654 | 32.7225 | 0.48125 | 0.46875 | 8.8213 | 74.8093 | 1.2 | 3.5378 | 1.0751 | 0.065952
2016-06-15 16:00 | 81.89 | 49.6367 | 32.2533 | 73.8235 | 23.3186 | 75.6719 | 64.0939 | 25.9061 | 81.5528 | 70.5562 | 24.5745 | 37.2275 | 0.48 | 0.46667 | 9.8268 | 71.6288 | 1.5 | 3.7384 | 1.0744 | 0.063106
2016-06-15 17:00 | 90.46 | 55.6433 | 34.8167 | 90.8448 | 23.3204 | 90.6697 | 67.4646 | 22.5354 | 96.1988 | 83.9581 | 9.562 | 41.7325 | 0.47875 | 0.46458 | 10.8269 | 62.1214 | 1.6 | 3.5413 | 1.0751 | 0.054765
2016-06-15 18:00 | 99.03 | 61.65 | 37.38 | 113.3493 | 23.3222 | 105.6675 | 70.7448 | 19.2552 | 110.5173 | 96.9882 | 0 | 46.2375 | 0.4775 | 0.4625 | 11.8217 | 58.0592 | 2.1 | 3.9144 | 1.0738 | 0.051122
2016-06-15 19:00 | 88.1033 | 52.7933 | 35.31 | 126.0572 | 23.324 | 120.6652 | 73.7332 | 16.2668 | 124.633 | 109.4157 | 0 | 39.595 | 0.47625 | 0.46042 | 10.4898 | 50.0848 | 1.7 | 3.2652 | 1.0761 | 0.044194
2016-06-15 20:00 | 77.1767 | 43.9367 | 33.24 | 139.8745 | 23.3258 | 135.663 | 76.2526 | 13.7474 | 138.648 | 120.8405 | 0 | 32.9525 | 0.475 | 0.45833 | 9.1647 | 42.1172 | 2 | 3.3162 | 1.0759 | 0.037157
2016-06-15 21:00 | 66.25 | 35.08 | 31.17 | 151.8533 | 23.3275 | 150.6608 | 78.155 | 11.845 | 152.6313 | 130.5476 | 0 | 26.31 | 0.47375 | 0.45625 | 7.8465 | 34.1565 | 1.9 | 2.9674 | 1.0771 | 0.030168
2016-06-15 22:00 | 58.14 | 37.31 | 20.83 | 112.4819 | 23.3293 | 165.6586 | 79.3281 | 10.6719 | 166.6174 | 137.3363 | 0 | 27.9825 | 0.4725 | 0.45417 | 6.8678 | 34.8503 | 2.1 | 3.1891 | 1.0763 | 0.030759
2016-06-15 23:00 | 50.03 | 39.54 | 10.49 | 58.677 | 23.331 | 180.6563 | 79.7016 | 10.2984 | -179.3875 | 139.6973 | 0 | 29.655 | 0.47125 | 0.45208 | 5.8942 | 35.5492 | 2 | 3.1109 | 1.0766 | 0.031384
2016-06-16 | 41.92 | 41.77 | 0.15 | 0.80441 | 23.3327 | -164.3459 | 79.253 | 10.747 | -165.3931 | 136.8947 | 0 | 31.3275 | 0.47 | 0.45 | 4.9256 | 36.2531 | 1.9 | 3.0329 | 1.0769 | 0.032013
2016-06-16 01:00 | 57.5733 | 57.4633 | 0.11 | 0.52948 | 23.3344 | -149.3481 | 78.0093 | 11.9907 | -151.4084 | 129.788 | 0 | 43.0975 | 0.46875 | 0.44792 | 6.7469 | 49.8444 | 2.3 | 3.8576 | 1.074 | 0.043897
2016-06-16 02:00 | 73.2267 | 73.1567 | 0.07 | 0.29025 | 23.3361 | -134.3504 | 76.0445 | 13.9555 | -137.4252 | 119.8894 | 0 | 54.8675 | 0.4675 | 0.44583 | 8.5584 | 63.4259 | 2.5 | 4.4821 | 1.0718 | 0.055744
2016-06-16 03:00 | 88.88 | 88.85 | 0.03 | 0.10547 | 23.3378 | -119.3526 | 73.4743 | 16.5257 | -123.4058 | 108.3539 | 0 | 66.6375 | 0.46625 | 0.44375 | 10.3601 | 76.9976 | 2.3 | 4.7062 | 1.071 | 0.067623
2016-06-16 04:00 | 109.4067 | 108.7167 | 0.69 | 2.0619 | 23.3394 | -104.3548 | 70.4497 | 19.5503 | -109.2781 | 95.8613 | 0 | 81.5375 | 0.465 | 0.44167 | 12.7185 | 94.256 | 2.7 | 5.6455 | 1.0677 | 0.082526
2016-06-16 05:00 | 129.9333 | 128.5833 | 1.35 | 3.4765 | 23.3411 | -89.357 | 67.1499 | 22.8501 | -94.9374 | 82.7919 | 0.43621 | 96.4375 | 0.46375 | 0.43958 | 15.0641 | 111.9379 | 2.1 | 5.5981 | 1.0679 | 0.098022
2016-06-16 06:00 | 150.46 | 148.45 | 2.01 | 4.5491 | 23.3427 | -74.3593 | 63.7782 | 26.2218 | -80.2577 | 69.3665 | 1.603 | 111.3375 | 0.4625 | 0.4375 | 17.3969 | 130.3375 | 2.1 | 6.173 | 1.0659 | 0.11392
2016-06-16 07:00 | 151.4567 | 149.0567 | 2.4 | 4.8823 | 23.3444 | -59.3615 | 60.5562 | 29.4438 | -65.1122 | 55.7247 | 2.7496 | 111.7925 | 0.46125 | 0.43542 | 17.4648 | 132.0069 | 2.3 | 6.4252 | 1.065 | 0.11528
2016-06-16 08:00 | 152.4533 | 149.6633 | 2.79 | 5.2237 | 23.346 | -44.3637 | 57.7171 | 32.2829 | -49.4064 | 41.9733 | 3.8836 | 112.2475 | 0.46 | 0.43333 | 17.5321 | 133.6633 | 2.8 | 6.977 | 1.0631 | 0.11652
2016-06-16 09:00 | 153.45 | 150.27 | 3.18 | 5.613 | 23.3476 | -29.366 | 55.4903 | 34.5097 | -33.1189 | 28.2408 | 4.9448 | 112.7025 | 0.45875 | 0.43125 | 17.5988 | 135.2461 | 2.6 | 6.8264 | 1.0636 | 0.11796
2016-06-16 10:00 | 156.9333 | 152.2267 | 4.7067 | 8.0223 | 23.3492 | -14.3682 | 54.077 | 35.923 | -16.3401 | 14.9093 | 7.7522 | 114.17 | 0.4575 | 0.42917 | 17.9492 | 139.8715 | 3.1 | 7.471 | 1.0614 | 0.12173
2016-06-16 11:00 | 160.4167 | 154.1833 | 6.2333 | 10.5083 | 23.3508 | 0.62956 | 53.6168 | 36.3832 | 0.71795 | 6.4114 | 10.4426 | 115.6375 | 0.45625 | 0.42708 | 18.2975 | 144.3776 | 3.1 | 7.6118 | 1.0609 | 0.12559
2016-06-16 12:00 | 163.9 | 156.14 | 7.76 | 13.2522 | 23.3524 | 15.6273 | 54.1571 | 35.8429 | 17.7635 | 15.9847 | 12.7398 | 117.105 | 0.455 | 0.425 | 18.6436 | 148.4884 | 3.2 | 7.8403 | 1.0601 | 0.12907
2016-06-16 13:00 | 201.3367 | 149.35 | 51.9867 | 92.1159 | 23.3539 | 30.6251 | 55.642 | 34.358 | 34.5084 | 29.3885 | 80.2617 | 112.0125 | 0.45375 | 0.42292 | 22.8391 | 215.1134 | 3.2 | 9.9223 | 1.0528 | 0.1857
2016-06-16 14:00 | 238.7733 | 142.56 | 96.2133 | 181.1855 | 23.3555 | 45.6228 | 57.9255 | 32.0745 | 50.7499 | 43.1293 | 132.2315 | 106.92 | 0.4525 | 0.42083 | 27.0112 | 266.1627 | 3.3 | 11.6176 | 1.0468 | 0.22848
2016-06-16 15:00 | 276.21 | 135.77 | 140.44 | 287.8951 | 23.357 | 60.6206 | 60.8028 | 29.1972 | 66.4076 | 56.8743 | 157.3281 | 101.8275 | 0.45125 | 0.41875 | 31.1599 | 290.3156 | 3.3 | 12.3724 | 1.0442 | 0.24858
2016-06-16 16:00 | 240.33 | 135.8967 | 104.4333 | 238.5994 | 23.3585 | 75.6184 | 64.0432 | 25.9568 | 81.5106 | 70.5005 | 79.644 | 101.9225 | 0.45 | 0.41667 | 27.0371 | 208.6036 | 3.7 | 10.2189 | 1.0517 | 0.1799
2016-06-16 17:00 | 204.45 | 136.0233 | 68.4267 | 178.1632 | 23.3601 | 90.6161 | 67.4142 | 22.5858 | 96.1576 | 83.9 | 18.9325 | 102.0175 | 0.44875 | 0.41458 | 22.9367 | 143.8867 | 3.6 | 8.0965 | 1.0592 | 0.12497
2016-06-16 18:00 | 168.57 | 136.15 | 32.42 | 98.0659 | 23.3616 | 105.6139 | 70.6952 | 19.3048 | 110.4761 | 96.9279 | 0 | 102.1125 | 0.4475 | 0.4125 | 18.8588 | 120.9713 | 3.8 | 7.5804 | 1.061 | 0.10524
2016-06-16 19:00 | 131.7433 | 109.8333 | 21.91 | 77.9942 | 23.3631 | 120.6116 | 73.685 | 16.315 | 124.591 | 109.3537 | 0 | 82.375 | 0.44625 | 0.41042 | 14.6976 | 97.0726 | 3.4 | 6.4335 | 1.065 | 0.084772
2016-06-16 20:00 | 94.9167 | 83.5167 | 11.4 | 47.8137 | 23.3645 | 135.6094 | 76.2064 | 13.7936 | 138.6045 | 120.7779 | 0 | 62.6375 | 0.445 | 0.40833 | 10.5595 | 73.197 | 3.8 | 6.0874 | 1.0662 | 0.063995
2016-06-16 21:00 | 58.09 | 57.2 | 0.89 | 4.3201 | 23.366 | 150.6072 | 78.1112 | 11.8888 | 152.5857 | 130.4869 | 0 | 42.9 | 0.44375 | 0.40625 | 6.4444 | 49.3444 | 3.4 | 4.942 | 1.0702 | 0.043303
2016-06-16 22:00 | 64.4667 | 63.01 | 1.4567 | 7.8363 | 23.3675 | 165.6049 | 79.2871 | 10.7129 | 166.5696 | 137.2833 | 0 | 47.2575 | 0.4425 | 0.40417 | 7.1316 | 54.3891 | 3.4 | 5.0997 | 1.0697 | 0.047705
2016-06-16 23:00 | 70.8433 | 68.82 | 2.0233 | 11.2768 | 23.3689 | 180.6027 | 79.6638 | 10.3362 | -179.4376 | 139.6601 | 0 | 51.615 | 0.44125 | 0.40208 | 7.8149 | 59.4299 | 3.3 | 5.1572 | 1.0694 | 0.052117
2016-06-17 | 77.22 | 74.63 | 2.59 | 13.8455 | 23.3703 | -164.3996 | 79.2185 | 10.7815 | -165.4455 | 136.8785 | 0 | 55.9725 | 0.44 | 0.4 | 8.4942 | 64.4667 | 3 | 5.0146 | 1.0699 | 0.05656
2016-06-17 01:00 | 99.95 | 97.2233 | 2.7267 | 13.0909 | 23.3717 | -149.4018 | 77.978 | 12.022 | -151.4629 | 129.7904 | 0 | 72.9175 | 0.43875 | 0.39792 | 10.9633 | 83.8808 | 3.1 | 5.7213 | 1.0675 | 0.073423
2016-06-17 02:00 | 122.68 | 119.8167 | 2.8633 | 11.8492 | 23.3732 | -134.4041 | 76.0161 | 13.9839 | -137.4816 | 119.9055 | 0 | 89.8625 | 0.4375 | 0.39583 | 13.4181 | 103.2806 | 3.2 | 6.4275 | 1.065 | 0.090195
2016-06-17 03:00 | 145.41 | 142.41 | 3 | 10.5308 | 23.3745 | -119.4063 | 73.4484 | 16.5516 | -123.4641 | 108.3796 | 0 | 106.8075 | 0.43625 | 0.39375 | 15.8588 | 122.6663 | 3.2 | 7.0333 | 1.0629 | 0.10691
2016-06-17 04:00 | 156.8133 | 153.3433 | 3.47 | 10.3573 | 23.3759 | -104.4086 | 70.4256 | 19.5744 | -109.338 | 95.8939 | 0 | 115.0075 | 0.435 | 0.39167 | 17.0535 | 132.0609 | 3.1 | 7.2269 | 1.0622 | 0.11503
2016-06-17 05:00 | 168.2167 | 164.2767 | 3.94 | 10.1366 | 23.3773 | -89.4108 | 67.1269 | 22.8731 | -94.999 | 82.8299 | 1.2652 | 123.2075 | 0.43375 | 0.38958 | 18.241 | 142.7137 | 3.4 | 7.8598 | 1.06 | 0.12405
2016-06-17 06:00 | 179.62 | 175.21 | 4.41 | 9.9727 | 23.3787 | -74.413 | 63.7553 | 26.2447 | -80.3207 | 69.4087 | 3.5074 | 131.4075 | 0.4325 | 0.3875 | 19.4214 | 154.3363 | 3.4 | 8.223 | 1.0587 | 0.13399
2016-06-17 07:00 | 208.9333 | 204.9233 | 4.01 | 8.1516 | 23.38 | -59.4153 | 60.5325 | 29.4675 | -65.1767 | 55.7706 | 4.5853 | 153.6925 | 0.43125 | 0.38542 | 22.5256 | 180.8034 | 3.3 | 8.9501 | 1.0562 | 0.15659
2016-06-17 08:00 | 238.2467 | 234.6367 | 3.61 | 6.7543 | 23.3813 | -44.4175 | 57.6916 | 32.3084 | -49.4716 | 42.0229 | 5.0176 | 175.9775 | 0.43 | 0.38333 | 25.6115 | 206.6066 | 3.4 | 9.8565 | 1.053 | 0.1784
2016-06-17 09:00 | 267.56 | 264.35 | 3.21 | 5.6619 | 23.3827 | -29.4198 | 55.4622 | 34.5378 | -33.184 | 28.2944 | 4.9854 | 198.2625 | 0.42875 | 0.38125 | 28.6791 | 231.927 | 3.6 | 10.8477 | 1.0495 | 0.1996
2016-06-17 10:00 | 291.07 | 262.0333 | 29.0367 | 49.4545 | 23.384 | -14.422 | 54.0457 | 35.9543 | -16.404 | 14.9683 | 47.7764 | 196.525 | 0.4275 | 0.37917 | 31.1081 | 275.4095 | 3.6 | 12.2065 | 1.0448 | 0.23595
2016-06-17 11:00 | 314.58 | 259.7167 | 54.8633 | 92.4139 | 23.3853 | 0.5757 | 53.5821 | 36.4179 | 0.65665 | 6.4413 | 91.8305 | 194.7875 | 0.42625 | 0.37708 | 33.5224 | 320.1404 | 3.6 | 13.6044 | 1.0399 | 0.27299
2016-06-17 12:00 | 338.09 | 257.4 | 80.69 | 137.6729 | 23.3866 | 15.5735 | 54.1193 | 35.8807 | 17.7058 | 15.9506 | 132.3724 | 193.05 | 0.425 | 0.375 | 35.9221 | 361.3444 | 3.5 | 14.792 | 1.0357 | 0.30689
2016-06-17 13:00 | 290.3433 | 224.7167 | 65.6267 | 116.1648 | 23.3879 | 30.5712 | 55.6016 | 34.3984 | 34.4547 | 29.3434 | 101.2606 | 168.5375 | 0.42375 | 0.37292 | 30.7582 | 300.5564 | 3.5 | 12.8924 | 1.0424 | 0.2569
2016-06-17 14:00 | 242.5967 | 192.0333 | 50.5633 | 95.1067 | 23.3891 | 45.5689 | 57.8831 | 32.1169 | 50.7001 | 43.0797 | 69.4663 | 144.025 | 0.4225 | 0.37083 | 25.6243 | 239.1156 | 3.7 | 11.1724 | 1.0484 | 0.20556
2016-06-17 15:00 | 194.85 | 159.35 | 35.5 | 72.6742 | 23.3904 | 60.5667 | 60.7592 | 29.2408 | 66.361 | 56.8218 | 39.7706 | 119.5125 | 0.42125 | 0.36875 | 20.5201 | 179.8032 | 3.8 | 9.4189 | 1.0545 | 0.15548
2016-06-17 16:00 | 186.0067 | 151.01 | 34.9967 | 79.8309 | 23.3916 | 75.5644 | 63.9991 | 26.0009 | 81.4661 | 70.4458 | 26.7193 | 113.2575 | 0.42 | 0.36667 | 19.5307 | 159.5075 | 3.5 | 8.4846 | 1.0578 | 0.13836
2016-06-17 17:00 | 177.1633 | 142.67 | 34.4933 | 89.6456 | 23.3928 | 90.5622 | 67.3703 | 22.6297 | 96.1143 | 83.8434 | 9.6142 | 107.0025 | 0.41875 | 0.36458 | 18.5468 | 135.1635 | 3.5 | 7.7239 | 1.0605 | 0.11754
2016-06-17 18:00 | 168.32 | 134.33 | 33.99 | 102.595 | 23.3941 | 105.5599 | 70.6521 | 19.3479 | 110.433 | 96.8698 | 0 | 100.7475 | 0.4175 | 0.3625 | 17.5684 | 118.3159 | 3.7 | 7.3974 | 1.0616 | 0.103
2016-06-17 19:00 | 159.2467 | 101.4367 | 57.81 | 205.2806 | 23.3953 | 120.5577 | 73.6434 | 16.3566 | 124.5473 | 109.2947 | 0 | 76.0775 | 0.41625 | 0.36042 | 16.5716 | 92.6491 | 3.8 | 6.6953 | 1.0641 | 0.08084
2016-06-17 20:00 | 150.1733 | 68.5433 | 81.63 | 341.4111 | 23.3965 | 135.5554 | 76.1668 | 13.8332 | 138.5594 | 120.7193 | 0 | 51.4075 | 0.415 | 0.35833 | 15.5805 | 66.988 | 3.6 | 5.6934 | 1.0676 | 0.058642
2016-06-17 21:00 | 141.1 | 35.65 | 105.45 | 510.296 | 23.3976 | 150.5532 | 78.0742 | 11.9258 | 152.539 | 130.4314 | 0 | 26.7375 | 0.41375 | 0.35625 | 14.595 | 41.3325 | 3.6 | 4.8916 | 1.0704 | 0.036278
2016-06-17 22:00 | 126.0267 | 51.12 | 74.9067 | 401.7026 | 23.3988 | 165.5509 | 79.253 | 10.747 | 166.521 | 137.2366 | 0 | 38.34 | 0.4125 | 0.35417 | 12.9965 | 51.3365 | 3.6 | 5.2043 | 1.0693 | 0.045013
2016-06-17 23:00 | 110.9533 | 66.59 | 44.3633 | 246.5236 | 23.4 | 180.5486 | 79.6328 | 10.3672 | -179.4881 | 139.6298 | 0 | 49.9425 | 0.41125 | 0.35208 | 11.4074 | 61.3499 | 3.2 | 5.1172 | 1.0696 | 0.053808
2016-06-18 | 95.88 | 82.06 | 13.82 | 73.6917 | 23.4011 | -164.4536 | 79.1909 | 10.8091 | -165.4979 | 136.8686 | 0 | 61.545 | 0.41 | 0.35 | 9.8277 | 71.3727 | 3.5 | 5.7304 | 1.0674 | 0.062473
2016-06-18 01:00 | 126.2367 | 91.1033 | 35.1333 | 168.3401 | 23.4022 | -149.4559 | 77.9536 | 12.0464 | -151.517 | 129.7982 | 0 | 68.3275 | 0.40875 | 0.34792 | 12.8998 | 81.2273 | 3.4 | 5.9384 | 1.0667 | 0.07105
2016-06-18 02:00 | 156.5933 | 100.1467 | 56.4467 | 233.2374 | 23.4034 | -134.4581 | 75.9946 | 14.0054 | -137.5372 | 119.926 | 0 | 75.11 | 0.4075 | 0.34583 | 15.9529 | 91.0629 | 3.7 | 6.5457 | 1.0646 | 0.079495
2016-06-18 03:00 | 186.95 | 109.19 | 77.76 | 272.6529 | 23.4045 | -119.4604 | 73.4293 | 16.5707 | -123.5211 | 108.4089 | 0 | 81.8925 | 0.40625 | 0.34375 | 18.9871 | 100.8796 | 3.1 | 6.2525 | 1.0656 | 0.088149
2016-06-18 04:00 | 221.3733 | 140.1733 | 81.2 | 242.16 | 23.4056 | -104.4627 | 70.4083 | 19.5917 | -109.3966 | 95.9294 | 0 | 105.13 | 0.405 | 0.34167 | 22.414 | 127.544 | 3.1 | 7.0858 | 1.0627 | 0.11114
2016-06-18 05:00 | 255.7967 | 171.1567 | 84.64 | 217.6095 | 23.4067 | -89.4649 | 67.1106 | 22.8894 | -95.059 | 82.8699 | 27.0102 | 128.3675 | 0.40375 | 0.33958 | 25.8195 | 181.1972 | 3.2 | 8.8624 | 1.0565 | 0.15697
2016-06-18 06:00 | 290.22 | 202.14 | 88.08 | 199.0693 | 23.4077 | -74.4672 | 63.7391 | 26.2609 | -80.3823 | 69.4524 | 69.8704 | 151.605 | 0.4025 | 0.3375 | 29.2034 | 250.6787 | 3.1 | 10.9337 | 1.0492 | 0.21568
2016-06-18 07:00 | 350.92 | 215.7133 | 135.2067 | 274.7056 | 23.4088 | -59.4694 | 60.5155 | 29.4845 | -65.2397 | 55.8175 | 154.338 | 161.785 | 0.40125 | 0.33542 | 35.2017 | 351.3246 | 3.2 | 14.1789 | 1.0379 | 0.299
2016-06-18 08:00 | 411.62 | 229.2867 | 182.3333 | 340.9676 | 23.4098 | -44.4717 | 57.6729 | 32.3271 | -49.5357 | 42.0727 | 253.0984 | 171.965 | 0.4 | 0.33333 | 41.162 | 466.2254 | 3.2 | 17.7695 | 1.0253 | 0.39198
2016-06-18 09:00 | 472.32 | 242.86 | 229.46 | 404.5088 | 23.4109 | -29.474 | 55.4409 | 34.5591 | -33.2485 | 28.3475 | 356.0019 | 182.145 | 0.39875 | 0.33125 | 47.0844 | 585.2313 | 3.4 | 21.6885 | 1.0116 | 0.48545
2016-06-18 10:00 | 471.7233 | 247.1167 | 224.6067 | 382.3197 | 23.4119 | -14.4762 | 54.0213 | 35.9787 | -16.4677 | 15.025 | 369.2493 | 185.3375 | 0.3975 | 0.32917 | 46.8775 | 601.4643 | 3.4 | 22.1958 | 1.0098 | 0.49804
2016-06-18 11:00 | 471.1267 | 251.3733 | 219.7533 | 369.9178 | 23.4129 | 0.52151 | 53.5544 | 36.4456 | 0.59493 | 6.4648 | 367.5656 | 188.53 | 0.39625 | 0.32708 | 46.671 | 602.7665 | 3.7 | 22.5365 | 1.0086 | 0.49853
2016-06-18 12:00 | 470.53 | 255.63 | 214.9 | 366.3876 | 23.4139 | 15.5192 | 54.0883 | 35.9117 | 17.6471 | 15.9139 | 352.3456 | 191.7225 | 0.395 | 0.325 | 46.4648 | 590.533 | 3.9 | 22.3542 | 1.0093 | 0.48872
2016-06-18 13:00 | 430.44 | 232.7467 | 197.6933 | 349.6336 | 23.4149 | 30.517 | 55.5678 | 34.4322 | 34.3996 | 29.2973 | 304.9127 | 174.56 | 0.39375 | 0.32292 | 42.3714 | 521.8442 | 3.7 | 20.0076 | 1.0175 | 0.43539
2016-06-18 14:00 | 390.35 | 209.8633 | 180.4867 | 339.1479 | 23.4159 | 45.5147 | 57.8473 | 32.1527 | 50.6484 | 43.0299 | 247.9164 | 157.3975 | 0.3925 | 0.32083 | 38.3031 | 443.617 | 3.4 | 17.263 | 1.0271 | 0.37362
2016-06-18 15:00 | 350.26 | 186.98 | 163.28 | 333.8753 | 23.4169 | 60.5125 | 60.7222 | 29.2778 | 66.3122 | 56.7697 | 182.9654 | 140.235 | 0.39125 | 0.31875 | 34.2598 | 357.4603 | 3.6 | 14.7706 | 1.0358 | 0.30361
2016-06-18 16:00 | 324.3433 | 161.5067 | 162.8367 | 370.9487 | 23.4178 | 75.5102 | 63.9616 | 26.0384 | 81.4195 | 70.3921 | 124.4838 | 121.13 | 0.39 | 0.31667 | 31.6235 | 277.2373 | 4.2 | 12.8637 | 1.0425 | 0.23699
2016-06-18 17:00 | 298.4267 | 136.0333 | 162.3933 | 421.3902 | 23.4188 | 90.5079 | 67.333 | 22.667 | 96.0688 | 83.7884 | 45.5948 | 102.025 | 0.38875 | 0.31458 | 29.0033 | 176.6232 | 4.1 | 9.6195 | 1.0538 | 0.15263
2016-06-18 18:00 | 272.51 | 110.56 | 161.95 | 487.9446 | 23.4197 | 105.5057 | 70.6157 | 19.3843 | 110.3879 | 96.814 | 0 | 82.92 | 0.3875 | 0.3125 | 26.3994 | 109.3194 | 4.4 | 7.8162 | 1.0601 | 0.095033
2016-06-18 19:00 | 237.4067 | 87.5433 | 149.8633 | 531.0553 | 23.4206 | 120.5034 | 73.6085 | 16.3915 | 124.5018 | 109.2389 | 0 | 65.6575 | 0.38625 | 0.31042 | 22.9246 | 88.5821 | 4.5 | 7.2682 | 1.0621 | 0.077145
2016-06-18 20:00 | 202.3033 | 64.5267 | 137.7767 | 574.9021 | 23.4215 | 135.5011 | 76.134 | 13.866 | 138.513 | 120.6647 | 0 | 48.395 | 0.385 | 0.30833 | 19.4717 | 67.8667 | 3.7 | 5.8208 | 1.0671 | 0.059386
2016-06-18 21:00 | 167.2 | 41.51 | 125.69 | 606.7242 | 23.4224 | 150.4989 | 78.0439 | 11.9561 | 152.4913 | 130.3812 | 0 | 31.1325 | 0.38375 | 0.30625 | 16.0407 | 47.1733 | 4.1 | 5.5742 | 1.068 | 0.041312
2016-06-18 22:00 | 158.44 | 41.11 | 117.33 | 627.6303 | 23.4233 | 165.4966 | 79.2257 | 10.7743 | 166.4718 | 137.1961 | 0 | 30.8325 | 0.3825 | 0.30417 | 15.1508 | 45.9833 | 3.8 | 5.237 | 1.0692 | 0.040314
2016-06-18 23:00 | 149.68 | 40.71 | 108.97 | 604.1487 | 23.4242 | 180.4943 | 79.6087 | 10.3913 | -179.5389 | 139.6063 | 0 | 30.5325 | 0.38125 | 0.30208 | 14.2664 | 44.7989 | 3.4 | 4.8 | 1.0707 | 0.039332
2016-06-19 | 140.92 | 40.31 | 100.61 | 535.459 | 23.425 | -164.508 | 79.17 | 10.83 | -165.55 | 136.865 | 0 | 30.2325 | 0.38 | 0.3 | 13.3874 | 43.6199 | 3.2 | 4.5631 | 1.0715 | 0.038327
2016-06-19 01:00 | 173.0467 | 48.3333 | 124.7133 | 596.6991 | 23.4259 | -149.5102 | 77.9359 | 12.0641 | -151.5704 | 129.8114 | 0 | 36.25 | 0.37875 | 0.29792 | 16.3854 | 52.6354 | 3.4 | 5.0449 | 1.0698 | 0.046175
2016-06-19 02:00 | 205.1733 | 56.3567 | 148.8167 | 614.2757 | 23.4267 | -134.5125 | 75.9798 | 14.0202 | -137.5919 | 119.9509 | 0 | 42.2675 | 0.3775 | 0.29583 | 19.3632 | 61.6307 | 3.7 | 5.626 | 1.0678 | 0.053964
2016-06-19 03:00 | 237.3 | 64.38 | 172.92 | 605.8769 | 23.4275 | -119.5148 | 73.417 | 16.583 | -123.577 | 108.4416 | 0 | 48.285 | 0.37625 | 0.29375 | 22.321 | 70.606 | 3.8 | 6.0064 | 1.0665 | 0.061746
2016-06-19 04:00 | 286.2067 | 77.9833 | 208.2233 | 620.6549 | 23.4283 | -104.517 | 70.3977 | 19.6023 | -109.4537 | 95.9675 | 0 | 58.4875 | 0.375 | 0.29167 | 26.8319 | 85.3194 | 3.5 | 6.1662 | 1.0659 | 0.074574
2016-06-19 05:00 | 335.1133 | 91.5867 | 243.5267 | 625.8591 | 23.4291 | -89.5193 | 67.101 | 22.899 | -95.1175 | 82.912 | 77.2266 | 68.69 | 0.37375 | 0.28958 | 31.3122 | 177.2288 | 4.6 | 10.1384 | 1.052 | 0.15289
2016-06-19 06:00 | 384.02 | 105.19 | 278.83 | 629.9722 | 23.4299 | -74.5216 | 63.7297 | 26.2703 | -80.4423 | 69.4976 | 220.6456 | 78.8925 | 0.3725 | 0.2875 | 35.7619 | 335.3 | 4.8 | 15.2781 | 1.034 | 0.2843
2016-06-19 07:00 | 419.7033 | 110.98 | 308.7233 | 627.0495 | 23.4307 | -59.5238 | 60.5053 | 29.4947 | -65.3012 | 55.8653 | 351.8632 | 83.235 | 0.37125 | 0.28542 | 38.9537 | 474.0519 | 5.2 | 20.0141 | 1.0175 | 0.39551
2016-06-19 08:00 | 455.3867 | 116.77 | 338.6167 | 633.0131 | 23.4315 | -44.5261 | 57.6609 | 32.3391 | -49.5985 | 42.1228 | 469.5117 | 87.5775 | 0.37 | 0.28333 | 42.1233 | 599.2125 | 5.3 | 24.0254 | 1.0034 | 0.49303
2016-06-19 09:00 | 491.07 | 122.56 | 368.51 | 649.3991 | 23.4322 | -29.5284 | 55.4265 | 34.5735 | -33.312 | 28.3998 | 571.2441 | 91.92 | 0.36875 | 0.28125 | 45.2705 | 708.4346 | 5.6 | 27.7386 | 0.99041 | 0.57535
2016-06-19 10:00 | 499.7333 | 127.9033 | 371.83 | 632.653 | 23.433 | -14.5307 | 54.0038 | 35.9962 | -16.5311 | 15.0792 | 610.8691 | 95.9275 | 0.3675 | 0.27917 | 45.913 | 752.7096 | 5.5 | 29.0222 | 0.98592 | 0.60853
2016-06-19 11:00 | 508.3967 | 133.2467 | 375.15 | 631.1903 | 23.4337 | 0.46708 | 53.5335 | 36.4665 | 0.53289 | 6.4818 | 627.1555 | 99.935 | 0.36625 | 0.27708 | 46.5501 | 773.6406 | 6.3 | 30.4763 | 0.98083 | 0.62223
2016-06-19 12:00 | 517.06 | 138.59 | 378.47 | 644.8863 | 23.4344 | 15.4648 | 54.0642 | 35.9358 | 17.5875 | 15.8747 | 620.2917 | 103.9425 | 0.365 | 0.275 | 47.1817 | 771.4159 | 5.4 | 29.5067 | 0.98423 | 0.62258
2016-06-19 13:00 | 471.73 | 129.44 | 342.29 | 604.9475 | 23.4351 | 30.4625 | 55.5409 | 34.4591 | 34.343 | 29.2502 | 527.8132 | 97.08 | 0.36375 | 0.27292 | 42.8979 | 667.7911 | 5.5 | 26.3685 | 0.99521 | 0.54497
2016-06-19 14:00 | 426.4 | 120.29 | 306.11 | 574.74 | 23.4358 | 45.4603 | 57.8183 | 32.1817 | 50.5949 | 42.9799 | 420.4759 | 90.2175 | 0.3625 | 0.27083 | 38.6425 | 549.3359 | 5.2 | 22.3667 | 1.0092 | 0.45461
2016-06-19 15:00 | 381.07 | 111.14 | 269.93 | 551.4321 | 23.4365 | 60.458 | 60.6918 | 29.3082 | 66.2615 | 56.7181 | 302.6033 | 83.355 | 0.36125 | 0.26875 | 34.4154 | 420.3737 | 4.4 | 17.5367 | 1.0261 | 0.35371
2016-06-19 16:00 | 305.4733 | 111.8333 | 193.64 | 440.6335 | 23.4372 | 75.4557 | 63.9307 | 26.0693 | 81.3707 | 70.3394 | 148.2504 | 83.875 | 0.36 | 0.26667 | 27.4926 | 259.618 | 4 | 12.1131 | 1.0451 | 0.22249
2016-06-19 17:00 | 229.8767 | 112.5267 | 117.35 | 304.1183 | 23.4378 | 90.4534 | 67.3023 | 22.6977 | 96.0213 | 83.7351 | 33.1871 | 84.395 | 0.35875 | 0.26458 | 20.6171 | 138.1992 | 3.7 | 8.0187 | 1.0594 | 0.12006
2016-06-19 18:00 | 154.28 | 113.22 | 41.06 | 123.5286 | 23.4385 | 105.4512 | 70.5859 | 19.4141 | 110.3409 | 96.7606 | 0 | 84.915 | 0.3575 | 0.2625 | 13.7888 | 98.7038 | 3.8 | 6.8845 | 1.0634 | 0.086069
2016-06-19 19:00 | 147.28 | 102.2433 | 45.0367 | 159.3249 | 23.4391 | 120.4489 | 73.5803 | 16.4197 | 124.4546 | 109.1862 | 0 | 76.6825 | 0.35625 | 0.26042 | 13.1171 | 89.7996 | 3.3 | 6.1062 | 1.0661 | 0.078505
2016-06-19 20:00 | 140.28 | 91.2667 | 49.0133 | 204.1417 | 23.4397 | 135.4466 | 76.1079 | 13.8921 | 138.4652 | 120.6143 | 0 | 68.45 | 0.355 | 0.25833 | 12.4498 | 80.8999 | 3 | 5.5281 | 1.0682 | 0.070859
2016-06-19 21:00 | 133.28 | 80.29 | 52.99 | 255.2966 | 23.4403 | 150.4443 | 78.0205 | 11.9795 | 152.4426 | 130.3361 | 0 | 60.2175 | 0.35375 | 0.25625 | 11.7869 | 72.0045 | 2.9 | 5.1501 | 1.0695 | 0.063146
2016-06-19 22:00 | 134.4567 | 66.1433 | 68.3133 | 364.7417 | 23.4409 | 165.4421 | 79.2052 | 10.7948 | 166.422 | 137.1619 | 0 | 49.6075 | 0.3525 | 0.25417 | 11.849 | 61.4565 | 2.9 | 4.8205 | 1.0706 | 0.053954
2016-06-19 23:00 | 135.6333 | 51.9967 | 83.6367 | 462.9364 | 23.4415 | 180.4398 | 79.5915 | 10.4085 | -179.5898 | 139.5895 | 0 | 38.9975 | 0.35125 | 0.25208 | 11.9103 | 50.9078 | 3.4 | 4.9909 | 1.07 | 0.044668
2016-06-20 | 136.81 | 37.85 | 98.96 | 526.0077 | 23.4421 | -164.5625 | 79.1561 | 10.8439 | -165.6019 | 136.8679 | 0 | 28.3875 | 0.35 | 0.25 | 11.9709 | 40.3584 | 3.1 | 4.3612 | 1.0722 | 0.035484
2016-06-20 01:00 | 131.1367 | 43.77 | 87.3667 | 417.6431 | 23.4426 | -149.5648 | 77.9251 | 12.0749 | -151.6233 | 129.83 | 0 | 32.8275 | 0.34946 | 0.24911 | 11.4569 | 44.2844 | 3 | 4.3839 | 1.0722 | 0.038933
2016-06-20 02:00 | 125.4633 | 49.69 | 75.7733 | 312.5983 | 23.4432 | -134.567 | 75.9719 | 14.0281 | -137.6456 | 119.9801 | 0 | 37.2675 | 0.34893 | 0.24821 | 10.9444 | 48.2119 | 2.7 | 4.2066 | 1.0728 | 0.042411
2016-06-20 03:00 | 119.79 | 55.61 | 64.18 | 224.8 | 23.4437 | -119.5693 | 73.4114 | 16.5886 | -123.6316 | 108.4777 | 0 | 41.7075 | 0.34839 | 0.24732 | 10.4335 | 52.141 | 2.4 | 4.0294 | 1.0734 | 0.045894
2016-06-20 04:00 | 143.54 | 74.0667 | 69.4733 | 207.041 | 23.4443 | -104.5716 | 70.3938 | 19.6062 | -109.5093 | 96.0083 | 0 | 55.55 | 0.34786 | 0.24643 | 12.4829 | 68.0329 | 2.4 | 4.526 | 1.0717 | 0.059785
2016-06-20 05:00 | 167.29 | 92.5233 | 74.7667 | 192.126 | 23.4448 | -89.5739 | 67.0981 | 22.9019 | -95.1744 | 82.9561 | 23.5603 | 69.3925 | 0.34732 | 0.24554 | 14.5259 | 107.4787 | 2.7 | 6.0587 | 1.0663 | 0.093975
2016-06-20 06:00 | 191.04 | 110.98 | 80.06 | 180.8653 | 23.4453 | -74.5761 | 63.7269 | 26.2731 | -80.5007 | 69.5441 | 63.2098 | 83.235 | 0.34679 | 0.24464 | 16.5625 | 163.0073 | 3 | 8.094 | 1.0592 | 0.14158
2016-06-20 07:00 | 225.05 | 121.6433 | 103.4067 | 210.0072 | 23.4458 | -59.5784 | 60.5018 | 29.4982 | -65.3611 | 55.9138 | 117.6965 | 91.2325 | 0.34625 | 0.24375 | 19.4809 | 228.4099 | 3.2 | 10.3378 | 1.0513 | 0.19691
2016-06-20 08:00 | 259.06 | 132.3067 | 126.7533 | 236.9204 | 23.4462 | -44.5807 | 57.6558 | 32.3442 | -49.66 | 42.1729 | 175.5869 | 99.23 | 0.34571 | 0.24286 | 22.3902 | 297.2071 | 3.2 | 12.4877 | 1.0438 | 0.25438
2016-06-20 09:00 | 293.07 | 142.97 | 150.1 | 264.4599 | 23.4467 | -29.583 | 55.4189 | 34.5811 | -33.3747 | 28.4513 | 232.5189 | 107.2275 | 0.34518 | 0.24196 | 25.2904 | 365.0368 | 3.2 | 14.6074 | 1.0364 | 0.31022
2016-06-20 10:00 | 279.16 | 144.5633 | 134.5967 | 228.952 | 23.4472 | -14.5852 | 53.9932 | 36.0068 | -16.5941 | 15.1309 | 221.0147 | 108.4225 | 0.34464 | 0.24107 | 24.0526 | 353.4899 | 3.5 | 14.5466 | 1.0366 | 0.30047
2016-06-20 11:00 | 265.25 | 146.1567 | 119.0933 | 200.3084 | 23.4476 | 0.41249 | 53.5194 | 36.4806 | 0.47064 | 6.4925 | 199.0238 | 109.6175 | 0.34411 | 0.24018 | 22.8186 | 331.4599 | 3.2 | 13.5581 | 1.04 | 0.28268
2016-06-20 12:00 | 251.34 | 147.75 | 103.59 | 176.4366 | 23.448 | 15.4102 | 54.0469 | 35.9531 | 17.527 | 15.833 | 169.7428 | 110.8125 | 0.34357 | 0.23929 | 21.5883 | 302.1436 | 3.5 | 12.942 | 1.0422 | 0.25821
2016-06-20 13:00 | 243.37 | 129.79 | 113.58 | 200.6333 | 23.4484 | 30.4079 | 55.5208 | 34.4792 | 34.285 | 29.2022 | 175.1335 | 97.3425 | 0.34304 | 0.23839 | 20.8712 | 293.3472 | 3.3 | 12.4671 | 1.0439 | 0.2511
2016-06-20 14:00 | 235.4 | 111.83 | 123.57 | 231.8666 | 23.4489 | 45.4057 | 57.796 | 32.204 | 50.5397 | 42.9298 | 169.7702 | 83.8725 | 0.3425 | 0.2375 | 20.1561 | 273.7988 | 3.2 | 11.7562 | 1.0464 | 0.23492
2016-06-20 15:00 | 227.43 | 93.87 | 133.56 | 272.6449 | 23.4492 | 60.4034 | 60.6681 | 29.3319 | 66.2088 | 56.667 | 149.8195 | 70.4025 | 0.34196 | 0.23661 | 19.4432 | 239.6653 | 3.4 | 10.8895 | 1.0494 | 0.20623
2016-06-20 16:00 | 212.67 | 101.3367 | 111.3333 | 253.1231 | 23.4496 | 75.4011 | 63.9064 | 26.0936 | 81.32 | 70.2878 | 85.3772 | 76.0025 | 0.34143 | 0.23571 | 18.1529 | 179.5326 | 3.4 | 9.0104 | 1.056 | 0.15546
2016-06-20 17:00 | 197.91 | 108.8033 | 89.1067 | 230.6927 | 23.45 | 90.3988 | 67.2782 | 22.7218 | 95.9719 | 83.6836 | 25.3807 | 81.6025 | 0.34089 | 0.23482 | 16.8665 | 123.8497 | 3.5 | 7.3703 | 1.0617 | 0.10782
2016-06-20 18:00 | 183.15 | 116.27 | 66.88 | 200.9775 | 23.4504 | 105.3965 | 70.5628 | 19.4372 | 110.2921 | 96.7097 | 0 | 87.2025 | 0.34036 | 0.23393 | 15.5841 | 102.7866 | 3.2 | 6.4121 | 1.0651 | 0.089768
2016-06-20 19:00 | 157.8467 | 97.9933 | 59.8533 | 211.4718 | 23.4507 | 120.3943 | 73.5587 | 16.4413 | 124.4059 | 109.1368 | 0 | 73.495 | 0.33982 | 0.23304 | 13.4099 | 86.9049 | 3.5 | 6.2158 | 1.0657 | 0.075947
2016-06-20 20:00 | 132.5433 | 79.7167 | 52.8267 | 219.7244 | 23.451 | 135.392 | 76.0885 | 13.9115 | 138.4162 | 120.5682 | 0 | 59.7875 | 0.33929 | 0.23214 | 11.2425 | 71.03 | 3.6 | 5.8197 | 1.0671 | 0.062155
2016-06-20 21:00 | 107.24 | 61.44 | 45.8 | 220.3542 | 23.4514 | 150.3897 | 78.0038 | 11.9962 | 152.393 | 130.2964 | 0 | 46.08 | 0.33875 | 0.23125 | 9.0819 | 55.1619 | 3.3 | 5.0238 | 1.0699 | 0.048395
2016-06-20 22:00 | 111.6733 | 52.4633 | 59.21 | 315.7428 | 23.4517 | 165.3874 | 79.1916 | 10.8084 | 166.3717 | 137.1341 | 0 | 39.3475 | 0.33821 | 0.23036 | 9.4424 | 48.7899 | 3 | 4.5247 | 1.0717 | 0.042875
2016-06-20 23:00 | 116.1067 | 43.4867 | 72.62 | 401.562 | 23.452 | 180.3852 | 79.5811 | 10.4189 | -179.6407 | 139.5796 | 0 | 32.615 | 0.33768 | 0.22946 | 9.8017 | 42.4167 | 2.9 | 4.2255 | 1.0727 | 0.037311
2016-06-21 | 120.54 | 34.51 | 86.03 | 456.9843 | 23.4523 | -164.6171 | 79.149 | 10.851 | -165.6535 | 136.8771 | 0 | 25.8825 | 0.33714 | 0.22857 | 10.1598 | 36.0423 | 2.8 | 3.9263 | 1.0738 | 0.031735
2016-06-21 01:00 | 129.3833 | 39.2867 | 90.0967 | 430.5538 | 23.4525 | -149.6194 | 77.9211 | 12.0789 | -151.6754 | 129.8539 | 0 | 29.465 | 0.33661 | 0.22768 | 10.8878 | 40.3528 | 2.8 | 4.061 | 1.0733 | 0.035514
2016-06-21 02:00 | 138.2267 | 44.0633 | 94.1633 | 388.4331 | 23.4528 | -134.6217 | 75.9707 | 14.0293 | -137.6982 | 120.0136 | 0 | 33.0475 | 0.33607 | 0.22679 | 11.6135 | 44.661 | 2.8 | 4.1957 | 1.0728 | 0.039289
2016-06-21 03:00 | 147.07 | 48.84 | 98.23 | 344.088 | 23.4531 | -119.6239 | 73.4125 | 16.5875 | -123.6848 | 108.5172 | 0 | 36.63 | 0.33554 | 0.22589 | 12.3368 | 48.9668 | 3.2 | 4.7302 | 1.0709 | 0.043001
2016-06-21 04:00 | 189.0467 | 64.3833 | 124.6633 | 371.567 | 23.4533 | -104.6262 | 70.3966 | 19.6034 | -109.5633 | 96.0517 | 0 | 48.2875 | 0.335 | 0.225 | 15.8327 | 64.1202 | 3.8 | 5.8038 | 1.0672 | 0.056111
2016-06-21 05:00 | 231.0233 | 79.9267 | 151.0967 | 388.3301 | 23.4535 | -89.6285 | 67.1019 | 22.8981 | -95.2295 | 83.0021 | 47.3115 | 59.945 | 0.33446 | 0.22411 | 19.3173 | 126.5738 | 3.6 | 7.5554 | 1.0611 | 0.11013
2016-06-21 06:00 | 273 | 95.47 | 177.53 | 401.118 | 23.4537 | -74.6308 | 63.7309 | 26.2691 | -80.5572 | 69.592 | 139.8712 | 71.6025 | 0.33393 | 0.22321 | 22.7906 | 234.2643 | 4.3 | 11.6208 | 1.0468 | 0.20109
2016-06-21 07:00 | 341.63 | 103.5067 | 238.1233 | 483.6497 | 23.4539 | -59.6331 | 60.5051 | 29.4949 | -65.4194 | 55.9629 | 270.7128 | 77.63 | 0.33339 | 0.22232 | 28.4743 | 376.8171 | 4.2 | 15.9755 | 1.0316 | 0.31875
2016-06-21 08:00 | 410.26 | 111.5433 | 298.7167 | 558.3702 | 23.4541 | -44.6353 | 57.6575 | 32.3425 | -49.7201 | 42.2231 | 413.492 | 83.6575 | 0.33286 | 0.22143 | 34.1395 | 531.289 | 3.5 | 20.1028 | 1.0171 | 0.44312
2016-06-21 09:00 | 478.89 | 119.58 | 359.31 | 633.0531 | 23.4543 | -29.6376 | 55.4182 | 34.5818 | -33.4363 | 28.502 | 556.3271 | 89.685 | 0.33232 | 0.22054 | 39.7864 | 685.7985 | 3.6 | 25.0312 | 0.99989 | 0.56229
2016-06-21 10:00 | 461.7933 | 128.1167 | 333.6767 | 567.5402 | 23.4545 | -14.6399 | 53.9894 | 36.0106 | -16.6565 | 15.1799 | 547.7377 | 96.0875 | 0.33179 | 0.21964 | 38.3041 | 682.1293 | 3.9 | 25.2165 | 0.99924 | 0.55892
2016-06-21 11:00 | 444.6967 | 136.6533 | 308.0433 | 518.0247 | 23.4546 | 0.35783 | 53.5123 | 36.4877 | 0.4083 | 6.4966 | 514.6982 | 102.49 | 0.33125 | 0.21875 | 36.8264 | 654.0147 | 3.9 | 24.338 | 1.0023 | 0.53753
2016-06-21 12:00 | 427.6 | 145.19 | 282.41 | 480.8858 | 23.4548 | 15.3556 | 54.0365 | 35.9635 | 17.4658 | 15.7887 | 462.7427 | 108.8925 | 0.33071 | 0.21786 | 35.3534 | 606.9886 | 3.8 | 22.7684 | 1.0078 | 0.50162
2016-06-21 13:00 | 396.69 | 130.3667 | 266.3233 | 470.2872 | 23.4549 | 30.3533 | 55.5074 | 34.4926 | 34.2259 | 29.1532 | 410.7113 | 97.775 | 0.33018 | 0.21696 | 32.7446 | 541.231 | 4.6 | 21.5135 | 1.0122 | 0.44923
2016-06-21 14:00 | 365.78 | 115.5433 | 250.2367 | 469.3413 | 23.455 | 45.351 | 57.7804 | 32.2196 | 50.4829 | 42.8796 | 343.9263 | 86.6575 | 0.32964 | 0.21607 | 30.1442 | 460.7279 | 5.6 | 19.9977 | 1.0175 | 0.38441
2016-06-21 15:00 | 334.87 | 100.72 | 234.15 | 477.7336 | 23.4551 | 60.3487 | 60.6511 | 29.3489 | 66.1542 | 56.6165 | 262.8681 | 75.54 | 0.32911 | 0.21518 | 27.552 | 365.9602 | 5.7 | 17.1363 | 1.0275 | 0.30835
2016-06-21 16:00 | 281.7833 | 109.44 | 172.3433 | 391.5872 | 23.4552 | 75.3464 | 63.8888 | 26.1112 | 81.2674 | 70.2375 | 132.4042 | 82.08 | 0.32857 | 0.21429 | 23.1465 | 237.6307 | 5.7 | 13.126 | 1.0416 | 0.20296
2016-06-21 17:00 | 228.6967 | 118.16 | 110.5367 | 285.9664 | 23.4553 | 90.3442 | 67.2608 | 22.7392 | 95.9206 | 83.6339 | 31.7084 | 88.62 | 0.32804 | 0.21339 | 18.7552 | 139.0836 | 5.8 | 10.1464 | 1.052 | 0.11998
2016-06-21 18:00 | 175.61 | 126.88 | 48.73 | 146.3169 | 23.4554 | 105.3419 | 70.5463 | 19.4537 | 110.2416 | 96.6613 | 0 | 95.16 | 0.3275 | 0.2125 | 14.3781 | 109.5381 | 5.2 | 8.6231 | 1.0573 | 0.09497
2016-06-21 19:00 | 139.7533 | 105.1467 | 34.6067 | 122.1641 | 23.4554 | 120.3396 | 73.5439 | 16.4561 | 124.3557 | 109.0907 | 0 | 78.86 | 0.32696 | 0.21161 | 11.4236 | 90.2836 | 4.5 | 7.3214 | 1.0619 | 0.078613
2016-06-21 20:00 | 103.8967 | 83.4133 | 20.4833 | 85.1218 | 23.4555 | 135.3373 | 76.076 | 13.924 | 138.366 | 120.5263 | 0 | 62.56 | 0.32643 | 0.21071 | 8.4787 | 71.0387 | 3.9 | 6.12 | 1.0661 | 0.062101
2016-06-21 21:00 | 68.04 | 61.68 | 6.36 | 30.5747 | 23.4555 | 150.3351 | 77.9939 | 12.0061 | 152.3425 | 130.2621 | 0 | 46.26 | 0.32589 | 0.20982 | 5.5434 | 51.8034 | 3.6 | 5.2189 | 1.0692 | 0.04542
2016-06-21 22:00 | 64.4067 | 60.1667 | 4.24 | 22.5962 | 23.4556 | 165.3328 | 79.1848 | 10.8152 | 166.321 | 137.1127 | 0 | 45.125 | 0.32536 | 0.20893 | 5.2388 | 50.3638 | 3.8 | 5.3739 | 1.0687 | 0.044135
2016-06-21 23:00 | 60.7733 | 58.6533 | 2.12 | 11.7189 | 23.4556 | 180.3305 | 79.5776 | 10.4224 | -179.6917 | 139.5765 | 0 | 43.99 | 0.32482 | 0.20804 | 4.9351 | 48.9251 | 3.6 | 5.1289 | 1.0695 | 0.042909
2016-06-22 | 57.14 | 57.14 | 0 | 0 | 23.4556 | -164.6718 | 79.1487 | 10.8513 | -165.7047 | 136.8926 | 0 | 42.855 | 0.32429 | 0.20714 | 4.6324 | 47.4874 | 3.2 | 4.684 | 1.0711 | 0.041709
2016-06-22 01:00 | 71.9767 | 71.9767 | 0 | 0 | 23.4556 | -149.674 | 77.924 | 12.076 | -151.7266 | 129.8831 | 0 | 53.9825 | 0.32375 | 0.20625 | 5.8256 | 59.8081 | 3.5 | 5.369 | 1.0687 | 0.052412
2016-06-22 02:00 | 86.8133 | 86.8133 | 0 | 0 | 23.4555 | -134.6763 | 75.9763 | 14.0237 | -137.7496 | 120.0513 | 0 | 65.11 | 0.32321 | 0.20536 | 7.0148 | 72.1248 | 3.2 | 5.4539 | 1.0684 | 0.063188
2016-06-22 03:00 | 101.65 | 101.65 | 0 | 0 | 23.4555 | -119.6786 | 73.4204 | 16.5796 | -123.7365 | 108.56 | 0 | 76.2375 | 0.32268 | 0.20446 | 8.2001 | 84.4376 | 3.5 | 6.1387 | 1.066 | 0.07381
2016-06-22 04:00 | 127.9067 | 127.85 | 0.056667 | 0.16898 | 23.4555 | -104.6809 | 70.4061 | 19.5939 | -109.6156 | 96.0975 | 0 | 95.8875 | 0.32214 | 0.20357 | 10.3011 | 106.1886 | 3.8 | 7.1184 | 1.0626 | 0.092524
2016-06-22 05:00 | 154.1633 | 154.05 | 0.11333 | 0.2914 | 23.4554 | -89.6831 | 67.1124 | 22.8876 | -95.2827 | 83.0499 | 0.035261 | 115.5375 | 0.32161 | 0.20268 | 12.395 | 127.9678 | 3.4 | 7.399 | 1.0616 | 0.1114
2016-06-22 06:00 | 180.42 | 180.25 | 0.17 | 0.38425 | 23.4553 | -74.6854 | 63.7415 | 26.2585 | -80.6118 | 69.641 | 0.13368 | 135.1875 | 0.32107 | 0.20179 | 14.4819 | 149.8031 | 4.1 | 8.7813 | 1.0568 | 0.12981
2016-06-22 07:00 | 218.0833 | 215.6433 | 2.44 | 4.9574 | 23.4552 | -59.6877 | 60.515 | 29.485 | -65.4758 | 56.0127 | 2.7712 | 161.7325 | 0.32054 | 0.20089 | 17.4759 | 181.9796 | 4.8 | 10.4869 | 1.0508 | 0.1568
2016-06-22 08:00 | 255.7467 | 251.0367 | 4.71 | 8.8061 | 23.4551 | -44.69 | 57.6659 | 32.3341 | -49.7786 | 42.2732 | 6.516 | 188.2775 | 0.32 | 0.2 | 20.4597 | 215.2533 | 5.1 | 11.8267 | 1.0461 | 0.18465
2016-06-22 09:00 | 293.41 | 286.43 | 6.98 | 12.2997 | 23.455 | -29.6922 | 55.4242 | 34.5758 | -33.4967 | 28.5518 | 10.8038 | 214.8225 | 0.31946 | 0.19911 | 23.4335 | 249.0598 | 4.4 | 12.1831 | 1.0449 | 0.21339
2016-06-22 10:00 | 288.9033 | 278.75 | 10.1533 | 17.2708 | 23.4549 | -14.6945 | 53.9925 | 36.0075 | -16.7184 | 15.2264 | 16.6645 | 209.0625 | 0.31893 | 0.19821 | 23.0349 | 248.7619 | 4.7 | 12.4738 | 1.0438 | 0.21293
2016-06-22 11:00 | 284.3967 | 271.07 | 13.3267 | 22.4108 | 23.4548 | 0.30321 | 53.5121 | 36.4879 | 0.34598 | 6.4943 | 22.267 | 203.3025 | 0.31839 | 0.19732 | 22.6375 | 248.207 | 4.9 | 12.6565 | 1.0432 | 0.21232
2016-06-22 12:00 | 279.89 | 263.39 | 16.5 | 28.0937 | 23.4546 | 15.3009 | 54.0329 | 35.9671 | 17.4041 | 15.7421 | 27.04 | 197.5425 | 0.31786 | 0.19643 | 22.2413 | 246.8237 | 4.7 | 12.4132 | 1.0441 | 0.21131
2016-06-22 13:00 | 238.4433 | 227.25 | 11.1933 | 19.7625 | 23.4545 | 30.2987 | 55.5009 | 34.4991 | 34.1656 | 29.1034 | 17.2673 | 170.4375 | 0.31732 | 0.19554 | 18.9158 | 206.6206 | 4.5 | 10.9569 | 1.0492 | 0.17776
2016-06-22 14:00 | 196.9967 | 191.11 | 5.8867 | 11.0383 | 23.4543 | 45.2964 | 57.7716 | 32.2284 | 50.4246 | 42.8295 | 8.0952 | 143.3325 | 0.31679 | 0.19464 | 15.6014 | 167.0292 | 4.9 | 10.1197 | 1.0521 | 0.1441
2016-06-22 15:00 | 155.55 | 154.97 | 0.58 | 1.183 | 23.4541 | 60.2941 | 60.6408 | 29.3592 | 66.098 | 56.5667 | 0.65179 | 116.2275 | 0.31625 | 0.19375 | 12.2982 | 129.1775 | 4.4 | 8.4368 | 1.058 | 0.11207
2016-06-22 16:00 | 135.99 | 135.28 | 0.71 | 1.6126 | 23.454 | 75.2918 | 63.8779 | 26.1221 | 81.2129 | 70.1885 | 0.54655 | 101.46 | 0.31571 | 0.19286 | 10.7335 | 112.74 | 4.3 | 7.8231 | 1.0601 | 0.098005
2016-06-22 17:00 | 116.43 | 115.59 | 0.84 | 2.1722 | 23.4538 | 90.2896 | 67.2501 | 22.7499 | 95.8675 | 83.5861 | 0.24265 | 86.6925 | 0.31518 | 0.19196 | 9.1741 | 96.1092 | 4.3 | 7.3034 | 1.0619 | 0.083691
2016-06-22 18:00 | 96.87 | 95.9 | 0.97 | 2.9111 | 23.4535 | 105.2873 | 70.5366 | 19.4634 | 110.1894 | 96.6154 | 0 | 71.925 | 0.31464 | 0.19107 | 7.6199 | 79.5449 | 4.3 | 6.7858 | 1.0637 | 0.069385
2016-06-22 19:00 | 85.51 | 84.26 | 1.25 | 4.4105 | 23.4533 | 120.285 | 73.5358 | 16.4642 | 124.3042 | 109.048 | 0 | 63.195 | 0.31411 | 0.19018 | 6.7148 | 69.9098 | 4 | 6.1847 | 1.0659 | 0.061101
2016-06-22 20:00 | 74.15 | 72.62 | 1.53 | 6.3556 | 23.4531 | 135.2828 | 76.0702 | 13.9298 | 138.3147 | 120.4887 | 0 | 54.465 | 0.31357 | 0.18929 | 5.8128 | 60.2778 | 4.4 | 6.2837 | 1.0655 | 0.052666
2016-06-22 21:00 | 62.79 | 60.98 | 1.81 | 8.6991 | 23.4528 | 150.2805 | 77.9909 | 12.0091 | 152.2914 | 130.2331 | 0 | 45.735 | 0.31304 | 0.18839 | 4.9139 | 50.6489 | 4.6 | 6.1828 | 1.0659 | 0.044267
2016-06-22 22:00 | 76.95 | 63.21 | 13.74 | 73.2249 | 23.4526 | 165.2782 | 79.1848 | 10.8152 | 166.2699 | 137.0976 | 0 | 47.4075 | 0.3125 | 0.1875 | 6.0117 | 53.4192 | 4.8 | 6.4694 | 1.0649 | 0.046645
2016-06-22 23:00 | 91.11 | 65.44 | 25.67 | 141.9433 | 23.4523 | 180.2759 | 79.5809 | 10.4191 | -179.7426 | 139.5801 | 0 | 49.08 | 0.31196 | 0.18661 | 7.1058 | 56.1858 | 4.1 | 5.8558 | 1.067 | 0.049159
2016-06-23 | 105.27 | 67.67 | 37.6 | 199.8436 | 23.452 | -164.7263 | 79.1553 | 10.8447 | -165.7553 | 136.9144 | 0 | 50.7525 | 0.31143 | 0.18571 | 8.196 | 58.9485 | 3.8 | 5.6421 | 1.0678 | 0.051613
2016-06-23 01:00 | 130.01 | 88.7033 | 41.3067 | 197.5976 | 23.4517 | -149.7286 | 77.9336 | 12.0664 | -151.777 | 129.9176 | 0 | 66.5275 | 0.31089 | 0.18482 | 10.1048 | 76.6323 | 4.5 | 6.8948 | 1.0634 | 0.06682
2016-06-23 02:00 | 154.75 | 109.7367 | 45.0133 | 185.9176 | 23.4514 | -134.7309 | 75.9886 | 14.0114 | -137.7998 | 120.0932 | 0 | 82.3025 | 0.31036 | 0.18393 | 12.0069 | 94.3094 | 3.6 | 6.5472 | 1.0646 | 0.082328
2016-06-23 03:00 | 179.49 | 130.77 | 48.72 | 170.8848 | 23.4511 | -119.7331 | 73.4349 | 16.5651 | -123.7867 | 108.606 | 0 | 98.0775 | 0.30982 | 0.18304 | 13.9025 | 111.98 | 3.8 | 7.2994 | 1.062 | 0.097512
2016-06-23 04:00 | 217.26 | 152.0767 | 65.1833 | 194.5279 | 23.4507 | -104.7354 | 70.4223 | 19.5777 | -109.6661 | 96.1458 | 0 | 114.0575 | 0.30929 | 0.18214 | 16.7989 | 130.8564 | 4 | 8.0893 | 1.0592 | 0.11365
2016-06-23 05:00 | 255.03 | 173.3833 | 81.6467 | 210.0774 | 23.4504 | -89.7377 | 67.1295 | 22.8705 | -95.334 | 83.0994 | 25.2401 | 130.0375 | 0.30875 | 0.18125 | 19.6851 | 174.9627 | 4.4 | 9.8676 | 1.053 | 0.15107
2016-06-23 06:00 | 292.8 | 194.69 | 98.11 | 221.8922 | 23.45 | -74.74 | 63.7588 | 26.2412 | -80.6645 | 69.6912 | 77.0143 | 146.0175 | 0.30821 | 0.18036 | 22.5613 | 245.5931 | 4.1 | 11.7748 | 1.0463 | 0.21071
2016-06-23 07:00 | 322.7933 | 229.2733 | 93.52 | 190.1033 | 23.4497 | -59.7422 | 60.5316 | 29.4684 | -65.5304 | 56.0631 | 106.1309 | 171.955 | 0.30768 | 0.17946 | 24.8291 | 302.915 | 3.9 | 13.3661 | 1.0407 | 0.2585
2016-06-23 08:00 | 352.7867 | 263.8567 | 88.93 | 166.3386 | 23.4493 | -44.7445 | 57.681 | 32.319 | -49.8354 | 42.3232 | 122.9839 | 197.8925 | 0.30714 | 0.17857 | 27.089 | 347.9653 | 4.3 | 15.1739 | 1.0344 | 0.29514
2016-06-23 09:00 | 382.78 | 298.44 | 84.34 | 148.6664 | 23.4489 | -29.7468 | 55.4371 | 34.5629 | -33.5559 | 28.6006 | 130.5259 | 223.83 | 0.30661 | 0.17768 | 29.3408 | 383.6966 | 4 | 15.9905 | 1.0315 | 0.32455
2016-06-23 10:00 | 341.8133 | 281.1733 | 60.64 | 103.173 | 23.4485 | -14.749 | 54.0025 | 35.9975 | -16.7795 | 15.2701 | 99.5305 | 210.88 | 0.30607 | 0.17679 | 26.1548 | 336.5653 | 4.3 | 14.8177 | 1.0356 | 0.28582
2016-06-23 11:00 | 300.8467 | 263.9067 | 36.94 | 62.13 | 23.4481 | 0.24871 | 53.5187 | 36.4813 | 0.28378 | 6.4856 | 61.7324 | 197.93 | 0.30554 | 0.17589 | 22.9799 | 282.6422 | 4.2 | 13.0326 | 1.0419 | 0.24147
2016-06-23 12:00 | 259.88 | 246.64 | 13.24 | 22.5448 | 23.4476 | 15.2464 | 54.0362 | 35.9638 | 17.3419 | 15.693 | 21.7045 | 184.98 | 0.305 | 0.175 | 19.8159 | 226.5003 | 3.3 | 10.3781 | 1.0512 | 0.19524
2016-06-23 13:00 | 240.8067 | 226.9767 | 13.83 | 24.4179 | 23.4472 | 30.2442 | 55.5012 | 34.4988 | 34.1043 | 29.0529 | 21.3454 | 170.2325 | 0.30446 | 0.17411 | 18.3293 | 209.9072 | 3.7 | 10.2596 | 1.0516 | 0.181
2016-06-23 14:00 | 221.7333 | 207.3133 | 14.42 | 27.0379 | 23.4467 | 45.2419 | 57.7696 | 32.2304 | 50.3649 | 42.7795 | 19.8451 | 155.485 | 0.30393 | 0.17321 | 16.8478 | 192.1778 | 4.2 | 10.2056 | 1.0518 | 0.16575
2016-06-23 15:00 | 202.66 | 187.65 | 15.01 | 30.6116 | 23.4463 | 60.2396 | 60.6372 | 29.3628 | 66.0401 | 56.5177 | 16.8878 | 140.7375 | 0.30339 | 0.17232 | 15.3714 | 172.9966 | 3.5 | 8.9061 | 1.0563 | 0.14985
2016-06-23 16:00 | 182.41 | 172.1367 | 10.2733 | 23.3298 | 23.4458 | 75.2374 | 63.8736 | 26.1264 | 81.1567 | 70.1408 | 7.9254 | 129.1025 | 0.30286 | 0.17143 | 13.811 | 150.8389 | 3.7 | 8.4137 | 1.0581 | 0.13087
2016-06-23 17:00 | 162.16 | 156.6233 | 5.5367 | 14.315 | 23.4453 | 90.2351 | 67.246 | 22.754 | 95.8127 | 83.5403 | 1.6105 | 117.4675 | 0.30232 | 0.17054 | 12.2561 | 131.3341 | 3.3 | 7.4042 | 1.0616 | 0.11433
2016-06-23 18:00 | 141.91 | 141.11 | 0.8 | 2.4006 | 23.4448 | 105.2328 | 70.5336 | 19.4664 | 110.1358 | 96.5723 | 0 | 105.8325 | 0.30179 | 0.16964 | 10.7066 | 116.5391 | 3.9 | 7.5418 | 1.0611 | 0.1014
2016-06-23 19:00 | 125.1 | 124.5667 | 0.53333 | 1.8817 | 23.4443 | 120.2306 | 73.5345 | 16.4655 | 124.2512 | 109.0087 | 0 | 93.425 | 0.30125 | 0.16875 | 9.4216 | 102.8466 | 5.1 | 8.314 | 1.0584 | 0.089259
2016-06-23 20:00 | 108.29 | 108.0233 | 0.26667 | 1.1078 | 23.4438 | 135.2283 | 76.0712 | 13.9288 | 138.2624 | 120.4555 | 0 | 81.0175 | 0.30071 | 0.16786 | 8.1411 | 89.1586 | 5.2 | 7.9862 | 1.0595 | 0.077464
2016-06-23 21:00 | 91.48 | 91.48 | 0 | 0 | 23.4432 | 150.2261 | 77.9947 | 12.0053 | 152.2395 | 130.2096 | 0 | 68.61 | 0.30018 | 0.16696 | 6.8651 | 75.4751 | 5.3 | 7.6586 | 1.0607 | 0.065646
2016-06-23 22:00 | 77.9267 | 76.7533 | 1.1733 | 6.257 | 23.4427 | 165.2238 | 79.1918 | 10.8082 | 166.2186 | 137.089 | 0 | 57.565 | 0.29964 | 0.16607 | 5.8375 | 63.4025 | 5.3 | 7.2813 | 1.062 | 0.055214
2016-06-23 23:00 | 64.3733 | 62.0267 | 2.3467 | 12.9886 | 23.4421 | 180.2215 | 79.5911 | 10.4089 | -179.7934 | 139.5906 | 0 | 46.52 | 0.29911 | 0.16518 | 4.8136 | 51.3336 | 4.2 | 5.8042 | 1.0672 | 0.044922
2016-06-24 | 50.82 | 47.3 | 3.52 | 18.7317 | 23.4416 | -164.7807 | 79.1688 | 10.8312 | -165.8054 | 136.9425 | 0 | 35.475 | 0.29857 | 0.16429 | 3.7933 | 39.2683 | 4.5 | 5.7271 | 1.0675 | 0.034372
2016-06-24 01:00 | 60.7367 | 58 | 2.7367 | 13.1089 | 23.441 | -149.783 | 77.9501 | 12.0499 | -151.8264 | 129.9573 | 0 | 43.5 | 0.29804 | 0.16339 | 4.5254 | 48.0254 | 4.2 | 5.7008 | 1.0675 | 0.042041
2016-06-24 02:00 | 70.6533 | 68.7 | 1.9533 | 8.0786 | 23.4404 | -134.7853 | 76.0077 | 13.9923 | -137.8486 | 120.1392 | 0 | 51.525 | 0.2975 | 0.1625 | 5.2548 | 56.7798 | 3.9 | 5.6744 | 1.0676 | 0.049709
2016-06-24 03:00 | 80.57 | 79.4 | 1.17 | 4.1089 | 23.4398 | -119.7875 | 73.4562 | 16.5438 | -123.8352 | 108.6552 | 0 | 59.55 | 0.29696 | 0.16161 | 5.9816 | 65.5316 | 4.3 | 6.3479 | 1.0653 | 0.057244
2016-06-24 04:00 | 101.8233 | 99.15 | 2.6733 | 7.987 | 23.4392 | -104.7898 | 70.4451 | 19.5549 | -109.7148 | 96.1965 | 0 | 74.3625 | 0.29643 | 0.16071 | 7.5458 | 81.9083 | 4.8 | 7.3596 | 1.0617 | 0.071312
2016-06-24 05:00 | 123.0767 | 118.9 | 4.1767 | 10.7571 | 23.4385 | -89.792 | 67.1532 | 22.8468 | -95.3834 | 83.1507 | 1.2829 | 89.175 | 0.29589 | 0.15982 | 9.1044 | 99.5623 | 5 | 8.1113 | 1.0591 | 0.086467
2016-06-24 06:00 | 144.33 | 138.65 | 5.68 | 12.8571 | 23.4379 | -74.7943 | 63.7826 | 26.2174 | -80.7152 | 69.7424 | 4.4517 | 103.9875 | 0.29536 | 0.15893 | 10.6572 | 119.0964 | 5.2 | 8.9218 | 1.0563 | 0.10315
2016-06-24 07:00 | 226.5133 | 180.4567 | 46.0567 | 93.6893 | 23.4372 | -59.7966 | 60.5549 | 29.4451 | -65.583 | 56.1138 | 52.236 | 135.3425 | 0.29482 | 0.15804 | 16.6952 | 204.2737 | 5.3 | 11.6836 | 1.0466 | 0.17531
2016-06-24 08:00 | 308.6967 | 222.2633 | 86.4333 | 161.7664 | 23.4366 | -44.7988 | 57.7029 | 32.2971 | -49.8905 | 42.373 | 119.5086 | 166.6975 | 0.29429 | 0.15714 | 22.7113 | 308.9174 | 5.3 | 14.9537 | 1.0352 | 0.26222
2016-06-24 09:00 | 390.88 | 264.07 | 126.81 | 223.6399 | 23.4359 | -29.8011 | 55.4568 | 34.5432 | -33.6136 | 28.6483 | 196.2617 | 198.0525 | 0.29375 | 0.15625 | 28.7052 | 423.0195 | 6.1 | 19.3194 | 1.0199 | 0.35377
2016-06-24 10:00 | 393.3667 | 254.5233 | 138.8433 | 236.3238 | 23.4352 | -14.8033 | 54.0193 | 35.9807 | -16.8397 | 15.3112 | 227.9357 | 190.8925 | 0.29321 | 0.15536 | 28.8352 | 447.6634 | 5.8 | 19.7895 | 1.0182 | 0.37378
2016-06-24 11:00 | 395.8533 | 244.9767 | 150.8767 | 253.843 | 23.4345 | 0.19442 | 53.5323 | 36.4677 | 0.22181 | 6.4704 | 252.2261 | 183.7325 | 0.29268 | 0.15446 | 28.9644 | 464.9231 | 6 | 20.5288 | 1.0156 | 0.3872
2016-06-24 12:00 | 398.34 | 235.43 | 162.91 | 277.4684 | 23.4338 | 15.1922 | 54.0464 | 35.9536 | 17.2792 | 15.6416 | 267.193 | 176.5725 | 0.29214 | 0.15357 | 29.093 | 472.8586 | 6.1 | 20.8768 | 1.0144 | 0.39334
2016-06-24 13:00 | 397.2067 | 194.7733 | 202.4333 | 357.476 | 23.433 | 30.1899 | 55.5084 | 34.4916 | 34.0421 | 29.0018 | 312.6502 | 146.08 | 0.29161 | 0.15268 | 28.9571 | 487.6873 | 5.8 | 21.0402 | 1.0139 | 0.40545
2016-06-24 14:00 | 396.0733 | 154.1167 | 241.9567 | 453.7352 | 23.4323 | 45.1877 | 57.7743 | 32.2257 | 50.3039 | 42.7298 | 333.2968 | 115.5875 | 0.29107 | 0.15179 | 28.8214 | 477.7057 | 6.7 | 21.6283 | 1.0118 | 0.39634
2016-06-24 15:00 | 394.94 | 113.46 | 281.48 | 574.1101 | 23.4315 | 60.1854 | 60.6404 | 29.3596 | 65.9806 | 56.4696 | 317.1267 | 85.095 | 0.29054 | 0.15089 | 28.686 | 430.9078 | 6.8 | 20.2659 | 1.0166 | 0.3592
2016-06-24 16:00 | 339.0133 | 121.6133 | 217.4 | 493.7391 | 23.4308 | 75.1831 | 63.8761 | 26.1239 | 81.0989 | 70.0946 | 168.1022 | 91.21 | 0.29 | 0.15 | 24.5785 | 283.8907 | 5.9 | 14.7716 | 1.0358 | 0.24112
2016-06-24 17:00 | 283.0867 | 129.7667 | 153.32 | 396.4503 | 23.43 | 90.1809 | 67.2487 | 22.7513 | 95.7564 | 83.4965 | 44.9033 | 97.325 | 0.28946 | 0.14911 | 20.4859 | 162.7142 | 5.7 | 10.7848 | 1.0498 | 0.14006
2016-06-24 18:00 | 227.16 | 137.92 | 89.24 | 267.8319 | 23.4292 | 105.1786 | 70.5372 | 19.4628 | 110.0806 | 96.5318 | 0 | 103.44 | 0.28893 | 0.14821 | 16.4083 | 119.8483 | 5.8 | 9.5453 | 1.0541 | 0.10359
2016-06-24 19:00 | 190.3933 | 119.26 | 71.1333 | 251.0471 | 23.4284 | 120.1764 | 73.54 | 16.46 | 124.1971 | 108.9729 | 0 | 89.445 | 0.28839 | 0.14732 | 13.727 | 103.172 | 5.6 | 8.8241 | 1.0566 | 0.089391
2016-06-24 20:00 | 153.6267 | 100.6 | 53.0267 | 220.4077 | 23.4276 | 135.1741 | 76.079 | 13.921 | 138.2091 | 120.4267 | 0 | 75.45 | 0.28786 | 0.14643 | 11.0556 | 86.5056 | 5.7 | 8.4033 | 1.0581 | 0.075055
2016-06-24 21:00 | 116.86 | 81.94 | 34.92 | 168.0297 | 23.4268 | 150.1719 | 78.0053 | 11.9947 | 152.1871 | 130.1915 | 0 | 61.455 | 0.28732 | 0.14554 | 8.3941 | 69.8491 | 5.3 | 7.4828 | 1.0613 | 0.060788
2016-06-24 22:00 | 117.3167 | 72.3067 | 45.01 | 240.3279 | 23.426 | 165.1696 | 79.2056 | 10.7944 | 166.1671 | 137.0868 | 0 | 54.23 | 0.28679 | 0.14464 | 8.4112 | 62.6412 | 5.5 | 7.4575 | 1.0614 | 0.05452
2016-06-24 23:00 | 117.7733 | 62.6733 | 55.1 | 305.4681 | 23.4251 | 180.1674 | 79.6082 | 10.3918 | -179.8439 | 139.6079 | 0 | 47.005 | 0.28625 | 0.14375 | 8.4282 | 55.4332 | 5 | 6.7323 | 1.0639 | 0.048361
2016-06-25 | 118.23 | 53.04 | 65.19 | 347.5511 | 23.4243 | -164.8349 | 79.189 | 10.811 | -165.8548 | 136.9768 | 0 | 39.78 | 0.28571 | 0.14286 | 8.445 | 48.225 | 4.5 | 6.007 | 1.0665 | 0.042173
2016-06-25 01:00 | 154.2767 | 59.15 | 95.1267 | 456.5341 | 23.4234 | -149.8371 | 77.9733 | 12.0267 | -151.8748 | 130.0022 | 0 | 44.3625 | 0.28518 | 0.14196 | 10.9991 | 55.3616 | 4.9 | 6.63 | 1.0643 | 0.048315
2016-06-25 02:00 | 190.3233 | 65.26 | 125.0633 | 518.1742 | 23.4225 | -134.8394 | 76.0335 | 13.9665 | -137.896 | 120.1893 | 0 | 48.945 | 0.28464 | 0.14107 | 13.5435 | 62.4885 | 5.9 | 7.8528 | 1.06 | 0.054316
2016-06-25 03:00 | 226.37 | 71.37 | 155 | 545.2336 | 23.4216 | -119.8416 | 73.4841 | 16.5159 | -123.882 | 108.7074 | 0 | 53.5275 | 0.28411 | 0.14018 | 16.0783 | 69.6058 | 6.1 | 8.2752 | 1.0585 | 0.060418
2016-06-25 04:00 | 275.7333 | 82.8767 | 192.8567 | 577.0255 | 23.4207 | -104.8439 | 70.4745 | 19.5255 | -109.7615 | 96.2494 | 0 | 62.1575 | 0.28357 | 0.13929 | 19.5475 | 81.705 | 5.5 | 8.0533 | 1.0593 | 0.070972
2016-06-25 05:00 | 325.0967 | 94.3833 | 230.7133 | 594.957 | 23.4198 | -89.8461 | 67.1835 | 22.8165 | -95.4306 | 83.2035 | 70.4094 | 70.7875 | 0.28304 | 0.13839 | 23.0035 | 164.2004 | 5 | 10.1313 | 1.052 | 0.14165
2016-06-25 06:00 | 374.46 | 105.89 | 268.57 | 608.5879 | 23.4189 | -74.8484 | 63.8131 | 26.1869 | -80.7636 | 69.7946 | 210.198 | 79.4175 | 0.2825 | 0.1375 | 26.4462 | 316.0617 | 6.7 | 16.5769 | 1.0295 | 0.26681
2016-06-25 07:00 | 424.43 | 109.7667 | 314.6633 | 640.6866 | 23.4179 | -59.8506 | 60.5848 | 29.4152 | -65.6335 | 56.165 | 356.7364 | 82.325 | 0.28196 | 0.13661 | 29.9185 | 468.9799 | 6.7 | 21.3556 | 1.0128 | 0.38947
2016-06-25 08:00 | 474.4 | 113.6433 | 360.7567 | 675.7157 | 23.417 | -44.8528 | 57.7315 | 32.2685 | -49.9437 | 42.4225 | 498.8068 | 85.2325 | 0.28143 | 0.13571 | 33.3774 | 617.4167 | 6.9 | 26.1943 | 0.99582 | 0.50417
2016-06-25 09:00 | 524.37 | 117.52 | 406.85 | 717.995 | 23.416 | -29.8551 | 55.4832 | 34.5168 | -33.67 | 28.6949 | 629.8174 | 88.14 | 0.28089 | 0.13482 | 36.8229 | 754.7804 | 6.6 | 30.1869 | 0.98185 | 0.60768
2016-06-25 10:00 | 514.9567 | 115.7533 | 399.2033 | 679.8663 | 23.415 | -14.8573 | 54.0429 | 35.9571 | -16.899 | 15.3495 | 655.615 | 86.815 | 0.28036 | 0.13393 | 36.0929 | 778.5229 | 7 | 31.3288 | 0.97785 | 0.62425
2016-06-25 11:00 | 505.5433 | 113.9867 | 391.5567 | 659.0937 | 23.414 | 0.14043 | 53.5527 | 36.4473 | 0.1602 | 6.4487 | 654.9235 | 85.49 | 0.27982 | 0.13304 | 35.3655 | 775.7789 | 6.6 | 30.8431 | 0.97955 | 0.62313
2016-06-25 12:00 | 496.13 | 112.22 | 383.91 | 654.1446 | 23.413 | 15.1382 | 54.0635 | 35.9365 | 17.2164 | 15.5879 | 630.0847 | 84.165 | 0.27929 | 0.13214 | 34.6405 | 748.8902 | 7.3 | 30.7028 | 0.98004 | 0.60183
2016-06-25 13:00 | 481.9133 | 95.2967 | 386.6167 | 682.9675 | 23.412 | 30.1359 | 55.5224 | 34.4776 | 33.9791 | 28.95 | 597.6256 | 71.4725 | 0.27875 | 0.13125 | 33.5833 | 702.6814 | 7.6 | 29.5588 | 0.98404 | 0.56701
2016-06-25 14:00 | 467.6967 | 78.3733 | 389.3233 | 730.3221 | 23.411 | 45.1337 | 57.7859 | 32.2141 | 50.2417 | 42.6802 | 536.8951 | 58.78 | 0.27821 | 0.13036 | 32.53 | 628.205 | 8 | 27.6314 | 0.99079 | 0.51038
2016-06-25 15:00 | 453.48 | 61.45 | 392.03 | 799.8358 | 23.41 | 60.1315 | 60.6503 | 29.3497 | 65.9197 | 56.4224 | 442.3624 | 46.0875 | 0.27768 | 0.12946 | 31.4804 | 519.9303 | 7.1 | 23.3478 | 1.0058 | 0.42881
2016-06-25 16:00 | 395.1067 | 77.3733 | 317.7333 | 721.8437 | 23.4089 | 75.1292 | 63.8853 | 26.1147 | 81.0395 | 70.0499 | 246.2938 | 58.03 | 0.27714 | 0.12857 | 27.3752 | 331.699 | 7.1 | 17.4656 | 1.0264 | 0.27917
2016-06-25 17:00 | 336.7333 | 93.2967 | 243.4367 | 629.7175 | 23.4078 | 90.127 | 67.2581 | 22.7419 | 95.6985 | 83.4549 | 71.7784 | 69.9725 | 0.27661 | 0.12768 | 23.2857 | 165.0366 | 6.9 | 12.0574 | 1.0453 | 0.14146
2016-06-25 18:00 | 278.36 | 109.22 | 169.14 | 507.8936 | 23.4068 | 105.1248 | 70.5477 | 19.4523 | 110.0241 | 96.4942 | 0 | 81.915 | 0.27607 | 0.12679 | 19.2118 | 101.1268 | 7.4 | 10.5602 | 1.0505 | 0.087115
2016-06-25 19:00 | 232.4667 | 98.28 | 134.1867 | 473.9197 | 23.4057 | 120.1225 | 73.5522 | 16.4478 | 124.1418 | 108.9407 | 0 | 73.71 | 0.27554 | 0.12589 | 16.0132 | 89.7232 | 6.6 | 9.4039 | 1.0546 | 0.077589
2016-06-25 20:00 | 186.5733 | 87.34 | 99.2333 | 412.8926 | 23.4046 | 135.1203 | 76.0936 | 13.9064 | 138.155 | 120.4024 | 0 | 65.505 | 0.275 | 0.125 | 12.8269 | 78.3319 | 7.6 | 10.0479 | 1.0523 | 0.067594
2016-06-25 21:00 | 140.68 | 76.4 | 64.28 | 309.7504 | 23.4035 | 150.118 | 78.0228 | 11.9772 | 152.1342 | 130.179 | 0 | 57.3 | 0.27446 | 0.12411 | 9.6529 | 66.9529 | 5.2 | 7.2923 | 1.062 | 0.058304
2016-06-25 22:00 | 143.2167 | 61.19 | 82.0267 | 438.8051 | 23.4024 | 165.1158 | 79.2262 | 10.7738 | 166.1155 | 137.091 | 0 | 45.8925 | 0.27393 | 0.12321 | 9.8078 | 55.7003 | 6 | 7.7406 | 1.0604 | 0.048433
2016-06-25 23:00 | 145.7533 | 45.98 | 99.7733 | 554.3932 | 23.4012 | 180.1136 | 79.6321 | 10.3679 | -179.894 | 139.6319 | 0 | 34.485 | 0.27339 | 0.12232 | 9.962 | 44.447 | 5.7 | 7.089 | 1.0627 | 0.038731
2016-06-26 | 148.29 | 30.77 | 117.52 | 628.0955 | 23.4001 | -164.8887 | 79.2161 | 10.7839 | -165.9035 | 137.0174 | 0 | 23.0775 | 0.27286 | 0.12143 | 10.1155 | 33.193 | 5.7 | 6.7373 | 1.0639 | 0.028958
2016-06-26 01:00 | 174.3033 | 40.4933 | 133.81 | 643.766 | 23.3989 | -149.8909 | 78.0033 | 11.9967 | -151.922 | 130.0522 | 0 | 30.37 | 0.27232 | 0.12054 | 11.8666 | 42.2366 | 6.2 | 7.5199 | 1.0612 | 0.036753
2016-06-26 02:00 | 200.3167 | 50.2167 | 150.1 | 623.331 | 23.3978 | -134.8931 | 76.0661 | 13.9339 | -137.942 | 120.2433 | 0 | 37.6625 | 0.27179 | 0.11964 | 13.6108 | 51.2733 | 6 | 7.6023 | 1.0609 | 0.044604
2016-06-26 03:00 | 226.33 | 59.94 | 166.39 | 586.4923 | 23.3966 | -119.8953 | 73.5186 | 16.4814 | -123.9271 | 108.7627 | 0 | 44.955 | 0.27125 | 0.11875 | 15.348 | 60.303 | 6.6 | 8.4845 | 1.0578 | 0.052307
2016-06-26 04:00 | 275.6933 | 91.2133 | 184.48 | 552.9429 | 23.3954 | -104.8976 | 70.5106 | 19.4894 | -109.8061 | 96.3045 | 0 | 68.41 | 0.27071 | 0.11786 | 18.6585 | 87.0685 | 6.8 | 9.5209 | 1.0542 | 0.075264
2016-06-26 05:00 | 325.0567 | 122.4867 | 202.57 | 523.182 | 23.3942 | -89.8998 | 67.2203 | 22.7797 | -95.4756 | 83.2578 | 61.4225 | 91.865 | 0.27018 | 0.11696 | 21.9558 | 175.2434 | 6.4 | 11.8764 | 1.0459 | 0.1503
2016-06-26 06:00 | 374.42 | 153.76 | 220.66 | 500.6808 | 23.393 | -74.902 | 63.8502 | 26.1498 | -80.8099 | 69.8477 | 172.4927 | 115.32 | 0.26964 | 0.11607 | 25.2399 | 313.0526 | 5.6 | 15.3829 | 1.0337 | 0.26534
2016-06-26 07:00 | 332.2167 | 170.3133 | 161.9033 | 330.0249 | 23.3918 | -59.9043 | 60.6213 | 29.3787 | -65.6819 | 56.2165 | 183.5126 | 127.735 | 0.26911 | 0.11518 | 22.3505 | 333.5981 | 7.3 | 17.7249 | 1.0255 | 0.28052
2016-06-26 08:00 | 290.0133 | 186.8667 | 103.1467 | 193.3874 | 23.3905 | -44.9065 | 57.7667 | 32.2333 | -49.995 | 42.4717 | 142.6447 | 140.15 | 0.26857 | 0.11429 | 19.4723 | 302.267 | 7.7 | 17.1458 | 1.0275 | 0.25467
2016-06-26 09:00 | 247.81 | 203.42 | 44.39 | 78.404 | 23.3893 | -29.9087 | 55.5164 | 34.4836 | -33.7247 | 28.7402 | 68.7453 | 152.565 | 0.26804 | 0.11339 | 16.6055 | 237.9158 | 7.1 | 14.5349 | 1.0366 | 0.20224
2016-06-26 10:00 | 252.52 | 199.6867 | 52.8333 | 90.0442 | 23.388 | -14.9109 | 54.0734 | 35.9266 | -16.9572 | 15.3849 | 86.8175 | 149.765 | 0.2675 | 0.1125 | 16.8873 | 253.4698 | 7.1 | 15.0209 | 1.0349 | 0.2151
2016-06-26 11:00 | 257.23 | 195.9533 | 61.2767 | 103.2114 | 23.3867 | 0.086838 | 53.58 | 36.42 | 0.09905 | 6.4206 | 102.5641 | 146.965 | 0.26696 | 0.11161 | 17.1678 | 266.6969 | 6.8 | 15.1343 | 1.0345 | 0.22624
2016-06-26 12:00 | 261.94 | 192.22 | 69.72 | 118.8645 | 23.3854 | 15.0846 | 54.0874 | 35.9126 | 17.1533 | 15.532 | 114.5237 | 144.165 | 0.26643 | 0.11071 | 17.4471 | 276.1358 | 6.5 | 15.1292 | 1.0345 | 0.23425
2016-06-26 13:00 | 228.2633 | 178.8967 | 49.3667 | 87.2537 | 23.3841 | 30.0824 | 55.5433 | 34.4567 | 33.9154 | 28.8977 | 76.3891 | 134.1725 | 0.26589 | 0.10982 | 15.1734 | 225.735 | 6.8 | 13.8542 | 1.039 | 0.19232
2016-06-26 14:00 | 194.5867 | 165.5733 | 29.0133 | 54.4531 | 23.3828 | 45.0802 | 57.8043 | 32.1957 | 50.1784 | 42.6311 | 40.0628 | 124.18 | 0.26536 | 0.10893 | 12.9087 | 177.1515 | 6.5 | 12.036 | 1.0454 | 0.15186
2016-06-26 15:00 | 160.91 | 152.25 | 8.66 | 17.6777 | 23.3815 | 60.078 | 60.667 | 29.333 | 65.8575 | 56.3761 | 9.7888 | 114.1875 | 0.26482 | 0.10804 | 10.6531 | 134.6294 | 6.3 | 10.5072 | 1.0507 | 0.116
2016-06-26 16:00 | 139.84 | 131.5033 | 8.3367 | 18.9505 | 23.3802 | 75.0757 | 63.9013 | 26.0987 | 80.9787 | 70.0068 | 6.4793 | 98.6275 | 0.26429 | 0.10714 | 9.2394 | 114.3462 | 7 | 10.5733 | 1.0505 | 0.098498
2016-06-26 17:00 | 118.77 | 110.7567 | 8.0133 | 20.7427 | 23.3788 | 90.0735 | 67.2742 | 22.7258 | 95.6392 | 83.4155 | 2.3785 | 83.0675 | 0.26375 | 0.10625 | 7.8314 | 93.2774 | 7.1 | 10.0149 | 1.0524 | 0.080499
2016-06-26 18:00 | 97.7 | 90.01 | 7.69 | 23.1111 | 23.3775 | 105.0713 | 70.5648 | 19.4352 | 109.9663 | 96.4594 | 0 | 67.5075 | 0.26321 | 0.10536 | 6.429 | 73.9365 | 6.6 | 8.9105 | 1.0563 | 0.064042
2016-06-26 19:00 | 86.7333 | 76.8033 | 9.93 | 35.1101 | 23.3761 | 120.0691 | 73.5712 | 16.4288 | 124.0855 | 108.9121 | 0 | 57.6025 | 0.26268 | 0.10446 | 5.6957 | 63.2982 | 6.7 | 8.6781 | 1.0571 | 0.05487
2016-06-26 20:00 | 75.7667 | 63.5967 | 12.17 | 50.7138 | 23.3747 | 135.0669 | 76.115 | 13.885 | 138.1001 | 120.3826 | 0 | 47.6975 | 0.26214 | 0.10357 | 4.9654 | 52.6629 | 6.5 | 8.1457 | 1.059 | 0.045731
2016-06-26 21:00 | 64.8 | 50.39 | 14.41 | 69.5776 | 23.3733 | 150.0646 | 78.0471 | 11.9529 | 152.0809 | 130.1719 | 0 | 37.7925 | 0.26161 | 0.10268 | 4.238 | 42.0305 | 6.2 | 7.5135 | 1.0612 | 0.036574
2016-06-26 22:00 | 55.2333 | 45.6033 | 9.63 | 51.6463 | 23.3719 | 165.0624 | 79.2537 | 10.7463 | 166.0639 | 137.1017 | 0 | 34.2025 | 0.26107 | 0.10179 | 3.605 | 37.8075 | 6 | 7.1815 | 1.0624 | 0.032936
2016-06-26 23:00 | 45.6667 | 40.8167 | 4.85 | 27.0284 | 23.3705 | 180.0602 | 79.6628 | 10.3372 | -179.9438 | 139.6628 | 0 | 30.6125 | 0.26054 | 0.10089 | 2.9744 | 33.5869 | 5.9 | 6.9496 | 1.0632 | 0.029281
2016-06-27 | 36.1 | 36.03 | 0.07 | 0.37529 | 23.3691 | -164.942 | 79.25 | 10.75 | -165.9514 | 137.0641 | 0 | 27.0225 | 0.26 | 0.1 | 2.3465 | 29.369 | 5.9 | 6.8178 | 1.0636 | 0.025615
2016-06-27 01:00 | 47.8267 | 45.92 | 1.9067 | 9.2008 | 23.3676 | -149.9442 | 78.0401 | 11.9599 | -151.968 | 130.1072 | 0 | 34.44 | 0.25978 | 0.09963 | 3.1061 | 37.5461 | 5.9 | 7.0733 | 1.0627 | 0.03272
2016-06-27 02:00 | 59.5533 | 55.81 | 3.7433 | 15.5882 | 23.3662 | -134.9464 | 76.1053 | 13.8947 | -137.9863 | 120.3012 | 0 | 41.8575 | 0.25956 | 0.099259 | 3.8643 | 45.7218 | 6 | 7.4288 | 1.0615 | 0.039798
2016-06-27 03:00 | 71.28 | 65.7 | 5.58 | 19.7163 | 23.3647 | -119.9486 | 73.5598 | 16.4402 | -123.9702 | 108.8209 | 0 | 49.275 | 0.25933 | 0.098889 | 4.6213 | 53.8963 | 6.1 | 7.7843 | 1.0603 | 0.046858
2016-06-27 04:00 | 66.4333 | 57.64 | 8.7933 | 26.4118 | 23.3633 | -104.9508 | 70.5531 | 19.4469 | -109.8487 | 96.3618 | 0 | 43.23 | 0.25911 | 0.098519 | 4.3034 | 47.5334 | 5.9 | 7.3854 | 1.0617 | 0.04138
2016-06-27 05:00 | 61.5867 | 49.58 | 12.0067 | 31.0659 | 23.3618 | -89.953 | 67.2637 | 22.7363 | -95.5184 | 83.3136 | 3.6172 | 37.185 | 0.25889 | 0.098148 | 3.986 | 44.7882 | 5.8 | 7.1996 | 1.0623 | 0.039014
2016-06-27 06:00 | 56.74 | 41.52 | 15.22 | 34.588 | 23.3603 | -74.9552 | 63.8938 | 26.1062 | -80.8538 | 69.9017 | 11.8856 | 31.14 | 0.25867 | 0.097778 | 3.6692 | 46.6947 | 5.7 | 7.1592 | 1.0624 | 0.040681
2016-06-27 07:00 | 78.6667 | 65.1167 | 13.55 | 27.6574 | 23.3588 | -59.9575 | 60.6644 | 29.3356 | -65.728 | 56.2682 | 15.3583 | 48.8375 | 0.25844 | 0.097407 | 5.0827 | 69.2786 | 5.8 | 7.965 | 1.0596 | 0.060195
2016-06-27 08:00 | 100.5933 | 88.7133 | 11.88 | 22.2994 | 23.3572 | -44.9597 | 57.8086 | 32.1914 | -50.0443 | 42.5205 | 16.4355 | 66.535 | 0.25822 | 0.097037 | 6.4939 | 89.4643 | 5.6 | 8.3958 | 1.0581 | 0.077624
2016-06-27 09:00 | 122.52 | 112.31 | 10.21 | 18.0518 | 23.3557 | -29.9619 | 55.5563 | 34.4437 | -33.7778 | 28.7844 | 15.8213 | 84.2325 | 0.258 | 0.096667 | 7.9025 | 107.9563 | 5.6 | 8.9736 | 1.0561 | 0.09349
2016-06-27 10:00 | 132.7533 | 120.4167 | 12.3367 | 21.0444 | 23.3542 | -14.9641 | 54.1106 | 35.8894 | -17.0143 | 15.4176 | 20.2871 | 90.3125 | 0.25778 | 0.096296 | 8.5552 | 119.1548 | 5.8 | 9.5236 | 1.0542 | 0.103
2016-06-27 11:00 | 142.9867 | 128.5233 | 14.4633 | 24.381 | 23.3526 | 0.033731 | 53.6141 | 36.3859 | 0.038467 | 6.386 | 24.2297 | 96.3925 | 0.25756 | 0.095926 | 9.2068 | 129.829 | 5.5 | 9.5572 | 1.054 | 0.11221
2016-06-27 12:00 | 153.22 | 136.63 | 16.59 | 28.305 | 23.351 | 15.0315 | 54.1182 | 35.8818 | 17.0903 | 15.474 | 27.279 | 102.4725 | 0.25733 | 0.095556 | 9.8572 | 139.6087 | 5.6 | 9.9628 | 1.0526 | 0.1205
2016-06-27 13:00 | 159.5467 | 142.8967 | 16.65 | 29.449 | 23.3494 | 30.0293 | 55.571 | 34.429 | 33.8511 | 28.8451 | 25.7952 | 107.1725 | 0.25711 | 0.095185 | 10.2553 | 143.223 | 5.9 | 10.3757 | 1.0512 | 0.12345
2016-06-27 14:00 | 165.8733 | 149.1633 | 16.71 | 31.3838 | 23.3478 | 45.0271 | 57.8295 | 32.1705 | 50.1141 | 42.5824 | 23.108 | 111.8725 | 0.25689 | 0.094815 | 10.6528 | 145.6333 | 5.4 | 9.951 | 1.0527 | 0.12571
2016-06-27 15:00 | 172.2 | 155.43 | 16.77 | 34.2576 | 23.3462 | 60.0249 | 60.6905 | 29.3095 | 65.794 | 56.331 | 18.9922 | 116.5725 | 0.25667 | 0.094444 | 11.0495 | 146.6142 | 6 | 10.5817 | 1.0505 | 0.12629
2016-06-27 16:00 | 176.9767 | 127.3933 | 49.5833 | 112.8013 | 23.3446 | 75.0227 | 63.924 | 26.076 | 80.9165 | 69.9654 | 38.6443 | 95.545 | 0.25644 | 0.094074 | 11.3462 | 145.5354 | 5.1 | 9.648 | 1.0537 | 0.12575
2016-06-27 17:00 | 181.7533 | 99.3567 | 82.3967 | 213.4889 | 23.343 | 90.0205 | 67.2971 | 22.7029 | 95.5786 | 83.3784 | 24.6179 | 74.5175 | 0.25622 | 0.093704 | 11.6423 | 110.7777 | 5.9 | 9.3618 | 1.0547 | 0.09581
2016-06-27 18:00 | 186.53 | 71.32 | 115.21 | 346.6568 | 23.3413 | 105.0183 | 70.5888 | 19.4112 | 109.9073 | 96.4275 | 0 | 53.49 | 0.256 | 0.093333 | 11.9379 | 65.4279 | 5 | 7.0446 | 1.0628 | 0.057023
2016-06-27 19:00 | 166.9133 | 62.67 | 104.2433 | 369.1427 | 23.3397 | 120.0162 | 73.5969 | 16.4031 | 124.0282 | 108.8872 | 0 | 47.0025 | 0.25578 | 0.092963 | 10.6732 | 57.6757 | 4.3 | 6.1024 | 1.0661 | 0.050422
2016-06-27 20:00 | 147.2967 | 54.02 | 93.2767 | 389.4712 | 23.338 | 135.014 | 76.1432 | 13.8568 | 138.0446 | 120.3673 | 0 | 40.515 | 0.25556 | 0.092593 | 9.4106 | 49.9256 | 4.7 | 6.2602 | 1.0656 | 0.043624
2016-06-27 21:00 | 127.68 | 45.37 | 82.31 | 398.4512 | 23.3364 | 150.0118 | 78.0783 | 11.9217 | 152.0273 | 130.1705 | 0 | 34.0275 | 0.25533 | 0.092222 | 8.1502 | 42.1777 | 4.9 | 6.2181 | 1.0657 | 0.036859
2016-06-27 22:00 | 131.38 | 43.3833 | 87.9967 | 473.4264 | 23.3347 | 165.0096 | 79.288 | 10.712 | 166.0123 | 137.1188 | 0 | 32.5375 | 0.25511 | 0.091852 | 8.3791 | 40.9166 | 4.7 | 5.9786 | 1.0666 | 0.035785
2016-06-27 23:00 | 135.08 | 41.3967 | 93.6833 | 523.9682 | 23.333 | 180.0074 | 79.7004 | 10.2996 | -179.9931 | 139.7004 | 0 | 31.0475 | 0.25489 | 0.091481 | 8.6076 | 39.6551 | 4 | 5.2392 | 1.0692 | 0.034766
2016-06-28 | 138.78 | 39.41 | 99.37 | 534.7438 | 23.3313 | -164.9948 | 79.2906 | 10.7094 | -165.9983 | 137.117 | 0 | 29.5575 | 0.25467 | 0.091111 | 8.8357 | 38.3932 | 4.3 | 5.4998 | 1.0683 | 0.033631
2016-06-28 01:00 | 136.2333 | 54.3933 | 81.84 | 396.347 | 23.3295 | -149.997 | 78.0835 | 11.9165 | -152.0127 | 130.1673 | 0 | 40.795 | 0.25444 | 0.090741 | 8.666 | 49.461 | 4.5 | 6.0457 | 1.0663 | 0.043249
2016-06-28 02:00 | 133.6867 | 69.3767 | 64.31 | 268.6723 | 23.3278 | -134.9992 | 76.1511 | 13.8489 | -138.0291 | 120.3631 | 0 | 52.0325 | 0.25422 | 0.09037 | 8.4965 | 60.529 | 5 | 6.8915 | 1.0634 | 0.05278
2016-06-28 03:00 | 131.14 | 84.36 | 46.78 | 165.7599 | 23.326 | -120.0014 | 73.6075 | 16.3925 | -124.0114 | 108.882 | 0 | 63.27 | 0.254 | 0.09 | 8.3274 | 71.5974 | 4.5 | 6.7374 | 1.0639 | 0.062463
2016-06-28 04:00 | 161.1233 | 104.2833 | 56.84 | 171.1408 | 23.3243 | -105.0035 | 70.6022 | 19.3978 | -109.8891 | 96.4212 | 0 | 78.2125 | 0.25378 | 0.08963 | 10.2224 | 88.4349 | 3.9 | 6.6636 | 1.0642 | 0.077171
2016-06-28 05:00 | 191.1067 | 124.2067 | 66.9 | 173.4569 | 23.3225 | -90.0057 | 67.3136 | 22.6864 | -95.5588 | 83.3708 | 20.0245 | 93.155 | 0.25356 | 0.089259 | 12.114 | 125.2935 | 4.1 | 8.0154 | 1.0594 | 0.10885
2016-06-28 06:00 | 221.09 | 144.13 | 76.96 | 175.2071 | 23.3207 | -75.0079 | 63.9439 | 26.0561 | -80.8954 | 69.9564 | 60.0497 | 108.0975 | 0.25333 | 0.088889 | 14.0024 | 182.1496 | 4.6 | 10.2922 | 1.0515 | 0.15705
2016-06-28 07:00 | 236.3867 | 166.94 | 69.4467 | 141.9689 | 23.3189 | -60.0101 | 60.7141 | 29.2859 | -65.7718 | 56.32 | 78.7294 | 125.205 | 0.25311 | 0.088519 | 14.958 | 218.8924 | 4.8 | 11.6404 | 1.0468 | 0.18788
2016-06-28 08:00 | 251.6833 | 189.75 | 61.9333 | 116.4088 | 23.3171 | -45.0123 | 57.8571 | 32.1429 | -50.0914 | 42.5688 | 85.7311 | 142.3125 | 0.25289 | 0.088148 | 15.912 | 243.9556 | 5 | 12.6236 | 1.0433 | 0.20871
2016-06-28 09:00 | 266.98 | 212.56 | 54.42 | 96.3314 | 23.3153 | -30.0144 | 55.6029 | 34.3971 | -33.8291 | 28.8273 | 84.3938 | 159.42 | 0.25267 | 0.087778 | 16.8642 | 260.678 | 4.6 | 12.7462 | 1.0429 | 0.22292
2016-06-28 10:00 | 298.19 | 212.3167 | 85.8733 | 146.6419 | 23.3135 | -15.0166 | 54.1547 | 35.8453 | -17.0701 | 15.4475 | 141.3444 | 159.2375 | 0.25244 | 0.087407 | 18.8191 | 319.401 | 5.4 | 15.3813 | 1.0337 | 0.27073
2016-06-28 11:00 | 329.4 | 212.0733 | 117.3267 | 197.9711 | 23.3116 | -0.018801 | 53.655 | 36.345 | -0.021437 | 6.345 | 196.7584 | 159.055 | 0.25222 | 0.087037 | 20.7705 | 376.5839 | 7.4 | 19.1682 | 1.0204 | 0.3151
2016-06-28 12:00 | 360.61 | 211.83 | 148.78 | 254.0721 | 23.3098 | 14.979 | 54.1559 | 35.8441 | 17.0273 | 15.414 | 244.9332 | 158.8725 | 0.252 | 0.086667 | 22.7184 | 426.5241 | 9.1 | 22.4289 | 1.009 | 0.3529
2016-06-28 13:00 | 314.4633 | 185.48 | 128.9833 | 228.3348 | 23.3079 | 29.9768 | 55.6056 | 34.3944 | 33.7864 | 28.7921 | 200.1065 | 139.11 | 0.25178 | 0.086296 | 19.7937 | 359.0102 | 7.6 | 18.8191 | 1.0216 | 0.30076
2016-06-28 14:00 | 268.3167 | 159.13 | 109.1867 | 205.2503 | 23.306 | 44.9747 | 57.8615 | 32.1385 | 50.0489 | 42.5343 | 151.2435 | 119.3475 | 0.25156 | 0.085926 | 16.8741 | 287.4651 | 7.8 | 16.7833 | 1.0288 | 0.2425
2016-06-28 15:00 | 222.17 | 132.78 | 89.39 | 182.7768 | 23.3041 | 59.9725 | 60.7208 | 29.2792 | 65.7294 | 56.2871 | 101.447 | 99.585 | 0.25133 | 0.085556 | 13.9597 | 214.9917 | 7.2 | 13.9185 | 1.0388 | 0.18313
2016-06-28 16:00 | 206.2767 | 112.9067 | 93.37 | 212.6387 | 23.3022 | 74.9703 | 63.9534 | 26.0466 | 80.8531 | 69.9258 | 72.9855 | 84.68 | 0.25111 | 0.085185 | 12.9496 | 170.6151 | 7.1 | 12.4317 | 1.044 | 0.14606
2016-06-28 17:00 | 190.3833 | 93.0333 | 97.35 | 252.5449 | 23.3003 | 89.9682 | 67.3267 | 22.6733 | 95.5167 | 83.3435 | 29.274 | 69.775 | 0.25089 | 0.084815 | 11.9413 | 110.9902 | 7.2 | 10.6684 | 1.0502 | 0.095577
2016-06-28 18:00 | 174.49 | 73.16 | 101.33 | 305.3573 | 23.2984 | 104.966 | 70.6195 | 19.3805 | 109.8472 | 96.3986 | 0 | 54.87 | 0.25067 | 0.084444 | 10.9347 | 65.8047 | 6.4 | 8.4564 | 1.0579 | 0.057084
2016-06-28 19:00 | 159.5867 | 63.0867 | 96.5 | 342.383 | 23.2965 | 119.9638 | 73.6295 | 16.3705 | 123.97 | 108.8661 | 0 | 47.315 | 0.25044 | 0.084074 | 9.9919 | 57.3069 | 6.3 | 8.0908 | 1.0592 | 0.049773
2016-06-28 20:00 | 144.6833 | 53.0133 | 91.67 | 383.714 | 23.2945 | 134.9617 | 76.1783 | 13.8217 | 137.9884 | 120.3567 | 0 | 39.76 | 0.25022 | 0.083704 | 9.0507 | 48.8107 | 6.8 | 8.3253 | 1.0584 | 0.042361
2016-06-28 21:00 | 129.78 | 42.94 | 86.84 | 421.7042 | 23.2926 | 149.9595 | 78.1163 | 11.8837 | 151.9734 | 130.1746 | 0 | 32.205 | 0.25 | 0.083333 | 8.1112 | 40.3162 | 6.1 | 7.3599 | 1.0617 | 0.0351
2016-06-28 22:00 | 121.26 | 42.35 | 78.91 | 426.1579 | 23.2906 | 164.9573 | 79.3292 | 10.6708 | 165.9609 | 137.1424 | 0 | 31.7625 | 0.24978 | 0.082963 | 7.572 | 39.3345 | 5.7 | 6.9292 | 1.0632 | 0.034294
2016-06-28 23:00 | 112.74 | 41.76 | 70.98 | 398.6879 | 23.2886 | 179.9552 | 79.7447 | 10.2553 | 179.9582 | 139.7447 | 0 | 31.32 | 0.24956 | 0.082593 | 7.0337 | 38.3537 | 5.7 | 6.8986 | 1.0634 | 0.033443
2016-06-29 | 104.22 | 41.17 | 63.05 | 340.7848 | 23.2866 | -165.047 | 79.338 | 10.662 | -166.0443 | 137.176 | 0 | 30.8775 | 0.24933 | 0.082222 | 6.4964 | 37.3739 | 4.7 | 5.8679 | 1.067 | 0.032699
2016-06-29 01:00 | 109.2733 | 52.5133 | 56.76 | 276.0308 | 23.2846 | -150.0491 | 78.1337 | 11.8663 | -152.056 | 130.2323 | 0 | 39.385 | 0.24911 | 0.081852 | 6.8053 | 46.1903 | 5.2 | 6.6434 | 1.0642 | 0.04031
2016-06-29 02:00 | 114.3267 | 63.8567 | 50.47 | 211.6381 | 23.2826 | -135.0513 | 76.2036 | 13.7964 | -138.07 | 120.4287 | 0 | 47.8925 | 0.24889 | 0.081481 | 7.1137 | 55.0062 | 5 | 6.7189 | 1.064 | 0.047991
2016-06-29 03:00 | 119.38 | 75.2 | 44.18 | 157.0529 | 23.2805 | -120.0535 | 73.6618 | 16.3382 | -124.0506 | 108.9458 | 0 | 56.4 | 0.24867 | 0.081111 | 7.4215 | 63.8215 | 5 | 6.9944 | 1.063 | 0.055632
2016-06-29 04:00 | 149.3967 | 91.9233 | 57.4733 | 173.5259 | 23.2785 | -105.0556 | 70.6578 | 19.3422 | -109.9272 | 96.4825 | 0 | 68.9425 | 0.24844 | 0.080741 | 9.2792 | 78.2217 | 5.9 | 8.3444 | 1.0583 | 0.067881
2016-06-29 05:00 | 179.4133 | 108.6467 | 70.7667 | 183.9151 | 23.2764 | -90.0578 | 67.37 | 22.63 | -95.5969 | 83.4292 | 21.0454 | 81.485 | 0.24822 | 0.08037 | 11.1336 | 113.664 | 4 | 7.552 | 1.0611 | 0.098896
2016-06-29 06:00 | 209.43 | 125.37 | 84.06 | 191.7581 | 23.2744 | -75.0599 | 64.0004 | 25.9996 | -80.9345 | 70.0118 | 65.5482 | 94.0275 | 0.248 | 0.08 | 12.9847 | 172.5603 | 4.4 | 9.7925 | 1.0532 | 0.14903
2016-06-29 07:00 | 228.41 | 153.17 | 75.24 | 154.0814 | 23.2723 | -60.0621 | 60.7702 | 29.2298 | -65.8132 | 56.372 | 85.3301 | 114.8775 | 0.24778 | 0.07963 | 14.1487 | 214.3563 | 4.4 | 11.0986 | 1.0487 | 0.18432
2016-06-29 08:00 | 247.39 | 180.97 | 66.42 | 125.0331 | 23.2702 | -45.0642 | 57.9121 | 32.0879 | -50.1363 | 42.6165 | 92.0121 | 135.7275 | 0.24756 | 0.079259 | 15.3107 | 243.0503 | 4.6 | 12.1953 | 1.0448 | 0.20823
2016-06-29 09:00 | 266.37 | 208.77 | 57.6 | 102.0992 | 23.2681 | -30.0664 | 55.6562 | 34.3438 | -33.8785 | 28.8688 | 89.4111 | 156.5775 | 0.24733 | 0.078889 | 16.4705 | 262.4592 | 4.2 | 12.4018 | 1.0441 | 0.22471
2016-06-29 10:00 | 246.4967 | 203.93 | 42.5667 | 72.7785 | 23.266 | -15.0685 | 54.2055 | 35.7945 | -17.1245 | 15.4746 | 70.1402 | 152.9475 | 0.24711 | 0.078519 | 15.228 | 238.3157 | 4.1 | 11.5474 | 1.0471 | 0.20462
2016-06-29 11:00 | 226.6233 | 199.09 | 27.5333 | 46.5111 | 23.2639 | -0.070669 | 53.7028 | 36.2972 | -0.080554 | 6.2975 | 46.2304 | 149.3175 | 0.24689 | 0.078148 | 13.9877 | 209.5356 | 4 | 10.548 | 1.0506 | 0.18051
2016-06-29 12:00 | 206.75 | 194.25 | 12.5 | 21.3693 | 23.2617 | 14.9272 | 54.2004 | 35.7996 | 16.9644 | 15.3521 | 20.6068 | 145.6875 | 0.24667 | 0.077778 | 12.7496 | 179.0438 | 4.2 | 9.7951 | 1.0532 | 0.15463
2016-06-29 13:00 | 180.2967 | 167.1733 | 13.1233 | 23.2563 | 23.2596 | 29.925 | 55.6469 | 34.3531 | 33.7213 | 28.7389 | 20.3916 | 125.38 | 0.24644 | 0.077407 | 11.1083 | 156.8799 | 3.8 | 8.7025 | 1.057 | 0.13598
2016-06-29 14:00 | 153.8433 | 140.0967 | 13.7467 | 25.869 | 23.2574 | 44.9229 | 57.9003 | 32.0997 | 49.9829 | 42.4867 | 19.0767 | 105.0725 | 0.24622 | 0.077037 | 9.4699 | 133.6191 | 3.4 | 7.5756 | 1.061 | 0.11625
2016-06-29 15:00 | 127.39 | 113.02 | 14.37 | 29.4164 | 23.2552 | 59.9208 | 60.7578 | 29.2422 | 65.6638 | 56.2444 | 16.3453 | 84.765 | 0.246 | 0.076667 | 7.8345 | 108.9448 | 3.4 | 6.8045 | 1.0637 | 0.095024
2016-06-29 16:00 | 125.16 | 107.43 | 17.73 | 40.4302 | 23.2531 | 74.9186 | 63.9896 | 26.0104 | 80.7886 | 69.888 | 13.9022 | 80.5725 | 0.24578 | 0.076296 | 7.6904 | 102.1651 | 3.4 | 6.5927 | 1.0644 | 0.089173
2016-06-29 17:00 | 122.93 | 101.84 | 21.09 | 54.7948 | 23.2509 | 89.9165 | 67.3631 | 22.6369 | 95.4537 | 83.3112 | 6.3824 | 76.38 | 0.24556 | 0.075926 | 7.5465 | 90.3089 | 3.7 | 6.5222 | 1.0647 | 0.078843
2016-06-29 18:00 | 120.7 | 96.25 | 24.45 | 73.8171 | 23.2487 | 104.9143 | 70.6569 | 19.3431 | 109.7861 | 96.3728 | 0 | 72.1875 | 0.24533 | 0.075556 | 7.4029 | 79.5904 | 4.3 | 6.7872 | 1.0637 | 0.069424
2016-06-29 19:00 | 114.26 | 84.2933 | 29.9667 | 106.5711 | 23.2464 | 119.9122 | 73.6688 | 16.3312 | 123.911 | 108.8487 | 0 | 63.22 | 0.24511 | 0.075185 | 7.0016 | 70.2216 | 3.7 | 5.8944 | 1.0669 | 0.061432
2016-06-29 20:00 | 107.82 | 72.3367 | 35.4833 | 148.969 | 23.2442 | 134.9101 | 76.2201 | 13.7799 | 137.9318 | 120.3507 | 0 | 54.2525 | 0.24489 | 0.074815 | 6.601 | 60.8535 | 3.6 | 5.5017 | 1.0682 | 0.053305
2016-06-29 21:00 | 101.38 | 60.38 | 41 | 199.8428 | 23.242 | 149.9079 | 78.1611 | 11.8389 | 151.9193 | 130.1843 | 0 | 45.285 | 0.24467 | 0.074444 | 6.2011 | 51.4861 | 3.7 | 5.3089 | 1.0689 | 0.045128
2016-06-29 22:00 | 106.5633 | 51.6767 | 54.8867 | 297.7415 | 23.2397 | 164.9058 | 79.3771 | 10.6229 | 165.9097 | 137.1724 | 0 | 38.7575 | 0.24444 | 0.074074 | 6.5122 | 45.2697 | 3.5 | 4.9147 | 1.0703 | 0.039731
2016-06-29 23:00 | 111.7467 | 42.9733 | 68.7733 | 388.209 | 23.2374 | 179.9037 | 79.7959 | 10.2041 | 179.9101 | 139.7958 | 0 | 32.23 | 0.24422 | 0.073704 | 6.8228 | 39.0528 | 4.3 | 5.5204 | 1.0682 | 0.034207
2016-06-30 | 116.93 | 34.27 | 82.66 | 449.0312 | 23.2352 | -165.0985 | 79.3922 | 10.6078 | -166.0893 | 137.2411 | 0 | 25.7025 | 0.244 | 0.073333 | 7.1327 | 32.8352 | 4 | 5.0261 | 1.0699 | 0.028807
2016-06-30 01:00 | 98.16 | 36.3133 | 61.8467 | 302.1942 | 23.2329 | -150.1006 | 78.1905 | 11.8095 | -152.0979 | 130.3022 | 0 | 27.235 | 0.24378 | 0.072963 | 5.9823 | 33.2173 | 3.8 | 4.838 | 1.0706 | 0.02916
2016-06-30 02:00 | 79.39 | 38.3567 | 41.0333 | 172.7922 | 23.2306 | -135.1027 | 76.2626 | 13.7374 | -138.1092 | 120.498 | 0 | 28.7675 | 0.24356 | 0.072593 | 4.834 | 33.6015 | 4 | 5.05 | 1.0698 | 0.029477
2016-06-30 03:00 | 60.62 | 40.4 | 20.22 | 72.1401 | 23.2282 | -120.1048 | 73.7226 | 16.2774 | -124.0877 | 109.0124 | 0 | 30.3 | 0.24333 | 0.072222 | 3.6877 | 33.9877 | 4.4 | 5.4621 | 1.0684 | 0.029776
2016-06-30 04:00 | 96.87 | 49.4533 | 47.4167 | 143.6055 | 23.2259 | -105.107 | 70.7199 | 19.2801 | -109.963 | 96.5457 | 0 | 37.09 | 0.24311 | 0.071852 | 5.8875 | 42.9775 | 5.1 | 6.443 | 1.0649 | 0.037531
2016-06-30 05:00 | 133.12 | 58.5067 | 74.6133 | 194.4232 | 23.2236 | -90.1091 | 67.4327 | 22.5673 | -95.6324 | 83.4889 | 22.0467 | 43.88 | 0.24289 | 0.071481 | 8.0833 | 74.01 | 4.8 | 7.1128 | 1.0626 | 0.064488
2016-06-30 06:00 | 169.37 | 67.56 | 101.81 | 232.7742 | 23.2212 | -75.1112 | 64.0634 | 25.9366 | -80.971 | 70.0677 | 79.3548 | 50.67 | 0.24267 | 0.071111 | 10.2751 | 140.2999 | 4.8 | 9.1844 | 1.0554 | 0.12141
2016-06-30 07:00 | 223.3767 | 126.16 | 97.2167 | 199.4763 | 23.2189 | -60.1133 | 60.8328 | 29.1672 | -65.852 | 56.424 | 110.319 | 94.62 | 0.24244 | 0.070741 | 13.5391 | 218.4781 | 5 | 11.8274 | 1.0461 | 0.18741
2016-06-30 08:00 | 277.3833 | 184.76 | 92.6233 | 174.6595 | 23.2165 | -45.1154 | 57.9737 | 32.0263 | -50.1789 | 42.6637 | 128.4348 | 138.57 | 0.24222 | 0.07037 | 16.7971 | 283.8019 | 4.7 | 13.5688 | 1.04 | 0.24203
2016-06-30 09:00 | 331.39 | 243.36 | 88.03 | 156.2774 | 23.2141 | -30.1176 | 55.7161 | 34.2839 | -33.9259 | 28.9089 | 136.8036 | 182.52 | 0.242 | 0.07 | 20.0491 | 339.3726 | 4.7 | 15.3054 | 1.0339 | 0.28773
2016-06-30 10:00 | 327.4267 | 230.1633 | 97.2633 | 166.5282 | 23.2117 | -15.1197 | 54.263 | 35.737 | -17.1774 | 15.4989 | 160.4725 | 172.6225 | 0.24178 | 0.06963 | 19.7911 | 352.8862 | 4.6 | 15.6277 | 1.0328 | 0.29886
2016-06-30 11:00 | 323.4633 | 216.9667 | 106.4967 | 180.1347 | 23.2093 | -0.12178 | 53.7574 | 36.2426 | -0.13878 | 6.2437 | 179.0662 | 162.725 | 0.24156 | 0.069259 | 19.5336 | 361.3248 | 4.8 | 16.0914 | 1.0312 | 0.30552
2016-06-30 12:00 | 319.5 | 203.77 | 115.73 | 198.0915 | 23.2069 | 14.8761 | 54.2517 | 35.7483 | 16.9019 | 15.2884 | 191.0812 | 152.8275 | 0.24133 | 0.068889 | 19.2765 | 363.1852 | 5 | 16.3495 | 1.0303 | 0.30683
2016-06-30 13:00 | 298.7467 | 187.83 | 110.9167 | 196.8018 | 23.2045 | 29.874 | 55.6952 | 34.3048 | 33.6559 | 28.6856 | 172.6478 | 140.8725 | 0.24111 | 0.068519 | 18.0078 | 331.5281 | 5.2 | 15.5603 | 1.033 | 0.28083
2016-06-30 14:00 | 277.9933 | 171.89 | 106.1033 | 199.9232 | 23.202 | 44.8719 | 57.9459 | 32.0541 | 49.9163 | 42.4399 | 147.5404 | 128.9175 | 0.24089 | 0.068148 | 16.7414 | 293.1993 | 5 | 14.1625 | 1.0379 | 0.24954
2016-06-30 15:00 | 257.24 | 155.95 | 101.29 | 207.6315 | 23.1996 | 59.8698 | 60.8016 | 29.1984 | 65.5972 | 56.203 | 115.4954 | 116.9625 | 0.24067 | 0.067778 | 15.4773 | 247.9351 | 5.1 | 12.848 | 1.0425 | 0.21195
2016-06-30 16:00 | 230.73 | 138.3467 | 92.3833 | 210.9883 | 23.1971 | 74.8677 | 64.0326 | 25.9674 | 80.723 | 69.852 | 72.674 | 103.76 | 0.24044 | 0.067407 | 13.8694 | 190.3035 | 5.2 | 11.147 | 1.0485 | 0.16361
2016-06-30 17:00 | 204.22 | 120.7433 | 83.4767 | 217.2764 | 23.1946 | 89.8656 | 67.4062 | 22.5938 | 95.3897 | 83.2812 | 25.4204 | 90.5575 | 0.24022 | 0.067037 | 12.2645 | 128.2425 | 5.3 | 9.3076 | 1.0549 | 0.11093
2016-06-30 18:00 | 177.71 | 103.14 | 74.57 | 225.6304 | 23.1921 | 104.8635 | 70.7011 | 19.2989 | 109.724 | 96.3501 | 0 | 77.355 | 0.24 | 0.066667 | 10.6626 | 88.0176 | 5.5 | 8.2506 | 1.0586 | 0.076406
2016-06-30 19:00 | 145.3367 | 81.5967 | 63.74 | 227.3041 | 23.1896 | 119.8614 | 73.7149 | 16.2851 | 123.8512 | 108.8351 | 0 | 61.1975 | 0.23978 | 0.066296 | 8.7121 | 69.9096 | 5.9 | 8.0847 | 1.0592 | 0.06072
2016-06-30 20:00 | 112.9633 | 60.0533 | 52.91 | 222.9025 | 23.1871 | 134.8593 | 76.2687 | 13.7313 | 137.8747 | 120.3494 | 0 | 45.04 | 0.23956 | 0.065926 | 6.7652 | 51.8052 | 5.2 | 6.8189 | 1.0636 | 0.045183
2016-06-30 21:00 | 80.59 | 38.51 | 42.08 | 205.9919 | 23.1846 | 149.8572 | 78.2127 | 11.7873 | 151.8652 | 130.1996 | 0 | 28.8825 | 0.23933 | 0.065556 | 4.822 | 33.7045 | 5.2 | 6.2533 | 1.0656 | 0.029451
2016-06-30 22:00 | 76.31 | 42.1867 | 34.1233 | 186.0556 | 23.182 | 164.8551 | 79.4319 | 10.5681 | 165.8589 | 137.2089 | 0 | 31.64 | 0.23911 | 0.065185 | 4.5616 | 36.2016 | 4.9 | 6.0313 | 1.0664 | 0.031656
2016-06-30 23:00 | 72.03 | 45.8633 | 26.1667 | 148.5387 | 23.1795 | 179.853 | 79.8538 | 10.1462 | 179.8627 | 139.8536 | 0 | 34.3975 | 0.23889 | 0.064815 | 4.3018 | 38.6993 | 5 | 6.2094 | 1.0658 | 0.03382
2016-07-01 | 67.75 | 49.54 | 18.21 | 99.4859 | 23.1769 | -165.1491 | 79.4531 | 10.5469 | -166.1331 | 137.3123 | 0 | 37.155 | 0.23867 | 0.064444 | 4.0424 | 41.1974 | 4.7 | 5.9874 | 1.0665 | 0.03603
2016-07-01 01:00 | 78.5567 | 66.3167 | 12.24 | 60.1254 | 23.1744 | -150.1512 | 78.2539 | 11.7461 | -152.1383 | 130.377 | 0 | 49.7375 | 0.23844 | 0.064074 | 4.6829 | 54.4204 | 4.6 | 6.3006 | 1.0654 | 0.047545
2016-07-01 02:00 | 89.3633 | 83.0933 | 6.27 | 26.5274 | 23.1718 | -135.1533 | 76.3282 | 13.6718 | -138.1465 | 120.571 | 0 | 62.32 | 0.23822 | 0.063704 | 5.3221 | 67.6421 | 4.3 | 6.4138 | 1.0651 | 0.059075
2016-07-01 03:00 | 100.17 | 99.87 | 0.3 | 1.0746 | 23.1692 | -120.1554 | 73.7899 | 16.2101 | -124.1226 | 109.0817 | 0 | 74.9025 | 0.238 | 0.063333 | 5.9601 | 80.8626 | 4.3 | 6.827 | 1.0636 | 0.070525
2016-07-01 04:00 | 136.0133 | 127.26 | 8.7533 | 26.6011 | 23.1666 | -105.1575 | 70.7883 | 19.2117 | -109.9964 | 96.6108 | 0 | 95.445 | 0.23778 | 0.062963 | 8.0852 | 103.5302 | 4 | 7.2353 | 1.0622 | 0.090173
2016-07-01 05:00 | 171.8567 | 154.65 | 17.2067 | 44.9668 | 23.164 | -90.1596 | 67.5019 | 22.4981 | -95.6654 | 83.5497 | 5.0516 | 115.9875 | 0.23756 | 0.062593 | 10.2064 | 131.2455 | 4 | 8.1014 | 1.0591 | 0.11399
2016-07-01 06:00 | 207.7 | 182.04 | 25.66 | 58.8144 | 23.1613 | -75.1617 | 64.1327 | 25.8673 | -81.0049 | 70.1243 | 19.9958 | 136.53 | 0.23733 | 0.062222 | 12.3235 | 168.8493 | 5 | 10.2765 | 1.0515 | 0.14559
2016-07-01 07:00 | 238.9233 | 199.6567 | 39.2667 | 80.7446 | 23.1587 | -60.1637 | 60.9019 | 29.0981 | -65.8883 | 56.4759 | 44.5942 | 149.7425 | 0.23711 | 0.061852 | 14.1628 | 208.4996 | 4.8 | 11.3156 | 1.0479 | 0.17916
2016-07-01 08:00 | 270.1467 | 217.2733 | 52.8733 | 99.893 | 23.156 | -45.1658 | 58.0419 | 31.9581 | -50.2191 | 42.7103 | 73.4007 | 162.955 | 0.23689 | 0.061481 | 15.9987 | 252.3544 | 5.1 | 12.9861 | 1.042 | 0.21563
2016-07-01 09:00 | 301.37 | 234.89 | 66.48 | 118.2216 | 23.1534 | -30.1679 | 55.7827 | 34.2173 | -33.9713 | 28.9477 | 103.4513 | 176.1675 | 0.23667 | 0.061111 | 17.8311 | 297.4498 | 5.5 | 14.7953 | 1.0357 | 0.25262
2016-07-01 10:00 | 299.92 | 234.4167 | 65.5033 | 112.3258 | 23.1507 | -15.17 | 54.3272 | 35.6728 | -17.2288 | 15.5204 | 108.2299 | 175.8125 | 0.23644 | 0.060741 | 17.7286 | 301.771 | 5.4 | 14.8303 | 1.0356 | 0.25626
2016-07-01 11:00 | 298.47 | 233.9433 | 64.5267 | 109.3039 | 23.148 | -0.17205 | 53.8187 | 36.1813 | -0.196 | 6.1834 | 108.668 | 175.4575 | 0.23622 | 0.06037 | 17.6263 | 301.7518 | 5.7 | 15.1297 | 1.0345 | 0.25598
2016-07-01 12:00 | 297.02 | 233.47 | 63.55 | 108.9302 | 23.1453 | 14.8259 | 54.3099 | 35.6901 | 16.8398 | 15.223 | 105.108 | 175.1025 | 0.236 | 0.06 | 17.5242 | 297.7347 | 5.4 | 14.7042 | 1.036 | 0.25294
2016-07-01 13:00 | 280.51 | 235.6167 | 44.8933 | 79.7675 | 23.1426 | 29.8238 | 55.7502 | 34.2498 | 33.5904 | 28.6322 | 70.013 | 176.7125 | 0.23578 | 0.05963 | 16.5345 | 263.26 | 6.2 | 14.4269 | 1.037 | 0.22386
2016-07-01 14:00 | 264 | 237.7633 | 26.2367 | 49.5083 | 23.1399 | 44.8217 | 57.9983 | 32.0017 | 49.8491 | 42.3939 | 36.5632 | 178.3225 | 0.23556 | 0.059259 | 15.5467 | 230.4324 | 5.8 | 13.001 | 1.042 | 0.19689
2016-07-01 15:00 | 247.49 | 239.91 | 7.58 | 15.5626 | 23.1371 | 59.8197 | 60.8522 | 29.1478 | 65.5298 | 56.1631 | 8.6657 | 179.9325 | 0.23533 | 0.058889 | 14.5607 | 203.1589 | 6.5 | 12.8487 | 1.0425 | 0.17368
2016-07-01 16:00 | 210.2367 | 200.94 | 9.2967 | 21.27 | 23.1344 | 74.8176 | 64.0823 | 25.9177 | 80.6564 | 69.8181 | 7.3382 | 150.705 | 0.23511 | 0.058519 | 12.3572 | 170.4004 | 8.4 | 13.725 | 1.0395 | 0.14524
2016-07-01 17:00 | 172.9833 | 161.97 | 11.0133 | 28.726 | 23.1316 | 89.8155 | 67.456 | 22.544 | 95.3247 | 83.2539 | 3.3744 | 121.4775 | 0.23489 | 0.058148 | 10.158 | 135.0099 | 7.7 | 11.9191 | 1.0458 | 0.11578
2016-07-01 18:00 | 135.73 | 123 | 12.73 | 38.6159 | 23.1288 | 104.8135 | 70.7521 | 19.2479 | 109.6612 | 96.3305 | 0 | 92.25 | 0.23467 | 0.057778 | 7.9628 | 100.2128 | 6.8 | 9.9317 | 1.0527 | 0.086508
2016-07-01 19:00 | 117.1433 | 100.0033 | 17.14 | 61.3169 | 23.1261 | 119.8114 | 73.7678 | 16.2322 | 123.7909 | 108.8254 | 0 | 75.0025 | 0.23444 | 0.057407 | 6.8659 | 81.8684 | 6 | 8.5584 | 1.0575 | 0.070995
2016-07-01 20:00 | 98.5567 | 77.0067 | 21.55 | 91.148 | 23.1233 | 134.8093 | 76.3241 | 13.6759 | 137.8172 | 120.3528 | 0 | 57.755 | 0.23422 | 0.057037 | 5.771 | 63.526 | 6.1 | 8.0852 | 1.0592 | 0.055175
2016-07-01 21:00 | 79.97 | 54.01 | 25.96 | 127.7042 | 23.1205 | 149.8073 | 78.271 | 11.729 | 151.8111 | 130.2205 | 0 | 40.5075 | 0.234 | 0.056667 | 4.6782 | 45.1857 | 4.8 | 6.2121 | 1.0658 | 0.039489
2016-07-01 22:00 | 82.5233 | 50.6133 | 31.91 | 174.9951 | 23.1176 | 164.8052 | 79.4934 | 10.5066 | 165.8084 | 137.2519 | 0 | 37.96 | 0.23378 | 0.056296 | 4.823 | 42.783 | 5.1 | 6.437 | 1.065 | 0.037361
2016-07-01 23:00 | 85.0767 | 47.2167 | 37.86 | 216.2815 | 23.1148 | 179.8032 | 79.9185 | 10.0815 | 179.8161 | 139.9181 | 0 | 35.4125 | 0.23356 | 0.055926 | 4.9675 | 40.38 | 4.9 | 6.1619 | 1.0659 | 0.035295
2016-07-02 | 87.63 | 43.82 | 43.81 | 240.8704 | 23.112 | -165.1989 | 79.5206 | 10.4794 | -166.1757 | 137.3894 | 0 | 32.865 | 0.23333 | 0.055556 | 5.1117 | 37.9768 | 5.2 | 6.3868 | 1.0651 | 0.03317
2016-07-02 01:00 | 87.56 | 58.2533 | 29.3067 | 144.8121 | 23.1091 | -150.201 | 78.324 | 11.676 | -152.177 | 130.4565 | 0 | 43.69 | 0.23311 | 0.055185 | 5.1028 | 48.7928 | 5.5 | 7.0248 | 1.0629 | 0.042527
2016-07-02 02:00 | 87.49 | 72.6867 | 14.8033 | 62.9564 | 23.1063 | -135.203 | 76.4003 | 13.5997 | -138.1819 | 120.6475 | 0 | 54.515 | 0.23289 | 0.054815 | 5.0939 | 59.6089 | 5.7 | 7.5628 | 1.061 | 0.051862
2016-07-02 03:00 | 87.42 | 87.12 | 0.3 | 1.0794 | 23.1034 | -120.2051 | 73.8636 | 16.1364 | -124.1552 | 109.1535 | 0 | 65.34 | 0.23267 | 0.054444 | 5.0849 | 70.4249 | 5.6 | 7.8008 | 1.0602 | 0.061225
2016-07-02 04:00 | 116.6333 | 104.1233 | 12.51 | 38.1605 | 23.1005 | -105.2071 | 70.8631 | 19.1369 | -110.0273 | 96.6776 | 0 | 78.0925 | 0.23244 | 0.054074 | 6.7777 | 84.8702 | 5.9 | 8.5522 | 1.0576 | 0.0736
2016-07-02 05:00 | 145.8467 | 121.1267 | 24.72 | 64.8079 | 23.0976 | -90.2092 | 67.5774 | 22.4226 | -95.6957 | 83.6116 | 7.211 | 90.845 | 0.23222 | 0.053704 | 8.4672 | 106.5232 | 6.5 | 9.8288 | 1.0531 | 0.091987
2016-07-02 06:00 | 175.06 | 138.13 | 36.93 | 84.8773 | 23.0947 | -75.2112 | 64.2084 | 25.7916 | -81.036 | 70.1813 | 28.7773 | 103.5975 | 0.232 | 0.053333 | 10.1535 | 142.5282 | 6.4 | 10.854 | 1.0495 | 0.12266
2016-07-02 07:00 | 184.22 | 147.4567 | 36.7633 | 75.7763 | 23.0918 | -60.2132 | 60.9773 | 29.0227 | -65.9219 | 56.5278 | 41.7931 | 110.5925 | 0.23178 | 0.052963 | 10.6745 | 163.0601 | 7.1 | 12.1956 | 1.0448 | 0.1397
2016-07-02 08:00 | 193.38 | 156.7833 | 36.5967 | 69.2863 | 23.0888 | -45.2153 | 58.1164 | 31.8836 | -50.2568 | 42.7561 | 50.8735 | 117.5875 | 0.23156 | 0.052593 | 11.1946 | 179.6555 | 6.7 | 12.3142 | 1.0444 | 0.15386
2016-07-02 09:00 | 202.54 | 166.11 | 36.43 | 64.9054 | 23.0859 | -30.2173 | 55.8558 | 34.1442 | -34.0146 | 28.985 | 56.7758 | 124.5825 | 0.23133 | 0.052222 | 11.7136 | 193.0719 | 6.5 | 12.5335 | 1.0436 | 0.16523
2016-07-02 10:00 | 185.8967 | 153.6233 | 32.2733 | 55.4382 | 23.0829 | -15.2194 | 54.3981 | 35.6019 | -17.2784 | 15.5391 | 53.4119 | 115.2175 | 0.23111 | 0.051852 | 10.7407 | 179.37 | 5.9 | 11.5053 | 1.0472 | 0.15403
2016-07-02 11:00 | 169.2533 | 141.1367 | 28.1167 | 47.7053 | 23.0799 | -0.2214 | 53.8868 | 36.1132 | -0.25212 | 6.1168 | 47.4337 | 105.8525 | 0.23089 | 0.051481 | 9.7697 | 163.0559 | 6.5 | 11.5955 | 1.0469 | 0.13998
2016-07-02 12:00 | 152.61 | 128.65 | 23.96 | 41.1345 | 23.077 | 14.7766 | 54.3748 | 35.6252 | 16.7781 | 15.156 | 39.7037 | 96.4875 | 0.23067 | 0.051111 | 8.8005 | 144.9917 | 8.1 | 12.631 | 1.0433 | 0.12404
2016-07-02 13:00 | 125.12 | 105.6067 | 19.5133 | 34.7268 | 23.074 | 29.7745 | 55.812 | 34.188 | 33.5249 | 28.579 | 30.4956 | 79.205 | 0.23044 | 0.050741 | 7.2083 | 116.9089 | 8 | 11.6534 | 1.0467 | 0.10034
2016-07-02 14:00 | 97.63 | 82.5633 | 15.0667 | 28.4777 | 23.071 | 44.7725 | 58.0575 | 31.9425 | 49.7815 | 42.3489 | 21.0466 | 61.9225 | 0.23022 | 0.05037 | 5.6191 | 88.5883 | 7.6 | 10.3684 | 1.0512 | 0.076362
2016-07-02 15:00 | 70.14 | 59.52 | 10.62 | 21.8433 | 23.068 | 59.7705 | 60.9095 | 29.0905 | 65.4617 | 56.1247 | 12.1752 | 44.64 | 0.23 | 0.05 | 4.033 | 60.8482 | 6.3 | 8.2015 | 1.0588 | 0.052829
2016-07-02 16:00 | 64.4767 | 55.68 | 8.7967 | 20.1669 | 23.0649 | 74.7684 | 64.1387 | 25.8613 | 80.589 | 69.7862 | 6.9681 | 41.76 | 0.22978 | 0.04963 | 3.7038 | 52.432 | 6.9 | 8.5385 | 1.0576 | 0.045471
2016-07-02 17:00 | 58.8133 | 51.84 | 6.9733 | 18.2319 | 23.0619 | 89.7664 | 67.5126 | 22.4874 | 95.2589 | 83.2291 | 2.1495 | 38.88 | 0.22956 | 0.049259 | 3.3752 | 44.4048 | 7.6 | 8.9876 | 1.056 | 0.038453
2016-07-02 18:00 | 53.15 | 48 | 5.15 | 15.6675 | 23.0588 | 104.7644 | 70.8098 | 19.1902 | 109.5975 | 96.3142 | 0 | 36 | 0.22933 | 0.048889 | 3.0473 | 39.0473 | 6.7 | 7.9202 | 1.0598 | 0.033933
2016-07-02 19:00 | 46.1133 | 38.6733 | 7.44 | 26.7115 | 23.0558 | 119.7624 | 73.8274 | 16.1726 | 123.73 | 108.8196 | 0 | 29.005 | 0.22911 | 0.048519 | 2.6413 | 31.6463 | 6.7 | 7.6889 | 1.0606 | 0.027522
2016-07-02 20:00 | 39.0767 | 29.3467 | 9.73 | 41.3385 | 23.0527 | 134.7604 | 76.3863 | 13.6137 | 137.7596 | 120.3609 | 0 | 22.01 | 0.22889 | 0.048148 | 2.2361 | 24.2461 | 7.4 | 8.1577 | 1.0589 | 0.021054
2016-07-02 21:00 | 32.04 | 20.02 | 12.02 | 59.4553 | 23.0496 | 149.7583 | 78.3362 | 11.6638 | 151.757 | 130.2471 | 0 | 15.015 | 0.22867 | 0.047778 | 1.8316 | 16.8466 | 7.1 | 7.6265 | 1.0608 | 0.014654
2016-07-02 22:00 | 53.7767 | 25.18 | 28.5967 | 157.8392 | 23.0465 | 164.7563 | 79.5617 | 10.4383 | 165.7584 | 137.3013 | 0 | 18.885 | 0.22844 | 0.047407 | 3.0712 | 21.9562 | 5.5 | 6.1861 | 1.0658 | 0.01919
2016-07-02 23:00 | 75.5133 | 30.34 | 45.1733 | 259.881 | 23.0434 | 179.7543 | 79.9898 | 10.0102 | 179.7704 | 139.9892 | 0 | 22.755 | 0.22822 | 0.047037 | 4.3085 | 27.0635 | 6.1 | 6.9457 | 1.0632 | 0.023594
2016-07-03 | 97.25 | 35.5 | 61.75 | 341.8995 | 23.0403 | -165.2477 | 79.5948 | 10.4052 | -166.217 | 137.4724 | 0 | 26.625 | 0.228 | 0.046667 | 5.5432 | 32.1683 | 5.7 | 6.7053 | 1.064 | 0.028067
2016-07-03 01:00 | 81.1967 | 39.99 | 41.2067 | 204.9396 | 23.0371 | -150.2497 | 78.4006 | 11.5994 | -152.2141 | 130.5407 | 0 | 29.9925 | 0.22778 | 0.046296 | 4.6237 | 34.6162 | 5.7 | 6.7818 | 1.0638 | 0.030195
2016-07-03 02:00 | 65.1433 | 44.48 | 20.6633 | 88.3793 | 23.034 | -135.2517 | 76.4789 | 13.5211 | -138.2153 | 120.7275 | 0 | 33.36 | 0.22756 | 0.045926 | 3.7059 | 37.0659 | 6.4 | 7.5583 | 1.061 | 0.032249
2016-07-03 03:00 | 49.09 | 48.97 | 0.12 | 0.43387 | 23.0309 | -120.2537 | 73.9437 | 16.0563 | -124.1855 | 109.2278 | 0 | 36.7275 | 0.22733 | 0.045556 | 2.7899 | 39.5174 | 5.9 | 7.1349 | 1.0625 | 0.03443
2016-07-03 04:00 | 55.2133 | 54.54 | 0.67333 | 2.0624 | 23.0277 | -105.2557 | 70.9443 | 19.0557 | -110.0556 | 96.7461 | 0 | 40.905 | 0.22711 | 0.045185 | 3.1349 | 44.0399 | 7 | 8.3762 | 1.0582 | 0.038214
2016-07-03 05:00 | 61.3367 | 60.11 | 1.2267 | 3.2271 | 23.0245 | -90.2577 | 67.6592 | 22.3408 | -95.7233 | 83.6745 | 0.35555 | 45.0825 | 0.22689 | 0.044815 | 3.4792 | 48.9172 | 6.1 | 7.6287 | 1.0608 | 0.042551
2016-07-03 06:00 | 67.46 | 65.68 | 1.78 | 4.1032 | 23.0213 | -75.2597 | 64.2904 | 25.7096 | -81.0644 | 70.2387 | 1.3873 | 49.26 | 0.22667 | 0.044444 | 3.8227 | 54.47 | 6.7 | 8.4022 | 1.0581 | 0.04726
2016-07-03 07:00 | 64.62 | 63.4067 | 1.2133 | 2.5074 | 23.0181 | -60.2617 | 61.0591 | 28.9409 | -65.9528 | 56.5795 | 1.381 | 47.555 | 0.22644 | 0.044074 | 3.6582 | 52.5942 | 6.1 | 7.7436 | 1.0604 | 0.045732
2016-07-03 08:00 | 61.78 | 61.1333 | 0.64667 | 1.2271 | 23.0149 | -45.2637 | 58.1974 | 31.8026 | -50.2919 | 42.8012 | 0.90033 | 45.85 | 0.22622 | 0.043704 | 3.494 | 50.2443 | 6.4 | 7.9701 | 1.0596 | 0.043656
2016-07-03 09:00 | 58.94 | 58.86 | 0.08 | 0.14282 | 23.0117 | -30.2657 | 55.9354 | 34.0646 | -34.0556 | 29.0208 | 0.12489 | 44.145 | 0.226 | 0.043333 | 3.3301 | 47.6 | 6.1 | 7.5875 | 1.0609 | 0.041411
2016-07-03 10:00 | 86.21 | 86.1567 | 0.053333 | 0.091788 | 23.0084 | -15.2677 | 54.4757 | 35.5243 | -17.3263 | 15.5551 | 0.088426 | 64.6175 | 0.22578 | 0.042963 | 4.8661 | 69.572 | 6.6 | 8.7741 | 1.0568 | 0.060289
2016-07-03 11:00 | 113.48 | 113.4533 | 0.026667 | 0.045326 | 23.0052 | -0.26972 | 53.9616 | 36.0384 | -0.30703 | 6.0438 | 0.045074 | 85.09 | 0.22556 | 0.042593 | 6.399 | 91.5341 | 6.8 | 9.6604 | 1.0537 | 0.079088
2016-07-03 12:00 | 140.75 | 140.75 | 0 | 0 | 23.0019 | 14.7283 | 54.4465 | 35.5535 | 16.7171 | 15.0877 | 0 | 105.5625 | 0.22533 | 0.042222 | 7.9289 | 113.4914 | 7.4 | 10.9466 | 1.0492 | 0.09764
2016-07-03 13:00 | 117.7433 | 117.7433 | 0 | 0 | 22.9987 | 29.7263 | 55.8807 | 34.1193 | 33.4594 | 28.5261 | 0 | 88.3075 | 0.22511 | 0.041852 | 6.6263 | 94.9338 | 6.6 | 9.5667 | 1.054 | 0.082051
2016-07-03 14:00 | 94.7367 | 94.7367 | 0 | 0 | 22.9954 | 44.7243 | 58.1234 | 31.8766 | 49.7135 | 42.3048 | 0 | 71.0525 | 0.22489 | 0.041481 | 5.3263 | 76.3788 | 7.1 | 9.4868 | 1.0543 | 0.066031
2016-07-03 15:00 | 71.73 | 71.73 | 0 | 0 | 22.9921 | 59.7223 | 60.9736 | 29.0264 | 65.3929 | 56.0879 | 0 | 53.7975 | 0.22467 | 0.041111 | 4.0288 | 57.8263 | 7.2 | 9.0071 | 1.056 | 0.050072
2016-07-03 16:00 | 51.1733 | 51.1733 | 0 | 0 | 22.9888 | 74.7203 | 64.2019 | 25.7981 | 80.5208 | 69.7565 | 0 | 38.38 | 0.22444 | 0.040741 | 2.8714 | 41.2514 | 7.7 | 8.9891 | 1.056 | 0.035722
2016-07-03 17:00 | 30.6167 | 30.6167 | 0 | 0 | 22.9855 | 89.7184 | 67.576 | 22.424 | 95.1923 | 83.2071 | 0 | 22.9625 | 0.22422 | 0.04037 | 1.7162 | 24.6787 | 8.2 | 8.9712 | 1.0561 | 0.021372
2016-07-03 18:00 | 10.06 | 10.06 | 0 | 0 | 22.9821 | 104.7164 | 70.8742 | 19.1258 | 109.5333 | 96.3011 | 0 | 7.545 | 0.224 | 0.04 | 0.56336 | 8.1084 | 7.7 | 7.9534 | 1.0597 | 0.0070455
2016-07-03 19:00 | 22.7967 | 11.89 | 10.9067 | 39.3147 | 22.9788 | 119.7144 | 73.8937 | 16.1063 | 123.6687 | 108.8178 | 0 | 8.9175 | 0.22378 | 0.03963 | 1.2753 | 10.1928 | 9 | 9.3185 | 1.0549 | 0.0088169
2016-07-03 20:00 | 35.5333 | 13.72 | 21.8133 | 93.138 | 22.9754 | 134.7124 | 76.4553 | 13.5447 | 137.7017 | 120.3738 | 0 | 10.29 | 0.22356 | 0.039259 | 1.9859 | 12.2759 | 8.5 | 8.8836 | 1.0564 | 0.010634
2016-07-03 21:00 | 48.27 | 15.55 | 32.72 | 162.8351 | 22.9721 | 149.7105 | 78.4081 | 11.5919 | 151.7032 | 130.2794 | 0 | 11.6625 | 0.22333 | 0.038889 | 2.6951 | 14.3576 | 7.8 | 8.2487 | 1.0586 | 0.012463
2016-07-03 22:00 | 67.8 | 19.13 | 48.67 | 270.5571 | 22.9687 | 164.7085 | 79.6368 | 10.3632 | 165.7089 | 137.3572 | 0 | 14.3475 | 0.22311 | 0.038519 | 3.7817 | 18.1292 | 7 | 7.5665 | 1.061 | 0.015773
2016-07-03 23:00 | 87.33 | 22.71 | 64.62 | 374.649 | 22.9653 | 179.7065 | 80.0679 | 9.9321 | 179.7257 | 140.067 | 0 | 17.0325 | 0.22289 | 0.038148 | 4.8662 | 21.8987 | 6.7 | 7.3843 | 1.0617 | 0.019064
2016-07-04 | 106.86 | 26.29 | 80.57 | 449.5559 | 22.9619 | -165.2954 | 79.6756 | 10.3244 | -166.2569 | 137.5614 | 0 | 19.7175 | 0.22267 | 0.037778 | 5.9485 | 25.666 | 5.6 | 6.4021 | 1.0651 | 0.022416
2016-07-04 01:00 | 90.4533 | 33.12 | 57.3333 | 287.1757 | 22.9585 | -150.2974 | 78.4838 | 11.5162 | -152.2495 | 130.6296 | 0 | 24.84 | 0.22244 | 0.037407 | 5.0302 | 29.8702 | 6.2 | 7.1334 | 1.0625 | 0.026025
2016-07-04 02:00 | 74.0467 | 39.95 | 34.0967 | 146.7409 | 22.9551 | -135.2994 | 76.564 | 13.436 | -138.2465 | 120.8109 | 0 | 29.9625 | 0.22222 | 0.037037 | 4.1137 | 34.0762 | 5.8 | 6.8649 | 1.0635 | 0.029716
2016-07-04 03:00 | 57.64 | 46.78 | 10.86 | 39.472 | 22.9516 | -120.3013 | 74.0301 | 15.9699 | -124.2135 | 109.3045 | 0 | 35.085 | 0.222 | 0.036667 | 3.199 | 38.284 | 5.4 | 6.5964 | 1.0644 | 0.033415
2016-07-04 04:00 | 64.8433 | 57.5533 | 7.29 | 22.4277 | 22.9482 | -105.3033 | 71.0317 | 18.9683 | -110.0813 | 96.8161 | 0 | 43.165 | 0.22178 | 0.036296 | 3.5952 | 46.7602 | 6 | 7.4613 | 1.0614 | 0.040697
2016-07-04 05:00 | 72.0467 | 68.3267 | 3.72 | 9.8232 | 22.9447 | -90.3053 | 67.7472 | 22.2528 | -95.7481 | 83.7383 | 1.0714 | 51.245 | 0.22156 | 0.035926 | 3.9906 | 56.307 | 6.3 | 8.0596 | 1.0593 | 0.048909
2016-07-04 06:00 | 79.25 | 79.1 | 0.15 | 0.34688 | 22.9413 | -75.3072 | 64.3787 | 25.6213 | -81.09 | 70.2964 | 0.11695 | 59.325 | 0.22133 | 0.035556 | 4.3852 | 63.8271 | 5.6 | 7.5946 | 1.0609 | 0.055527
2016-07-04 07:00 | 94.9833 | 94.3167 | 0.66667 | 1.3815 | 22.9378 | -60.3092 | 61.1471 | 28.8529 | -65.9809 | 56.631 | 0.75987 | 70.7375 | 0.22111 | 0.035185 | 5.2505 | 76.7478 | 5.7 | 8.0984 | 1.0592 | 0.066656
2016-07-04 08:00 | 110.7167 | 109.5333 | 1.1833 | 2.251 | 22.9343 | -45.3111 | 58.2848 | 31.7152 | -50.3244 | 42.8456 | 1.6504 | 82.15 | 0.22089 | 0.034815 | 6.114 | 89.9144 | 4.9 | 7.7098 | 1.0605 | 0.078192
2016-07-04 09:00 | 126.45 | 124.75 | 1.7 | 3.0418 | 22.9308 | -30.3131 | 56.0215 | 33.9785 | -34.0942 | 29.0552 | 2.659 | 93.5625 | 0.22067 | 0.034444 | 6.9758 | 103.1973 | 4.6 | 7.8249 | 1.0601 | 0.089709
2016-07-04 10:00 | 153.0633 | 148.8567 | 4.2067 | 7.2547 | 22.9273 | -15.315 | 54.5598 | 35.4402 | -17.3724 | 15.5684 | 6.9885 | 111.6425 | 0.22044 | 0.034074 | 8.4355 | 127.0665 | 5.1 | 9.0708 | 1.0558 | 0.11
2016-07-04 11:00 | 179.6767 | 172.9633 | 6.7133 | 11.4333 | 22.9238 | -0.31695 | 54.0431 | 35.9569 | -0.36064 | 5.9645 | 11.3714 | 129.7225 | 0.22022 | 0.033704 | 9.8922 | 150.9861 | 5.2 | 9.9183 | 1.0528 | 0.13034
2016-07-04 12:00 | 206.29 | 197.07 | 9.22 | 15.887 | 22.9202 | 14.6811 | 54.525 | 35.475 | 16.6568 | 15.0181 | 15.3444 | 147.8025 | 0.22 | 0.033333 | 11.346 | 174.4928 | 4.7 | 10.1529 | 1.052 | 0.15052
2016-07-04 13:00 | 200.2167 | 191.5333 | 8.6833 | 15.5107 | 22.9167 | 29.6792 | 55.956 | 34.044 | 33.3941 | 28.4735 | 13.6345 | 143.65 | 0.21978 | 0.032963 | 11.0008 | 168.2853 | 4.6 | 9.8589 | 1.053 | 0.14531
2016-07-04 14:00 | 194.1433 | 185.9967 | 8.1467 | 15.4582 | 22.9131 | 44.6772 | 58.1961 | 31.8039 | 49.6453 | 42.2619 | 11.4403 | 139.4975 | 0.21956 | 0.032593 | 10.6563 | 161.5941 | 5.2 | 10.2498 | 1.0516 | 0.13935
2016-07-04 15:00 | 188.07 | 180.46 | 7.61 | 15.7189 | 22.9095 | 59.6753 | 61.0444 | 28.9556 | 65.3236 | 56.0528 | 8.7779 | 135.345 | 0.21933 | 0.032222 | 10.3125 | 154.4354 | 5.1 | 9.9261 | 1.0528 | 0.13332
2016-07-04 16:00 | 161.4933 | 156.3333 | 5.16 | 11.8866 | 22.906 | 74.6734 | 64.2719 | 25.7281 | 80.452 | 69.729 | 4.1183 | 117.25 | 0.21911 | 0.031852 | 8.8462 | 130.2145 | 4.8 | 8.8692 | 1.0565 | 0.1128
2016-07-04 17:00 | 134.9167 | 132.2067 | 2.71 | 7.1254 | 22.9024 | 89.6714 | 67.646 | 22.354 | 95.125 | 83.1878 | 0.84519 | 99.155 | 0.21889 | 0.031481 | 7.3829 | 107.3831 | 4.8 | 8.1557 | 1.059 | 0.093245
2016-07-04 18:00 | 108.34 | 108.08 | 0.26 | 0.7964 | 22.8987 | 104.6695 | 70.9453 | 19.0547 | 109.4684 | 96.2914 | 0 | 81.06 | 0.21867 | 0.031111 | 5.9226 | 86.9826 | 4.8 | 7.5182 | 1.0612 | 0.07569
2016-07-04 19:00 | 105.7367 | 88.16 | 17.5767 | 63.639 | 22.8951 | 119.6676 | 73.9668 | 16.0332 | 123.607 | 108.82 | 0 | 66.12 | 0.21844 | 0.030741 | 5.7744 | 71.8944 | 4.5 | 6.7467 | 1.0639 | 0.06272
2016-07-04 20:00 | 103.1333 | 68.24 | 34.8933 | 149.8081 | 22.8915 | 134.6656 | 76.5309 | 13.4691 | 137.6438 | 120.3915 | 0 | 51.18 | 0.21822 | 0.03037 | 5.6265 | 56.8065 | 4.3 | 6.0752 | 1.0662 | 0.049667
2016-07-04 21:00 | 100.53 | 48.32 | 52.21 | 261.5798 | 22.8879 | 149.6637 | 78.4867 | 11.5133 | 151.6495 | 130.3173 | 0 | 36.24 | 0.218 | 0.03 | 5.4789 | 41.7189 | 4.2 | 5.5037 | 1.0682 | 0.036544
2016-07-04 22:00 | 92.8067 | 52.79 | 40.0167 | 224.2021 | 22.8842 | 164.6618 | 79.7185 | 10.2815 | 165.6601 | 137.4195 | 0 | 39.5925 | 0.21778 | 0.02963 | 5.0528 | 44.6453 | 4.3 | 5.6952 | 1.0676 | 0.039083
2016-07-04 23:00 | 85.0833 | 57.26 | 27.8233 | 162.6857 | 22.8805 | 179.6599 | 80.1526 | 9.8474 | 179.682 | 140.1514 | 0 | 42.945 | 0.21756 | 0.029259 | 4.6276 | 47.5726 | 4 | 5.4866 | 1.0683 | 0.041674
2016-07-05 | 77.36 | 61.73 | 15.63 | 87.947 | 22.8769 | -165.342 | 79.763 | 10.237 | -166.2954 | 137.6562 | 0 | 46.2975 | 0.21733 | 0.028889 | 4.2032 | 50.5007 | 3.4 | 4.9781 | 1.0701 | 0.044313
2016-07-05 01:00 | 98.8667 | 84.0333 | 14.8333 | 74.8734 | 22.8732 | -150.344 | 78.5734 | 11.4266 | -152.283 | 130.723 | 0 | 63.025 | 0.21711 | 0.028519 | 5.3663 | 68.3913 | 3.5 | 5.6372 | 1.0678 | 0.059881
2016-07-05 02:00 | 120.3733 | 106.3367 | 14.0367 | 60.8155 | 22.8695 | -135.3459 | 76.6554 | 13.3446 | -138.2756 | 120.8977 | 0 | 79.7525 | 0.21689 | 0.028148 | 6.5269 | 86.2794 | 3.3 | 5.9962 | 1.0665 | 0.075455
2016-07-05 03:00 | 141.88 | 128.64 | 13.24 | 48.3962 | 22.8658 | -120.3478 | 74.1229 | 15.8771 | -124.239 | 109.3835 | 0 | 96.48 | 0.21667 | 0.027778 | 7.6852 | 104.1652 | 4.9 | 8.1552 | 1.059 | 0.090451
2016-07-05 04:00 | 179.04 | 161.9167 | 17.1233 | 52.9318 | 22.8621 | -105.3497 | 71.1254 | 18.8746 | -110.1043 | 96.8877 | 0 | 121.4375 | 0.21644 | 0.027407 | 9.6881 | 131.1256 | 5.5 | 9.5977 | 1.0539 | 0.11332
2016-07-05 05:00 | 216.2 | 195.1933 | 21.0067 | 55.6953 | 22.8583 | -90.3516 | 67.8414 | 22.1586 | -95.7701 | 83.8029 | 6.0122 | 146.395 | 0.21622 | 0.027037 | 11.6868 | 164.094 | 5.7 | 10.8279 | 1.0496 | 0.14123
2016-07-05 06:00 | 253.36 | 228.47 | 24.89 | 57.7582 | 22.8546 | -75.3535 | 64.4731 | 25.5269 | -81.1126 | 70.3544 | 19.4184 | 171.3525 | 0.216 | 0.026667 | 13.6814 | 204.4523 | 6.2 | 12.5891 | 1.0434 | 0.17493
2016-07-05 07:00 | 313.1133 | 251.8467 | 61.2667 | 127.3417 | 22.8508 | -60.3554 | 61.2414 | 28.7586 | -66.0061 | 56.6822 | 69.9466 | 188.885 | 0.21578 | 0.026296 | 16.8907 | 275.7223 | 6.1 | 14.7163 | 1.036 | 0.23423
2016-07-05 08:00 | 372.8667 | 275.2233 | 97.6433 | 186.2338 | 22.847 | -45.3573 | 58.3785 | 31.6215 | -50.3542 | 42.8891 | 136.4484 | 206.4175 | 0.21556 | 0.025926 | 20.0934 | 362.9593 | 5.8 | 17.1425 | 1.0275 | 0.30581
2016-07-05 09:00 | 432.62 | 298.6 | 134.02 | 240.3763 | 22.8433 | -30.3592 | 56.114 | 33.886 | -34.1305 | 29.0881 | 210.0585 | 223.95 | 0.21533 | 0.025556 | 23.2894 | 457.2979 | 5.9 | 20.1906 | 1.0168 | 0.3813
2016-07-05 10:00 | 443.1667 | 290.04 | 153.1267 | 264.6672 | 22.8395 | -15.3611 | 54.6505 | 35.3495 | -17.4164 | 15.579 | 254.9436 | 217.53 | 0.21511 | 0.025185 | 23.8325 | 496.3061 | 6.2 | 21.7096 | 1.0115 | 0.41166
2016-07-05 11:00 | 453.7133 | 281.48 | 172.2333 | 293.9487 | 22.8357 | -0.363 | 54.1313 | 35.8687 | -0.41283 | 5.8789 | 292.4027 | 211.11 | 0.21489 | 0.024815 | 24.3745 | 527.8871 | 6 | 22.4965 | 1.0088 | 0.43666
2016-07-05 12:00 | 464.26 | 272.92 | 191.34 | 330.3884 | 22.8319 | 14.6351 | 54.6102 | 35.3898 | 16.5973 | 14.9473 | 319.2092 | 204.69 | 0.21467 | 0.024444 | 24.9153 | 548.8145 | 5.8 | 22.9505 | 1.0072 | 0.45326
2016-07-05 13:00 | 404.5033 | 268.12 | 136.3833 | 244.1343 | 22.828 | 29.6332 | 56.0382 | 33.9618 | 33.3292 | 28.4213 | 214.7092 | 201.09 | 0.21444 | 0.024074 | 21.6859 | 437.4851 | 6.5 | 20.1714 | 1.0169 | 0.3648
2016-07-05 14:00 | 344.7467 | 263.32 | 81.4267 | 154.8525 | 22.8242 | 44.6313 | 58.2756 | 31.7244 | 49.5769 | 42.2202 | 114.6787 | 197.49 | 0.21422 | 0.023704 | 18.4631 | 330.6318 | 6.2 | 16.5322 | 1.0296 | 0.27915
2016-07-05 15:00 | 284.99 | 258.52 | 26.47 | 54.8094 | 22.8204 | 59.6295 | 61.122 | 28.878 | 65.2539 | 56.0195 | 30.6335 | 193.89 | 0.214 | 0.023333 | 15.247 | 239.7705 | 6.1 | 13.5928 | 1.0399 | 0.20446
2016-07-05 16:00 | 271.5133 | 215.7233 | 55.79 | 128.8761 | 22.8165 | 74.6276 | 64.3485 | 25.6515 | 80.3826 | 69.7038 | 44.7038 | 161.7925 | 0.21378 | 0.022963 | 14.5109 | 221.0072 | 5.2 | 12.1065 | 1.0451 | 0.1894
2016-07-05 17:00 | 258.0367 | 172.9267 | 85.11 | 224.5121 | 22.8126 | 89.6257 | 67.7228 | 22.2772 | 95.0572 | 83.1713 | 26.6949 | 129.695 | 0.21356 | 0.022593 | 13.7763 | 170.1662 | 6.1 | 11.4177 | 1.0475 | 0.14617
2016-07-05 18:00 | 244.56 | 130.13 | 114.43 | 351.8917 | 22.8087 | 104.6238 | 71.0232 | 18.9768 | 109.4031 | 96.2851 | 0 | 97.5975 | 0.21333 | 0.022222 | 13.0432 | 110.6407 | 5.2 | 8.6575 | 1.0572 | 0.095915
2016-07-05 19:00 | 192.3333 | 110.2267 | 82.1067 | 298.7278 | 22.8048 | 119.6219 | 74.0467 | 15.9533 | 123.545 | 108.8263 | 0 | 82.67 | 0.21311 | 0.021852 | 10.2471 | 92.9171 | 5.3 | 8.2037 | 1.0588 | 0.080671
2016-07-05 20:00 | 140.1067 | 90.3233 | 49.7833 | 215.0268 | 22.8009 | 134.6201 | 76.6133 | 13.3867 | 137.5858 | 120.4139 | 0 | 67.7425 | 0.21289 | 0.021481 | 7.4568 | 75.1993 | 5.4 | 7.75 | 1.0604 | 0.065386
2016-07-05 21:00 | 87.88 | 70.42 | 17.46 | 88.1216 | 22.797 | 149.6182 | 78.5721 | 11.4279 | 151.5962 | 130.361 | 0 | 52.815 | 0.21267 | 0.021111 | 4.6723 | 57.4873 | 6 | 7.7965 | 1.0602 | 0.049978
2016-07-05 22:00 | 84.69 | 72.2267 | 12.4633 | 70.4276 | 22.7931 | 164.6163 | 79.8069 | 10.1931 | 165.612 | 137.4883 | 0 | 54.17 | 0.21244 | 0.020741 | 4.498 | 58.668 | 5.9 | 7.7334 | 1.0604 | 0.051015
2016-07-05 23:00 | 81.5 | 74.0333 | 7.4667 | 44.063 | 22.7892 | 179.6145 | 80.2439 | 9.7561 | 179.6393 | 140.2424 | 0 | 55.525 | 0.21222 | 0.02037 | 4.324 | 59.849 | 3.1 | 4.9703 | 1.0701 | 0.052517
2016-07-06 | 78.31 | 75.84 | 2.47 | 14.0256 | 22.7852 | -165.3874 | 79.8569 | 10.1431 | -166.3325 | 137.7567 | 0 | 56.88 | 0.2 | 0 | 3.9155 | 60.7955 | 4 | 5.8999 | 1.0669 | 0.053185
2016-07-06 01:00 | 104.95 | 96.7733 | 8.1767 | 41.6183 | 22.7812 | -150.3893 | 78.6695 | 11.3305 | -152.3147 | 130.8209 | 0 | 72.58 | 0.2 | 0 | 5.2475 | 77.8275 | 4.3 | 6.7321 | 1.0639 | 0.067899
2016-07-06 02:00 | 131.59 | 117.7067 | 13.8833 | 60.5871 | 22.7773 | -135.3911 | 76.7532 | 13.2468 | -138.3025 | 120.9877 | 0 | 88.28 | 0.2 | 0 | 6.5795 | 94.8595 | 5 | 7.9644 | 1.0596 | 0.082423
2016-07-06 03:00 | 158.23 | 138.64 | 19.59 | 72.0452 | 22.7733 | -120.393 | 74.2219 | 15.7781 | -124.262 | 109.4647 | 0 | 103.98 | 0.2 | 0 | 7.9115 | 111.8915 | 4.9 | 8.3966 | 1.0581 | 0.097083
2016-07-06 04:00 | 204.26 | 176.26 | 28 | 86.9974 | 22.7693 | -105.3948 | 71.2252 | 18.7748 | -110.1246 | 96.9607 | 0 | 132.195 | 0.2 | 0 | 10.213 | 142.408 | 4.2 | 8.6502 | 1.0572 | 0.12346
2016-07-06 05:00 | 250.29 | 213.88 | 36.41 | 96.9515 | 22.7653 | -90.3967 | 67.9418 | 22.0582 | -95.7892 | 83.8683 | 10.3557 | 160.41 | 0.2 | 0 | 12.5145 | 183.2802 | 4.9 | 10.6275 | 1.0503 | 0.15785
2016-07-06 06:00 | 296.32 | 251.5 | 44.82 | 104.3904 | 22.7613 | -75.3986 | 64.5737 | 25.4263 | -81.1323 | 70.4126 | 34.9964 | 188.625 | 0.2 | 0 | 14.816 | 238.4374 | 5.3 | 12.7512 | 1.0429 | 0.2039
2016-07-06 07:00 | 313.9067 | 266.78 | 47.1267 | 98.2661 | 22.7572 | -60.4004 | 61.3419 | 28.6581 | -66.0283 | 56.733 | 53.903 | 200.085 | 0.2 | 0 | 15.6953 | 269.6833 | 5.7 | 14.1276 | 1.0381 | 0.22956
2016-07-06 08:00 | 331.4933 | 282.06 | 49.4333 | 94.5516 | 22.7532 | -45.4022 | 58.4785 | 31.5215 | -50.3812 | 42.9317 | 69.2275 | 211.545 | 0.2 | 0 | 16.5747 | 297.3472 | 5.9 | 15.1921 | 1.0343 | 0.25219
2016-07-06 09:00 | 349.08 | 297.34 | 51.74 | 93.0394 | 22.7491 | -30.4041 | 56.2129 | 33.7871 | -34.1643 | 29.1194 | 81.2799 | 223.005 | 0.2 | 0 | 17.454 | 321.7389 | 5.5 | 15.5543 | 1.0331 | 0.27255
2016-07-06 10:00 | 327.28 | 291.66 | 35.62 | 61.714 | 22.7451 | -15.4059 | 54.7476 | 35.2524 | -17.4585 | 15.5871 | 59.4443 | 218.745 | 0.2 | 0 | 16.364 | 294.5533 | 5.8 | 15.0048 | 1.035 | 0.24998
2016-07-06 11:00 | 305.48 | 285.98 | 19.5 | 33.3568 | 22.741 | -0.40777 | 54.226 | 35.774 | -0.46353 | 5.787 | 33.1868 | 214.485 | 0.2 | 0 | 15.274 | 262.9458 | 5.6 | 13.8171 | 1.0391 | 0.22405
2016-07-06 12:00 | 283.68 | 280.3 | 3.38 | 5.8495 | 22.7369 | 14.5904 | 54.702 | 35.298 | 16.5388 | 14.8757 | 5.6534 | 210.225 | 0.2 | 0 | 14.184 | 230.0624 | 5.8 | 12.9895 | 1.042 | 0.19658
2016-07-06 13:00 | 212.7467 | 210.4933 | 2.2533 | 4.0429 | 22.7328 | 29.5886 | 56.127 | 33.873 | 33.2646 | 28.3698 | 3.5574 | 157.87 | 0.2 | 0 | 10.6373 | 172.0647 | 5.7 | 11.077 | 1.0487 | 0.14797
2016-07-06 14:00 | 141.8133 | 140.6867 | 1.1267 | 2.1479 | 22.7287 | 44.5867 | 58.3618 | 31.6382 | 49.5086 | 42.1799 | 1.5916 | 105.515 | 0.2 | 0 | 7.0907 | 114.1973 | 5.6 | 9.1687 | 1.0554 | 0.09883
2016-07-06 15:00 | 70.88 | 70.88 | 0 | 0 | 22.7246 | 59.5849 | 61.2062 | 28.7938 | 65.1839 | 55.9881 | 0 | 53.16 | 0.2 | 0 | 3.544 | 56.704 | 6 | 7.772 | 1.0603 | 0.049301
2016-07-06 16:00 | 75.71 | 75.48 | 0.23 | 0.53292 | 22.7204 | 74.5831 | 64.4318 | 25.5682 | 80.3127 | 69.6809 | 0.18506 | 56.61 | 0.2 | 0 | 3.7855 | 60.5806 | 5.5 | 7.3931 | 1.0616 | 0.052737
2016-07-06 17:00 | 80.54 | 80.08 | 0.46 | 1.2178 | 22.7163 | 89.5812 | 67.8062 | 22.1938 | 94.9889 | 83.1576 | 0.14508 | 60.06 | 0.2 | 0 | 4.027 | 64.2321 | 4.7 | 6.7073 | 1.064 | 0.056043
2016-07-06 18:00 | 85.37 | 84.68 | 0.69 | 2.131 | 22.7121 | 104.5794 | 71.1078 | 18.8922 | 109.3375 | 96.2822 | 0 | 63.51 | 0.2 | 0 | 4.2685 | 67.7785 | 5.3 | 7.4181 | 1.0615 | 0.058998
2016-07-06 19:00 | 76.9867 | 76.48 | 0.50667 | 1.8532 | 22.708 | 119.5776 | 74.1332 | 15.8668 | 123.4828 | 108.8366 | 0 | 57.36 | 0.2 | 0 | 3.8493 | 61.2093 | 4.8 | 6.7128 | 1.064 | 0.053404
2016-07-06 20:00 | 68.6033 | 68.28 | 0.32333 | 1.4057 | 22.7038 | 134.5758 | 76.7024 | 13.2976 | 137.5279 | 120.4413 | 0 | 51.21 | 0.2 | 0 | 3.4302 | 54.6402 | 5.9 | 7.6075 | 1.0609 | 0.047532
2016-07-06 21:00 | 60.22 | 60.08 | 0.14 | 0.71225 | 22.6996 | 149.574 | 78.6641 | 11.3359 | 151.5433 | 130.4103 | 0 | 45.06 | 0.2 | 0 | 3.011 | 48.071 | 6.4 | 7.9022 | 1.0598 | 0.041777
2016-07-06 22:00 | 60.61 | 49.9867 | 10.6233 | 60.5892 | 22.6954 | 164.5721 | 79.9019 | 10.0981 | 165.5646 | 137.5635 | 0 | 37.49 | 0.2 | 0 | 3.0305 | 40.5205 | 6.5 | 7.7663 | 1.0603 | 0.035231
2016-07-06 23:00 | 61 | 39.8933 | 21.1067 | 125.8071 | 22.6912 | 179.5703 | 80.3418 | 9.6582 | 179.5979 | 140.3399 | 0 | 29.92 | 0.2 | 0 | 3.05 | 32.97 | 6.8 | 7.8303 | 1.0601 | 0.02866
2016-07-07 | 61.39 | 29.8 | 31.59 | 181.1545 | 22.687 | -165.4315 | 79.9573 | 10.0427 | -166.3679 | 137.863 | 0 | 22.35 | 0.2 | 0 | 3.0695 | 25.4195 | 7 | 7.7944 | 1.0602 | 0.022099
2016-07-07 01:00 | 61.2067 | 37.0067 | 24.2 | 124.2849 | 22.6827 | -150.4333 | 78.772 | 11.228 | -152.3444 | 130.9232 | 0 | 27.755 | 0.2 | 0 | 3.0603 | 30.8153 | 6.5 | 7.463 | 1.0614 | 0.02682
2016-07-07 02:00 | 61.0233 | 44.2133 | 16.81 | 73.9297 | 22.6785 | -135.4351 | 76.8572 | 13.1428 | -138.3271 | 121.0808 | 0 | 33.16 | 0.2 | 0 | 3.0512 | 36.2112 | 6.9 | 8.0316 | 1.0594 | 0.031457
2016-07-07 03:00 | 60.84 | 51.42 | 9.42 | 34.8701 | 22.6742 | -120.4369 | 74.3271 | 15.6729 | -124.2824 | 109.5481 | 0 | 38.565 | 0.2 | 0 | 3.042 | 41.607 | 6.2 | 7.5002 | 1.0612 | 0.036207
2016-07-07 04:00 | 82.5367 | 71.63 | 10.9067 | 34.073 | 22.67 | -105.4387 | 71.3312 | 18.6688 | -110.1421 | 97.035 | 0 | 53.7225 | 0.2 | 0 | 4.1268 | 57.8493 | 5.7 | 7.5078 | 1.0612 | 0.050341
2016-07-07 05:00 | 104.2333 | 91.84 | 12.3933 | 33.1527 | 22.6657 | -90.4405 | 68.0482 | 21.9518 | -95.8053 | 83.9344 | 3.5031 | 68.88 | 0.2 | 0 | 5.2117 | 77.5948 | 5.9 | 8.3248 | 1.0584 | 0.067341
2016-07-07 06:00 | 125.93 | 112.05 | 13.88 | 32.4551 | 22.6614 | -75.4423 | 64.6804 | 25.3196 | -81.1489 | 70.4709 | 10.8493 | 84.0375 | 0.2 | 0 | 6.2965 | 101.1833 | 6.6 | 9.762 | 1.0533 | 0.087395
2016-07-07 07:00 | 153.0533 | 126.07 | 26.9833 | 56.4566 | 22.6571 | -60.4441 | 61.4485 | 28.5515 | -66.0476 | 56.7835 | 30.9272 | 94.5525 | 0.2 | 0 | 7.6527 | 133.1323 | 7.2 | 11.3604 | 1.0477 | 0.11438
2016-07-07 08:00 | 180.1767 | 140.09 | 40.0867 | 76.9067 | 22.6528 | -45.4459 | 58.5847 | 31.4153 | -50.4054 | 42.9734 | 56.2704 | 105.0675 | 0.2 | 0 | 9.0088 | 170.3467 | 6.7 | 12.0233 | 1.0454 | 0.14603
2016-07-07 09:00 | 207.3 | 154.11 | 53.19 | 95.9103 | 22.6484 | -30.4476 | 56.3182 | 33.6818 | -34.1955 | 29.1492 | 83.7637 | 115.5825 | 0.2 | 0 | 10.365 | 209.7112 | 7.4 | 13.9535 | 1.0387 | 0.17861
2016-07-07 10:00 | 225.18 | 165.16 | 60.02 | 104.2556 | 22.6441 | -15.4494 | 54.8513 | 35.1487 | -17.4984 | 15.5925 | 100.4187 | 123.87 | 0.2 | 0 | 11.259 | 235.5477 | 7.4 | 14.7609 | 1.0358 | 0.20007
2016-07-07 11:00 | 243.06 | 176.21 | 66.85 | 114.6354 | 22.6397 | -0.45121 | 54.3274 | 35.6726 | -0.51263 | 5.6889 | 114.0708 | 132.1575 | 0.2 | 0 | 12.153 | 258.3813 | 8.3 | 16.3744 | 1.0302 | 0.21827
2016-07-07 12:00 | 260.94 | 187.26 | 73.68 | 127.8224 | 22.6354 | 14.547 | 54.8005 | 35.1995 | 16.4813 | 14.8033 | 123.5798 | 140.445 | 0.2 | 0 | 13.047 | 277.0718 | 9.4 | 18.0585 | 1.0243 | 0.23272
2016-07-07 13:00 | 246.9233 | 164.56 | 82.3633 | 148.1438 | 22.631 | 29.5452 | 56.2225 | 33.7775 | 33.2005 | 28.319 | 130.414 | 123.42 | 0.2 | 0 | 12.3462 | 266.1801 | 9.7 | 18.0181 | 1.0244 | 0.2236
2016-07-07 14:00 | 232.9067 | 141.86 | 91.0467 | 174.0278 | 22.6266 | 44.5435 | 58.4547 | 31.5453 | 49.4403 | 42.141 | 129.041 | 106.395 | 0.2 | 0 | 11.6453 | 247.0814 | 8.5 | 16.2213 | 1.0307 | 0.20883
2016-07-07 15:00 | 218.89 | 119.16 | 99.73 | 207.6555 | 22.6222 | 59.5417 | 61.2972 | 28.7028 | 65.1137 | 55.9586 | 116.2439 | 89.37 | 0.2 | 0 | 10.9445 | 216.5584 | 8.2 | 14.9674 | 1.0351 | 0.18381
2016-07-07 16:00 | 198.49 | 116.2067 | 82.2833 | 191.2821 | 22.6178 | 74.5399 | 64.5218 | 25.4782 | 80.2425 | 69.6605 | 66.4863 | 87.155 | 0.2 | 0 | 9.9245 | 163.5658 | 8.2 | 13.3114 | 1.0409 | 0.13961
2016-07-07 17:00 | 178.09 | 113.2533 | 64.8367 | 172.3078 | 22.6134 | 89.5382 | 67.8963 | 22.1037 | 94.9202 | 83.1469 | 20.5603 | 84.94 | 0.2 | 0 | 8.9045 | 114.4048 | 9.1 | 12.6752 | 1.0431 | 0.097859
2016-07-07 18:00 | 157.69 | 110.3 | 47.39 | 147.0448 | 22.609 | 104.5364 | 71.199 | 18.801 | 109.2715 | 96.2828 | 0 | 82.725 | 0.2 | 0 | 7.8845 | 90.6095 | 9.4 | 12.2315 | 1.0447 | 0.07762
2016-07-07 19:00 | 132.4667 | 95.81 | 36.6567 | 134.8475 | 22.6045 | 119.5346 | 74.2263 | 15.7737 | 123.4206 | 108.851 | 0 | 71.8575 | 0.2 | 0 | 6.6233 | 78.4808 | 8.3 | 10.7525 | 1.0499 | 0.067563
2016-07-07 20:00 | 107.2433 | 81.32 | 25.9233 | 113.5086 | 22.6001 | 134.5329 | 76.7982 | 13.2018 | 137.4702 | 120.4735 | 0 | 60.99 | 0.2 | 0 | 5.3622 | 66.3522 | 8.7 | 10.7735 | 1.0498 | 0.057118
2016-07-07 21:00 | 82.02 | 66.83 | 15.19 | 77.9485 | 22.5956 | 149.5311 | 78.7627 | 11.2373 | 151.4909 | 130.4653 | 0 | 50.1225 | 0.2 | 0 | 4.101 | 54.2235 | 9.1 | 10.7945 | 1.0497 | 0.046674
2016-07-07 22:00 | 85.8967 | 62.23 | 23.6667 | 136.339 | 22.5912 | 164.5294 | 80.0036 | 9.9964 | 165.5181 | 137.6451 | 0 | 46.6725 | 0.2 | 0 | 4.2948 | 50.9673 | 8 | 9.5927 | 1.0539 | 0.044047
2016-07-07 23:00 | 89.7733 | 57.63 | 32.1433 | 193.6664 | 22.5867 | 179.5276 | 80.4463 | 9.5537 | 179.5577 | 140.444 | 0 | 43.2225 | 0.2 | 0 | 4.4887 | 47.7112 | 8.4 | 9.891 | 1.0529 | 0.041192
2016-07-08 | 93.65 | 53.03 | 40.62 | 235.4178 | 22.5822 | -165.4741 | 80.0642 | 9.9358 | -166.4017 | 137.9749 | 0 | 39.7725 | 0.2 | 0 | 4.6825 | 44.455 | 7.7 | 9.0892 | 1.0557 | 0.038483
2016-07-08 01:00 | 111.0467 | 70.9233 | 40.1233 | 208.0544 | 22.5777 | -150.4759 | 78.8808 | 11.1192 | -152.3721 | 131.0298 | 0 | 53.1925 | 0.2 | 0 | 5.5523 | 58.7448 | 7.7 | 9.5358 | 1.0541 | 0.050778
2016-07-08 02:00 | 128.4433 | 88.8167 | 39.6267 | 175.7258 | 22.5731 | -135.4776 | 76.9676 | 13.0324 | -138.3493 | 121.177 | 0 | 66.6125 | 0.2 | 0 | 6.4222 | 73.0347 | 7.6 | 9.8823 | 1.0529 | 0.063057
2016-07-08 03:00 | 145.84 | 106.71 | 39.13 | 145.8586 | 22.5686 | -120.4794 | 74.4384 | 15.5616 | -124.3001 | 109.6335 | 0 | 80.0325 | 0.2 | 0 | 7.292 | 87.3245 | 6.8 | 9.5289 | 1.0541 | 0.075483
2016-07-08 04:00 | 169.8733 | 128.95 | 40.9233 | 128.5911 | 22.5641 | -105.4811 | 71.4432 | 18.5568 | -110.1567 | 97.1106 | 0 | 96.7125 | 0.2 | 0 | 8.4937 | 105.2062 | 7.4 | 10.6877 | 1.0501 | 0.090591
2016-07-08 05:00 | 193.9067 | 151.19 | 42.7167 | 114.8282 | 22.5595 | -90.4828 | 68.1607 | 21.8393 | -95.8184 | 84.0011 | 12.0006 | 113.3925 | 0.2 | 0 | 9.6953 | 135.0884 | 7.4 | 11.6215 | 1.0468 | 0.11596
2016-07-08 06:00 | 217.94 | 173.43 | 44.51 | 104.5109 | 22.555 | -75.4846 | 64.7931 | 25.2069 | -81.1624 | 70.5292 | 34.8362 | 130.0725 | 0.2 | 0 | 10.897 | 175.8057 | 8 | 13.4939 | 1.0403 | 0.14997
2016-07-08 07:00 | 296.26 | 193.46 | 102.8 | 215.8669 | 22.5504 | -60.4863 | 61.5612 | 28.4388 | -66.0637 | 56.8335 | 118.0951 | 145.095 | 0.2 | 0 | 14.813 | 278.0031 | 7.6 | 16.2876 | 1.0305 | 0.23491
2016-07-08 08:00 | 374.58 | 213.49 | 161.09 | 310.0494 | 22.5458 | -45.488 | 58.6971 | 31.3029 | -50.4266 | 43.0142 | 226.7035 | 160.1175 | 0.2 | 0 | 18.729 | 405.55 | 8.2 | 20.8734 | 1.0144 | 0.33735
2016-07-08 09:00 | 452.9 | 233.52 | 219.38 | 396.7382 | 22.5412 | -30.4898 | 56.4297 | 33.5703 | -34.2241 | 29.1775 | 346.3974 | 175.14 | 0.2 | 0 | 22.645 | 544.1824 | 8.8 | 25.8057 | 0.99718 | 0.44497
2016-07-08 10:00 | 459.9567 | 240.2233 | 219.7333 | 382.7249 | 22.5366 | -15.4915 | 54.9614 | 35.0386 | -17.536 | 15.5955 | 368.6343 | 180.1675 | 0.2 | 0 | 22.9978 | 571.7997 | 8.5 | 26.3687 | 0.99521 | 0.46663
2016-07-08 11:00 | 467.0133 | 246.9267 | 220.0867 | 378.4011 | 22.532 | -0.49321 | 54.4352 | 35.5648 | -0.56003 | 5.5846 | 376.6051 | 185.195 | 0.2 | 0 | 23.3507 | 585.1507 | 8.2 | 26.486 | 0.9948 | 0.47733
2016-07-08 12:00 | 474.07 | 253.63 | 220.44 | 383.424 | 22.5273 | 14.5051 | 54.9056 | 35.0944 | 16.4249 | 14.7303 | 370.8221 | 190.2225 | 0.2 | 0 | 23.7035 | 584.7481 | 8.8 | 27.0734 | 0.99274 | 0.47601
2016-07-08 13:00 | 435.38 | 222.7467 | 212.6333 | 383.4786 | 22.5227 | 29.5034 | 56.3247 | 33.6753 | 33.137 | 28.2691 | 337.7422 | 167.06 | 0.2 | 0 | 21.769 | 526.5712 | 9.3 | 25.7553 | 0.99736 | 0.43065
2016-07-08 14:00 | 396.69 | 191.8633 | 204.8267 | 392.6202 | 22.518 | 44.5016 | 58.5542 | 31.4458 | 49.3721 | 42.1036 | 291.2983 | 143.8975 | 0.2 | 0 | 19.8345 | 455.0303 | 8.9 | 23.1197 | 1.0066 | 0.37558
2016-07-08 15:00 | 358 | 160.98 | 197.02 | 411.5116 | 22.5134 | 59.4999 | 61.3948 | 28.6052 | 65.0434 | 55.9312 | 230.524 | 120.735 | 0.2 | 0 | 17.9 | 369.159 | 7.7 | 19.2362 | 1.0202 | 0.30882
2016-07-08 16:00 | 314.43 | 157.0633 | 157.3667 | 367.1268 | 22.5087 | 74.4982 | 64.6185 | 25.3815 | 80.1721 | 69.6426 | 127.7143 | 117.7975 | 0.2 | 0 | 15.7215 | 261.2333 | 7.7 | 15.8635 | 1.032 | 0.22106
2016-07-08 17:00 | 270.86 | 153.1467 | 117.7133 | 314.1378 | 22.504 | 89.4965 | 67.9931 | 22.0069 | 94.8513 | 83.1393 | 37.5258 | 114.86 | 0.2 | 0 | 13.543 | 165.9288 | 8.1 | 13.2853 | 1.041 | 0.14164
2016-07-08 18:00 | 227.29 | 149.23 | 78.06 | 243.4315 | 22.4993 | 104.4948 | 71.2968 | 18.7032 | 109.2054 | 96.2869 | 0 | 111.9225 | 0.2 | 0 | 11.3645 | 123.287 | 8.2 | 12.0527 | 1.0453 | 0.10568
2016-07-08 19:00 | 189.9467 | 122.0333 | 67.9133 | 251.3811 | 22.4946 | 119.4931 | 74.3262 | 15.6738 | 123.3583 | 108.8696 | 0 | 91.525 | 0.2 | 0 | 9.4973 | 101.0223 | 7.1 | 10.2569 | 1.0516 | 0.087113
2016-07-08 20:00 | 152.6033 | 94.8367 | 57.7667 | 254.8805 | 22.4899 | 134.4914 | 76.9005 | 13.0995 | 137.4128 | 120.5105 | 0 | 71.1275 | 0.2 | 0 | 7.6302 | 78.7577 | 6.9 | 9.3612 | 1.0547 | 0.068116
2016-07-08 21:00 | 115.26 | 67.64 | 47.62 | 246.6466 | 22.4851 | 149.4897 | 78.868 | 11.132 | 151.4391 | 130.5259 | 0 | 50.73 | 0.2 | 0 | 5.763 | 56.493 | 7.2 | 8.9654 | 1.0561 | 0.048924
2016-07-08 22:00 | 104.9667 | 70.4967 | 34.47 | 200.726 | 22.4804 | 164.488 | 80.1118 | 9.8882 | 165.4726 | 137.7331 | 0 | 52.8725 | 0.2 | 0 | 5.2483 | 58.1208 | 7 | 8.8163 | 1.0566 | 0.050359
2016-07-08 23:00 | 94.6733 | 73.3533 | 21.32 | 129.9503 | 22.4756 | 179.4863 | 80.5572 | 9.4428 | 179.5188 | 140.5545 | 0 | 55.015 | 0.2 | 0 | 4.7337 | 59.7487 | 6.1 | 7.9671 | 1.0596 | 0.051915
2016-07-09 | 84.38 | 76.21 | 8.17 | 47.8909 | 22.4709 | -165.5153 | 80.1775 | 9.8225 | -166.4338 | 138.0925 | 0 | 57.1575 | 0.2 | 0 | 4.219 | 61.3765 | 6.4 | 8.318 | 1.0584 | 0.053267
2016-07-09 01:00 | 111.71 | 96.34 | 15.37 | 80.5227 | 22.4661 | -150.517 | 78.996 | 11.004 | -152.3977 | 131.1406 | 0 | 72.255 | 0.2 | 0 | 5.5855 | 77.8405 | 6.4 | 8.8325 | 1.0566 | 0.067441
2016-07-09 02:00 | 139.04 | 116.47 | 22.57 | 100.9747 | 22.4613 | -135.5187 | 77.0841 | 12.9159 | -138.3691 | 121.2762 | 0 | 87.3525 | 0.2 | 0 | 6.952 | 94.3045 | 6.7 | 9.647 | 1.0537 | 0.081485
2016-07-09 03:00 | 166.37 | 136.6 | 29.77 | 111.7919 | 22.4565 | -120.5204 | 74.5559 | 15.4441 | -124.3152 | 109.7209 | 0 | 102.45 | 0.2 | 0 | 8.3185 | 110.7685 | 5.7 | 9.1615 | 1.0554 | 0.095865
2016-07-09 04:00 | 217.0867 | 152.1667 | 64.92 | 205.2547 | 22.4517 | -105.5221 | 71.5613 | 18.4387 | -110.1684 | 97.1874 | 0 | 114.125 | 0.2 | 0 | 10.8543 | 124.9793 | 6.1 | 10.0056 | 1.0525 | 0.10786
2016-07-09 05:00 | 267.8033 | 167.7333 | 100.07 | 270.3972 | 22.4469 | -90.5237 | 68.2791 | 21.7209 | -95.8284 | 84.0683 | 27.9435 | 125.8 | 0.2 | 0 | 13.3902 | 167.1336 | 6.5 | 11.7229 | 1.0465 | 0.14342
2016-07-09 06:00 | 318.52 | 183.3 | 135.22 | 318.9047 | 22.442 | -75.5254 | 64.9117 | 25.0883 | -81.1727 | 70.5876 | 105.993 | 137.475 | 0.2 | 0 | 15.926 | 259.394 | 6 | 14.1061 | 1.0381 | 0.22081
2016-07-09 07:00 | 386.6133 | 166.7133 | 219.9 | 463.5366 | 22.4372 | -60.5271 | 61.68 | 28.32 | -66.0767 | 56.8831 | 253.2531 | 125.035 | 0.2 | 0 | 19.3307 | 397.6187 | 6.1 | 18.5256 | 1.0227 | 0.33344
2016-07-09 08:00 | 454.7067 | 150.1267 | 304.58 | 588.2261 | 22.4323 | -45.5287 | 58.8156 | 31.1844 | -50.4448 | 43.0539 | 429.8235 | 112.595 | 0.2 | 0 | 22.7353 | 565.1538 | 5.5 | 23.1611 | 1.0064 | 0.46641
2016-07-09 09:00 | 522.8 | 133.54 | 389.26 | 706.1472 | 22.4275 | -30.5304 | 56.5475 | 33.4525 | -34.25 | 29.2043 | 616.3857 | 100.155 | 0.2 | 0 | 26.14 | 742.6807 | 5.9 | 29.1088 | 0.98562 | 0.60024
2016-07-09 10:00 | 525.97 | 120.6067 | 405.3633 | 708.1035 | 22.4226 | -15.5321 | 55.0778 | 34.9222 | -17.5714 | 15.5961 | 682.0316 | 90.455 | 0.2 | 0 | 26.2985 | 798.7851 | 6.1 | 31.062 | 0.97878 | 0.64111
2016-07-09 11:00 | 529.14 | 107.6733 | 421.4667 | 726.6692 | 22.4177 | -0.53372 | 54.5496 | 35.4504 | -0.60566 | 5.4741 | 723.3552 | 80.755 | 0.2 | 0 | 26.457 | 830.5672 | 6.9 | 32.8552 | 0.97251 | 0.66234
2016-07-09 12:00 | 532.31 | 94.74 | 437.57 | 763.2095 | 22.4128 | 14.4646 | 55.0173 | 34.9827 | 16.3697 | 14.657 | 738.3729 | 71.055 | 0.2 | 0 | 26.6155 | 836.0434 | 6.6 | 32.7264 | 0.97296 | 0.66702
2016-07-09 13:00 | 489.8533 | 102.5467 | 387.3067 | 700.495 | 22.4079 | 29.463 | 56.4335 | 33.5665 | 33.0742 | 28.2202 | 617.2318 | 76.91 | 0.2 | 0 | 24.4927 | 718.6345 | 6.9 | 29.3573 | 0.98475 | 0.58029
2016-07-09 14:00 | 447.3967 | 110.3533 | 337.0433 | 648.0237 | 22.403 | 44.4613 | 58.6604 | 31.3396 | 49.3043 | 42.0679 | 481.0615 | 82.765 | 0.2 | 0 | 22.3698 | 586.1963 | 6.7 | 25.0186 | 0.99993 | 0.48065
2016-07-09 15:00 | 404.94 | 118.16 | 286.78 | 600.9978 | 22.398 | 59.4597 | 61.4991 | 28.5009 | 64.973 | 55.9059 | 336.8917 | 88.62 | 0.2 | 0 | 20.247 | 445.7587 | 6.3 | 20.23 | 1.0167 | 0.37162
2016-07-09 16:00 | 346.9 | 126.1733 | 220.7267 | 516.9068 | 22.3931 | 74.458 | 64.7218 | 25.2782 | 80.1014 | 69.6273 | 179.9485 | 94.63 | 0.2 | 0 | 17.345 | 291.9235 | 6 | 15.1226 | 1.0346 | 0.24765
2016-07-09 17:00 | 288.86 | 134.1867 | 154.6733 | 414.6235 | 22.3881 | 89.4564 | 68.0964 | 21.9036 | 94.7821 | 83.1346 | 49.5627 | 100.64 | 0.2 | 0 | 14.443 | 164.6457 | 6.6 | 11.7452 | 1.0464 | 0.14127
2016-07-09 18:00 | 230.82 | 142.2 | 88.62 | 277.8603 | 22.3832 | 104.4548 | 71.4013 | 18.5987 | 109.1391 | 96.2946 | 0 | 106.65 | 0.2 | 0 | 11.541 | 118.191 | 6.2 | 9.8935 | 1.0529 | 0.10204
2016-07-09 19:00 | 199.94 | 109.0167 | 90.9233 | 338.7961 | 22.3782 | 119.4531 | 74.4326 | 15.5674 | 123.2961 | 108.8924 | 0 | 81.7625 | 0.2 | 0 | 9.997 | 91.7595 | 5.6 | 8.4675 | 1.0579 | 0.079597
2016-07-09 20:00 | 169.06 | 75.8333 | 93.2267 | 414.7294 | 22.3732 | 134.4515 | 77.0095 | 12.9905 | 137.3556 | 120.5524 | 0 | 56.875 | 0.2 | 0 | 8.453 | 65.328 | 5.2 | 7.2415 | 1.0622 | 0.056899
2016-07-09 21:00 | 138.18 | 42.65 | 95.53 | 499.7543 | 22.3682 | 149.4499 | 78.9799 | 11.0201 | 151.3879 | 130.5923 | 0 | 31.9875 | 0.2 | 0 | 6.909 | 38.8965 | 4.9 | 6.1155 | 1.0661 | 0.034003
2016-07-09 22:00 | 131.6333 | 42.0733 | 89.56 | 527.5891 | 22.3632 | 164.4482 | 80.2265 | 9.7735 | 165.428 | 137.8274 | 0 | 31.555 | 0.2 | 0 | 6.5817 | 38.1367 | 4.7 | 5.8918 | 1.0669 | 0.033364
2016-07-09 23:00 | 125.0867 | 41.4967 | 83.59 | 515.8572 | 22.3582 | 179.4466 | 80.6746 | 9.3254 | 179.4814 | 140.6715 | 0 | 31.1225 | 0.2 | 0 | 6.2543 | 37.3768 | 5.1 | 6.268 | 1.0656 | 0.032658
2016-07-10 | 118.54 | 40.92 | 77.62 | 460.549 | 22.3531 | -165.555 | 80.2972 | 9.7028 | -166.4641 | 138.2156 | 0 | 30.69 | 0.2 | 0 | 5.927 | 36.617 | 5.6 | 6.7443 | 1.0639 | 0.031944
2016-07-10 01:00 | 153.32 | 43.2533 | 110.0667 | 582.9884 | 22.3481 | -150.5566 | 79.1174 | 10.8826 | -152.4212 | 131.2556 | 0 | 32.44 | 0.2 | 0 | 7.666 | 40.106 | 4.9 | 6.1533 | 1.066 | 0.035056
2016-07-10 02:00 | 188.1 | 45.5867 | 142.5133 | 643.5921 | 22.343 | -135.5582 | 77.2067 | 12.7933 | -138.3864 | 121.3782 | 0 | 34.19 | 0.2 | 0 | 9.405 | 43.595 | 5.5 | 6.8623 | 1.0635 | 0.038017
2016-07-10 03:00 | 222.88 | 47.92 | 174.96 | 662.1744 | 22.3379 | -120.5598 | 74.6794 | 15.3206 | -124.3275 | 109.8102 | 0 | 35.94 | 0.2 | 0 | 11.144 | 47.084 | 4.8 | 6.2714 | 1.0656 | 0.04114
2016-07-10 04:00 | 268.8933 | 59.1833 | 209.71 | 667.3649 | 22.3329 | -105.5615 | 71.6853 | 18.3147 | -110.1771 | 97.2652 | 0 | 44.3875 | 0.2 | 0 | 13.4447 | 57.8322 | 5.1 | 6.9073 | 1.0633 | 0.050425
2016-07-10 05:00 | 314.9067 | 70.4467 | 244.46 | 664.171 | 22.3278 | -90.5631 | 68.4035 | 21.5965 | -95.8353 | 84.136 | 67.8566 | 52.835 | 0.2 | 0 | 15.7453 | 136.4369 | 4.7 | 8.9637 | 1.0561 | 0.11816
2016-07-10 06:00 | 360.92 | 81.71 | 279.21 | 661.5672 | 22.3227 | -75.5647 | 65.0363 | 24.9637 | -81.1799 | 70.6458 | 219.2475 | 61.2825 | 0.2 | 0 | 18.046 | 298.576 | 5.6 | 14.9305 | 1.0352 | 0.25346
2016-07-10 07:00 | 357.9567 | 122.52 | 235.4367 | 498.3007 | 22.3176 | -60.5663 | 61.8047 | 28.1953 | -66.0866 | 56.9321 | 271.8894 | 91.89 | 0.2 | 0 | 17.8978 | 381.6773 | 6.1 | 18.0274 | 1.0244 | 0.32061
2016-07-10 08:00 | 354.9933 | 163.33 | 191.6633 | 371.4889 | 22.3124 | -45.5679 | 58.9402 | 31.0598 | -50.46 | 43.0927 | 271.2793 | 122.4975 | 0.2 | 0 | 17.7497 | 411.5265 | 6.5 | 19.3602 | 1.0197 | 0.34411
2016-07-10 09:00 | 352.03 | 204.14 | 147.89 | 269.1659 | 22.3073 | -30.5695 | 56.6715 | 33.3285 | -34.2731 | 29.2295 | 234.8932 | 153.105 | 0.2 | 0 | 17.6015 | 405.5997 | 6.7 | 19.375 | 1.0197 | 0.33914
2016-07-10 10:00 | 326.2833 | 193.1533 | 133.13 | 233.2728 | 22.3022 | -15.5711 | 55.2006 | 34.7994 | -17.6044 | 15.5944 | 224.6858 | 144.865 | 0.2 | 0 | 16.3142 | 385.8649 | 6.9 | 18.9583 | 1.0211 | 0.3231
2016-07-10 11:00 | 300.5367 | 182.1667 | 118.37 | 204.6935 | 22.297 | -0.57264 | 54.6704 | 35.3296 | -0.64943 | 5.3575 | 203.7993 | 136.625 | 0.2 | 0 | 15.0268 | 355.4511 | 7.4 | 18.5078 | 1.0227 | 0.29809
2016-07-10 12:00 | 274.79 | 171.18 | 103.61 | 181.2514 | 22.2918 | 14.4258 | 55.1355 | 34.8645 | 16.3159 | 14.5836 | 175.4117 | 128.385 | 0.2 | 0 | 13.7395 | 317.5362 | 7.7 | 17.623 | 1.0258 | 0.2671
2016-07-10 13:00 | 241.7333 | 154.07 | 87.6633 | 159.0337 | 22.2866 | 29.4242 | 56.5489 | 33.4511 | 33.0122 | 28.1725 | 140.193 | 115.5525 | 0.2 | 0 | 12.0867 | 267.8321 | 7.5 | 15.8698 | 1.032 | 0.22664
2016-07-10 14:00 | 208.6767 | 136.96 | 71.7167 | 138.3351 | 22.2815 | 44.4226 | 58.7732 | 31.2268 | 49.2368 | 42.0339 | 102.7482 | 102.72 | 0.2 | 0 | 10.4338 | 215.902 | 7.2 | 13.9469 | 1.0387 | 0.18389
2016-07-10 15:00 | 175.62 | 119.85 | 55.77 | 117.294 | 22.2763 | 59.421 | 61.6099 | 28.3901 | 64.9028 | 55.8828 | 65.7887 | 89.8875 | 0.2 | 0 | 8.781 | 164.4572 | 6.5 | 11.6393 | 1.0468 | 0.14116
2016-07-10 16:00 | 135.0333 | 91.31 | 43.7233 | 102.8109 | 22.271 | 74.4195 | 64.8317 | 25.1683 | 80.0307 | 69.6147 | 35.8123 | 68.4825 | 0.2 | 0 | 6.7517 | 111.0465 | 7 | 10.4702 | 1.0509 | 0.095689
2016-07-10 17:00 | 94.4467 | 62.77 | 31.6767 | 85.3212 | 22.2658 | 89.4179 | 68.2064 | 21.7936 | 94.7129 | 83.1331 | 10.2013 | 47.0775 | 0.2 | 0 | 4.7223 | 62.0011 | 5.6 | 7.5375 | 1.0611 | 0.053948
2016-07-10 18:00 | 53.86 | 34.23 | 19.63 | 61.9049 | 22.2606 | 104.4163 | 71.5124 | 18.4876 | 109.0728 | 96.3059 | 0 | 25.6725 | 0.2 | 0 | 2.693 | 28.3655 | 5.6 | 6.4864 | 1.0648 | 0.024767
2016-07-10 19:00 | 48.55 | 31.1567 | 17.3933 | 65.2729 | 22.2553 | 119.4147 | 74.5456 | 15.4544 | 123.234 | 108.9193 | 0 | 23.3675 | 0.2 | 0 | 2.4275 | 25.795 | 5 | 5.8061 | 1.0672 | 0.022573
2016-07-10 20:00 | 43.24 | 28.0833 | 15.1567 | 68.021 | 22.2501 | 134.4132 | 77.1251 | 12.8749 | 137.2989 | 120.5993 | 0 | 21.0625 | 0.2 | 0 | 2.162 | 23.2245 | 5.4 | 6.1258 | 1.0661 | 0.020302
2016-07-10 21:00 | 37.93 | 25.01 | 12.92 | 68.3145 | 22.2448 | 149.4116 | 79.0983 | 10.9017 | 151.3374 | 130.6643 | 0 | 18.7575 | 0.2 | 0 | 1.8965 | 20.654 | 4.7 | 5.3454 | 1.0688 | 0.018101
2016-07-10 22:00 | 40.6533 | 26.7533 | 13.9 | 82.9021 | 22.2395 | 164.4101 | 80.3478 | 9.6522 | 165.3846 | 137.9281 | 0 | 20.065 | 0.2 | 0 | 2.0327 | 22.0977 | 4.5 | 5.1906 | 1.0693 | 0.019376
2016-07-10 23:00 | 43.3767 | 28.4967 | 14.88 | 93.0535 | 22.2342 | 179.4085 | 80.7984 | 9.2016 | 179.4454 | 140.7948 | 0 | 21.3725 | 0.2 | 0 | 2.1688 | 23.5413 | 3.9 | 4.6357 | 1.0713 | 0.02068
2016-07-11 | 46.1 | 30.24 | 15.86 | 95.3295 | 22.2289 | -165.593 | 80.4231 | 9.5769 | -166.4926 | 138.3441 | 0 | 22.68 | 0.2 | 0 | 2.305 | 24.985 | 3.8 | 4.5808 | 1.0715 | 0.021952
2016-07-11 01:00 | 49.7867 | 29.3067 | 20.48 | 109.7477 | 22.2236 | -150.5946 | 79.245 | 10.755 | -152.4424 | 131.3747 | 0 | 21.98 | 0.2 | 0 | 2.4893 | 24.4693 | 4.3 | 5.0647 | 1.0698 | 0.021465
2016-07-11 02:00 | 53.4733 | 28.3733 | 25.1 | 114.485 | 22.2183 | -135.5961 | 77.3354 | 12.6646 | -138.4012 | 121.4831 | 0 | 21.28 | 0.2 | 0 | 2.6737 | 23.9537 | 4.2 | 4.9486 | 1.0702 | 0.02102
2016-07-11 03:00 | 57.16 | 27.44 | 29.72 | 113.4176 | 22.213 | -120.5977 | 74.8088 | 15.1912 | -124.3369 | 109.9012 | 0 | 20.58 | 0.2 | 0 | 2.858 | 23.438 | 4 | 4.7324 | 1.0709 | 0.020582
2016-07-11 04:00 | 63.12 | 40.1467 | 22.9733 | 73.613 | 22.2076 | -105.5992 | 71.8152 | 18.1848 | -110.1827 | 97.3441 | 0 | 30.11 | 0.2 | 0 | 3.156 | 33.266 | 4.2 | 5.2396 | 1.0692 | 0.029165
2016-07-11 05:00 | 69.08 | 52.8533 | 16.2267 | 44.3408 | 22.2023 | -90.6008 | 68.5337 | 21.4663 | -95.8389 | 84.2041 | 4.4778 | 39.64 | 0.2 | 0 | 3.454 | 47.5718 | 4.2 | 5.6866 | 1.0676 | 0.041646
2016-07-11 06:00 | 75.04 | 65.56 | 9.48 | 22.5726 | 22.1969 | -75.6023 | 65.1668 | 24.8332 | -81.1837 | 70.704 | 7.4591 | 49.17 | 0.2 | 0 | 3.752 | 60.3811 | 4 | 5.8869 | 1.0669 | 0.052825
2016-07-11 07:00 | 72.3567 | 65.9267 | 6.43 | 13.6672 | 22.1915 | -60.6038 | 61.9353 | 28.0647 | -66.0932 | 56.9805 | 7.4476 | 49.445 | 0.2 | 0 | 3.6178 | 60.5104 | 4.1 | 5.991 | 1.0665 | 0.05292
2016-07-11 08:00 | 69.6733 | 66.2933 | 3.38 | 6.5761 | 22.1861 | -45.6053 | 59.0707 | 30.9293 | -50.472 | 43.1305 | 4.7993 | 49.72 | 0.2 | 0 | 3.4837 | 58.0029 | 4.1 | 5.9126 | 1.0668 | 0.05074
2016-07-11 09:00 | 66.99 | 66.66 | 0.33 | 0.6027 | 22.1807 | -30.6069 | 56.8017 | 33.1983 | -34.2933 | 29.2533 | 0.52583 | 49.995 | 0.2 | 0 | 3.3495 | 53.8703 | 4.1 | 5.7834 | 1.0673 | 0.047145
2016-07-11 10:00 | 71.8533 | 70.72 | 1.1333 | 1.9923 | 22.1753 | -15.6084 | 55.3296 | 34.6704 | -17.635 | 15.5903 | 1.919 | 53.04 | 0.2 | 0 | 3.5927 | 58.5517 | 4.7 | 6.5297 | 1.0646 | 0.051116
2016-07-11 11:00 | 76.7167 | 74.78 | 1.9367 | 3.3595 | 22.1699 | -0.60991 | 54.7976 | 35.2024 | -0.69124 | 5.2348 | 3.3455 | 56.085 | 0.2 | 0 | 3.8358 | 63.2664 | 5.9 | 7.8771 | 1.0599 | 0.054988
2016-07-11 12:00 | 81.58 | 78.84 | 2.74 | 4.8083 | 22.1645 | 14.3886 | 55.2602 | 34.7398 | 16.2634 | 14.5102 | 4.6549 | 59.13 | 0.2 | 0 | 4.079 | 67.8639 | 5.5 | 7.6207 | 1.0608 | 0.059033
2016-07-11 13:00 | 77.7 | 75.8733 | 1.8267 | 3.3245 | 22.159 | 29.3871 | 56.6708 | 33.3292 | 32.9512 | 28.1261 | 2.932 | 56.905 | 0.2 | 0 | 3.885 | 63.722 | 5.9 | 7.8913 | 1.0599 | 0.055381
2016-07-11 14:00 | 73.82 | 72.9067 | 0.91333 | 1.7678 | 22.1536 | 44.3855 | 58.8926 | 31.1074 | 49.1699 | 42.0019 | 1.3137 | 54.68 | 0.2 | 0 | 3.691 | 59.6847 | 5.8 | 7.6651 | 1.0607 | 0.051911
2016-07-11 15:00 | 69.94 | 69.94 | 0 | 0 | 22.1481 | 59.384 | 61.7274 | 28.2726 | 64.8327 | 55.8621 | 0 | 52.455 | 0.2 | 0 | 3.497 | 55.952 | 5 | 6.7485 | 1.0639 | 0.048812
2016-07-11 16:00 | 49.26 | 49.26 | 0 | 0 | 22.1426 | 74.3825 | 64.9481 | 25.0519 | 79.9601 | 69.6048 | 0 | 36.945 | 0.2 | 0 | 2.463 | 39.408 | 4.7 | 5.9315 | 1.0667 | 0.034471
2016-07-11 17:00 | 28.58 | 28.58 | 0 | 0 | 22.1371 | 89.381 | 68.323 | 21.677 | 94.6436 | 83.1348 | 0 | 21.435 | 0.2 | 0 | 1.429 | 22.864 | 4.7 | 5.4145 | 1.0685 | 0.020034
2016-07-11 18:00 | 7.9 | 7.9 | 0 | 0 | 22.1316 | 104.3795 | 71.6301 | 18.3699 | 109.0066 | 96.3209 | 0 | 5.925 | 0.2 | 0 | 0.395 | 6.32 | 5.5 | 5.6975 | 1.0676 | 0.0055325
2016-07-11 19:00 | 9.65 | 8.6933 | 0.95667 | 3.6174 | 22.1261 | 119.378 | 74.6652 | 15.3348 | 123.1722 | 108.9505 | 0 | 6.52 | 0.2 | 0 | 0.4825 | 7.0025 | 4.8 | 5.0188 | 1.0699 | 0.0061436
2016-07-11 20:00 | 11.4 | 9.4867 | 1.9133 | 8.6676 | 22.1206 | 134.3766 | 77.2472 | 12.7528 | 137.2426 | 120.651 | 0 | 7.115 | 0.2 | 0 | 0.57 | 7.685 | 6.2 | 6.4402 | 1.065 | 0.0067111
2016-07-11 21:00 | 13.15 | 10.28 | 2.87 | 15.3489 | 22.1151 | 149.3751 | 79.2232 | 10.7768 | 151.2877 | 130.742 | 0 | 7.71 | 0.2 | 0 | 0.6575 | 8.3675 | 7.1 | 7.3615 | 1.0617 | 0.0072849
2016-07-11 22:00 | 22.2733 | 13.2933 | 8.98 | 54.2695 | 22.1095 | 164.3736 | 80.4754 | 9.5246 | 165.3422 | 138.0352 | 0 | 9.97 | 0.2 | 0 | 1.1137 | 11.0837 | 4.8 | 5.1464 | 1.0695 | 0.0097202
2016-07-11 23:00 | 31.3967 | 16.3067 | 15.09 | 95.7095 | 22.104 | 179.3721 | 80.9286 | 9.0714 | 179.4109 | 140.9245 | 0 | 12.23 | 0.2 | 0 | 1.5698 | 13.7998 | 4.6 | 5.0312 | 1.0699 | 0.012107
2016-07-12 | 40.52 | 19.32 | 21.2 | 129.1941 | 22.0984 | -165.6294 | 80.5554 | 9.4446 | -166.5191 | 138.478 | 0 | 14.49 | 0.2 | 0 | 2.026 | 16.516 | 4.8 | 5.3161 | 1.0689 | 0.014476
2016-07-12 01:00 | 52.15 | 23.6467 | 28.5033 | 154.6439 | 22.0928 | -150.6309 | 79.3787 | 10.6213 | -152.4614 | 131.4977 | 0 | 17.735 | 0.2 | 0 | 2.6075 | 20.3425 | 5.6 | 6.2357 | 1.0657 | 0.017776
2016-07-12 02:00 | 63.78 | 27.9733 | 35.8067 | 165.0478 | 22.0872 | -135.6323 | 77.4702 | 12.5298 | -138.4134 | 121.5906 | 0 | 20.98 | 0.2 | 0 | 3.189 | 24.169 | 6.1 | 6.8553 | 1.0635 | 0.021077
2016-07-12 03:00 | 75.41 | 32.3 | 43.11 | 165.9611 | 22.0816 | -120.6338 | 74.9442 | 15.0558 | -124.3435 | 109.9939 | 0 | 24.225 | 0.2 | 0 | 3.7705 | 27.9955 | 6.6 | 7.4749 | 1.0613 | 0.024364
2016-07-12 04:00 | 94.01 | 37.86 | 56.15 | 181.2279 | 22.076 | -105.6353 | 71.951 | 18.049 | -110.1853 | 97.4238 | 0 | 28.395 | 0.2 | 0 | 4.7005 | 33.0955 | 6.1 | 7.1342 | 1.0625 | 0.028835
2016-07-12 05:00 | 112.61 | 43.42 | 69.19 | 190.2163 | 22.0704 | -90.6367 | 68.6697 | 21.3303 | -95.8394 | 84.2725 | 18.9832 | 32.565 | 0.2 | 0 | 5.6305 | 57.1787 | 6.6 | 8.3868 | 1.0581 | 0.049613
2016-07-12 06:00 | 131.21 | 48.98 | 82.23 | 196.8077 | 22.0648 | -75.6382 | 65.303 | 24.697 | -81.1843 | 70.762 | 64.8469 | 36.735 | 0.2 | 0 | 6.5605 | 108.1424 | 6.5 | 9.8794 | 1.0529 | 0.09337
2016-07-12 07:00 | 130.4667 | 63.6733 | 66.7933 | 142.6093 | 22.0591 | -60.6397 | 62.0717 | 27.9283 | -66.0964 | 57.0282 | 77.6117 | 47.755 | 0.2 | 0 | 6.5233 | 131.89 | 6.2 | 10.3216 | 1.0514 | 0.11371
2016-07-12 08:00 | 129.7233 | 78.3667 | 51.3567 | 100.3189 | 22.0535 | -45.6411 | 59.2072 | 30.7928 | -50.4809 | 43.1672 | 73.1686 | 58.775 | 0.2 | 0 | 6.4862 | 138.4298 | 6.5 | 10.8259 | 1.0496 | 0.11914
2016-07-12 09:00 | 128.98 | 93.06 | 35.92 | 65.842 | 22.0478 | -30.6426 | 56.9378 | 33.0622 | -34.3107 | 29.2755 | 57.4326 | 69.795 | 0.2 | 0 | 6.449 | 133.6766 | 7.3 | 11.4774 | 1.0473 | 0.1148
2016-07-12 10:00 | 126.13 | 94.96 | 31.17 | 54.9821 | 22.0422 | -15.644 | 55.4649 | 34.5351 | -17.663 | 15.5842 | 52.9608 | 71.22 | 0.2 | 0 | 6.3065 | 130.4873 | 7 | 11.0777 | 1.0487 | 0.11221
2016-07-12 11:00 | 123.28 | 96.86 | 26.42 | 45.983 | 22.0365 | -0.64546 | 54.9311 | 35.0689 | -0.73102 | 5.1061 | 45.8005 | 72.645 | 0.2 | 0 | 6.164 | 124.6095 | 6.8 | 10.694 | 1.0501 | 0.1073
2016-07-12 12:00 | 120.43 | 98.76 | 21.67 | 38.1536 | 22.0308 | 14.3531 | 55.3914 | 34.6086 | 16.2125 | 14.4372 | 36.9488 | 74.07 | 0.2 | 0 | 6.0215 | 117.0403 | 7.7 | 11.3575 | 1.0477 | 0.10056
2016-07-12 13:00 | 135.3467 | 102.2367 | 33.11 | 60.4668 | 22.0251 | 29.3517 | 56.7993 | 33.2007 | 32.8911 | 28.0812 | 53.3487 | 76.6775 | 0.2 | 0 | 6.7673 | 136.7935 | 7.7 | 11.9748 | 1.0456 | 0.11728
2016-07-12 14:00 | 150.2633 | 105.7133 | 44.55 | 86.5449 | 22.0193 | 44.3502 | 59.0185 | 30.9815 | 49.1035 | 41.9718 | 64.3439 | 79.285 | 0.2 | 0 | 7.5132 | 151.142 | 7 | 11.7232 | 1.0465 | 0.1297
2016-07-12 15:00 | 165.18 | 109.19 | 55.99 | 118.6831 | 22.0136 | 59.3488 | 61.8514 | 28.1486 | 64.7629 | 55.8438 | 66.6348 | 81.8925 | 0.2 | 0 | 8.259 | 156.7863 | 7.4 | 12.2996 | 1.0445 | 0.13428
2016-07-12 16:00 | 146.4133 | 90.7433 | 55.67 | 132.0782 | 22.0079 | 74.3474 | 65.0711 | 24.9289 | 79.8895 | 69.5977 | 46.0438 | 68.0575 | 0.2 | 0 | 7.3207 | 121.422 | 6.8 | 10.5944 | 1.0504 | 0.10459
2016-07-12 17:00 | 127.6467 | 72.2967 | 55.35 | 150.6628 | 22.0021 | 89.3459 | 68.4461 | 21.5539 | 94.5744 | 83.1397 | 17.9966 | 54.2225 | 0.2 | 0 | 6.3823 | 78.6014 | 7 | 9.4563 | 1.0544 | 0.06796
2016-07-12 18:00 | 108.88 | 53.85 | 55.03 | 175.7621 | 21.9964 | 104.3445 | 71.7542 | 18.2458 | 108.9405 | 96.3395 | 0 | 40.3875 | 0.2 | 0 | 5.444 | 45.8315 | 7.2 | 8.6322 | 1.0573 | 0.039735
2016-07-12 19:00 | 89.9433 | 44.7333 | 45.21 | 172.3363 | 21.9906 | 119.3431 | 74.7913 | 15.2087 | 123.1107 | 108.986 | 0 | 33.55 | 0.2 | 0 | 4.4972 | 38.0472 | 6.7 | 7.889 | 1.0599 | 0.033067
2016-07-12 20:00 | 71.0067 | 35.6167 | 35.39 | 161.9264 | 21.9848 | 134.3417 | 77.3758 | 12.6242 | 137.1869 | 120.7077 | 0 | 26.7125 | 0.2 | 0 | 3.5503 | 30.2628 | 6.8 | 7.7457 | 1.0604 | 0.026314
2016-07-12 21:00 | 52.07 | 26.5 | 25.57 | 138.417 | 21.979 | 149.3403 | 79.3545 | 10.6455 | 151.2389 | 130.8253 | 0 | 19.875 | 0.2 | 0 | 2.6035 | 22.4785 | 6.1 | 6.8025 | 1.0637 | 0.019606
2016-07-12 22:00 | 42.3367 | 22.7667 | 19.57 | 119.9421 | 21.9732 | 164.3388 | 80.6095 | 9.3905 | 165.3011 | 138.1485 | 0 | 17.075 | 0.2 | 0 | 2.1168 | 19.1918 | 5.8 | 6.3997 | 1.0651 | 0.016762
2016-07-12 23:00 | 32.6033 | 19.0333 | 13.57 | 87.3728 | 21.9674 | 179.3374 | 81.0651 | 8.9349 | 179.378 | 141.0605 | 0 | 14.275 | 0.2 | 0 | 1.6302 | 15.9052 | 5.9 | 6.397 | 1.0651 | 0.013891
2016-07-13 | 22.87 | 15.3 | 7.57 | 46.8122 | 21.9616 | -165.664 | 80.6938 | 9.3062 | -166.5437 | 138.6173 | 0 | 11.475 | 0.2 | 0 | 1.1435 | 12.6185 | 5.1 | 5.4943 | 1.0683 | 0.011054
2016-07-13 01:00 | 29.2467 | 19.9733 | 9.2733 | 50.9758 | 21.9557 | -150.6654 | 79.5186 | 10.4814 | -152.4781 | 131.6246 | 0 | 14.98 | 0.2 | 0 | 1.4623 | 16.4423 | 5.1 | 5.6138 | 1.0679 | 0.014398
2016-07-13 02:00 | 35.6233 | 24.6467 | 10.9767 | 51.1616 | 21.9499 | -135.6668 | 77.6109 | 12.3891 | -138.423 | 121.7007 | 0 | 18.485 | 0.2 | 0 | 1.7812 | 20.2662 | 5 | 5.6333 | 1.0678 | 0.017745
2016-07-13 03:00 | 42 | 29.32 | 12.68 | 49.2659 | 21.944 | -120.6682 | 75.0854 | 14.9146 | -124.3472 | 110.0882 | 0 | 21.99 | 0.2 | 0 | 2.1 | 24.09 | 4.9 | 5.6528 | 1.0677 | 0.021091
2016-07-13 04:00 | 44.03 | 31.98 | 12.05 | 39.1893 | 21.9381 | -105.6696 | 72.0925 | 17.9075 | -110.1847 | 97.5044 | 0 | 23.985 | 0.2 | 0 | 2.2015 | 26.1865 | 5.2 | 6.0183 | 1.0664 | 0.0229
2016-07-13 05:00 | 46.06 | 34.64 | 11.42 | 31.596 | 21.9323 | -90.6709 | 68.8114 | 21.1886 | -95.8365 | 84.3411 | 3.1156 | 25.98 | 0.2 | 0 | 2.303 | 31.3986 | 5.2 | 6.1812 | 1.0659 | 0.027443
2016-07-13 06:00 | 48.09 | 37.3 | 10.79 | 25.9646 | 21.9264 | -75.6723 | 65.445 | 24.555 | -81.1815 | 70.8197 | 8.5305 | 27.975 | 0.2 | 0 | 2.4045 | 38.91 | 5.3 | 6.5159 | 1.0647 | 0.03397
2016-07-13 07:00 | 56.4633 | 36.0867 | 20.3767 | 43.7107 | 21.9205 | -60.6737 | 62.214 | 27.786 | -66.0964 | 57.0753 | 23.7583 | 27.065 | 0.2 | 0 | 2.8232 | 53.6465 | 5.1 | 6.7765 | 1.0638 | 0.046796
2016-07-13 08:00 | 64.8367 | 34.8733 | 29.9633 | 58.7749 | 21.9145 | -45.6751 | 59.3496 | 30.6504 | -50.4866 | 43.2028 | 42.8431 | 26.155 | 0.2 | 0 | 3.2418 | 72.2399 | 6 | 8.2575 | 1.0586 | 0.062708
2016-07-13 09:00 | 73.21 | 33.66 | 39.55 | 72.7735 | 21.9086 | -30.6765 | 57.08 | 32.92 | -34.325 | 29.2962 | 63.4659 | 25.245 | 0.2 | 0 | 3.6605 | 92.3714 | 5.2 | 8.0866 | 1.0592 | 0.080228
2016-07-13 10:00 | 79.8733 | 34.9867 | 44.8867 | 79.4627 | 21.9027 | -15.6778 | 55.6063 | 34.3937 | -17.6885 | 15.5759 | 76.5445 | 26.24 | 0.2 | 0 | 3.9937 | 106.7782 | 5.7 | 9.0368 | 1.0559 | 0.09245
2016-07-13 11:00 | 86.5367 | 36.3133 | 50.2233 | 87.7169 | 21.8967 | -0.67922 | 55.071 | 34.929 | -0.76869 | 4.9715 | 87.3869 | 27.235 | 0.2 | 0 | 4.3268 | 118.9487 | 6 | 9.7171 | 1.0535 | 0.10276
2016-07-13 12:00 | 93.2 | 37.64 | 55.56 | 98.1643 | 21.8908 | 14.3194 | 55.5289 | 34.4711 | 16.1631 | 14.3647 | 95.0953 | 28.23 | 0.2 | 0 | 4.66 | 127.9853 | 5.6 | 9.5995 | 1.0539 | 0.1106
2016-07-13 13:00 | 83.0367 | 45.7533 | 37.2833 | 68.3343 | 21.8848 | 29.3181 | 56.9342 | 33.0658 | 32.8321 | 28.0379 | 60.3144 | 34.315 | 0.2 | 0 | 4.1518 | 98.7812 | 6.3 | 9.3869 | 1.0546 | 0.085427
2016-07-13 14:00 | 72.8733 | 53.8667 | 19.0067 | 37.066 | 21.8788 | 44.3167 | 59.1509 | 30.8491 | 49.0378 | 41.9439 | 27.5697 | 40.4 | 0.2 | 0 | 3.6437 | 71.6133 | 6.4 | 8.6379 | 1.0573 | 0.062086
2016-07-13 15:00 | 62.71 | 61.98 | 0.73 | 1.554 | 21.8728 | 59.3153 | 61.9819 | 28.0181 | 64.6936 | 55.828 | 0.87286 | 46.485 | 0.2 | 0 | 3.1355 | 50.4934 | 6.1 | 7.6779 | 1.0606 | 0.043915
2016-07-13 16:00 | 85.9767 | 63.6067 | 22.37 | 53.3328 | 21.8668 | 74.314 | 65.2007 | 24.7993 | 79.8192 | 69.5935 | 18.596 | 47.705 | 0.2 | 0 | 4.2988 | 70.5999 | 6.9 | 9.1062 | 1.0556 | 0.061112
2016-07-13 17:00 | 109.2433 | 65.2333 | 44.01 | 120.4855 | 21.8608 | 89.3126 | 68.5757 | 21.4243 | 94.5054 | 83.1479 | 14.3748 | 48.925 | 0.2 | 0 | 5.4622 | 68.762 | 7.1 | 9.2488 | 1.0551 | 0.059493
2016-07-13 18:00 | 132.51 | 66.86 | 65.65 | 211.1429 | 21.8548 | 104.3113 | 71.8849 | 18.1151 | 108.8747 | 96.3619 | 0 | 50.145 | 0.2 | 0 | 6.6255 | 56.7705 | 7.1 | 8.8741 | 1.0564 | 0.049179
2016-07-13 19:00 | 125.1933 | 56.55 | 68.6433 | 263.9089 | 21.8488 | 119.3099 | 74.9239 | 15.0761 | 123.0496 | 109.0257 | 0 | 42.4125 | 0.2 | 0 | 6.2597 | 48.6722 | 7.1 | 8.621 | 1.0573 | 0.042199
2016-07-13 20:00 | 117.8767 | 46.24 | 71.6367 | 331.2594 | 21.8427 | 134.3086 | 77.5108 | 12.4892 | 137.1319 | 120.7692 | 0 | 34.68 | 0.2 | 0 | 5.8938 | 40.5738 | 7.3 | 8.5679 | 1.0575 | 0.035184
2016-07-13 21:00 | 110.56 | 35.93 | 74.63 | 409.2274 | 21.8367 | 149.3073 | 79.4923 | 10.5077 | 151.1911 | 130.9143 | 0 | 26.9475 | 0.2 | 0 | 5.528 | 32.4755 | 6.2 | 7.2149 | 1.0622 | 0.028288
2016-07-13 22:00 | 93.4533 | 34.62 | 58.8333 | 366.0078 | 21.8306 | 164.3059 | 80.75 | 9.25 | 165.2613 | 138.2681 | 0 | 25.965 | 0.2 | 0 | 4.6727 | 30.6377 | 5.3 | 6.2574 | 1.0656 | 0.026771
2016-07-13 23:00 | 76.3467 | 33.31 | 43.0367 | 281.5623 | 21.8245 | 179.3046 | 81.2079 | 8.7921 | 179.3468 | 141.2028 | 0 | 24.9825 | 0.2 | 0 | 3.8173 | 28.7998 | 5 | 5.9 | 1.0669 | 0.025195
2016-07-14 | 59.24 | 32 | 27.24 | 171.0851 | 21.8185 | -165.6967 | 80.8384 | 9.1616 | -166.5663 | 138.7618 | 0 | 24 | 0.2 | 0 | 2.962 | 26.962 | 5.6 | 6.4426 | 1.065 | 0.023545
2016-07-14 01:00 | 63.6367 | 43.2567 | 20.38 | 113.5929 | 21.8124 | -150.6981 | 79.6645 | 10.3355 | -152.4923 | 131.7553 | 0 | 32.4425 | 0.2 | 0 | 3.1818 | 35.6243 | 7 | 8.1133 | 1.0591 | 0.030938
2016-07-14 02:00 | 68.0333 | 54.5133 | 13.52 | 63.7589 | 21.8062 | -135.6994 | 77.7576 | 12.2424 | -138.4298 | 121.8133 | 0 | 40.885 | 0.2 | 0 | 3.4017 | 44.2867 | 6.4 | 7.784 | 1.0603 | 0.038503
2016-07-14 03:00 | 72.43 | 65.77 | 6.66 | 26.1281 | 21.8001 | -120.7007 | 75.2324 | 14.7676 | -124.3479 | 110.184 | 0 | 49.3275 | 0.2 | 0 | 3.6215 | 52.949 | 6.4 | 8.0547 | 1.0593 | 0.045993
2016-07-14 04:00 | 81.61 | 76.1367 | 5.4733 | 17.9433 | 21.794 | -105.702 | 72.2397 | 17.7603 | -110.181 | 97.5858 | 0 | 57.1025 | 0.2 | 0 | 4.0805 | 61.183 | 6.9 | 8.812 | 1.0567 | 0.053013
2016-07-14 05:00 | 90.79 | 86.5033 | 4.2867 | 11.9393 | 21.7879 | -90.7033 | 68.9588 | 21.0412 | -95.8304 | 84.4099 | 1.163 | 64.8775 | 0.2 | 0 | 4.5395 | 70.58 | 8.1 | 10.3056 | 1.0514 | 0.060852
2016-07-14 06:00 | 99.97 | 96.87 | 3.1 | 7.502 | 21.7817 | -75.7046 | 65.5926 | 24.4074 | -81.1753 | 70.8771 | 2.4576 | 72.6525 | 0.2 | 0 | 4.9985 | 80.1086 | 7.5 | 10.0034 | 1.0525 | 0.069137
2016-07-14 07:00 | 111.6367 | 95.7067 | 15.93 | 34.3404 | 21.7755 | -60.7059 | 62.3619 | 27.6381 | -66.093 | 57.1217 | 18.6419 | 71.78 | 0.2 | 0 | 5.5818 | 96.0037 | 9.3 | 12.3001 | 1.0444 | 0.082222
2016-07-14 08:00 | 123.3033 | 94.5433 | 28.76 | 56.662 | 21.7694 | -45.7072 | 59.4978 | 30.5022 | -50.489 | 43.2374 | 41.2795 | 70.9075 | 0.2 | 0 | 6.1652 | 118.3522 | 8.3 | 11.9985 | 1.0455 | 0.10147
2016-07-14 09:00 | 134.97 | 93.38 | 41.59 | 76.8343 | 21.7632 | -30.7085 | 57.2282 | 32.7718 | -34.3364 | 29.3155 | 66.9947 | 70.035 | 0.2 | 0 | 6.7485 | 143.7782 | 7.2 | 11.6931 | 1.0466 | 0.12339
2016-07-14 10:00 | 112.6933 | 75.7233 | 36.97 | 65.6952 | 21.757 | -15.7098 | 55.7538 | 34.2462 | -17.7113 | 15.5657 | 63.2857 | 56.7925 | 0.2 | 0 | 5.6347 | 125.7128 | 6.5 | 10.4285 | 1.051 | 0.10834
2016-07-14 11:00 | 90.4167 | 58.0667 | 32.35 | 56.7077 | 21.7508 | -0.71111 | 55.217 | 34.783 | -0.80418 | 4.8309 | 56.5062 | 43.55 | 0.2 | 0 | 4.5208 | 104.577 | 8.2 | 11.468 | 1.0474 | 0.089815
2016-07-14 12:00 | 68.14 | 40.41 | 27.73 | 49.1738 | 21.7446 | 14.2876 | 55.6728 | 34.3272 | 16.1154 | 14.2931 | 47.6517 | 30.3075 | 0.2 | 0 | 3.407 | 81.3662 | 7.3 | 9.8427 | 1.0531 | 0.07026
2016-07-14 13:00 | 63.4267 | 40.31 | 23.1167 | 42.5304 | 21.7383 | 29.2863 | 57.0755 | 32.9245 | 32.7743 | 27.9964 | 37.5534 | 30.2325 | 0.2 | 0 | 3.1713 | 70.9572 | 7.5 | 9.7174 | 1.0535 | 0.061297
2016-07-14 14:00 | 58.7133 | 40.21 | 18.5033 | 36.2315 | 21.7321 | 44.285 | 59.2897 | 30.7103 | 48.9728 | 41.9181 | 26.9599 | 30.1575 | 0.2 | 0 | 2.9357 | 60.0531 | 8.4 | 10.2767 | 1.0515 | 0.051781
2016-07-14 15:00 | 54 | 40.11 | 13.89 | 29.7024 | 21.7259 | 59.2838 | 62.1188 | 27.8812 | 64.6247 | 55.8148 | 16.6889 | 30.0825 | 0.2 | 0 | 2.7 | 49.4714 | 6.8 | 8.346 | 1.0583 | 0.042931
2016-07-14 16:00 | 52.3633 | 39.7867 | 12.5767 | 30.1392 | 21.7196 | 74.2825 | 65.3367 | 24.6633 | 79.7492 | 69.5922 | 10.5095 | 29.84 | 0.2 | 0 | 2.6182 | 42.9677 | 6.9 | 8.2427 | 1.0587 | 0.0373
2016-07-14 17:00 | 50.7267 | 39.4633 | 11.2633 | 31.0233 | 21.7133 | 89.2812 | 68.7117 | 21.2883 | 94.4367 | 83.1594 | 3.6951 | 29.5975 | 0.2 | 0 | 2.5363 | 35.829 | 6.4 | 7.5197 | 1.0612 | 0.031177
2016-07-14 18:00 | 49.09 | 39.14 | 9.95 | 32.237 | 21.707 | 104.2799 | 72.022 | 17.978 | 108.8092 | 96.3881 | 0 | 29.355 | 0.2 | 0 | 2.4545 | 31.8095 | 5.7 | 6.694 | 1.0641 | 0.027755
2016-07-14 19:00 | 39.59 | 32.33 | 7.26 | 28.1659 | 21.7008 | 119.2787 | 75.0629 | 14.9371 | 122.9889 | 109.0697 | 0 | 24.2475 | 0.2 | 0 | 1.9795 | 26.227 | 6.4 | 7.2196 | 1.0622 | 0.022844
2016-07-14 20:00 | 30.09 | 25.52 | 4.57 | 21.3707 | 21.6944 | 134.2774 | 77.6523 | 12.3477 | 137.0775 | 120.8357 | 0 | 19.14 | 0.2 | 0 | 1.5045 | 20.6445 | 5.6 | 6.2451 | 1.0656 | 0.01804
2016-07-14 21:00 | 20.59 | 18.71 | 1.88 | 10.4506 | 21.6881 | 149.2762 | 79.6364 | 10.3636 | 151.1442 | 131.0089 | 0 | 14.0325 | 0.2 | 0 | 1.0295 | 15.062 | 7.9 | 8.3707 | 1.0582 | 0.01307
2016-07-14 22:00 | 18.5933 | 16.4067 | 2.1867 | 13.8208 | 21.6818 | 164.2749 | 80.8967 | 9.1033 | 165.2229 | 138.3939 | 0 | 12.305 | 0.2 | 0 | 0.92967 | 13.2347 | 4.9 | 5.3136 | 1.0689 | 0.0116
2016-07-14 23:00 | 16.5967 | 14.1033 | 2.4933 | 16.5913 | 21.6755 | 179.2737 | 81.3569 | 8.6431 | 179.3173 | 141.3513 | 0 | 10.5775 | 0.2 | 0 | 0.82983 | 11.4073 | 5.6 | 5.9565 | 1.0667 | 0.0099775
2016-07-15 | 14.6 | 11.8 | 2.8 | 17.8774 | 21.6691 | -165.7276 | 80.9891 | 9.0109 | -166.5867 | 138.9114 | 0 | 8.85 | 0.2 | 0 | 0.73 | 9.58 | 5.4 | 5.6994 | 1.0676 | 0.0083863
2016-07-15 01:00 | 18.6433 | 15.4133 | 3.23 | 18.2687 | 21.6628 | -150.7288 | 79.8163 | 10.1837 | -152.5042 | 131.8897 | 0 | 11.56 | 0.2 | 0 | 0.93217 | 12.4922 | 4.9 | 5.2904 | 1.069 | 0.01095
2016-07-15 02:00 | 22.6867 | 19.0267 | 3.66 | 17.4746 | 21.6564 | -135.7301 | 77.91 | 12.09 | -138.4339 | 121.9283 | 0 | 14.27 | 0.2 | 0 | 1.1343 | 15.4043 | 5 | 5.4814 | 1.0683 | 0.013494
2016-07-15 03:00 | 26.73 | 22.64 | 4.09 | 16.2096 | 21.65 | -120.7313 | 75.3852 | 14.6148 | -124.3457 | 110.2813 | 0 | 16.98 | 0.2 | 0 | 1.3365 | 18.3165 | 4.8 | 5.3724 | 1.0687 | 0.016051
2016-07-15 04:00 | 117.0767 | 34.7133 | 82.3633 | 272.2809 | 21.6436 | -105.7325 | 72.3925 | 17.6075 | -110.174 | 97.6678 | 0 | 26.035 | 0.2 | 0 | 5.8538 | 31.8888 | 5.9 | 6.8965 | 1.0634 | 0.027806
2016-07-15 05:00 | 207.4233 | 46.7867 | 160.6367 | 450.5361 | 21.6373 | -90.7338 | 69.1118 | 20.8882 | -95.8208 | 84.4788 | 43.3483 | 35.09 | 0.2 | 0 | 10.3712 | 88.8095 | 6.1 | 8.8753 | 1.0564 | 0.076934
2016-07-15 06:00 | 297.77 | 58.86 | 238.91 | 581.5941 | 21.6308 | -75.735 | 65.7459 | 24.2541 | -81.1656 | 70.9341 | 189.9808 | 44.145 | 0.2 | 0 | 14.8885 | 249.0143 | 4.4 | 12.1817 | 1.0449 | 0.21335
2016-07-15 07:00 | 234.7 | 68.3767 | 166.3233 | 360.3904 | 21.6244 | -60.7362 | 62.5155 | 27.4845 | -66.0861 | 57.1673 | 195.3993 | 51.2825 | 0.2 | 0 | 11.735 | 258.4168 | 5.1 | 13.1755 | 1.0414 | 0.22067
2016-07-15 08:00 | 171.63 | 77.8933 | 93.7367 | 185.5238 | 21.618 | -45.7374 | 59.6518 | 30.3482 | -50.4881 | 43.2708 | 135.0841 | 58.42 | 0.2 | 0 | 8.5815 | 202.0856 | 5 | 11.3152 | 1.0479 | 0.17365
2016-07-15 09:00 | 108.56 | 87.41 | 21.15 | 39.237 | 21.6116 | -30.7387 | 57.3822 | 32.6178 | -34.3447 | 29.3333 | 34.2062 | 65.5575 | 0.2 | 0 | 5.428 | 105.1917 | 5 | 8.2872 | 1.0585 | 0.091303
2016-07-15 10:00 | 111.3233 | 84.2567 | 27.0667 | 48.2873 | 21.6051 | -15.7399 | 55.9073 | 34.0927 | -17.7314 | 15.5536 | 46.519 | 63.1925 | 0.2 | 0 | 5.5662 | 115.2777 | 6 | 9.6024 | 1.0539 | 0.099622
2016-07-15 11:00 | 114.0867 | 81.1033 | 32.9833 | 58.0401 | 21.5986 | -0.74108 | 55.3692 | 34.6308 | -0.83741 | 4.6845 | 57.8462 | 60.8275 | 0.2 | 0 | 5.7043 | 124.378 | 4.6 | 8.4868 | 1.0578 | 0.10788
2016-07-15 12:00 | 116.85 | 77.95 | 38.9 | 69.2478 | 21.5922 | 14.2577 | 55.823 | 34.177 | 16.0695 | 14.2225 | 67.1252 | 58.4625 | 0.2 | 0 | 5.8425 | 131.4302 | 5.3 | 9.4072 | 1.0546 | 0.11365
2016-07-15 13:00 | 106.1133 | 69.94 | 36.1733 | 66.8184 | 21.5857 | 29.2565 | 57.2232 | 32.7768 | 32.7177 | 27.9568 | 59.0208 | 52.455 | 0.2 | 0 | 5.3057 | 116.7815 | 6.1 | 9.7494 | 1.0534 | 0.10087
2016-07-15 14:00 | 95.3767 | 61.93 | 33.4467 | 65.7732 | 21.5792 | 44.2553 | 59.435 | 30.565 | 48.9087 | 41.8948 | 48.9597 | 46.4475 | 0.2 | 0 | 4.7688 | 100.1761 | 6.3 | 9.4305 | 1.0545 | 0.086621
2016-07-15 15:00 | 84.64 | 53.92 | 30.72 | 66.0042 | 21.5727 | 59.2541 | 62.2623 | 27.7377 | 64.5563 | 55.8042 | 37.0958 | 40.44 | 0.2 | 0 | 4.232 | 81.7678 | 6.4 | 8.9552 | 1.0562 | 0.070815
2016-07-15 16:00 | 81.81 | 51.5033 | 30.3067 | 73.0236 | 21.5662 | 74.2529 | 65.4791 | 24.5209 | 79.6796 | 69.594 | 25.4612 | 38.6275 | 0.2 | 0 | 4.0905 | 68.1792 | 3.8 | 5.9306 | 1.0667 | 0.059638
2016-07-15 17:00 | 78.98 | 49.0867 | 29.8933 | 82.8662 | 21.5596 | 89.2517 | 68.8542 | 21.1458 | 94.3683 | 83.1743 | 9.8487 | 36.815 | 0.2 | 0 | 3.949 | 50.6127 | 5.5 | 7.0816 | 1.0627 | 0.044105
2016-07-15 18:00 | 76.15 | 46.67 | 29.48 | 96.2557 | 21.5531 | 104.2506 | 72.1656 | 17.8344 | 108.7441 | 96.4181 | 0 | 35.0025 | 0.2 | 0 | 3.8075 | 38.81 | 5.2 | 6.4128 | 1.0651 | 0.033895
2016-07-15 19:00 | 63.67 | 39.41 | 24.26 | 95.0233 | 21.5466 | 119.2494 | 75.2083 | 14.7917 | 122.9289 | 109.118 | 0 | 29.5575 | 0.2 | 0 | 3.1835 | 32.741 | 4.8 | 5.8232 | 1.0671 | 0.02865
2016-07-15 20:00 | 51.19 | 32.15 | 19.04 | 90.0989 | 21.54 | 134.2482 | 77.8001 | 12.1999 | 137.024 | 120.9071 | 0 | 24.1125 | 0.2 | 0 | 2.5595 | 26.672 | 4.2 | 5.0335 | 1.0699 | 0.023399
2016-07-15 21:00 | 38.71 | 24.89 | 13.82 | 77.9425 | 21.5334 | 149.247 | 79.7869 | 10.2131 | 151.0984 | 131.1091 | 0 | 18.6675 | 0.2 | 0 | 1.9355 | 20.603 | 4 | 4.6438 | 1.0712 | 0.018098
2016-07-15 22:00 | 36.6633 | 26.3133 | 10.35 | 66.526 | 21.5269 | 164.2458 | 81.0497 | 8.9503 | 165.1859 | 138.5259 | 0 | 19.735 | 0.2 | 0 | 1.8332 | 21.5682 | 3.9 | 4.574 | 1.0715 | 0.01895
2016-07-15 23:00 | 34.6167 | 27.7367 | 6.88 | 46.6118 | 21.5203 | 179.2447 | 81.512 | 8.488 | 179.2896 | 141.5059 | 0 | 20.8025 | 0.2 | 0 | 1.7308 | 22.5333 | 5.1 | 5.8042 | 1.0672 | 0.019719
2016-07-16 | 32.57 | 29.16 | 3.41 | 22.1544 | 21.5137 | -165.7565 | 81.1459 | 8.8541 | -166.605 | 139.0662 | 0 | 21.87 | 0.2 | 0 | 1.6285 | 23.4985 | 4.8 | 5.5343 | 1.0681 | 0.020582
2016-07-16 01:00 | 47.3367 | 38.0133 | 9.3233 | 53.5533 | 21.5071 | -150.7576 | 79.974 | 10.026 | -152.5135 | 132.0276 | 0 | 28.51 | 0.2 | 0 | 2.3668 | 30.8768 | 4.1 | 5.0649 | 1.0698 | 0.027086
2016-07-16 02:00 | 62.1033 | 46.8667 | 15.2367 | 73.6975 | 21.5004 | -135.7588 | 78.0683 | 11.9317 | -138.4352 | 122.0455 | 0 | 35.15 | 0.2 | 0 | 3.1052 | 38.2552 | 4.5 | 5.6955 | 1.0676 | 0.033489
2016-07-16 03:00 | 76.87 | 55.72 | 21.15 | 84.7208 | 21.4938 | -120.76 | 75.5436 | 14.4564 | -124.3403 | 110.3798 | 0 | 41.79 | 0.2 | 0 | 3.8435 | 45.6335 | 4.2 | 5.626 | 1.0678 | 0.039957
2016-07-16 04:00 | 87.2933 | 73.08 | 14.2133 | 47.4003 | 21.4872 | -105.7611 | 72.551 | 17.449 | -110.1638 | 97.7504 | 0 | 54.81 | 0.2 | 0 | 4.3647 | 59.1747 | 3.8 | 5.6492 | 1.0677 | 0.05181
2016-07-16 05:00 | 97.7167 | 90.44 | 7.2767 | 20.5579 | 21.4805 | -90.7622 | 69.2703 | 20.7297 | -95.8079 | 84.5477 | 1.9534 | 67.83 | 0.2 | 0 | 4.8858 | 74.6692 | 5.3 | 7.6334 | 1.0608 | 0.06495
2016-07-16 06:00 | 108.14 | 107.8 | 0.34 | 0.83281 | 21.4739 | -75.7634 | 65.9046 | 24.0954 | -81.1525 | 70.9907 | 0.27126 | 80.85 | 0.2 | 0 | 5.407 | 86.5283 | 4.7 | 7.404 | 1.0616 | 0.075323
2016-07-16 07:00 | 136.1167 | 135.7833 | 0.33333 | 0.72615 | 21.4672 | -60.7645 | 62.6747 | 27.3253 | -66.0758 | 57.2121 | 0.39323 | 101.8375 | 0.2 | 0 | 6.8058 | 109.0366 | 5.7 | 9.1074 | 1.0556 | 0.094383
2016-07-16 08:00 | 164.0933 | 163.7667 | 0.32667 | 0.64963 | 21.4605 | -45.7657 | 59.8114 | 30.1886 | -50.4839 | 43.3031 | 0.47276 | 122.825 | 0.2 | 0 | 8.2047 | 131.5024 | 5.2 | 9.3095 | 1.0549 | 0.11375
2016-07-16 09:00 | 192.07 | 191.75 | 0.32 | 0.59626 | 21.4538 | -30.7668 | 57.5421 | 32.4579 | -34.3498 | 29.3497 | 0.51973 | 143.8125 | 0.2 | 0 | 9.6035 | 153.9357 | 5.6 | 10.4105 | 1.0511 | 0.13267
2016-07-16 10:00 | 216.4067 | 215.6433 | 0.76333 | 1.3674 | 21.4471 | -15.7679 | 56.0668 | 33.9332 | -17.7487 | 15.5398 | 1.3174 | 161.7325 | 0.2 | 0 | 10.8203 | 173.8703 | 5.6 | 11.0334 | 1.0489 | 0.14954
2016-07-16 11:00 | 240.7433 | 239.5367 | 1.2067 | 2.1319 | 21.4404 | -0.76905 | 55.5276 | 34.4724 | -0.86832 | 4.5322 | 2.1252 | 179.6525 | 0.2 | 0 | 12.0372 | 193.8149 | 5.6 | 11.6567 | 1.0467 | 0.16635
2016-07-16 12:00 | 265.08 | 263.43 | 1.65 | 2.9491 | 21.4337 | 14.2298 | 55.9794 | 34.0206 | 16.0254 | 14.1533 | 2.8596 | 197.5725 | 0.2 | 0 | 13.254 | 213.6861 | 6.1 | 12.7777 | 1.0428 | 0.18272
2016-07-16 13:00 | 255.6333 | 249.66 | 5.9733 | 11.0801 | 21.4269 | 29.2287 | 57.3772 | 32.6228 | 32.6626 | 27.9193 | 9.7904 | 187.245 | 0.2 | 0 | 12.7817 | 209.8171 | 6.5 | 13.0568 | 1.0418 | 0.17924
2016-07-16 14:00 | 246.1867 | 235.89 | 10.2967 | 20.3397 | 21.4202 | 44.2276 | 59.5866 | 30.4134 | 48.8456 | 41.8738 | 15.1453 | 176.9175 | 0.2 | 0 | 12.3093 | 204.3721 | 5.7 | 12.0866 | 1.0452 | 0.17516
2016-07-16 15:00 | 236.74 | 222.12 | 14.62 | 31.5692 | 21.4134 | 59.2265 | 62.412 | 27.588 | 64.4886 | 55.7964 | 17.7461 | 166.59 | 0.2 | 0 | 11.837 | 196.1731 | 5.7 | 11.8304 | 1.0461 | 0.16828
2016-07-16 16:00 | 212.7567 | 177.3433 | 35.4133 | 85.817 | 21.4066 | 74.2254 | 65.6279 | 24.3721 | 79.6104 | 69.5988 | 29.9151 | 133.0075 | 0.2 | 0 | 10.6378 | 173.5604 | 6 | 11.4238 | 1.0475 | 0.14908
2016-07-16 17:00 | 188.7733 | 132.5667 | 56.2067 | 156.8626 | 21.3999 | 89.2243 | 69.0031 | 20.9969 | 94.3003 | 83.1926 | 18.5933 | 99.425 | 0.2 | 0 | 9.4387 | 127.457 | 6.4 | 10.383 | 1.0512 | 0.10986
2016-07-16 18:00 | 164.79 | 87.79 | 77 | 253.4765 | 21.3931 | 104.2232 | 72.3155 | 17.6845 | 108.6794 | 96.4519 | 0 | 65.8425 | 0.2 | 0 | 8.2395 | 74.082 | 5.7 | 8.0151 | 1.0594 | 0.064358
2016-07-16 19:00 | 149.7067 | 69.3333 | 80.3733 | 318.0031 | 21.3863 | 119.2221 | 75.3601 | 14.6399 | 122.8694 | 109.1707 | 0 | 52 | 0.2 | 0 | 7.4853 | 59.4853 | 5.6 | 7.4589 | 1.0614 | 0.051773
2016-07-16 20:00 | 134.6233 | 50.8767 | 83.7467 | 401.2916 | 21.3795 | 134.221 | 77.9542 | 12.0458 | 136.9713 | 120.9834 | 0 | 38.1575 | 0.2 | 0 | 6.7312 | 44.8887 | 5.5 | 6.9028 | 1.0633 | 0.03914
2016-07-16 21:00 | 119.54 | 32.42 | 87.12 | 498.9193 | 21.3726 | 149.2199 | 79.9436 | 10.0564 | 151.0538 | 131.2149 | 0 | 24.315 | 0.2 | 0 | 5.977 | 30.292 | 4.6 | 5.5466 | 1.0681 | 0.026531
2016-07-16 22:00 | 111.0433 | 32.7533 | 78.29 | 512.2576 | 21.3658 | 164.2188 | 81.2088 | 8.7912 | 165.1503 | 138.6641 | 0 | 24.565 | 0.2 | 0 | 5.5522 | 30.1172 | 4.7 | 5.6412 | 1.0678 | 0.026369
2016-07-16 23:00 | 102.5467 | 33.0867 | 69.46 | 479.6348 | 21.359 | 179.2177 | 81.6732 | 8.3268 | 179.2637 | 141.6667 | 0 | 24.815 | 0.2 | 0 | 5.1273 | 29.9423 | 4.9 | 5.8357 | 1.0671 | 0.0262
2016-07-17 | 94.05 | 33.42 | 60.63 | 401.2223 | 21.3521 | -165.7834 | 81.3086 | 8.6914 | -166.6211 | 139.2259 | 0 | 25.065 | 0.2 | 0 | 4.7025 | 29.7675 | 5 | 5.9302 | 1.0667 | 0.026039
2016-07-17 01:00 | 97.19 | 43.52 | 53.67 | 313.3421 | 21.3453 | -150.7844 | 80.1376 | 9.8624 | -152.5203 | 132.169 | 0 | 32.64 | 0.2 | 0 | 4.8595 | 37.4995 | 4.6 | 5.7719 | 1.0673 | 0.032819
2016-07-17 02:00 | 100.33 | 53.62 | 46.71 | 229.0316 | 21.3384 | -135.7855 | 78.2322 | 11.7678 | -138.4337 | 122.1649 | 0 | 40.215 | 0.2 | 0 | 5.0165 | 45.2315 | 5.2 | 6.6135 | 1.0644 | 0.039477
2016-07-17 03:00 | 103.47 | 63.72 | 39.75 | 161.0153 | 21.3315 | -120.7866 | 75.7076 | 14.2924 | -124.3318 | 110.4795 | 0 | 47.79 | 0.2 | 0 | 5.1735 | 52.9635 | 5 | 6.6551 | 1.0642 | 0.046219
2016-07-17 04:00 | 115.95 | 88.7533 | 27.1967 | 91.5322 | 21.3246 | -105.7876 | 72.7149 | 17.2851 | -110.1503 | 97.8335 | 0 | 66.565 | 0.2 | 0 | 5.7975 | 72.3625 | 5.5 | 7.7613 | 1.0603 | 0.062917
2016-07-17 05:00 | 128.43 | 113.7867 | 14.6433 | 41.6854 | 21.3177 | -90.7887 | 69.4342 | 20.5658 | -95.7915 | 84.6165 | 3.911 | 85.34 | 0.2 | 0 | 6.4215 | 95.6725 | 4.7 | 7.6898 | 1.0606 | 0.083204
2016-07-17 06:00 | 140.91 | 138.82 | 2.09 | 5.1524 | 21.3108 | -75.7898 | 66.0688 | 23.9312 | -81.1359 | 71.0469 | 1.6735 | 104.115 | 0.2 | 0 | 7.0455 | 112.834 | 5.2 | 8.7261 | 1.057 | 0.097794
2016-07-17 07:00 | 158.3767 | 156.7667 | 1.61 | 3.5269 | 21.3039 | -60.7908 | 62.8393 | 27.1607 | -66.0619 | 57.2561 | 1.9077 | 117.575 | 0.2 | 0 | 7.9188 | 127.4015 | 4.9 | 8.8813 | 1.0564 | 0.11036
2016-07-17 08:00 | 175.8433 | 174.7133 | 1.13 | 2.2584 | 21.2969 | -45.7919 | 59.9767 | 30.0233 | -50.4763 | 43.3343 | 1.6427 | 131.035 | 0.2 | 0 | 8.7922 | 141.4698 | 5.2 | 9.6209 | 1.0538 | 0.12225
2016-07-17 09:00 | 193.31 | 192.66 | 0.65 | 1.2167 | 21.29 | -30.7929 | 57.7077 | 32.2923 | -34.3519 | 29.3647 | 1.0604 | 144.495 | 0.2 | 0 | 9.6655 | 155.2209 | 6.8 | 11.6507 | 1.0467 | 0.13323
2016-07-17 10:00 | 192.0667 | 191.5633 | 0.50333 | 0.90556 | 21.283 | -15.7939 | 56.2322 | 33.7678 | -17.7632 | 15.5244 | 0.87252 | 143.6725 | 0.2 | 0 | 9.6033 | 154.1484 | 9.9 | 14.7171 | 1.036 | 0.13095
2016-07-17 11:00 | 190.8233 | 190.4667 | 0.35667 | 0.63279 | 21.2761 | -0.79498 | 55.692 | 34.308 | -0.89684 | 4.3743 | 0.63095 | 142.85 | 0.2 | 0 | 9.5412 | 153.0221 | 9.5 | 14.2819 | 1.0375 | 0.13019
2016-07-17 12:00 | 189.58 | 189.37 | 0.21 | 0.37693 | 21.2691 | 14.204 | 56.142 | 33.858 | 15.9832 | 14.0857 | 0.36559 | 142.0275 | 0.2 | 0 | 9.479 | 151.8721 | 8.8 | 13.546 | 1.0401 | 0.12953
2016-07-17 13:00 | 155.9167 | 155.62 | 0.29667 | 0.55271 | 21.2621 | 29.203 | 57.5375 | 32.4625 | 32.6088 | 27.8841 | 0.48854 | 116.715 | 0.2 | 0 | 7.7958 | 124.9994 | 8 | 11.9062 | 1.0458 | 0.1072
2016-07-17 14:00 | 122.2533 | 121.87 | 0.38333 | 0.7608 | 21.2551 | 44.2019 | 59.7446 | 30.2554 | 48.7835 | 41.8555 | 0.56667 | 91.4025 | 0.2 | 0 | 6.1127 | 98.0818 | 7.8 | 10.8651 | 1.0495 | 0.084406
2016-07-17 15:00 | 88.59 | 88.12 | 0.47 | 1.0202 | 21.2481 | 59.2009 | 62.5682 | 27.4318 | 64.4217 | 55.7915 | 0.57356 | 66.09 | 0.2 | 0 | 4.4295 | 71.0931 | 8.7 | 10.9217 | 1.0493 | 0.061169
2016-07-17 16:00 | 73.28 | 72.5967 | 0.68333 | 1.6659 | 21.2411 | 74.1999 | 65.7831 | 24.2169 | 79.5419 | 69.6068 | 0.5805 | 54.4475 | 0.2 | 0 | 3.664 | 58.692 | 8.2 | 10.0341 | 1.0524 | 0.050648
2016-07-17 17:00 | 57.97 | 57.0733 | 0.89667 | 2.5202 | 21.234 | 89.1989 | 69.1583 | 20.8417 | 94.2329 | 83.2144 | 0.29778 | 42.805 | 0.2 | 0 | 2.8985 | 46.0013 | 7.6 | 9.0375 | 1.0559 | 0.039828
2016-07-17 18:00 | 42.66 | 41.55 | 1.11 | 3.6855 | 21.227 | 104.1979 | 72.4717 | 17.5283 | 108.6154 | 96.4896 | 0 | 31.1625 | 0.2 | 0 | 2.133 | 33.2955 | 7.6 | 8.6405 | 1.0573 | 0.028866
2016-07-17 19:00 | 35.6867 | 34.94 | 0.74667 | 2.9858 | 21.2199 | 119.1968 | 75.5181 | 14.4819 | 122.8107 | 109.2276 | 0 | 26.205 | 0.2 | 0 | 1.7843 | 27.9893 | 7.3 | 8.1747 | 1.0589 | 0.024303
2016-07-17 20:00 | 28.7133 | 28.33 | 0.38333 | 1.8613 | 21.2129 | 134.1958 | 78.1147 | 11.8853 | 136.9195 | 121.0646 | 0 | 21.2475 | 0.2 | 0 | 1.4357 | 22.6832 | 7.4 | 8.1088 | 1.0591 | 0.0197
2016-07-17 21:00 | 21.74 | 21.72 | 0.02 | 0.1164 | 21.2058 | 149.1948 | 80.1065 | 9.8935 | 151.0104 | 131.3263 | 0 | 16.29 | 0.2 | 0 | 1.087 | 17.377 | 6.6 | 7.143 | 1.0625 | 0.01514
2016-07-17 22:00 | 17.4267 | 17.3267 | 0.1 | 0.66675 | 21.1987 | 164.1938 | 81.3742 | 8.6258 | 165.1163 | 138.8084 | 0 | 12.995 | 0.2 | 0 | 0.87133 | 13.8663 | 7.6 | 8.0333 | 1.0594 | 0.012046
2016-07-17 23:00 | 13.1133 | 12.9333 | 0.18 | 1.2682 | 21.1916 | 179.1928 | 81.8405 | 8.1595 | 179.2397 | 141.8335 | 0 | 9.7 | 0.2 | 0 | 0.65567 | 10.3557 | 7.6 | 7.9236 | 1.0598 | 0.0089992
2016-07-18 | 8.8 | 8.54 | 0.26 | 1.7543 | 21.1845 | -165.8081 | 81.4772 | 8.5228 | -166.635 | 139.3906 | 0 | 6.405 | 0.2 | 0 | 0.44 | 6.845 | 8.1 | 8.3139 | 1.0584 | 0.0059407
2016-07-18 01:00 | 13.9733 | 13.6767 | 0.29667 | 1.762 | 21.1774 | -150.8091 | 80.307 | 9.693 | -152.5245 | 132.3138 | 0 | 10.2575 | 0.2 | 0 | 0.69867 | 10.9562 | 9.8 | 10.1424 | 1.052 | 0.0094512
2016-07-18 02:00 | 19.1467 | 18.8133 | 0.33333 | 1.658 | 21.1703 | -135.8101 | 78.4018 | 11.5982 | -138.4292 | 122.2865 | 0 | 14.11 | 0.2 | 0 | 0.95733 | 15.0673 | 5.7 | 6.1709 | 1.0659 | 0.013169
2016-07-18 03:00 | 24.32 | 23.95 | 0.37 | 1.5164 | 21.1632 | -120.8111 | 75.8771 | 14.1229 | -124.3203 | 110.5804 | 0 | 17.9625 | 0.2 | 0 | 1.216 | 19.1785 | 8.1 | 8.6993 | 1.0571 | 0.016624
2016-07-18 04:00 | 29.83 | 27.8967 | 1.9333 | 6.5692 | 21.156 | -105.8121 | 72.8842 | 17.1158 | -110.1334 | 97.917 | 0 | 20.9225 | 0.2 | 0 | 1.4915 | 22.414 | 8.1 | 8.8004 | 1.0567 | 0.019422
2016-07-18 05:00 | 35.34 | 31.8433 | 3.4967 | 10.0331 | 21.1489 | -90.813 | 69.6036 | 20.3964 | -95.7716 | 84.6853 | 0.92933 | 23.8825 | 0.2 | 0 | 1.767 | 26.5788 | 5.4 | 6.2306 | 1.0657 | 0.023226
2016-07-18 06:00 | 40.85 | 35.79 | 5.06 | 12.5579 | 21.1417 | -75.814 | 66.2384 | 23.7616 | -81.1157 | 71.1025 | 4.0672 | 26.8425 | 0.2 | 0 | 2.0425 | 32.9522 | 7.7 | 8.7298 | 1.0569 | 0.02856
2016-07-18 07:00 | 107.9833 | 103.38 | 4.6033 | 10.143 | 21.1345 | -60.815 | 63.0095 | 26.9905 | -66.0446 | 57.2992 | 5.4798 | 77.535 | 0.2 | 0 | 5.3992 | 88.4139 | 10.2 | 12.9629 | 1.0421 | 0.075554
2016-07-18 08:00 | 175.1167 | 170.97 | 4.1467 | 8.3305 | 21.1273 | -45.8159 | 60.1474 | 29.8526 | -50.4652 | 43.3643 | 6.0563 | 128.2275 | 0.2 | 0 | 8.7558 | 143.0396 | 10.3 | 14.77 | 1.0358 | 0.12149
2016-07-18 09:00 | 242.25 | 238.56 | 3.69 | 6.9399 | 21.1202 | -30.8169 | 57.879 | 32.121 | -34.3506 | 29.3783 | 6.0474 | 178.92 | 0.2 | 0 | 12.1125 | 197.0799 | 8.5 | 14.6587 | 1.0362 | 0.16745
2016-07-18 10:00 | 260.03 | 236.6433 | 23.3867 | 42.2645 | 21.1129 | -15.8179 | 56.4035 | 33.5965 | -17.7749 | 15.5075 | 40.7258 | 177.4825 | 0.2 | 0 | 13.0015 | 231.2098 | 8.7 | 15.9253 | 1.0318 | 0.19561
2016-07-18 11:00 | 277.81 | 234.7267 | 43.0833 | 76.7725 | 21.1057 | -0.8188 | 55.8624 | 34.1376 | -0.9229 | 4.2108 | 76.5653 | 176.045 | 0.2 | 0 | 13.8905 | 266.5008 | 7.9 | 16.2281 | 1.0307 | 0.22524
2016-07-18 12:00 | 295.59 | 232.81 | 62.78 | 113.1807 | 21.0985 | 14.1803 | 56.3108 | 33.6892 | 15.943 | 14.0201 | 109.8091 | 174.6075 | 0.2 | 0 | 14.7795 | 299.1961 | 7.8 | 17.1499 | 1.0275 | 0.25208
2016-07-18 13:00 | 330.63 | 191.77 | 138.86 | 259.8948 | 21.0913 | 29.1793 | 57.704 | 32.296 | 32.5566 | 27.8513 | 229.7894 | 143.8275 | 0.2 | 0 | 16.5315 | 390.1484 | 6.8 | 18.9921 | 1.021 | 0.32665
2016-07-18 14:00 | 365.67 | 150.73 | 214.94 | 428.699 | 21.084 | 44.1784 | 59.9088 | 30.0912 | 48.7226 | 41.8398 | 319.3863 | 113.0475 | 0.2 | 0 | 18.2835 | 450.7173 | 7.2 | 21.2849 | 1.013 | 0.37439
2016-07-18 15:00 | 400.71 | 109.69 | 291.02 | 635.1722 | 21.0768 | 59.1774 | 62.7306 | 27.2694 | 64.3556 | 55.7895 | 357.1161 | 82.2675 | 0.2 | 0 | 20.0355 | 459.4191 | 6.8 | 21.1568 | 1.0135 | 0.38179
2016-07-18 16:00 | 305.2833 | 107.3933 | 197.89 | 485.4756 | 21.0695 | 74.1765 | 65.9445 | 24.0555 | 79.474 | 69.618 | 169.0804 | 80.545 | 0.2 | 0 | 15.2642 | 264.8896 | 6.3 | 14.5778 | 1.0365 | 0.22513
2016-07-18 17:00 | 209.8567 | 105.0967 | 104.76 | 296.6432 | 21.0622 | 89.1756 | 69.3198 | 20.6802 | 94.166 | 83.2397 | 34.9195 | 78.8225 | 0.2 | 0 | 10.4928 | 124.2349 | 6.7 | 10.5823 | 1.0505 | 0.10701
2016-07-18 18:00 | 114.43 | 102.8 | 11.63 | 38.9653 | 21.0549 | 104.1747 | 72.6342 | 17.3658 | 108.552 | 96.5312 | 0 | 77.1 | 0.2 | 0 | 5.7215 | 82.8215 | 6.8 | 9.3882 | 1.0546 | 0.071625
2016-07-18 19:00 | 93.5033 | 83.6433 | 9.86 | 39.8713 | 21.0476 | 119.1737 | 75.6825 | 14.3175 | 122.7528 | 109.2889 | 0 | 62.7325 | 0.2 | 0 | 4.6752 | 67.4077 | 6.8 | 8.9065 | 1.0563 | 0.058388
2016-07-18 20:00 | 72.5767 | 64.4867 | 8.09 | 39.8312 | 21.0403 | 134.1728 | 78.2813 | 11.7187 | 136.8688 | 121.1506 | 0 | 48.365 | 0.2 | 0 | 3.6288 | 51.9938 | 6.4 | 8.0248 | 1.0594 | 0.045168
2016-07-18 21:00 | 51.65 | 45.33 | 6.32 | 37.4168 | 21.033 | 149.1719 | 80.2757 | 9.7243 | 150.9683 | 131.4432 | 0 | 33.9975 | 0.2 | 0 | 2.5825 | 36.58 | 6.1 | 7.2431 | 1.0621 | 0.03186
2016-07-18 22:00 | 36.25 | 32.0333 | 4.2167 | 28.6803 | 21.0257 | 164.171 | 81.5456 | 8.4544 | 165.084 | 138.9589 | 0 | 24.025 | 0.2 | 0 | 1.8125 | 25.8375 | 6.3 | 7.1074 | 1.0626 | 0.022514
2016-07-18 23:00 | 20.85 | 18.7367 | 2.1133 | 15.2108 | 21.0183 | 179.1701 | 82.0137 | 7.9863 | 179.2177 | 142.0063 | 0 | 14.0525 | 0.2 | 0 | 1.0425 | 15.095 | 6.2 | 6.6717 | 1.0641 | 0.013172
2016-07-19 | 5.45 | 5.44 | 0.01 | 0.068874 | 21.011 | -165.8308 | 81.6516 | 8.3484 | -166.6465 | 139.5601 | 0 | 4.08 | 0.2 | 0 | 0.2725 | 4.3525 | 5.9 | 6.036 | 1.0664 | 0.0038059
2016-07-19 01:00 | 6.21 | 6.2033 | 0.0066667 | 0.040317 | 21.0036 | -150.8317 | 80.482 | 9.518 | -152.5261 | 132.4619 | 0 | 4.6525 | 0.2 | 0 | 0.3105 | 4.963 | 6.6 | 6.7551 | 1.0639 | 0.0043295
2016-07-19 02:00 | 6.97 | 6.9667 | 0.0033333 | 0.016831 | 20.9963 | -135.8326 | 78.5769 | 11.4231 | -138.4219 | 122.4099 | 0 | 5.225 | 0.2 | 0 | 0.3485 | 5.5735 | 6.9 | 7.0742 | 1.0627 | 0.004857
2016-07-19 03:00 | 7.73 | 7.73 | 0 | 0 | 20.9889 | -120.8335 | 76.052 | 13.948 | -124.3055 | 110.6822 | 0 | 5.7975 | 0.2 | 0 | 0.3865 | 6.184 | 7.3 | 7.4932 | 1.0613 | 0.0053816
2016-07-19 04:00 | 7.9167 | 7.9167 | 0 | 0 | 20.9815 | -105.8344 | 73.0589 | 16.9411 | -110.1132 | 98.0009 | 0 | 5.9375 | 0.2 | 0 | 0.39583 | 6.3333 | 5.8 | 5.9979 | 1.0665 | 0.0055387
2016-07-19 05:00 | 8.1033 | 8.1033 | 0 | 0 | 20.9741 | -90.8352 | 69.7782 | 20.2218 | -95.7482 | 84.7538 | 0 | 6.0775 | 0.2 | 0 | 0.40517 | 6.4827 | 5.8 | 6.0026 | 1.0665 | 0.0056692
2016-07-19 06:00 | 8.29 | 8.29 | 0 | 0 | 20.9667 | -75.8361 | 66.4133 | 23.5867 | -81.092 | 71.1575 | 0 | 6.2175 | 0.2 | 0 | 0.4145 | 6.632 | 6.1 | 6.3072 | 1.0654 | 0.005794
2016-07-19 07:00 | 16.6267 | 15.82 | 0.80667 | 1.7882 | 20.9593 | -60.837 | 63.1849 | 26.8151 | -66.0236 | 57.3415 | 0.96495 | 11.865 | 0.2 | 0 | 0.83133 | 13.6613 | 5.8 | 6.2269 | 1.0657 | 0.011938
2016-07-19 08:00 | 24.9633 | 23.35 | 1.6133 | 3.2586 | 20.9518 | -45.8379 | 60.3237 | 29.6763 | -50.4507 | 43.3932 | 2.3679 | 17.5125 | 0.2 | 0 | 1.2482 | 21.1286 | 5.2 | 5.8603 | 1.067 | 0.018486
2016-07-19 09:00 | 33.3 | 30.88 | 2.42 | 4.5739 | 20.9444 | -30.8387 | 58.0559 | 31.9441 | -34.3462 | 29.3907 | 3.9852 | 23.16 | 0.2 | 0 | 1.665 | 28.8102 | 5.2 | 6.1003 | 1.0661 | 0.025187
2016-07-19 10:00 | 59.41 | 57.7967 | 1.6133 | 2.9293 | 20.9369 | -15.8396 | 56.5805 | 33.4195 | -17.7836 | 15.4893 | 2.8229 | 43.3475 | 0.2 | 0 | 2.9705 | 49.1409 | 5.6 | 7.1357 | 1.0625 | 0.042815
2016-07-19 11:00 | 85.52 | 84.7133 | 0.80667 | 1.444 | 20.9295 | -0.84046 | 56.0388 | 33.9612 | -0.94646 | 4.0417 | 1.4404 | 63.535 | 0.2 | 0 | 4.276 | 69.2514 | 4.8 | 6.9641 | 1.0631 | 0.060371
2016-07-19 12:00 | 111.63 | 111.63 | 0 | 0 | 20.922 | 14.1587 | 56.4855 | 33.5145 | 15.9049 | 13.9568 | 0 | 83.7225 | 0.2 | 0 | 5.5815 | 89.304 | 5.3 | 8.0907 | 1.0592 | 0.077563
2016-07-19 13:00 | 103.87 | 103.87 | 0 | 0 | 20.9145 | 29.1578 | 57.8767 | 32.1233 | 32.506 | 27.8211 | 0 | 77.9025 | 0.2 | 0 | 5.1935 | 83.096 | 4.4 | 6.9967 | 1.063 | 0.072432
2016-07-19 14:00 | 96.11 | 96.11 | 0 | 0 | 20.907 | 44.157 | 60.0793 | 29.9207 | 48.6628 | 41.8269 | 0 | 72.0825 | 0.2 | 0 | 4.8055 | 76.888 | 4.4 | 6.8027 | 1.0637 | 0.067064
2016-07-19 15:00 | 88.35 | 88.35 | 0 | 0 | 20.8995 | 59.1561 | 62.8993 | 27.1007 | 64.2904 | 55.7905 | 0 | 66.2625 | 0.2 | 0 | 4.4175 | 70.68 | 4.2 | 6.4088 | 1.0651 | 0.061729
2016-07-19 16:00 | 70.21 | 70.21 | 0 | 0 | 20.892 | 74.1553 | 66.1122 | 23.8878 | 79.4068 | 69.6324 | 0 | 52.6575 | 0.2 | 0 | 3.5105 | 56.168 | 3.8 | 5.5553 | 1.0681 | 0.049192
2016-07-19 17:00 | 52.07 | 52.07 | 0 | 0 | 20.8845 | 89.1545 | 69.4876 | 20.5124 | 94.0998 | 83.2686 | 0 | 39.0525 | 0.2 | 0 | 2.6035 | 41.656 | 4.1 | 5.4017 | 1.0686 | 0.036501
2016-07-19 18:00 | 33.93 | 33.93 | 0 | 0 | 20.877 | 104.1536 | 72.803 | 17.197 | 108.4893 | 96.5767 | 0 | 25.4475 | 0.2 | 0 | 1.6965 | 27.144 | 4.1 | 4.9482 | 1.0702 | 0.02382
2016-07-19 19:00 | 27.74 | 27.74 | 0 | 0 | 20.8694 | 119.1528 | 75.853 | 14.147 | 122.6957 | 109.3546 | 0 | 20.805 | 0.2 | 0 | 1.387 | 22.192 | 3.7 | 4.3935 | 1.0721 | 0.01951
2016-07-19 20:00 | 21.55 | 21.55 | 0 | 0 | 20.8619 | 134.152 | 78.4541 | 11.5459 | 136.8191 | 121.2416 | 0 | 16.1625 | 0.2 | 0 | 1.0775 | 17.24 | 3.6 | 4.1387 | 1.073 | 0.015169
2016-07-19 21:00 | 15.36 | 15.36 | 0 | 0 | 20.8543 | 149.1512 | 80.4509 | 9.5491 | 150.9276 | 131.5656 | 0 | 11.52 | 0.2 | 0 | 0.768 | 12.288 | 4.2 | 4.584 | 1.0715 | 0.010796
2016-07-19 22:00 | 24.7267 | 21.63 | 3.0967 | 21.5107 | 20.8467 | 164.1504 | 81.723 | 8.277 | 165.0532 | 139.1153 | 0 | 16.2225 | 0.2 | 0 | 1.2363 | 17.4588 | 4.5 | 5.0456 | 1.0698 | 0.015316
2016-07-19 23:00 | 34.0933 | 27.9 | 6.1933 | 45.5932 | 20.8391 | 179.1495 | 82.1929 | 7.8071 | 179.1977 | 142.185 | 0 | 20.925 | 0.2 | 0 | 1.7047 | 22.6297 | 5.3 | 6.0072 | 1.0665 | 0.01979
2016-07-20 | 43.46 | 34.17 | 9.29 | 65.3864 | 20.8315 | -165.8513 | 81.8319 | 8.1681 | -166.6557 | 139.7343 | 0 | 25.6275 | 0.2 | 0 | 2.173 | 27.8005 | 5.1 | 5.9688 | 1.0666 | 0.024315
2016-07-20 01:00 | 58.9433 | 48.72 | 10.2233 | 63.0113 | 20.8239 | -150.8521 | 80.6627 | 9.3373 | -152.5249 | 132.6131 | 0 | 36.54 | 0.2 | 0 | 2.9472 | 39.4872 | 3.9 | 5.134 | 1.0695 | 0.034631
2016-07-20 02:00 | 74.4267 | 63.27 | 11.1567 | 57.2253 | 20.8163 | -135.8529 | 78.7576 | 11.2424 | -138.4115 | 122.5353 | 0 | 47.4525 | 0.2 | 0 | 3.7213 | 51.1738 | 3.7 | 5.2992 | 1.069 | 0.044856
2016-07-20 03:00 | 89.91 | 77.82 | 12.09 | 50.8015 | 20.8087 | -120.8537 | 76.2323 | 13.7677 | -124.2875 | 110.785 | 0 | 58.365 | 0.2 | 0 | 4.4955 | 62.8605 | 3.8 | 5.7644 | 1.0673 | 0.055016
2016-07-20 04:00 | 126.4133 | 110.4167 | 15.9967 | 55.4705 | 20.8011 | -105.8545 | 73.2389 | 16.7611 | -110.0895 | 98.0849 | 0 | 82.8125 | 0.2 | 0 | 6.3207 | 89.1332 | 4 | 6.7854 | 1.0638 | 0.077749
2016-07-20 05:00 | 162.9167 | 143.0133 | 19.9033 | 58.0767 | 20.7934 | -90.8552 | 69.9581 | 20.0419 | -95.7213 | 84.8222 | 5.2413 | 107.26 | 0.2 | 0 | 8.1458 | 120.6471 | 5.8 | 9.5702 | 1.054 | 0.10427
2016-07-20 06:00 | 199.42 | 175.61 | 23.81 | 59.9366 | 20.7858 | -75.856 | 66.5934 | 23.4066 | -81.0646 | 71.2119 | 19.3037 | 131.7075 | 0.2 | 0 | 9.971 | 160.9822 | 6.1 | 11.1307 | 1.0485 | 0.13841
2016-07-20 07:00 | 268.9733 | 224.6967 | 44.2767 | 98.7671 | 20.7781 | -60.8568 | 63.3657 | 26.6343 | -65.9991 | 57.3828 | 53.2378 | 168.5225 | 0.2 | 0 | 13.4487 | 235.209 | 5.6 | 12.9503 | 1.0422 | 0.20101
2016-07-20 08:00 | 338.5267 | 273.7833 | 64.7433 | 131.5007 | 20.7704 | -45.8576 | 60.5054 | 29.4946 | -50.4327 | 43.4209 | 95.5121 | 205.3375 | 0.2 | 0 | 16.9263 | 317.7759 | 5.8 | 15.7305 | 1.0324 | 0.26903
2016-07-20 09:00 | 408.08 | 322.87 | 85.21 | 161.877 | 20.7627 | -30.8584 | 58.2383 | 31.7617 | -34.3385 | 29.4017 | 141.0271 | 242.1525 | 0.2 | 0 | 20.404 | 403.5836 | 6.5 | 19.112 | 1.0206 | 0.33776
2016-07-20 10:00 | 409.66 | 329.1733 | 80.4867 | 146.8467 | 20.755 | -15.8591 | 56.7632 | 33.2368 | -17.7893 | 15.4699 | 141.5265 | 246.88 | 0.2 | 0 | 20.483 | 408.8895 | 6.1 | 18.8778 | 1.0214 | 0.34247
2016-07-20 11:00 | 411.24 | 335.4767 | 75.7633 | 136.2671 | 20.7473 | -0.8599 | 56.221 | 33.779 | -0.96746 | 3.8672 | 135.9568 | 251.6075 | 0.2 | 0 | 20.562 | 408.1263 | 5.8 | 18.5539 | 1.0226 | 0.34221
2016-07-20 12:00 | 412.82 | 341.78 | 71.04 | 129.2779 | 20.7396 | 14.1393 | 56.6663 | 33.3337 | 15.8688 | 13.8959 | 125.4944 | 256.335 | 0.2 | 0 | 20.641 | 402.4704 | 6.3 | 18.8772 | 1.0214 | 0.3371
2016-07-20 13:00 | 352.86 | 289.51 | 63.35 | 119.7319 | 20.7319 | 29.1386 | 58.0554 | 31.9446 | 32.457 | 27.7937 | 105.9187 | 217.1325 | 0.2 | 0 | 17.643 | 340.6942 | 8.8 | 19.4467 | 1.0194 | 0.2848
2016-07-20 14:00 | 292.9 | 237.24 | 55.66 | 112.1889 | 20.7242 | 44.1378 | 60.2559 | 29.7441 | 48.6043 | 41.8169 | 83.612 | 177.93 | 0.2 | 0 | 14.645 | 276.187 | 7.2 | 15.8308 | 1.0321 | 0.23374
2016-07-20 15:00 | 232.94 | 184.97 | 47.97 | 105.932 | 20.7164 | 59.1371 | 63.0741 | 26.9259 | 64.2262 | 55.7946 | 59.5508 | 138.7275 | 0.2 | 0 | 11.647 | 209.9253 | 5.5 | 12.0602 | 1.0453 | 0.17993
2016-07-20 16:00 | 192.4 | 156.4667 | 35.9333 | 89.3488 | 20.7087 | 74.1363 | 66.2862 | 23.7138 | 79.3405 | 69.6502 | 31.0711 | 117.35 | 0.2 | 0 | 9.62 | 158.0411 | 6.6 | 11.5388 | 1.0471 | 0.1357
2016-07-20 17:00 | 151.86 | 127.9633 | 23.8967 | 68.7544 | 20.7009 | 89.1356 | 69.6615 | 20.3385 | 94.0344 | 83.3011 | 8.0203 | 95.9725 | 0.2 | 0 | 7.593 | 111.5858 | 6.3 | 9.7871 | 1.0532 | 0.096372
2016-07-20 18:00 | 111.32 | 99.46 | 11.86 | 40.5138 | 20.6931 | 104.1349 | 72.9779 | 17.0221 | 108.4274 | 96.6262 | 0 | 74.595 | 0.2 | 0 | 5.566 | 80.161 | 6.4 | 8.905 | 1.0563 | 0.069435
2016-07-20 19:00 | 93.57 | 81.2767 | 12.2933 | 50.9211 | 20.6853 | 119.1341 | 76.0297 | 13.9703 | 122.6395 | 109.4246 | 0 | 60.9575 | 0.2 | 0 | 4.6785 | 65.636 | 5.8 | 7.8511 | 1.06 | 0.057052
2016-07-20 20:00 | 75.82 | 63.0933 | 12.7267 | 64.5721 | 20.6775 | 134.1334 | 78.633 | 11.367 | 136.7706 | 121.3374 | 0 | 47.32 | 0.2 | 0 | 3.791 | 51.111 | 7.4 | 8.9972 | 1.056 | 0.044258
2016-07-20 21:00 | 58.07 | 44.91 | 13.16 | 80.8489 | 20.6697 | 149.1327 | 80.6321 | 9.3679 | 150.8882 | 131.6935 | 0 | 33.6825 | 0.2 | 0 | 2.9035 | 36.586 | 6.9 | 8.0433 | 1.0593 | 0.031781
2016-07-20 22:00 | 55.5033 | 42.7833 | 12.72 | 90.3462 | 20.6619 | 164.1319 | 81.9063 | 8.0937 | 165.0243 | 139.2778 | 0 | 32.0875 | 0.2 | 0 | 2.7752 | 34.8627 | 5.5 | 6.5895 | 1.0644 | 0.030429
2016-07-20 23:00 | 52.9367 | 40.6567 | 12.28 | 92.5816 | 20.6541 | 179.1312 | 82.3778 | 7.6222 | 179.1798 | 142.3696 | 0 | 30.4925 | 0.2 | 0 | 2.6468 | 33.1393 | 6.4 | 7.4356 | 1.0615 | 0.028845
2016-07-21 | 50.37 | 38.53 | 11.84 | 85.2624 | 20.6463 | -165.8695 | 82.0178 | 7.9822 | -166.6625 | 139.9132 | 0 | 28.8975 | 0.2 | 0 | 2.5185 | 31.416 | 6.9 | 7.8818 | 1.0599 | 0.027305
2016-07-21 01:00 | 69.3867 | 49.32 | 20.0667 | 126.1758 | 20.6384 | -150.8702 | 80.849 | 9.151 | -152.5211 | 132.7674 | 0 | 36.99 | 0.2 | 0 | 3.4693 | 40.4593 | 6.6 | 7.8644 | 1.06 | 0.035166
2016-07-21 02:00 | 88.4033 | 60.11 | 28.2933 | 147.5348 | 20.6306 | -135.8709 | 78.9437 | 11.0563 | -138.3982 | 122.6623 | 0 | 45.0825 | 0.2 | 0 | 4.4202 | 49.5027 | 5.3 | 6.847 | 1.0635 | 0.043171
2016-07-21 03:00 | 107.42 | 70.9 | 36.52 | 155.5119 | 20.6227 | -120.8716 | 76.418 | 13.582 | -124.2663 | 110.8886 | 0 | 53.175 | 0.2 | 0 | 5.371 | 58.546 | 5.3 | 7.1296 | 1.0625 | 0.05101
2016-07-21 04:00 | 143.24 | 94.9033 | 48.3367 | 169.4328 | 20.6148 | -105.8723 | 73.4241 | 16.5759 | -110.0625 | 98.1692 | 0 | 71.1775 | 0.2 | 0 | 7.162 | 78.3395 | 6 | 8.4481 | 1.0579 | 0.06796
2016-07-21 05:00 | 179.06 | 118.9067 | 60.1533 | 177.0924 | 20.6069 | -90.873 | 70.1431 | 19.8569 | -95.6909 | 84.8902 | 15.7728 | 89.18 | 0.2 | 0 | 8.953 | 113.9058 | 6.9 | 10.4596 | 1.0509 | 0.098156
2016-07-21 06:00 | 214.88 | 142.91 | 71.97 | 182.5336 | 20.599 | -75.8737 | 66.7787 | 23.2213 | -81.0337 | 71.2656 | 58.6264 | 107.1825 | 0.2 | 0 | 10.744 | 176.5529 | 7.3 | 12.8173 | 1.0426 | 0.15095
2016-07-21 07:00 | 273.0667 | 160.99 | 112.0767 | 251.6374 | 20.5911 | -60.8744 | 63.5517 | 26.4483 | -65.971 | 57.4232 | 135.4892 | 120.7425 | 0.2 | 0 | 13.6533 | 269.885 | 7.6 | 16.0339 | 1.0314 | 0.22825
2016-07-21 08:00 | 331.2533 | 179.07 | 152.1833 | 310.8963 | 20.5832 | -45.875 | 60.6924 | 29.3076 | -50.4112 | 43.4476 | 225.712 | 134.3025 | 0.2 | 0 | 16.5627 | 376.5771 | 6.6 | 18.368 | 1.0232 | 0.31596
2016-07-21 09:00 | 389.44 | 197.15 | 192.29 | 367.249 | 20.5753 | -30.8757 | 58.4262 | 31.5738 | -34.3275 | 29.4116 | 319.916 | 147.8625 | 0.2 | 0 | 19.472 | 487.2505 | 5.5 | 20.7266 | 1.015 | 0.40552
2016-07-21 10:00 | 391.2633 | 215.71 | 175.5533 | 321.9111 | 20.5673 | -15.8764 | 56.9516 | 33.0484 | -17.792 | 15.4494 | 310.2792 | 161.7825 | 0.2 | 0 | 19.5632 | 491.6248 | 6.3 | 21.6633 | 1.0117 | 0.40784
2016-07-21 11:00 | 393.0867 | 234.27 | 158.8167 | 287.0555 | 20.5594 | -0.87707 | 56.409 | 33.591 | -0.98584 | 3.6874 | 286.4612 | 175.7025 | 0.2 | 0 | 19.6543 | 481.818 | 7.1 | 22.1568 | 1.01 | 0.39902
2016-07-21 12:00 | 394.91 | 252.83 | 142.08 | 259.8446 | 20.5514 | 14.1223 | 56.853 | 33.147 | 15.8349 | 13.838 | 252.3029 | 189.6225 | 0.2 | 0 | 19.7455 | 461.6709 | 9.1 | 23.5272 | 1.0052 | 0.38052
2016-07-21 13:00 | 335.65 | 237.36 | 98.29 | 186.7355 | 20.5435 | 29.1216 | 58.2402 | 31.7598 | 32.4098 | 27.7691 | 165.2296 | 178.02 | 0.2 | 0 | 16.7825 | 360.0321 | 5.8 | 17.051 | 1.0278 | 0.30344
2016-07-21 14:00 | 276.39 | 221.89 | 54.5 | 110.4678 | 20.5355 | 44.1209 | 60.4386 | 29.5614 | 48.5472 | 41.81 | 82.3382 | 166.4175 | 0.2 | 0 | 13.8195 | 262.5752 | 6.7 | 14.9055 | 1.0353 | 0.22292
2016-07-21 15:00 | 217.13 | 206.42 | 10.71 | 23.799 | 20.5275 | 59.1203 | 63.2551 | 26.7449 | 64.1631 | 55.8019 | 13.3764 | 154.815 | 0.2 | 0 | 10.8565 | 179.0479 | 5.8 | 11.3952 | 1.0476 | 0.15381
2016-07-21 16:00 | 180.85 | 171.3167 | 9.5333 | 23.8757 | 20.5195 | 74.1196 | 66.4662 | 23.5338 | 79.275 | 69.6714 | 8.2945 | 128.4875 | 0.2 | 0 | 9.0425 | 145.8245 | 6.6 | 11.157 | 1.0485 | 0.12537
2016-07-21 17:00 | 144.57 | 136.2133 | 8.3567 | 24.2492 | 20.5115 | 89.119 | 69.8416 | 20.1584 | 93.9698 | 83.3373 | 2.8135 | 102.16 | 0.2 | 0 | 7.2285 | 112.202 | 5.7 | 9.2063 | 1.0553 | 0.097092
2016-07-21 18:00 | 108.29 | 101.11 | 7.18 | 24.7828 | 20.5035 | 104.1184 | 73.159 | 16.841 | 108.3664 | 96.6796 | 0 | 75.8325 | 0.2 | 0 | 5.4145 | 81.247 | 5 | 7.539 | 1.0611 | 0.070694
2016-07-21 19:00 | 107.28 | 78.6033 | 28.6767 | 120.3275 | 20.4955 | 119.1177 | 76.2125 | 13.7875 | 122.5843 | 109.499 | 0 | 58.9525 | 0.2 | 0 | 5.364 | 64.3165 | 5 | 7.0099 | 1.063 | 0.05606
2016-07-21 20:00 | 106.27 | 56.0967 | 50.1733 | 258.7236 | 20.4874 | 134.1171 | 78.818 | 11.182 | 136.7232 | 121.4381 | 0 | 42.0725 | 0.2 | 0 | 5.3135 | 47.386 | 4.9 | 6.3808 | 1.0652 | 0.041389
2016-07-21 21:00 | 105.26 | 33.59 | 71.67 | 449.2077 | 20.4794 | 149.1165 | 80.8194 | 9.1806 | 150.8503 | 131.8268 | 0 | 25.1925 | 0.2 | 0 | 5.263 | 30.4555 | 4.8 | 5.7517 | 1.0674 | 0.026656
2016-07-21 22:00 | 100.0067 | 32.3 | 67.7067 | 492.3384 | 20.4713 | 164.1158 | 82.0956 | 7.9044 | 164.9971 | 139.4463 | 0 | 24.225 | 0.2 | 0 | 5.0003 | 29.2253 | 4.7 | 5.6133 | 1.0679 | 0.025591
2016-07-21 23:00 | 94.7533 | 31.01 | 63.7433 | 492.839 | 20.4633 | 179.1152 | 82.5686 | 7.4314 | 179.164 | 142.56 | 0 | 23.2575 | 0.2 | 0 | 4.7377 | 27.9952 | 4.8 | 5.6748 | 1.0676 | 0.024509
2016-07-22 | 89.5 | 29.72 | 59.78 | 441.0076 | 20.4552 | -165.8854 | 82.2094 | 7.7906 | -166.6668 | 140.0966 | 0 | 22.29 | 0.2 | 0 | 4.475 | 26.765 | 4.8 | 5.6364 | 1.0678 | 0.023435
2016-07-22 01:00 | 99.44 | 37.1867 | 62.2533 | 399.7457 | 20.4471 | -150.886 | 81.0407 | 8.9593 | -152.5145 | 132.9246 | 0 | 27.89 | 0.2 | 0 | 4.972 | 32.862 | 4.5 | 5.5269 | 1.0682 | 0.028783
2016-07-22 02:00 | 109.38 | 44.6533 | 64.7267 | 343.3884 | 20.439 | -135.8866 | 79.1351 | 10.8649 | -138.3818 | 122.791 | 0 | 33.49 | 0.2 | 0 | 5.469 | 38.959 | 4.7 | 5.9175 | 1.0668 | 0.03408
2016-07-22 03:00 | 119.32 | 52.12 | 67.2 | 290.1576 | 20.4309 | -120.8872 | 76.6088 | 13.3912 | -124.2418 | 110.9929 | 0 | 39.09 | 0.2 | 0 | 5.966 | 45.056 | 4.7 | 6.108 | 1.0661 | 0.039389
2016-07-22 04:00 | 140.23 | 71.35 | 68.88 | 244.1689 | 20.4228 | -105.8878 | 73.6144 | 16.3856 | -110.032 | 98.2535 | 0 | 53.5125 | 0.2 | 0 | 7.0115 | 60.524 | 4.8 | 6.6914 | 1.0641 | 0.05281
2016-07-22 05:00 | 161.14 | 90.58 | 70.56 | 209.6572 | 20.4147 | -90.8884 | 70.3332 | 19.6668 | -95.6569 | 84.9578 | 18.4267 | 67.935 | 0.2 | 0 | 8.057 | 94.4187 | 5 | 7.9506 | 1.0597 | 0.082043
2016-07-22 06:00 | 182.05 | 109.81 | 72.24 | 184.6495 | 20.4065 | -75.889 | 66.9691 | 23.0309 | -80.9991 | 71.3186 | 59.1441 | 82.3575 | 0.2 | 0 | 9.1025 | 150.6041 | 4.9 | 9.6064 | 1.0539 | 0.13015
2016-07-22 07:00 | 224.39 | 139.72 | 84.67 | 191.3878 | 20.3984 | -60.8896 | 63.7429 | 26.2571 | -65.9393 | 57.4626 | 102.9381 | 104.79 | 0.2 | 0 | 11.2195 | 218.9476 | 5.1 | 11.9421 | 1.0457 | 0.18774
2016-07-22 08:00 | 266.73 | 169.63 | 97.1 | 199.5601 | 20.3903 | -45.8902 | 60.8846 | 29.1154 | -50.3862 | 43.473 | 144.8204 | 127.2225 | 0.2 | 0 | 13.3365 | 285.3794 | 5.2 | 14.1181 | 1.0381 | 0.24292
2016-07-22 09:00 | 309.07 | 199.54 | 109.53 | 210.3442 | 20.3821 | -30.8908 | 58.6196 | 31.3804 | -34.3131 | 29.4203 | 183.2182 | 149.655 | 0.2 | 0 | 15.4535 | 348.3267 | 5.6 | 16.4852 | 1.0298 | 0.29414
2016-07-22 10:00 | 312.1367 | 206.4433 | 105.6933 | 194.824 | 20.3739 | -15.8914 | 57.1455 | 32.8545 | -17.7917 | 15.4281 | 187.8035 | 154.8325 | 0.2 | 0 | 15.6068 | 358.2429 | 5.3 | 16.4951 | 1.0298 | 0.3025
2016-07-22 11:00 | 315.2033 | 213.3467 | 101.8567 | 185.0454 | 20.3657 | -0.89193 | 56.6027 | 33.3973 | -1.0016 | 3.5025 | 184.6998 | 160.01 | 0.2 | 0 | 15.7602 | 360.4699 | 5.6 | 16.8647 | 1.0285 | 0.304
2016-07-22 12:00 | 318.27 | 220.25 | 98.02 | 180.1934 | 20.3575 | 14.1075 | 57.0456 | 32.9544 | 15.8033 | 13.7833 | 175.0046 | 165.1875 | 0.2 | 0 | 15.9135 | 356.1056 | 5.5 | 16.6283 | 1.0293 | 0.30056
2016-07-22 13:00 | 275.7233 | 175.63 | 100.0933 | 191.1909 | 20.3493 | 29.1069 | 58.431 | 31.569 | 32.3644 | 27.7477 | 169.2051 | 131.7225 | 0.2 | 0 | 13.7862 | 314.7138 | 5.6 | 15.4348 | 1.0335 | 0.2667
2016-07-22 14:00 | 233.1767 | 131.01 | 102.1667 | 208.2957 | 20.3411 | 44.1064 | 60.6273 | 29.3727 | 48.4915 | 41.8062 | 155.2645 | 98.2575 | 0.2 | 0 | 11.6588 | 265.1808 | 5.8 | 14.0869 | 1.0382 | 0.22575
2016-07-22 15:00 | 190.63 | 86.39 | 104.24 | 233.1465 | 20.3329 | 59.1058 | 63.4422 | 26.5578 | 64.1011 | 55.8125 | 131.0057 | 64.7925 | 0.2 | 0 | 9.5315 | 205.3297 | 5.5 | 11.9166 | 1.0458 | 0.17608
2016-07-22 16:00 | 161.92 | 84.5867 | 77.3333 | 195.1339 | 20.3247 | 74.1053 | 66.6524 | 23.3476 | 79.2105 | 69.6961 | 67.7115 | 63.44 | 0.2 | 0 | 8.096 | 139.2475 | 5.6 | 9.9515 | 1.0527 | 0.1202
2016-07-22 17:00 | 133.21 | 82.7833 | 50.4267 | 147.6343 | 20.3164 | 89.1047 | 70.0278 | 19.9722 | 93.9062 | 83.3771 | 17.0274 | 62.0875 | 0.2 | 0 | 6.6605 | 85.7754 | 5.3 | 7.9805 | 1.0596 | 0.074526
2016-07-22 18:00 | 104.5 | 80.98 | 23.52 | 82.0687 | 20.3082 | 104.1042 | 73.3461 | 16.6539 | 108.3063 | 96.7369 | 0 | 60.735 | 0.2 | 0 | 5.225 | 65.96 | 5.4 | 7.4612 | 1.0614 | 0.057407
2016-07-22 19:00 | 96.4367 | 65.9 | 30.5367 | 129.877 | 20.2999 | 119.1036 | 76.4013 | 13.5987 | 122.5302 | 109.5777 | 0 | 49.425 | 0.2 | 0 | 4.8218 | 54.2468 | 5.8 | 7.4952 | 1.0613 | 0.047208
2016-07-22 20:00 | 88.3733 | 50.82 | 37.5533 | 196.9694 | 20.2916 | 134.1031 | 79.0089 | 10.9911 | 136.6771 | 121.5436 | 0 | 38.115 | 0.2 | 0 | 4.4187 | 42.5337 | 6.5 | 7.8292 | 1.0601 | 0.036974
2016-07-22 21:00 | 80.31 | 35.74 | 44.57 | 285.3055 | 20.2834 | 149.1026 | 81.0125 | 8.9875 | 150.8139 | 131.9655 | 0 | 26.805 | 0.2 | 0 | 4.0155 | 30.8205 | 6.5 | 7.4631 | 1.0614 | 0.026824
2016-07-22 22:00 | 78.3733 | 34.8367 | 43.5367 | 324.544 | 20.2751 | 164.102 | 82.2907 | 7.7093 | 164.9717 | 139.6207 | 0 | 26.1275 | 0.2 | 0 | 3.9187 | 30.0462 | 6.1 | 7.0389 | 1.0629 | 0.026187
2016-07-22 23:00 | 76.4367 | 33.9333 | 42.5033 | 337.4938 | 20.2668 | 179.1015 | 82.7651 | 7.2349 | 179.1504 | 142.7561 | 0 | 25.45 | 0.2 | 0 | 3.8218 | 29.2718 | 6.3 | 7.2147 | 1.0622 | 0.025497
2016-07-23 | 74.5 | 33.03 | 41.47 | 313.8262 | 20.2585 | -165.899 | 82.4065 | 7.5935 | -166.6686 | 140.2845 | 0 | 24.7725 | 0.2 | 0 | 3.725 | 28.4975 | 4.6 | 5.4905 | 1.0683 | 0.024964
2016-07-23 01:00 | 89.29 | 52.4467 | 36.8433 | 241.8619 | 20.2501 | -150.8995 | 81.2379 | 8.7621 | -152.5051 | 133.0846 | 0 | 39.335 | 0.2 | 0 | 4.4645 | 43.7995 | 3.7 | 5.0687 | 1.0698 | 0.038421
2016-07-23 02:00 | 104.08 | 71.8633 | 32.2167 | 174.0298 | 20.2418 | -135.9 | 79.3318 | 10.6682 | -138.3623 | 122.9213 | 0 | 53.8975 | 0.2 | 0 | 5.204 | 59.1015 | 3.8 | 5.6469 | 1.0677 | 0.051746
2016-07-23 03:00 | 118.87 | 91.28 | 27.59 | 120.8661 | 20.2335 | -120.9005 | 76.8048 | 13.1952 | -124.214 | 111.0979 | 0 | 68.46 | 0.2 | 0 | 5.9435 | 74.4035 | 4.9 | 7.2251 | 1.0622 | 0.064806
2016-07-23 04:00 | 155.07 | 123.17 | 31.9 | 114.408 | 20.2251 | -105.901 | 73.8098 | 16.1902 | -109.998 | 98.3379 | 0 | 92.3775 | 0.2 | 0 | 7.7535 | 100.131 | 5 | 8.1291 | 1.059 | 0.086956
2016-07-23 05:00 | 191.27 | 155.06 | 36.21 | 108.6276 | 20.2168 | -90.9015 | 70.5283 | 19.4717 | -95.6193 | 85.025 | 9.4203 | 116.295 | 0.2 | 0 | 9.5635 | 135.2788 | 5.3 | 9.5275 | 1.0542 | 0.11694
2016-07-23 06:00 | 227.47 | 186.95 | 40.52 | 104.4095 | 20.2084 | -75.902 | 67.1645 | 22.8355 | -80.9608 | 71.3709 | 33.3526 | 140.2125 | 0.2 | 0 | 11.3735 | 184.9386 | 6.4 | 12.1793 | 1.0449 | 0.15845
2016-07-23 07:00 | 252.7433 | 223.57 | 29.1733 | 66.4047 | 20.2 | -60.9025 | 63.9391 | 26.0609 | -65.9039 | 57.501 | 35.6783 | 167.6775 | 0.2 | 0 | 12.6372 | 215.9929 | 5 | 11.7498 | 1.0464 | 0.18533
2016-07-23 08:00 | 278.0167 | 260.19 | 17.8267 | 36.8657 | 20.1916 | -45.903 | 61.082 | 28.918 | -50.3576 | 43.4974 | 26.7426 | 195.1425 | 0.2 | 0 | 13.9008 | 235.7859 | 5.2 | 12.5683 | 1.0435 | 0.20176
2016-07-23 09:00 | 303.29 | 296.81 | 6.48 | 12.5156 | 20.1832 | -30.9035 | 58.8182 | 31.1818 | -34.2954 | 29.4278 | 10.9008 | 222.6075 | 0.2 | 0 | 15.1645 | 248.6728 | 5.1 | 12.871 | 1.0425 | 0.21257
2016-07-23 10:00 | 314.5733 | 300.1567 | 14.4167 | 26.7183 | 20.1748 | -15.904 | 57.345 | 32.655 | -17.7884 | 15.406 | 25.7583 | 225.1175 | 0.2 | 0 | 15.7287 | 266.6044 | 6.5 | 14.8314 | 1.0356 | 0.2264
2016-07-23 11:00 | 325.8567 | 303.5033 | 22.3533 | 40.8256 | 20.1664 | -0.90443 | 56.8021 | 33.1979 | -1.0146 | 3.3126 | 40.7573 | 227.6275 | 0.2 | 0 | 16.2928 | 284.6777 | 9.9 | 18.7962 | 1.0217 | 0.2385
2016-07-23 12:00 | 337.14 | 306.85 | 30.29 | 55.9825 | 20.158 | 14.0951 | 57.244 | 32.756 | 15.7739 | 13.7321 | 54.3823 | 230.1375 | 0.2 | 0 | 16.857 | 301.3768 | 6.6 | 16.018 | 1.0314 | 0.2549
2016-07-23 13:00 | 278.1 | 256.9 | 21.2 | 40.7224 | 20.1495 | 29.0946 | 58.6276 | 31.3724 | 32.3208 | 27.7295 | 36.0456 | 192.675 | 0.2 | 0 | 13.905 | 242.6256 | 6 | 13.582 | 1.04 | 0.2069
2016-07-23 14:00 | 219.06 | 206.95 | 12.11 | 24.8398 | 20.1411 | 44.0942 | 60.822 | 29.178 | 48.4374 | 41.8056 | 18.5159 | 155.2125 | 0.2 | 0 | 10.953 | 184.6814 | 8.1 | 13.8713 | 1.039 | 0.15734
2016-07-23 15:00 | 160.02 | 157 | 3.02 | 6.8005 | 20.1326 | 59.0937 | 63.6353 | 26.3647 | 64.0404 | 55.8264 | 3.8199 | 117.75 | 0.2 | 0 | 8.001 | 129.5709 | 8.2 | 12.2491 | 1.0446 | 0.11099
2016-07-23 16:00 | 145.6633 | 137.2067 | 8.4567 | 21.5058 | 20.1242 | 74.0933 | 66.8445 | 23.1555 | 79.1471 | 69.7242 | 7.4526 | 102.905 | 0.2 | 0 | 7.2832 | 117.6408 | 7.2 | 10.8763 | 1.0494 | 0.10123
2016-07-23 17:00 | 131.3067 | 117.4133 | 13.8933 | 41.0548 | 20.1157 | 89.0928 | 70.22 | 19.78 | 93.8434 | 83.4206 | 4.7041 | 88.06 | 0.2 | 0 | 6.5653 | 99.3294 | 6.6 | 9.704 | 1.0535 | 0.085811
2016-07-23 18:00 | 116.95 | 97.62 | 19.33 | 68.2176 | 20.1072 | 104.0924 | 73.5393 | 16.4607 | 108.2472 | 96.7983 | 0 | 73.215 | 0.2 | 0 | 5.8475 | 79.0625 | 6.3 | 8.7707 | 1.0568 | 0.068514
2016-07-23 19:00 | 113.54 | 76.1433 | 37.3967 | 161.322 | 20.0987 | 119.0919 | 76.5961 | 13.4039 | 122.4772 | 109.6608 | 0 | 57.1075 | 0.2 | 0 | 5.677 | 62.7845 | 5.6 | 7.562 | 1.061 | 0.054625
2016-07-23 20:00 | 110.13 | 54.6667 | 55.4633 | 296.15 | 20.0902 | 134.0915 | 79.2058 | 10.7942 | 136.6323 | 121.654 | 0 | 41 | 0.2 | 0 | 5.5065 | 46.5065 | 5 | 6.4533 | 1.0649 | 0.040611
2016-07-23 21:00 | 106.72 | 33.19 | 73.53 | 481.2593 | 20.0817 | 149.0911 | 81.2115 | 8.7885 | 150.7791 | 132.1097 | 0 | 24.8925 | 0.2 | 0 | 5.336 | 30.2285 | 5.3 | 6.2446 | 1.0656 | 0.026415
2016-07-23 22:00 | 97.5 | 31.91 | 65.59 | 501.9418 | 20.0732 | 164.0906 | 82.4915 | 7.5085 | 164.9482 | 139.8009 | 0 | 23.9325 | 0.2 | 0 | 4.875 | 28.8075 | 3.8 | 4.7002 | 1.071 | 0.0253
2016-07-23 23:00 | 88.28 | 30.63 | 57.65 | 470.8505 | 20.0646 | 179.0902 | 82.9672 | 7.0328 | 179.139 | 142.9579 | 0 | 22.9725 | 0.2 | 0 | 4.414 | 27.3865 | 4.8 | 5.6558 | 1.0677 | 0.023977
2016-07-24 | 79.06 | 29.35 | 49.71 | 386.4378 | 20.0561 | -165.9102 | 82.6092 | 7.3908 | -166.6679 | 140.4767 | 0 | 22.0125 | 0.2 | 0 | 3.953 | 25.9655 | 4 | 4.8114 | 1.0707 | 0.022796
2016-07-24 01:00 | 85.3033 | 42.9933 | 42.31 | 284.2691 | 20.0475 | -150.9106 | 81.4404 | 8.5596 | -152.4928 | 133.2473 | 0 | 32.245 | 0.2 | 0 | 4.2652 | 36.5102 | 4.4 | 5.5409 | 1.0681 | 0.031977
2016-07-24 02:00 | 91.5467 | 56.6367 | 34.91 | 192.1747 | 20.039 | -135.911 | 79.5337 | 10.4663 | -138.3398 | 123.0529 | 0 | 42.4775 | 0.2 | 0 | 4.5773 | 47.0548 | 4.1 | 5.5705 | 1.068 | 0.041209
2016-07-24 03:00 | 97.79 | 70.28 | 27.51 | 122.3476 | 20.0304 | -120.9114 | 77.0059 | 12.9941 | -124.1829 | 111.2034 | 0 | 52.71 | 0.2 | 0 | 4.8895 | 57.5995 | 5.3 | 7.1 | 1.0627 | 0.050191
2016-07-24 04:00 | 125.9167 | 94.9 | 31.0167 | 112.5967 | 20.0218 | -105.9118 | 74.0102 | 15.9898 | -109.9605 | 98.4222 | 0 | 71.175 | 0.2 | 0 | 6.2958 | 77.4708 | 4.7 | 7.121 | 1.0626 | 0.067501
2016-07-24 05:00 | 154.0433 | 119.52 | 34.5233 | 104.6013 | 20.0132 | -90.9122 | 70.7284 | 19.2716 | -95.578 | 85.0917 | 8.9499 | 89.64 | 0.2 | 0 | 7.7022 | 106.292 | 4.5 | 7.8216 | 1.0601 | 0.0924
2016-07-24 06:00 | 182.17 | 144.14 | 38.03 | 98.8145 | 20.0046 | -75.9126 | 67.3648 | 22.6352 | -80.9189 | 71.4224 | 31.4813 | 108.105 | 0.2 | 0 | 9.1085 | 148.6948 | 5.2 | 9.8467 | 1.053 | 0.1284
2016-07-24 07:00 | 204.46 | 173.6367 | 30.8233 | 70.6683 | 19.996 | -60.913 | 64.1403 | 25.8597 | -65.8649 | 57.5384 | 37.9301 | 130.2275 | 0.2 | 0 | 10.223 | 178.3806 | 4.6 | 10.1744 | 1.0519 | 0.15386
2016-07-24 08:00 | 226.75 | 203.1333 | 23.6167 | 49.1543 | 19.9874 | -45.9134 | 61.2845 | 28.7155 | -50.3255 | 43.5206 | 35.6431 | 152.35 | 0.2 | 0 | 11.3375 | 199.3306 | 4.7 | 10.9291 | 1.0492 | 0.1715
2016-07-24 09:00 | 249.04 | 232.63 | 16.41 | 31.8822 | 19.9787 | -30.9138 | 59.0221 | 30.9779 | -34.2743 | 29.4343 | 27.7669 | 174.4725 | 0.2 | 0 | 12.452 | 214.6914 | 5.7 | 12.4091 | 1.0441 | 0.1838
2016-07-24 10:00 | 264.8633 | 248.6833 | 16.18 | 30.1547 | 19.9701 | -15.9142 | 57.5498 | 32.4502 | -17.7819 | 15.3834 | 29.0744 | 186.5125 | 0.2 | 0 | 13.2432 | 228.83 | 6.3 | 13.4509 | 1.0404 | 0.19523
2016-07-24 11:00 | 280.6867 | 264.7367 | 15.95 | 29.291 | 19.9615 | -0.91453 | 57.0071 | 32.9929 | -1.0249 | 3.1179 | 29.2476 | 198.5525 | 0.2 | 0 | 14.0343 | 241.8345 | 6.4 | 13.9573 | 1.0386 | 0.20597
2016-07-24 12:00 | 296.51 | 280.79 | 15.72 | 29.2159 | 19.9528 | 14.0851 | 57.4481 | 32.5519 | 15.7469 | 13.6847 | 28.3865 | 210.5925 | 0.2 | 0 | 14.8255 | 253.8045 | 7.4 | 15.3314 | 1.0338 | 0.21516
2016-07-24 13:00 | 248.57 | 237.3 | 11.27 | 21.7745 | 19.9441 | 29.0847 | 58.8301 | 31.1699 | 32.2792 | 27.7148 | 19.2764 | 177.975 | 0.2 | 0 | 12.4285 | 209.6799 | 7.2 | 13.7525 | 1.0394 | 0.17871
2016-07-24 14:00 | 200.63 | 193.81 | 6.82 | 14.0774 | 19.9355 | 44.0844 | 61.0226 | 28.9774 | 48.3848 | 41.8083 | 10.493 | 145.3575 | 0.2 | 0 | 10.0315 | 165.882 | 8.5 | 13.6838 | 1.0396 | 0.14141
2016-07-24 15:00 | 152.69 | 150.32 | 2.37 | 5.3745 | 19.9268 | 59.084 | 63.8343 | 26.1657 | 63.9809 | 55.8437 | 3.0175 | 112.74 | 0.2 | 0 | 7.6345 | 123.392 | 7 | 10.856 | 1.0495 | 0.10619
2016-07-24 16:00 | 150.4133 | 123.53 | 26.8833 | 68.9237 | 19.9181 | 74.0837 | 67.0427 | 22.9573 | 79.0848 | 69.7558 | 23.8491 | 92.6475 | 0.2 | 0 | 7.5207 | 124.0172 | 6.9 | 10.7755 | 1.0498 | 0.10676
2016-07-24 17:00 | 148.1367 | 96.74 | 51.3967 | 153.3529 | 19.9094 | 89.0833 | 70.4182 | 19.5818 | 93.7818 | 83.4679 | 17.4455 | 72.555 | 0.2 | 0 | 7.4068 | 97.4073 | 5.7 | 8.744 | 1.0569 | 0.084418
2016-07-24 18:00 | 145.86 | 69.95 | 75.91 | 271.0843 | 19.9006 | 104.083 | 73.7384 | 16.2616 | 108.1891 | 96.8636 | 0 | 52.4625 | 0.2 | 0 | 7.293 | 59.7555 | 5.8 | 7.6674 | 1.0607 | 0.051972
2016-07-24 19:00 | 123.1367 | 58.6933 | 64.4433 | 282.1458 | 19.8919 | 119.0826 | 76.7968 | 13.2032 | 122.4254 | 109.7482 | 0 | 44.02 | 0.2 | 0 | 6.1568 | 50.1768 | 5.6 | 7.168 | 1.0624 | 0.043713
2016-07-24 20:00 | 100.4133 | 47.4367 | 52.9767 | 288.2238 | 19.8832 | 134.0823 | 79.4086 | 10.5914 | 136.5889 | 121.7691 | 0 | 35.5775 | 0.2 | 0 | 5.0207 | 40.5982 | 5.3 | 6.5687 | 1.0645 | 0.035438
2016-07-24 21:00 | 77.69 | 36.18 | 41.51 | 278.1184 | 19.8744 | 149.082 | 81.4164 | 8.5836 | 150.746 | 132.2591 | 0 | 27.135 | 0.2 | 0 | 3.8845 | 31.0195 | 5.4 | 6.3694 | 1.0652 | 0.027095
2016-07-24 22:00 | 77.7433 | 33.4367 | 44.3067 | 348.6031 | 19.8657 | 164.0816 | 82.6981 | 7.3019 | 164.9267 | 139.987 | 0 | 25.0775 | 0.2 | 0 | 3.8872 | 28.9647 | 5.4 | 6.3051 | 1.0654 | 0.025305
2016-07-24 23:00 | 77.7967 | 30.6933 | 47.1033 | 396.3595 | 19.8569 | 179.0813 | 83.1748 | 6.8252 | 179.1298 | 143.1654 | 0 | 23.02 | 0.2 | 0 | 3.8898 | 26.9098 | 5.2 | 6.0409 | 1.0664 | 0.02353
2016-07-25 | 77.85 | 27.95 | 49.9 | 399.0905 | 19.8481 | -165.919 | 82.8173 | 7.1827 | -166.6646 | 140.6732 | 0 | 20.9625 | 0.2 | 0 | 3.8925 | 24.855 | 3.8 | 4.5767 | 1.0715 | 0.021838
2016-07-25 01:00 | 85.4367 | 42.28 | 43.1567 | 297.1184 | 19.8394 | -150.9193 | 81.6482 | 8.3518 | -152.4777 | 133.4126 | 0 | 31.71 | 0.2 | 0 | 4.2718 | 35.9818 | 4.3 | 5.4244 | 1.0685 | 0.031527
2016-07-25 02:00 | 93.0233 | 56.61 | 36.4133 | 204.4504 | 19.8306 | -135.9196 | 79.7407 | 10.2593 | -138.3141 | 123.1859 | 0 | 42.4575 | 0.2 | 0 | 4.6512 | 47.1087 | 5 | 6.4721 | 1.0648 | 0.041134
2016-07-25 03:00 | 100.61 | 70.94 | 29.67 | 134.0438 | 19.8218 | -120.9199 | 77.2119 | 12.7881 | -124.1484 | 111.3093 | 0 | 53.205 | 0.2 | 0 | 5.0305 | 58.2355 | 5 | 6.8199 | 1.0636 | 0.050792
2016-07-25 04:00 | 124.27 | 99.71 | 24.56 | 90.287 | 19.813 | -105.9202 | 74.2154 | 15.7846 | -109.9195 | 98.5063 | 0 | 74.7825 | 0.2 | 0 | 6.2135 | 80.996 | 5.4 | 7.9311 | 1.0597 | 0.070385
2016-07-25 05:00 | 147.93 | 128.48 | 19.45 | 59.5404 | 19.8041 | -90.9205 | 70.9333 | 19.0667 | -95.5332 | 85.1578 | 5.0259 | 96.36 | 0.2 | 0 | 7.3965 | 108.7824 | 5.5 | 8.8994 | 1.0564 | 0.094228
2016-07-25 06:00 | 171.59 | 157.25 | 14.34 | 37.5831 | 19.7953 | -75.9208 | 67.57 | 22.43 | -80.8733 | 71.473 | 11.9421 | 117.9375 | 0.2 | 0 | 8.5795 | 138.4591 | 5.7 | 10.0268 | 1.0524 | 0.11949
2016-07-25 07:00 | 247.2433 | 188.5533 | 58.69 | 135.565 | 19.7865 | -60.9211 | 64.3464 | 25.6536 | -65.8222 | 57.5747 | 72.6898 | 141.415 | 0.2 | 0 | 12.3622 | 226.467 | 5.3 | 12.3771 | 1.0442 | 0.19391
2016-07-25 08:00 | 322.8967 | 219.8567 | 103.04 | 215.8901 | 19.7776 | -45.9214 | 61.4921 | 28.5079 | -50.2898 | 43.5428 | 156.4902 | 164.8925 | 0.2 | 0 | 16.1448 | 337.5275 | 6.8 | 17.3477 | 1.0268 | 0.28419
2016-07-25 09:00 | 398.55 | 251.16 | 147.39 | 288.1102 | 19.7688 | -30.9217 | 59.2312 | 30.7688 | -34.2498 | 29.4397 | 250.9074 | 188.37 | 0.2 | 0 | 19.9275 | 459.2049 | 7.7 | 22.0502 | 1.0103 | 0.38044
2016-07-25 10:00 | 378.2067 | 247.5667 | 130.64 | 244.8889 | 19.7599 | -15.9219 | 57.76 | 32.24 | -17.7723 | 15.3604 | 236.1411 | 185.675 | 0.2 | 0 | 18.9103 | 440.7265 | 6.8 | 20.5727 | 1.0155 | 0.367
2016-07-25 11:00 | 357.8633 | 243.9733 | 113.89 | 210.3422 | 19.751 | -0.9222 | 57.2175 | 32.7825 | -1.0324 | 2.9186 | 210.0694 | 182.98 | 0.2 | 0 | 17.8932 | 410.9426 | 7.1 | 19.942 | 1.0177 | 0.34294
2016-07-25 12:00 | 337.52 | 240.38 | 97.14 | 181.5792 | 19.7421 | 14.0775 | 57.6579 | 32.3421 | 15.7223 | 13.6416 | 176.4568 | 180.285 | 0.2 | 0 | 16.876 | 373.6178 | 6.2 | 17.8756 | 1.0249 | 0.31401
2016-07-25 13:00 | 296.41 | 227.0367 | 69.3733 | 134.846 | 19.7332 | 29.0773 | 59.0384 | 30.9616 | 32.2396 | 27.7036 | 119.3879 | 170.2775 | 0.2 | 0 | 14.8205 | 304.4859 | 8.3 | 17.8152 | 1.0251 | 0.25596
2016-07-25 14:00 | 255.3 | 213.6933 | 41.6067 | 86.445 | 19.7243 | 44.077 | 61.2291 | 28.7709 | 48.3338 | 41.8146 | 64.428 | 160.27 | 0.2 | 0 | 12.765 | 237.463 | 8.1 | 15.5207 | 1.0332 | 0.20118
2016-07-25 15:00 | 214.19 | 200.35 | 13.84 | 31.6158 | 19.7154 | 59.0768 | 64.0392 | 25.9608 | 63.9229 | 55.8645 | 17.7413 | 150.2625 | 0.2 | 0 | 10.7095 | 178.7133 | 7.6 | 13.1848 | 1.0414 | 0.15261
2016-07-25 16:00 | 200.4967 | 176.6333 | 23.8633 | 61.7002 | 19.7065 | 74.0765 | 67.2468 | 22.7532 | 79.0236 | 69.7911 | 21.3139 | 132.475 | 0.2 | 0 | 10.0248 | 163.8138 | 7.1 | 12.2192 | 1.0447 | 0.14034
2016-07-25 17:00 | 186.8033 | 152.9167 | 33.8867 | 102.1314 | 19.6975 | 89.0763 | 70.6222 | 19.3778 | 93.7212 | 83.5189 | 11.5281 | 114.6875 | 0.2 | 0 | 9.3402 | 135.5558 | 7.3 | 11.5361 | 1.0471 | 0.11639
2016-07-25 18:00 | 173.11 | 129.2 | 43.91 | 158.7564 | 19.6886 | 104.076 | 73.9434 | 16.0566 | 108.1322 | 96.933 | 0 | 96.9 | 0.2 | 0 | 8.6555 | 105.5555 | 5.8 | 9.0986 | 1.0557 | 0.091373
2016-07-25 19:00 | 147.2433 | 97.69 | 49.5533 | 220.3422 | 19.6796 | 119.0758 | 77.0034 | 12.9966 | 122.3748 | 109.8399 | 0 | 73.2675 | 0.2 | 0 | 7.3622 | 80.6297 | 6.4 | 8.9197 | 1.0563 | 0.069837
2016-07-25 20:00 | 121.3767 | 66.18 | 55.1967 | 306.2658 | 19.6707 | 134.0756 | 79.6172 | 10.3828 | 136.547 | 121.8889 | 0 | 49.635 | 0.2 | 0 | 6.0688 | 55.7038 | 6.8 | 8.5407 | 1.0576 | 0.048308
2016-07-25 21:00 | 95.51 | 34.67 | 60.84 | 417.8038 | 19.6617 | 149.0753 | 81.6269 | 8.3731 | 150.7145 | 132.4139 | 0 | 26.0025 | 0.2 | 0 | 4.7755 | 30.778 | 5.9 | 6.8618 | 1.0635 | 0.02684
2016-07-25 22:00 | 88.2867 | 34.01 | 54.2767 | 439.7579 | 19.6527 | 164.0751 | 82.9102 | 7.0898 | 164.9071 | 140.1788 | 0 | 25.5075 | 0.2 | 0 | 4.4143 | 29.9218 | 4.7 | 5.6351 | 1.0678 | 0.026199
2016-07-25 23:00 | 81.0633 | 33.35 | 47.7133 | 414.3759 | 19.6437 | 179.0749 | 83.388 | 6.612 | 179.1229 | 143.3783 | 0 | 25.0125 | 0.2 | 0 | 4.0532 | 29.0657 | 5.2 | 6.1083 | 1.0661 | 0.02541
2016-07-26 | 73.84 | 32.69 | 41.15 | 339.1359 | 19.6347 | -165.9253 | 83.0307 | 6.9693 | -166.6587 | 140.8739 | 0 | 24.5175 | 0.2 | 0 | 3.692 | 28.2095 | 4.3 | 5.1815 | 1.0694 | 0.024736
2016-07-26 01:00 | 104.1367 | 45.5433 | 58.5933 | 413.8766 | 19.6257 | -150.9255 | 81.8612 | 8.1388 | -152.4597 | 133.5804 | 0 | 34.1575 | 0.2 | 0 | 5.2068 | 39.3643 | 4.5 | 5.7301 | 1.0674 | 0.034456
2016-07-26 02:00 | 134.4333 | 58.3967 | 76.0367 | 435.8391 | 19.6167 | -135.9257 | 79.9527 | 10.0473 | -138.2852 | 123.32 | 0 | 43.7975 | 0.2 | 0 | 6.7217 | 50.5192 | 4.8 | 6.3787 | 1.0652 | 0.044126
2016-07-26 03:00 | 164.73 | 71.25 | 93.48 | 429.2931 | 19.6077 | -120.9259 | 77.4229 | 12.5771 | -124.1106 | 111.4156 | 0 | 53.4375 | 0.2 | 0 | 8.2365 | 61.674 | 6.2 | 8.1273 | 1.0591 | 0.053559
2016-07-26 04:00 | 212.7567 | 80.1333 | 132.6233 | 493.9572 | 19.5986 | -105.9261 | 74.4255 | 15.5745 | -109.875 | 98.5902 | 0 | 60.1 | 0.2 | 0 | 10.6378 | 70.7378 | 5.6 | 7.8106 | 1.0602 | 0.061495
2016-07-26 05:00 | 260.7833 | 89.0167 | 171.7667 | 531.4426 | 19.5896 | -90.9263 | 71.1429 | 18.8571 | -95.4847 | 85.2233 | 44.2542 | 66.7625 | 0.2 | 0 | 13.0392 | 124.0559 | 4.9 | 8.7767 | 1.0568 | 0.1075
2016-07-26 06:00 | 308.81 | 97.9 | 210.91 | 557.7193 | 19.5805 | -75.9265 | 67.7799 | 22.2201 | -80.8241 | 71.5227 | 176.7573 | 73.425 | 0.2 | 0 | 15.4405 | 265.6228 | 6.4 | 14.7007 | 1.036 | 0.22566
2016-07-26 07:00 | 366.33 | 110.6867 | 255.6433 | 595.0633 | 19.5715 | -60.9267 | 64.5574 | 25.4426 | -65.7759 | 57.6101 | 318.7624 | 83.015 | 0.2 | 0 | 18.3165 | 420.0939 | 7 | 20.1279 | 1.0171 | 0.35035
2016-07-26 08:00 | 423.85 | 123.4733 | 300.3767 | 633.6826 | 19.5624 | -45.9269 | 61.7046 | 28.2954 | -50.2505 | 43.5638 | 459.171 | 92.605 | 0.2 | 0 | 21.1925 | 572.9685 | 6.6 | 24.5053 | 1.0017 | 0.47065
2016-07-26 09:00 | 481.37 | 136.26 | 345.11 | 678.8697 | 19.5533 | -30.9271 | 59.4454 | 30.5546 | -34.2219 | 29.4443 | 591.183 | 102.195 | 0.2 | 0 | 24.0685 | 717.4465 | 7.1 | 29.5202 | 0.98418 | 0.579
2016-07-26 10:00 | 487.4533 | 140.69 | 346.7633 | 653.9226 | 19.5442 | -15.9272 | 57.9755 | 32.0245 | -17.7596 | 15.3372 | 630.6337 | 105.5175 | 0.2 | 0 | 24.3727 | 760.5239 | 8.3 | 32.0664 | 0.97527 | 0.60821
2016-07-26 11:00 | 493.5367 | 145.12 | 348.4167 | 647.2793 | 19.5351 | -0.92739 | 57.4335 | 32.5665 | -1.0371 | 2.7152 | 646.5526 | 108.84 | 0.2 | 0 | 24.6768 | 780.0694 | 9.6 | 33.9772 | 0.96858 | 0.61956
2016-07-26 12:00 | 499.62 | 149.55 | 350.07 | 658.2815 | 19.526 | 14.0724 | 57.8733 | 32.1267 | 15.7 | 13.603 | 639.8158 | 112.1625 | 0.2 | 0 | 24.981 | 776.9593 | 9.4 | 33.68 | 0.96962 | 0.61775
2016-07-26 13:00 | 457.6333 | 137.53 | 320.1033 | 626.1101 | 19.5169 | 29.0723 | 59.2524 | 30.7476 | 32.202 | 27.6962 | 554.3734 | 103.1475 | 0.2 | 0 | 22.8817 | 680.4026 | 7.2 | 28.4626 | 0.98788 | 0.55117
2016-07-26 14:00 | 415.6467 | 125.51 | 290.1367 | 606.9077 | 19.5077 | 44.0721 | 61.4414 | 28.5586 | 48.2845 | 41.8243 | 452.2633 | 94.1325 | 0.2 | 0 | 20.7823 | 567.1781 | 10.1 | 27.8243 | 0.99011 | 0.46049
2016-07-26 15:00 | 373.66 | 113.49 | 260.17 | 598.8558 | 19.4986 | 59.072 | 64.25 | 25.75 | 63.8662 | 55.8888 | 335.8388 | 85.1175 | 0.2 | 0 | 18.683 | 439.6393 | 9.6 | 23.3387 | 1.0058 | 0.3626
2016-07-26 16:00 | 316.91 | 102.55 | 214.36 | 559.1295 | 19.4894 | 74.0718 | 67.4567 | 22.5433 | 78.9637 | 69.83 | 192.7915 | 76.9125 | 0.2 | 0 | 15.8455 | 285.5495 | 8.9 | 17.8234 | 1.0251 | 0.24003
2016-07-26 17:00 | 260.16 | 91.61 | 168.55 | 513.3459 | 19.4803 | 89.0717 | 70.8322 | 19.1678 | 93.6618 | 83.5738 | 57.4558 | 68.7075 | 0.2 | 0 | 13.008 | 139.1713 | 8.5 | 12.8491 | 1.0425 | 0.11897
2016-07-26 18:00 | 203.41 | 80.67 | 122.74 | 449.5157 | 19.4711 | 104.0716 | 74.1542 | 15.8458 | 108.0765 | 97.0064 | 0 | 60.5025 | 0.2 | 0 | 10.1705 | 70.673 | 7.2 | 9.4085 | 1.0546 | 0.061114
2016-07-26 19:00 | 165.17 | 67.6333 | 97.5367 | 440.7851 | 19.4619 | 119.0714 | 77.2158 | 12.7842 | 122.3255 | 109.9359 | 0 | 50.725 | 0.2 | 0 | 8.2585 | 58.9835 | 7 | 8.8432 | 1.0565 | 0.051102
2016-07-26 20:00 | 126.93 | 54.5967 | 72.3333 | 409.717 | 19.4527 | 134.0713 | 79.8314 | 10.1686 | 136.5065 | 122.0135 | 0 | 40.9475 | 0.2 | 0 | 6.3465 | 47.294 | 6.5 | 7.9779 | 1.0596 | 0.041092
2016-07-26 21:00 | 88.69 | 41.56 | 47.13 | 332.1716 | 19.4436 | 149.0712 | 81.8431 | 8.1569 | 150.6848 | 132.5738 | 0 | 31.17 | 0.2 | 0 | 4.4345 | 35.6045 | 5.4 | 6.5126 | 1.0647 | 0.031085
2016-07-26 22:00 | 79.6933 | 38.6233 | 41.07 | 343.2444 | 19.4343 | 164.0711 | 83.128 | 6.872 | 164.8895 | 140.3763 | 0 | 28.9675 | 0.2 | 0 | 3.9847 | 32.9522 | 5.7 | 6.7298 | 1.0639 | 0.028749
2016-07-26 23:00 | 70.6967 | 35.6867 | 35.01 | 314.4011 | 19.4251 | 179.071 | 83.6066 | 6.3934 | 179.1184 | 143.5968 | 0 | 26.765 | 0.2 | 0 | 3.5348 | 30.2998 | 4.5 | 5.4469 | 1.0684 | 0.026546
2016-07-27 | 61.7 | 32.75 | 28.95 | 246.2818 | 19.4159 | -165.9292 | 83.2494 | 6.7506 | -166.6502 | 141.0786 | 0 | 24.5625 | 0.2 | 0 | 3.085 | 27.6475 | 4.5 | 5.364 | 1.0687 | 0.024229
2016-07-27 01:00 | 83.1567 | 51.01 | 32.1467 | 233.28 | 19.4067 | -150.9293 | 82.0793 | 7.9207 | -152.4387 | 133.7505 | 0 | 38.2575 | 0.2 | 0 | 4.1578 | 42.4153 | 3.9 | 5.2255 | 1.0692 | 0.037188
2016-07-27 02:00 | 104.6133 | 69.27 | 35.3433 | 207.0135 | 19.3974 | -135.9294 | 80.1698 | 9.8302 | -138.2532 | 123.4553 | 0 | 51.9525 | 0.2 | 0 | 5.2307 | 57.1832 | 6.4 | 8.187 | 1.0588 | 0.049649
2016-07-27 03:00 | 126.07 | 87.53 | 38.54 | 180.0298 | 19.3882 | -120.9295 | 77.6387 | 12.3613 | -124.0694 | 111.5221 | 0 | 65.6475 | 0.2 | 0 | 6.3035 | 71.951 | 6 | 8.2485 | 1.0586 | 0.062459
2016-07-27 04:00 | 159.45 | 121.3933 | 38.0567 | 143.6761 | 19.3789 | -105.9296 | 74.6403 | 15.3597 | -109.827 | 98.6738 | 0 | 91.045 | 0.2 | 0 | 7.9725 | 99.0175 | 6.3 | 9.3943 | 1.0546 | 0.085629
2016-07-27 05:00 | 192.83 | 155.2567 | 37.5733 | 117.5395 | 19.3696 | -90.9296 | 71.3573 | 18.6427 | -95.4326 | 85.2882 | 9.6551 | 116.4425 | 0.2 | 0 | 9.6415 | 135.7391 | 6.4 | 10.6418 | 1.0503 | 0.1169
2016-07-27 06:00 | 226.21 | 189.12 | 37.09 | 98.9874 | 19.3604 | -75.9297 | 67.9946 | 22.0054 | -80.7711 | 71.5715 | 31.2919 | 141.84 | 0.2 | 0 | 11.3105 | 184.4424 | 6.7 | 12.4638 | 1.0439 | 0.15788
2016-07-27 07:00 | 243.31 | 205.64 | 37.67 | 88.3849 | 19.3511 | -60.9298 | 64.7731 | 25.2269 | -65.7258 | 57.6444 | 47.3012 | 154.23 | 0.2 | 0 | 12.1655 | 213.6967 | 5.9 | 12.578 | 1.0435 | 0.18285
2016-07-27 08:00 | 260.41 | 222.16 | 38.25 | 81.2665 | 19.3418 | -45.9299 | 61.922 | 28.078 | -50.2076 | 43.5838 | 58.8668 | 166.62 | 0.2 | 0 | 13.0205 | 238.5073 | 6.2 | 13.6534 | 1.0397 | 0.20334
2016-07-27 09:00 | 277.51 | 238.68 | 38.83 | 76.8817 | 19.3325 | -30.9299 | 59.6646 | 30.3354 | -34.1906 | 29.4479 | 66.9488 | 179.01 | 0.2 | 0 | 13.8755 | 259.8343 | 6.3 | 14.4198 | 1.037 | 0.22095
2016-07-27 10:00 | 271.9833 | 233.59 | 38.3933 | 72.8508 | 19.3232 | -15.93 | 58.1962 | 31.8038 | -17.7437 | 15.3141 | 70.2641 | 175.1925 | 0.2 | 0 | 13.5992 | 259.0558 | 6.5 | 14.5955 | 1.0364 | 0.22016
2016-07-27 11:00 | 266.4567 | 228.5 | 37.9567 | 70.9444 | 19.3138 | -0.93007 | 57.6547 | 32.3453 | -1.0389 | 2.508 | 70.8765 | 171.375 | 0.2 | 0 | 13.3228 | 255.5743 | 6.5 | 14.4867 | 1.0368 | 0.21728
2016-07-27 12:00 | 260.93 | 223.41 | 37.52 | 70.99 | 19.3045 | 14.0699 | 58.0941 | 31.9059 | 15.6803 | 13.5693 | 69.0084 | 167.5575 | 0.2 | 0 | 13.0465 | 249.6124 | 7.2 | 15.0004 | 1.035 | 0.21185
2016-07-27 13:00 | 235.25 | 202.65 | 32.6 | 64.1784 | 19.2951 | 29.0698 | 59.472 | 30.528 | 32.1665 | 27.6926 | 56.827 | 151.9875 | 0.2 | 0 | 11.7625 | 220.577 | 5.3 | 12.193 | 1.0448 | 0.18898
2016-07-27 14:00 | 209.57 | 181.89 | 27.68 | 58.309 | 19.2858 | 44.0698 | 61.6594 | 28.3406 | 48.237 | 41.8377 | 43.4424 | 136.4175 | 0.2 | 0 | 10.4785 | 190.3384 | 5.1 | 11.0481 | 1.0488 | 0.1637
2016-07-27 15:00 | 183.89 | 161.13 | 22.76 | 52.8028 | 19.2764 | 59.0697 | 64.4665 | 25.5335 | 63.811 | 55.9168 | 29.5905 | 120.8475 | 0.2 | 0 | 9.1945 | 159.6325 | 4.9 | 9.8885 | 1.0529 | 0.13782
2016-07-27 16:00 | 157.1167 | 135.76 | 21.3567 | 56.2163 | 19.2671 | 74.0697 | 67.6724 | 22.3276 | 78.9052 | 69.8726 | 19.3445 | 101.82 | 0.2 | 0 | 7.8558 | 129.0203 | 4.5 | 8.5319 | 1.0576 | 0.11189
2016-07-27 17:00 | 130.3433 | 110.39 | 19.9533 | 61.4369 | 19.2577 | 89.0696 | 71.0479 | 18.9521 | 93.6036 | 83.6324 | 6.8138 | 82.7925 | 0.2 | 0 | 6.5172 | 96.1234 | 4.5 | 7.5039 | 1.0612 | 0.083648
2016-07-27 18:00 | 103.57 | 85.02 | 18.55 | 68.8539 | 19.2483 | 104.0696 | 74.3708 | 15.6292 | 108.022 | 97.0838 | 0 | 63.765 | 0.2 | 0 | 5.1785 | 68.9435 | 4.4 | 6.5545 | 1.0646 | 0.060183
2016-07-27 19:00 | 94.2467 | 67.2 | 27.0467 | 124.315 | 19.2389 | 119.0696 | 77.4339 | 12.5661 | 122.2776 | 110.0363 | 0 | 50.4 | 0.2 | 0 | 4.7123 | 55.1123 | 4.2 | 5.9223 | 1.0668 | 0.04821
2016-07-27 20:00 | 84.9233 | 49.38 | 35.5433 | 205.7327 | 19.2295 | 134.0696 | 80.0514 | 9.9486 | 136.4675 | 122.1428 | 0 | 37.035 | 0.2 | 0 | 4.2462 | 41.2812 | 4.2 | 5.49 | 1.0683 | 0.036162
2016-07-27 21:00 | 75.6 | 31.56 | 44.04 | 319.0104 | 19.2201 | 149.0696 | 82.0649 | 7.9351 | 150.6568 | 132.739 | 0 | 23.67 | 0.2 | 0 | 3.78 | 27.45 | 4.4 | 5.2578 | 1.0691 | 0.024064
2016-07-27 22:00 | 61.8033 | 30.79 | 31.0133 | 267.855 | 19.2106 | 164.0695 | 83.3511 | 6.6489 | 164.8741 | 140.5795 | 0 | 23.0925 | 0.2 | 0 | 3.0902 | 26.1827 | 4.2 | 5.0182 | 1.0699 | 0.022971
2016-07-27 23:00 | 48.0067 | 30.02 | 17.9867 | 167.3649 | 19.2012 | 179.0695 | 83.8305 | 6.1695 | 179.1162 | 143.8206 | 0 | 22.515 | 0.2 | 0 | 2.4003 | 24.9153 | 4.2 | 4.9786 | 1.0701 | 0.021862
2016-07-28 | 34.21 | 29.25 | 4.96 | 43.6362 | 19.1918 | -165.9305 | 83.4733 | 6.5267 | -166.639 | 141.2872 | 0 | 21.9375 | 0.2 | 0 | 1.7105 | 23.648 | 4 | 4.739 | 1.0709 | 0.020766
2016-07-28 01:00 | 47.47 | 43.3233 | 4.1467 | 30.958 | 19.1823 | -150.9305 | 82.3024 | 7.6976 | -152.4148 | 133.9229 | 0 | 32.4925 | 0.2 | 0 | 2.3735 | 34.866 | 4 | 5.0896 | 1.0697 | 0.030582
2016-07-28 02:00 | 60.73 | 57.3967 | 3.3333 | 19.9706 | 19.1728 | -135.9305 | 80.3917 | 9.6083 | -138.218 | 123.5914 | 0 | 43.0475 | 0.2 | 0 | 3.0365 | 46.084 | 3.7 | 5.1401 | 1.0695 | 0.040416
2016-07-28 03:00 | 73.99 | 71.47 | 2.52 | 11.9821 | 19.1634 | -120.9305 | 77.8592 | 12.1408 | -124.0248 | 111.6287 | 0 | 53.6025 | 0.2 | 0 | 3.6995 | 57.302 | 3.6 | 5.3907 | 1.0686 | 0.050213
2016-07-28 04:00 | 97.9933 | 96.0033 | 1.99 | 7.6192 | 19.1539 | -105.9304 | 74.8597 | 15.1403 | -109.7754 | 98.757 | 0 | 72.0025 | 0.2 | 0 | 4.8997 | 76.9022 | 3.5 | 5.9032 | 1.0668 | 0.067275
2016-07-28 05:00 | 121.9967 | 120.5367 | 1.46 | 4.6196 | 19.1444 | -90.9304 | 71.5763 | 18.4237 | -95.3769 | 85.3523 | 0.37432 | 90.4025 | 0.2 | 0 | 6.0998 | 96.8767 | 3.6 | 6.6274 | 1.0643 | 0.084547
2016-07-28 06:00 | 146 | 145.07 | 0.93 | 2.5058 | 19.1349 | -75.9304 | 68.2138 | 21.7862 | -80.7145 | 71.6194 | 0.79014 | 108.8025 | 0.2 | 0 | 7.3 | 116.8926 | 3.7 | 7.3529 | 1.0618 | 0.10177
2016-07-28 07:00 | 196.05 | 187.7667 | 8.2833 | 19.5953 | 19.1254 | -60.9304 | 64.9935 | 25.0065 | -65.6722 | 57.6776 | 10.4773 | 140.825 | 0.2 | 0 | 9.8025 | 161.1048 | 3.7 | 8.7345 | 1.0569 | 0.13963
2016-07-28 08:00 | 246.1 | 230.4633 | 15.6367 | 33.4654 | 19.1159 | -45.9303 | 62.1441 | 27.8559 | -50.1612 | 43.6027 | 24.2336 | 172.8475 | 0.2 | 0 | 12.305 | 209.3861 | 3.8 | 10.3433 | 1.0513 | 0.1805
2016-07-28 09:00 | 296.15 | 273.16 | 22.99 | 45.8259 | 19.1063 | -30.9303 | 59.8887 | 30.1113 | -34.1559 | 29.4508 | 39.9042 | 204.87 | 0.2 | 0 | 14.8075 | 259.5817 | 4 | 12.1119 | 1.0451 | 0.22246
2016-07-28 10:00 | 301.69 | 271.5033 | 30.1867 | 57.6456 | 19.0968 | -15.9303 | 58.4219 | 31.5781 | -17.7246 | 15.2911 | 55.6048 | 203.6275 | 0.2 | 0 | 15.0845 | 274.3168 | 4.2 | 12.7724 | 1.0428 | 0.23457
2016-07-28 11:00 | 307.23 | 269.8467 | 37.3833 | 70.3124 | 19.0873 | -0.93022 | 57.8813 | 32.1187 | -1.038 | 2.2977 | 70.2559 | 202.385 | 0.2 | 0 | 15.3615 | 288.0024 | 4.3 | 13.3001 | 1.0409 | 0.24583
2016-07-28 12:00 | 312.77 | 268.19 | 44.58 | 84.8872 | 19.0777 | 14.0698 | 58.3205 | 31.6795 | 15.663 | 13.5408 | 82.5276 | 201.1425 | 0.2 | 0 | 15.6385 | 299.3086 | 4.3 | 13.6534 | 1.0397 | 0.25518
2016-07-28 13:00 | 271.61 | 241.8333 | 29.7767 | 59.0139 | 19.0681 | 29.0699 | 59.6972 | 30.3028 | 32.1331 | 27.6931 | 52.2539 | 181.375 | 0.2 | 0 | 13.5805 | 247.2094 | 4.6 | 12.3253 | 1.0444 | 0.2117
2016-07-28 14:00 | 230.45 | 215.4767 | 14.9733 | 31.7721 | 19.0586 | 44.0699 | 61.883 | 28.117 | 48.1912 | 41.8549 | 23.665 | 161.6075 | 0.2 | 0 | 11.5225 | 196.795 | 4.4 | 10.5498 | 1.0506 | 0.16953
2016-07-28 15:00 | 189.29 | 189.12 | 0.17 | 0.39763 | 19.049 | 59.07 | 64.6888 | 25.3112 | 63.7573 | 55.9484 | 0.22265 | 141.84 | 0.2 | 0 | 9.4645 | 151.5271 | 4.5 | 9.2352 | 1.0552 | 0.13111
2016-07-28 16:00 | 163.6267 | 163.3933 | 0.23333 | 0.62003 | 19.0394 | 74.0701 | 67.8938 | 22.1062 | 78.8479 | 69.9189 | 0.21289 | 122.545 | 0.2 | 0 | 8.1813 | 130.9392 | 4.7 | 8.7919 | 1.0567 | 0.11346
2016-07-28 17:00 | 137.9633 | 137.6667 | 0.29667 | 0.92385 | 19.0298 | 89.0701 | 71.2693 | 18.7307 | 93.5467 | 83.6949 | 0.10146 | 103.25 | 0.2 | 0 | 6.8982 | 110.2496 | 4.6 | 8.0453 | 1.0593 | 0.095769
2016-07-28 18:00 | 112.3 | 111.94 | 0.36 | 1.355 | 19.0202 | 104.0702 | 74.593 | 15.407 | 107.9689 | 97.1652 | 0 | 83.955 | 0.2 | 0 | 5.615 | 89.57 | 4.7 | 7.4991 | 1.0613 | 0.077946
2016-07-28 19:00 | 94.1833 | 87.63 | 6.5533 | 30.6585 | 19.0106 | 119.0703 | 77.6577 | 12.3423 | 122.231 | 110.1409 | 0 | 65.7225 | 0.2 | 0 | 4.7092 | 70.4317 | 4.3 | 6.501 | 1.0647 | 0.061493
2016-07-28 20:00 | 76.0667 | 63.32 | 12.7467 | 75.475 | 19.0009 | 134.0704 | 80.277 | 9.723 | 136.4301 | 122.2767 | 0 | 47.49 | 0.2 | 0 | 3.8033 | 51.2933 | 4.3 | 5.9029 | 1.0668 | 0.044872
2016-07-28 21:00 | 57.95 | 39.01 | 18.94 | 141.2148 | 18.9913 | 149.0705 | 82.2922 | 7.7078 | 150.6307 | 132.9094 | 0 | 29.2575 | 0.2 | 0 | 2.8975 | 32.155 | 4.1 | 5.1048 | 1.0696 | 0.028203
2016-07-28 22:00 | 55.31 | 37.5067 | 17.8033 | 159.2137 | 18.9817 | 164.0706 | 83.5797 | 6.4203 | 164.8607 | 140.7883 | 0 | 28.13 | 0.2 | 0 | 2.7655 | 30.8955 | 4.3 | 5.2655 | 1.0691 | 0.027084
2016-07-28 23:00 | 52.67 | 36.0033 | 16.6667 | 161.0432 | 18.972 | 179.0707 | 84.0597 | 5.9403 | 179.1164 | 144.0497 | 0 | 27.0025 | 0.2 | 0 | 2.6335 | 29.636 | 3.7 | 4.6261 | 1.0713 | 0.026034
2016-07-29 | 50.03 | 34.5 | 15.53 | 141.574 | 18.9623 | -165.9292 | 83.7022 | 6.2978 | -166.6251 | 141.4996 | 0 | 25.875 | 0.2 | 0 | 2.5015 | 28.3765 | 3.7 | 4.5868 | 1.0714 | 0.024931
2016-07-29 01:00 | 66.8067 | 53.0967 | 13.71 | 105.4625 | 18.9527 | -150.9291 | 82.5305 | 7.4695 | -152.3879 | 134.0973 | 0 | 39.8225 | 0.2 | 0 | 3.3403 | 43.1628 | 4.3 | 5.6488 | 1.0677 | 0.037791
2016-07-29 02:00 | 83.5833 | 71.6933 | 11.89 | 72.9404 | 18.943 | -135.929 | 80.6184 | 9.3816 | -138.1796 | 123.7285 | 0 | 53.77 | 0.2 | 0 | 4.1792 | 57.9492 | 3.6 | 5.4109 | 1.0686 | 0.050776
2016-07-29 03:00 | 100.36 | 90.29 | 10.07 | 48.7724 | 18.9333 | -120.9289 | 78.0845 | 11.9155 | -123.9768 | 111.7354 | 0 | 67.7175 | 0.2 | 0 | 5.018 | 72.7355 | 4.1 | 6.373 | 1.0652 | 0.063532
2016-07-29 04:00 | 133.08 | 124.91 | 8.17 | 31.7397 | 18.9236 | -105.9288 | 75.0838 | 14.9162 | -109.7203 | 98.8398 | 0 | 93.6825 | 0.2 | 0 | 6.654 | 100.3365 | 4.3 | 7.4355 | 1.0615 | 0.087334
2016-07-29 05:00 | 165.8 | 159.53 | 6.27 | 20.0744 | 18.9139 | -90.9287 | 71.7998 | 18.2002 | -95.3175 | 85.4157 | 1.6045 | 119.6475 | 0.2 | 0 | 8.29 | 129.542 | 3.8 | 7.8482 | 1.06 | 0.1126
2016-07-29 06:00 | 198.52 | 194.15 | 4.37 | 11.8907 | 18.9042 | -75.9285 | 68.4377 | 21.5623 | -80.6542 | 71.6663 | 3.7402 | 145.6125 | 0.2 | 0 | 9.926 | 159.2787 | 4.2 | 9.1775 | 1.0554 | 0.13784
2016-07-29 07:00 | 214.99 | 204.8967 | 10.0933 | 24.08 | 18.8945 | -60.9284 | 65.2185 | 24.7815 | -65.6148 | 57.7098 | 12.8637 | 153.6725 | 0.2 | 0 | 10.7495 | 177.2857 | 3.8 | 9.3402 | 1.0548 | 0.15334
2016-07-29 08:00 | 231.46 | 215.6433 | 15.8167 | 34.1064 | 18.8847 | -45.9283 | 62.371 | 27.629 | -50.1112 | 43.6206 | 24.6904 | 161.7325 | 0.2 | 0 | 11.573 | 197.9959 | 4.3 | 10.4874 | 1.0508 | 0.1706
2016-07-29 09:00 | 247.93 | 226.39 | 21.54 | 43.2339 | 18.875 | -30.9281 | 60.1177 | 29.8823 | -34.1177 | 29.4529 | 37.6464 | 169.7925 | 0.2 | 0 | 12.3965 | 219.8354 | 4.5 | 11.3699 | 1.0477 | 0.18886
2016-07-29 10:00 | 275.56 | 243.9967 | 31.5633 | 60.6726 | 18.8652 | -15.928 | 58.6527 | 31.3473 | -17.7024 | 15.2685 | 58.531 | 182.9975 | 0.2 | 0 | 13.778 | 255.3065 | 5.4 | 13.3783 | 1.0407 | 0.21787
2016-07-29 11:00 | 303.19 | 261.6033 | 41.5867 | 78.7262 | 18.8555 | -0.92781 | 58.1131 | 31.8869 | -1.0341 | 2.0849 | 78.6741 | 196.2025 | 0.2 | 0 | 15.1595 | 290.0361 | 5.9 | 14.9636 | 1.0351 | 0.24618
2016-07-29 12:00 | 330.82 | 279.21 | 51.61 | 98.9223 | 18.8457 | 14.0723 | 58.5521 | 31.4479 | 15.6483 | 13.5179 | 96.1819 | 209.4075 | 0.2 | 0 | 16.541 | 322.1304 | 6.3 | 16.3666 | 1.0302 | 0.27213
2016-07-29 13:00 | 309.5567 | 251.8967 | 57.66 | 115.0691 | 18.8359 | 29.0725 | 59.9278 | 30.0722 | 32.1019 | 27.6979 | 101.8835 | 188.9225 | 0.2 | 0 | 15.4778 | 306.2838 | 5.6 | 15.1714 | 1.0344 | 0.25979
2016-07-29 14:00 | 288.2933 | 224.5833 | 63.71 | 136.2077 | 18.8261 | 44.0727 | 62.1122 | 27.8878 | 48.1473 | 41.8759 | 101.4192 | 168.4375 | 0.2 | 0 | 14.4147 | 284.2714 | 6.4 | 15.2835 | 1.034 | 0.24103
2016-07-29 15:00 | 267.03 | 197.27 | 69.76 | 164.5528 | 18.8163 | 59.0728 | 64.9166 | 25.0834 | 63.7053 | 55.9838 | 92.0554 | 147.9525 | 0.2 | 0 | 13.3515 | 253.3594 | 5.6 | 13.5175 | 1.0402 | 0.2161
2016-07-29 16:00 | 238.0667 | 158.3333 | 79.7333 | 213.9632 | 18.8065 | 74.073 | 68.1209 | 21.8791 | 78.7921 | 69.969 | 73.2887 | 118.75 | 0.2 | 0 | 11.9033 | 203.942 | 6.3 | 12.6732 | 1.0431 | 0.17445
2016-07-29 17:00 | 209.1033 | 119.3967 | 89.7067 | 282.6617 | 18.7967 | 89.0732 | 71.4964 | 18.5036 | 93.4912 | 83.7612 | 30.7175 | 89.5475 | 0.2 | 0 | 10.4552 | 130.7201 | 7.7 | 11.785 | 1.0463 | 0.11215
2016-07-29 18:00 | 180.14 | 80.46 | 99.68 | 380.6958 | 18.7869 | 104.0734 | 74.8209 | 15.1791 | 107.917 | 97.2507 | 0 | 60.345 | 0.2 | 0 | 9.007 | 69.352 | 6.4 | 8.5673 | 1.0575 | 0.060139
2016-07-29 19:00 | 146.0367 | 64.7067 | 81.33 | 387.5803 | 18.7771 | 119.0736 | 77.887 | 12.113 | 122.186 | 110.2498 | 0 | 48.53 | 0.2 | 0 | 7.3018 | 55.8318 | 5.7 | 7.4447 | 1.0614 | 0.048595
2016-07-29 20:00 | 111.9333 | 48.9533 | 62.98 | 381.9067 | 18.7672 | 134.0738 | 80.508 | 9.492 | 136.3944 | 122.4153 | 0 | 36.715 | 0.2 | 0 | 5.5967 | 42.3117 | 5.6 | 6.9222 | 1.0633 | 0.036891
2016-07-29 21:00 | 77.83 | 33.2 | 44.63 | 343.0551 | 18.7574 | 149.074 | 82.5249 | 7.4751 | 150.6064 | 133.0848 | 0 | 24.9 | 0.2 | 0 | 3.8915 | 28.7915 | 4.2 | 5.0997 | 1.0697 | 0.025253
2016-07-29 22:00 | 69.89 | 33.28 | 36.61 | 339.7288 | 18.7475 | 164.0742 | 83.8137 | 6.1863 | 164.8494 | 141.0027 | 0 | 24.96 | 0.2 | 0 | 3.4945 | 28.4545 | 3.5 | 4.3892 | 1.0721 | 0.025016
2016-07-29 23:00 | 61.95 | 33.36 | 28.59 | 287.5613 | 18.7376 | 179.0744 | 84.2941 | 5.7059 | 179.1191 | 144.2841 | 0 | 25.02 | 0.2 | 0 | 3.0975 | 28.1175 | 3.6 | 4.4787 | 1.0718 | 0.024712
2016-07-30 | 54.01 | 33.44 | 20.57 | 194.7281 | 18.7278 | -165.9254 | 83.9363 | 6.0637 | -166.6084 | 141.7158 | 0 | 25.08 | 0.2 | 0 | 2.7005 | 27.7805 | 3.3 | 4.1681 | 1.0729 | 0.024441
2016-07-30 01:00 | 76.2933 | 53.0233 | 23.27 | 184.7316 | 18.7179 | -150.9252 | 82.7634 | 7.2366 | -152.3581 | 134.2737 | 0 | 39.7675 | 0.2 | 0 | 3.8147 | 43.5822 | 3 | 4.3619 | 1.0722 | 0.038319
2016-07-30 02:00 | 98.5767 | 72.6067 | 25.97 | 163.3092 | 18.708 | -135.925 | 80.8498 | 9.1502 | -138.1379 | 123.8662 | 0 | 54.455 | 0.2 | 0 | 4.9288 | 59.3838 | 4.3 | 6.1557 | 1.066 | 0.051906
2016-07-30 03:00 | 120.86 | 92.19 | 28.67 | 141.5501 | 18.6981 | -120.9248 | 78.3143 | 11.6857 | -123.9254 | 111.8421 | 0 | 69.1425 | 0.2 | 0 | 6.043 | 75.1855 | 4 | 6.3495 | 1.0653 | 0.065677
2016-07-30 04:00 | 163.8433 | 115.69 | 48.1533 | 189.9168 | 18.6882 | -105.9245 | 75.3123 | 14.6877 | -109.6616 | 98.922 | 0 | 86.7675 | 0.2 | 0 | 8.1922 | 94.9597 | 6.6 | 9.5675 | 1.054 | 0.082073
2016-07-30 05:00 | 206.8267 | 139.19 | 67.6367 | 219.2033 | 18.6782 | -90.9243 | 72.0277 | 17.9723 | -95.2545 | 85.4782 | 17.2815 | 104.3925 | 0.2 | 0 | 10.3413 | 132.0154 | 6.7 | 10.8255 | 1.0496 | 0.11362
2016-07-30 06:00 | 249.81 | 162.69 | 87.12 | 239.4688 | 18.6683 | -75.9241 | 68.6659 | 21.3341 | -80.5903 | 71.7122 | 75.1429 | 122.0175 | 0.2 | 0 | 12.4905 | 209.6509 | 6.9 | 13.4516 | 1.0404 | 0.17886
2016-07-30 07:00 | 314.9467 | 159.1067 | 155.84 | 375.0495 | 18.6584 | -60.9238 | 65.448 | 24.552 | -65.5538 | 57.7409 | 200.1824 | 119.33 | 0.2 | 0 | 15.7473 | 335.2597 | 6.1 | 16.5769 | 1.0295 | 0.28302
2016-07-30 08:00 | 380.0833 | 155.5233 | 224.56 | 488.0033 | 18.6484 | -45.9236 | 62.6025 | 27.3975 | -50.0576 | 43.6376 | 353.1776 | 116.6425 | 0.2 | 0 | 19.0042 | 488.8243 | 6.5 | 21.7758 | 1.0113 | 0.40536
2016-07-30 09:00 | 445.22 | 151.94 | 293.28 | 592.8705 | 18.6385 | -30.9233 | 60.3515 | 29.6485 | -34.0762 | 29.4544 | 516.2404 | 113.955 | 0.2 | 0 | 22.261 | 652.4564 | 6.2 | 26.5893 | 0.99444 | 0.53204
2016-07-30 10:00 | 460.91 | 136.73 | 324.18 | 627.3983 | 18.6285 | -15.9231 | 58.8885 | 31.1115 | -17.6769 | 15.2466 | 605.3158 | 102.5475 | 0.2 | 0 | 23.0455 | 730.9088 | 7.1 | 29.9409 | 0.98271 | 0.58898
2016-07-30 11:00 | 476.6 | 121.52 | 355.08 | 676.6922 | 18.6185 | -0.92282 | 58.35 | 31.65 | -1.0273 | 1.871 | 676.3315 | 91.14 | 0.2 | 0 | 23.83 | 791.3015 | 8.4 | 33.1282 | 0.97155 | 0.63041
2016-07-30 12:00 | 492.29 | 106.31 | 385.98 | 744.8625 | 18.6085 | 14.0774 | 58.7891 | 31.2109 | 15.6361 | 13.5009 | 724.279 | 79.7325 | 0.2 | 0 | 24.6145 | 828.626 | 8.4 | 34.2946 | 0.96747 | 0.65737
2016-07-30 13:00 | 449.2767 | 98.9167 | 350.36 | 704.2125 | 18.5986 | 29.0777 | 60.1639 | 29.8361 | 32.0729 | 27.7069 | 623.4656 | 74.1875 | 0.2 | 0 | 22.4638 | 720.1169 | 9.4 | 31.9037 | 0.97584 | 0.57623
2016-07-30 14:00 | 406.2633 | 91.5233 | 314.74 | 678.1479 | 18.5886 | 44.078 | 62.3469 | 27.6531 | 48.1053 | 41.9009 | 504.7464 | 68.6425 | 0.2 | 0 | 20.3132 | 593.7021 | 8.2 | 26.7532 | 0.99386 | 0.48385
2016-07-30 15:00 | 363.25 | 84.13 | 279.12 | 664.1857 | 18.5785 | 59.0783 | 65.15 | 24.85 | 63.6548 | 56.0229 | 371.1875 | 63.0975 | 0.2 | 0 | 18.1625 | 452.4475 | 6.9 | 21.039 | 1.0139 | 0.37615
2016-07-30 16:00 | 287.31 | 94.2333 | 193.0767 | 523.4148 | 18.5685 | 74.0785 | 68.3535 | 21.6465 | 78.7378 | 70.0228 | 178.8227 | 70.675 | 0.2 | 0 | 14.3655 | 263.8632 | 9.3 | 17.5457 | 1.0261 | 0.22201
2016-07-30 17:00 | 211.37 | 104.3367 | 107.0333 | 341.4024 | 18.5585 | 89.0788 | 71.7291 | 18.2709 | 93.437 | 83.8314 | 36.6851 | 78.2525 | 0.2 | 0 | 10.5685 | 125.5061 | 9.7 | 13.6221 | 1.0398 | 0.10701
2016-07-30 18:00 | 135.43 | 114.44 | 20.99 | 81.3876 | 18.5485 | 104.0791 | 75.0544 | 14.9456 | 107.8666 | 97.3401 | 0 | 85.83 | 0.2 | 0 | 6.7715 | 92.6015 | 7.2 | 10.0938 | 1.0522 | 0.079895
2016-07-30 19:00 | 110.61 | 90.7733 | 19.8367 | 96.3736 | 18.5384 | 119.0794 | 78.1219 | 11.8781 | 122.1424 | 110.3629 | 0 | 68.08 | 0.2 | 0 | 5.5305 | 73.6105 | 8.1 | 10.4003 | 1.0511 | 0.063445
2016-07-30 20:00 | 85.79 | 67.1067 | 18.6833 | 116.1636 | 18.5284 | 134.0797 | 80.7446 | 9.2554 | 136.3603 | 122.5584 | 0 | 50.33 | 0.2 | 0 | 4.2895 | 54.6195 | 7.3 | 9.0069 | 1.056 | 0.047295
2016-07-30 21:00 | 60.97 | 43.44 | 17.53 | 139.1551 | 18.5183 | 149.08 | 82.763 | 7.237 | 150.584 | 133.2653 | 0 | 32.58 | 0.2 | 0 | 3.0485 | 35.6285 | 6.4 | 7.5134 | 1.0612 | 0.031003
2016-07-30 22:00 | 57.5067 | 36.7933 | 20.7133 | 199.9132 | 18.5082 | 164.0803 | 84.0528 | 5.9472 | 164.8403 | 141.2225 | 0 | 27.595 | 0.2 | 0 | 2.8753 | 30.4703 | 7.1 | 8.0522 | 1.0593 | 0.026468
2016-07-30 23:00 | 54.0433 | 30.1467 | 23.8967 | 250.8515 | 18.4982 | 179.0807 | 84.5336 | 5.4664 | 179.1242 | 144.5236 | 0 | 22.61 | 0.2 | 0 | 2.7022 | 25.3122 | 7.6 | 8.391 | 1.0581 | 0.021963
2016-07-31 | 50.58 | 23.5 | 27.08 | 266.8352 | 18.4881 | -165.919 | 84.1753 | 5.8247 | -166.589 | 141.9356 | 0 | 17.625 | 0.2 | 0 | 2.529 | 20.154 | 7.4 | 8.0298 | 1.0594 | 0.017508
2016-07-31 01:00 | 65.8433 | 37.14 | 28.7033 | 235.5646 | 18.478 | -150.9187 | 83.0012 | 6.9988 | -152.3252 | 134.4519 | 0 | 27.855 | 0.2 | 0 | 3.2922 | 31.1472 | 7.3 | 8.2733 | 1.0585 | 0.027036
2016-07-31 02:00 | 81.1067 | 50.78 | 30.3267 | 195.7132 | 18.4679 | -135.9184 | 81.0858 | 8.9142 | -138.093 | 124.0046 | 0 | 38.085 | 0.2 | 0 | 4.0553 | 42.1403 | 7.1 | 8.4169 | 1.058 | 0.036561
2016-07-31 03:00 | 96.37 | 64.42 | 31.95 | 160.9276 | 18.4578 | -120.918 | 78.5486 | 11.4514 | -123.8706 | 111.9487 | 0 | 48.315 | 0.2 | 0 | 4.8185 | 53.1335 | 7.3 | 8.9604 | 1.0561 | 0.046015
2016-07-31 04:00 | 118.5733 | 82.4233 | 36.15 | 144.8233 | 18.4476 | -105.9177 | 75.5453 | 14.4547 | -109.5994 | 99.0037 | 0 | 61.8175 | 0.2 | 0 | 5.9287 | 67.7462 | 6.5 | 8.6171 | 1.0573 | 0.058737
2016-07-31 05:00 | 140.7767 | 100.4267 | 40.35 | 132.4265 | 18.4375 | -90.9174 | 72.26 | 17.74 | -95.1879 | 85.5399 | 10.2981 | 75.32 | 0.2 | 0 | 7.0388 | 92.657 | 6.7 | 9.5955 | 1.0539 | 0.080075
2016-07-31 06:00 | 162.98 | 118.43 | 44.55 | 123.7431 | 18.4274 | -75.917 | 68.8986 | 21.1014 | -80.5226 | 71.7571 | 38.7373 | 88.8225 | 0.2 | 0 | 8.149 | 135.7088 | 7.4 | 11.6409 | 1.0468 | 0.11648
2016-07-31 07:00 | 193.4367 | 159.87 | 33.5667 | 81.5119 | 18.4172 | -60.9167 | 65.682 | 24.318 | -65.4892 | 57.7709 | 43.4708 | 119.9025 | 0.2 | 0 | 9.6718 | 173.0451 | 7.3 | 12.7077 | 1.043 | 0.148
2016-07-31 08:00 | 223.8933 | 201.31 | 22.5833 | 49.4707 | 18.4071 | -45.9163 | 62.8386 | 27.1614 | -50.0005 | 43.6535 | 35.7934 | 150.9825 | 0.2 | 0 | 11.1947 | 197.9706 | 6.4 | 12.5866 | 1.0434 | 0.16939
2016-07-31 09:00 | 254.35 | 242.75 | 11.6 | 23.6225 | 18.3969 | -30.916 | 60.59 | 29.41 | -34.0313 | 29.4553 | 20.5691 | 182.0625 | 0.2 | 0 | 12.7175 | 215.3491 | 6.3 | 13.0297 | 1.0419 | 0.18398
2016-07-31 10:00 | 262.4 | 241.9633 | 20.4367 | 39.8294 | 18.3867 | -15.9156 | 59.1291 | 30.8709 | -17.6483 | 15.2255 | 38.4314 | 181.4725 | 0.2 | 0 | 13.12 | 233.0239 | 6.2 | 13.482 | 1.0403 | 0.19878
2016-07-31 11:00 | 270.45 | 241.1767 | 29.2733 | 56.1729 | 18.3765 | -0.91522 | 58.592 | 31.408 | -1.0177 | 1.6577 | 56.1494 | 180.8825 | 0.2 | 0 | 13.5225 | 250.5544 | 5.5 | 13.3298 | 1.0408 | 0.21385
2016-07-31 12:00 | 278.5 | 240.39 | 38.11 | 74.0618 | 18.3663 | 14.0852 | 59.0313 | 30.9687 | 15.6265 | 13.4901 | 72.0185 | 180.2925 | 0.2 | 0 | 13.925 | 266.236 | 6.1 | 14.4199 | 1.037 | 0.2264
2016-07-31 13:00 | 253.9567 | 215.5933 | 38.3633 | 77.6804 | 18.3561 | 29.0855 | 60.4053 | 29.5947 | 32.0461 | 27.7205 | 68.7648 | 161.695 | 0.2 | 0 | 12.6978 | 243.1576 | 6.4 | 13.9987 | 1.0385 | 0.20707
2016-07-31 14:00 | 229.4133 | 190.7967 | 38.6167 | 83.8762 | 18.3459 | 44.0859 | 62.587 | 27.413 | 48.0653 | 41.9298 | 62.4008 | 143.0975 | 0.2 | 0 | 11.4707 | 216.969 | 7.4 | 14.1803 | 1.0379 | 0.18465
2016-07-31 15:00 | 204.87 | 166 | 38.87 | 93.335 | 18.3357 | 59.0863 | 65.3889 | 24.6111 | 63.6061 | 56.066 | 52.1031 | 124.5 | 0.2 | 0 | 10.2435 | 186.8466 | 7 | 12.839 | 1.0426 | 0.15974
2016-07-31 16:00 | 172.0733 | 145.2033 | 26.87 | 73.6139 | 18.3255 | 74.0867 | 68.5917 | 21.4083 | 78.6849 | 70.0805 | 25.0803 | 108.9025 | 0.2 | 0 | 8.6037 | 142.5864 | 6.4 | 10.8558 | 1.0495 | 0.12271
2016-07-31 17:00 | 139.2767 | 124.4067 | 14.87 | 48.0358 | 18.3153 | 89.0871 | 71.9672 | 18.0328 | 93.3842 | 83.9055 | 5.0999 | 93.305 | 0.2 | 0 | 6.9638 | 105.3687 | 6 | 9.2928 | 1.055 | 0.091152
2016-07-31 18:00 | 106.48 | 103.61 | 2.87 | 11.305 | 18.305 | 104.0875 | 75.2933 | 14.7067 | 107.8176 | 97.4336 | 0 | 77.7075 | 0.2 | 0 | 5.324 | 83.0315 | 5.7 | 8.2947 | 1.0585 | 0.072067
2016-07-31 19:00 | 86.1067 | 81.9333 | 4.1733 | 20.6882 | 18.2948 | 119.0879 | 78.3621 | 11.6379 | 122.1003 | 110.4803 | 0 | 61.45 | 0.2 | 0 | 4.3053 | 65.7553 | 5.2 | 7.2549 | 1.0621 | 0.057268
2016-07-31 20:00 | 65.7333 | 60.2567 | 5.4767 | 34.9572 | 18.2845 | 134.0883 | 80.9865 | 9.0135 | 136.3279 | 122.7061 | 0 | 45.1925 | 0.2 | 0 | 3.2867 | 48.4792 | 5.7 | 7.215 | 1.0622 | 0.042227
2016-07-31 21:00 | 45.36 | 38.58 | 6.78 | 55.6835 | 18.2742 | 149.0887 | 83.0063 | 6.9937 | 150.5635 | 133.4507 | 0 | 28.935 | 0.2 | 0 | 2.268 | 31.203 | 5.6 | 6.5751 | 1.0645 | 0.027236
2016-07-31 22:00 | 38.7867 | 32.6367 | 6.15 | 61.8904 | 18.264 | 164.0891 | 84.2971 | 5.7029 | 164.8334 | 141.4477 | 0 | 24.4775 | 0.2 | 0 | 1.9393 | 26.4168 | 5.3 | 6.1255 | 1.0661 | 0.023093
2016-07-31 23:00 | 32.2133 | 26.6933 | 5.52 | 60.6506 | 18.2537 | 179.0896 | 84.7781 | 5.2219 | 179.1318 | 144.7683 | 0 | 20.02 | 0.2 | 0 | 1.6107 | 21.6307 | 4.3 | 4.976 | 1.0701 | 0.01898
2016-08-01 | 25.64 | 20.75 | 4.89 | 50.2823 | 18.2434 | -165.91 | 84.4191 | 5.5809 | -166.5669 | 142.1588 | 0 | 15.5625 | 0.2 | 0 | 1.282 | 16.8445 | 3.8 | 4.3264 | 1.0724 | 0.014812
2016-08-01 01:00 | 52.2467 | 29.13 | 23.1167 | 196.4902 | 18.2331 | -150.9096 | 83.2436 | 6.7564 | -152.2893 | 134.6319 | 0 | 21.8475 | 0.2 | 0 | 2.6123 | 24.4598 | 3.8 | 4.5644 | 1.0715 | 0.021492
2016-08-01 02:00 | 78.8533 | 37.51 | 41.3433 | 274.1519 | 18.2228 | -135.9091 | 81.3265 | 8.6735 | -138.0449 | 124.1436 | 0 | 28.1325 | 0.2 | 0 | 3.9427 | 32.0752 | 5.3 | 6.3023 | 1.0654 | 0.028023
2016-08-01 03:00 | 105.46 | 45.89 | 59.57 | 306.3499 | 18.2124 | -120.9087 | 78.7874 | 11.2126 | -123.8123 | 112.055 | 0 | 34.4175 | 0.2 | 0 | 5.273 | 39.6905 | 5.1 | 6.3403 | 1.0653 | 0.034672
2016-08-01 04:00 | 133.3067 | 71.0933 | 62.2133 | 253.3095 | 18.2021 | -105.9083 | 75.7826 | 14.2174 | -109.5337 | 99.0847 | 0 | 53.32 | 0.2 | 0 | 6.6653 | 59.9853 | 4.7 | 6.5745 | 1.0645 | 0.05236
2016-08-01 05:00 | 161.1533 | 96.2967 | 64.8567 | 215.6415 | 18.1918 | -90.9078 | 72.4967 | 17.5033 | -95.1176 | 85.6006 | 16.5414 | 72.2225 | 0.2 | 0 | 8.0577 | 96.8216 | 5 | 8.0257 | 1.0594 | 0.08411
2016-08-01 06:00 | 189 | 121.5 | 67.5 | 189.5222 | 18.1814 | -75.9073 | 69.1355 | 20.8645 | -80.4514 | 71.8009 | 59.1915 | 91.125 | 0.2 | 0 | 9.45 | 159.7665 | 6.4 | 11.3927 | 1.0476 | 0.13725
2016-08-01 07:00 | 210.7433 | 153.2967 | 57.4467 | 140.7984 | 18.1711 | -60.9069 | 65.9203 | 24.0797 | -65.421 | 57.7999 | 75.0284 | 114.9725 | 0.2 | 0 | 10.5372 | 200.538 | 6.2 | 12.4668 | 1.0439 | 0.17165
2016-08-01 08:00 | 232.4867 | 185.0933 | 47.3933 | 104.6766 | 18.1607 | -45.9064 | 63.0791 | 26.9209 | -49.9398 | 43.6685 | 75.7174 | 138.82 | 0.2 | 0 | 11.6243 | 226.1618 | 5.6 | 12.6676 | 1.0432 | 0.19346
2016-08-01 09:00 | 254.23 | 216.89 | 37.34 | 76.6176 | 18.1503 | -30.906 | 60.8331 | 29.1669 | -33.9829 | 29.4557 | 66.7137 | 162.6675 | 0.2 | 0 | 12.7115 | 242.0927 | 5.9 | 13.4654 | 1.0404 | 0.20653
2016-08-01 10:00 | 275.1767 | 224.94 | 50.2367 | 98.6148 | 18.14 | -15.9055 | 59.3746 | 30.6254 | -17.6165 | 15.2054 | 95.1624 | 168.705 | 0.2 | 0 | 13.7588 | 277.6263 | 6 | 14.6758 | 1.0361 | 0.23588
2016-08-01 11:00 | 296.1233 | 232.99 | 63.1333 | 122.0094 | 18.1296 | -0.905 | 58.8389 | 31.1611 | -1.0051 | 1.4481 | 121.9705 | 174.7425 | 0.2 | 0 | 14.8062 | 311.5191 | 6.7 | 16.435 | 1.03 | 0.2631
2016-08-01 12:00 | 317.07 | 241.04 | 76.03 | 148.8262 | 18.1192 | 14.0955 | 59.2786 | 30.7214 | 15.6195 | 13.4859 | 144.7227 | 180.78 | 0.2 | 0 | 15.8535 | 341.3562 | 7 | 17.6674 | 1.0257 | 0.2871
2016-08-01 13:00 | 288.75 | 213.61 | 75.14 | 153.3116 | 18.1088 | 29.096 | 60.652 | 29.348 | 32.0216 | 27.7388 | 135.6929 | 160.2075 | 0.2 | 0 | 14.4375 | 310.3379 | 6.3 | 15.9981 | 1.0315 | 0.26249
2016-08-01 14:00 | 260.43 | 186.18 | 74.25 | 162.6173 | 18.0983 | 44.0965 | 62.8325 | 27.1675 | 48.0272 | 41.9629 | 120.9186 | 139.635 | 0.2 | 0 | 13.0215 | 273.5751 | 5.8 | 14.3492 | 1.0373 | 0.23269
2016-08-01 15:00 | 232.11 | 158.75 | 73.36 | 177.8092 | 18.0879 | 59.097 | 65.6332 | 24.3668 | 63.559 | 56.1129 | 99.139 | 119.0625 | 0.2 | 0 | 11.6055 | 229.807 | 5.4 | 12.5815 | 1.0435 | 0.19663
2016-08-01 16:00 | 198.6533 | 140.7467 | 57.9067 | 160.3834 | 18.0775 | 74.0975 | 68.8352 | 21.1648 | 78.6337 | 70.142 | 54.4807 | 105.56 | 0.2 | 0 | 9.9327 | 169.9734 | 5.8 | 11.1117 | 1.0486 | 0.14615
2016-08-01 17:00 | 165.1967 | 122.7433 | 42.4533 | 138.9563 | 18.0671 | 89.098 | 72.2108 | 17.7892 | 93.333 | 83.9834 | 14.5648 | 92.0575 | 0.2 | 0 | 8.2598 | 114.8821 | 6.1 | 9.6901 | 1.0536 | 0.099251
2016-08-01 18:00 | 131.74 | 104.74 | 27 | 108.111 | 18.0566 | 104.0985 | 75.5377 | 14.4623 | 107.7701 | 97.531 | 0 | 78.555 | 0.2 | 0 | 6.587 | 85.142 | 5.7 | 8.3607 | 1.0582 | 0.073882
2016-08-01 19:00 | 103.1167 | 82.8067 | 20.31 | 102.823 | 18.0461 | 119.099 | 78.6078 | 11.3922 | 122.0598 | 110.6018 | 0 | 62.105 | 0.2 | 0 | 5.1558 | 67.2608 | 5.8 | 7.9019 | 1.0598 | 0.058454
2016-08-01 20:00 | 74.4933 | 60.8733 | 13.62 | 89.3669 | 18.0357 | 134.0995 | 81.2337 | 8.7663 | 136.2972 | 122.8583 | 0 | 45.655 | 0.2 | 0 | 3.7247 | 49.3797 | 6.1 | 7.6431 | 1.0607 | 0.042951
2016-08-01 21:00 | 45.87 | 38.94 | 6.93 | 59.0027 | 18.0252 | 149.1 | 83.2549 | 6.7451 | 150.545 | 133.6411 | 0 | 29.205 | 0.2 | 0 | 2.2935 | 31.4985 | 5.6 | 6.5843 | 1.0645 | 0.027494
2016-08-01 22:00 | 42.51 | 34.63 | 7.88 | 82.9154 | 18.0147 | 164.1006 | 84.5466 | 5.4534 | 164.8288 | 141.6783 | 0 | 25.9725 | 0.2 | 0 | 2.1255 | 28.098 | 5.2 | 6.0781 | 1.0662 | 0.024566
2016-08-01 23:00 | 39.15 | 30.32 | 8.83 | 101.8734 | 18.0042 | 179.1011 | 85.0276 | 4.9724 | 179.1419 | 145.0179 | 0 | 22.74 | 0.2 | 0 | 1.9575 | 24.6975 | 3.7 | 4.4718 | 1.0718 | 0.021707
2016-08-02 | 35.79 | 26.01 | 9.78 | 105.2396 | 17.9937 | -165.8984 | 84.6678 | 5.3322 | -166.542 | 142.3855 | 0 | 19.5075 | 0.2 | 0 | 1.7895 | 21.297 | 3.8 | 4.4655 | 1.0719 | 0.018719
2016-08-02 01:00 | 60.5167 | 38.86 | 21.6567 | 191.0358 | 17.9832 | -150.8978 | 83.4907 | 6.5093 | -152.2503 | 134.8135 | 0 | 29.145 | 0.2 | 0 | 3.0258 | 32.1708 | 4.4 | 5.4053 | 1.0686 | 0.028189
2016-08-02 02:00 | 85.2433 | 51.71 | 33.5333 | 228.7802 | 17.9727 | -135.8973 | 81.5715 | 8.4285 | -137.9935 | 124.2829 | 0 | 38.7825 | 0.2 | 0 | 4.2622 | 43.0447 | 6.2 | 7.5451 | 1.0611 | 0.037453
2016-08-02 03:00 | 109.97 | 64.56 | 45.41 | 238.6391 | 17.9622 | -120.8967 | 79.0304 | 10.9696 | -123.7507 | 112.1611 | 0 | 48.42 | 0.2 | 0 | 5.4985 | 53.9185 | 6.6 | 8.285 | 1.0585 | 0.0468
2016-08-02 04:00 | 157.8133 | 88.61 | 69.2033 | 286.5404 | 17.9517 | -105.8962 | 76.0241 | 13.9759 | -109.4644 | 99.165 | 0 | 66.4575 | 0.2 | 0 | 7.8907 | 74.3482 | 4.8 | 7.1234 | 1.0626 | 0.06478
2016-08-02 05:00 | 205.6567 | 112.66 | 92.9967 | 313.3835 | 17.9411 | -90.8956 | 72.7375 | 17.2625 | -95.0437 | 85.6604 | 23.7129 | 84.495 | 0.2 | 0 | 10.2828 | 118.4907 | 6 | 9.7028 | 1.0535 | 0.10236
2016-08-02 06:00 | 253.5 | 136.71 | 116.79 | 331.5802 | 17.9306 | -75.895 | 69.3767 | 20.6233 | -80.3765 | 71.8437 | 103.3238 | 102.5325 | 0.2 | 0 | 12.675 | 218.5313 | 5.5 | 12.3291 | 1.0443 | 0.18714
2016-08-02 07:00 | 292.7067 | 160.84 | 131.8667 | 326.2919 | 17.92 | -60.8945 | 66.1629 | 23.8371 | -65.3491 | 57.8278 | 173.7393 | 120.63 | 0.2 | 0 | 14.6353 | 309.0046 | 6.1 | 15.7564 | 1.0324 | 0.26158
2016-08-02 08:00 | 331.9133 | 184.97 | 146.9433 | 327.3088 | 17.9094 | -45.8939 | 63.324 | 26.676 | -49.8756 | 43.6827 | 236.7019 | 138.7275 | 0.2 | 0 | 16.5957 | 392.0251 | 7.7 | 19.9508 | 1.0177 | 0.32714
2016-08-02 09:00 | 371.12 | 209.1 | 162.02 | 335.0452 | 17.8989 | -30.8933 | 61.0807 | 28.9193 | -33.9312 | 29.4558 | 291.7357 | 156.825 | 0.2 | 0 | 18.556 | 467.1167 | 7.1 | 21.6974 | 1.0116 | 0.38746
2016-08-02 10:00 | 388.3367 | 203.1733 | 185.1633 | 366.1804 | 17.8883 | -15.8927 | 59.6247 | 30.3753 | -17.5815 | 15.1866 | 353.3926 | 152.38 | 0.2 | 0 | 19.4168 | 525.1894 | 7.1 | 23.5122 | 1.0052 | 0.4329
2016-08-02 11:00 | 405.5533 | 197.2467 | 208.3067 | 405.5181 | 17.8777 | -0.89215 | 59.0907 | 30.9093 | -0.98962 | 1.2468 | 405.4221 | 147.935 | 0.2 | 0 | 20.2777 | 573.6347 | 7.2 | 25.1261 | 0.99956 | 0.47017
2016-08-02 12:00 | 422.77 | 191.32 | 231.45 | 456.443 | 17.8671 | 14.1084 | 59.5309 | 30.4691 | 15.6151 | 13.4884 | 443.8529 | 143.49 | 0.2 | 0 | 21.1385 | 608.4814 | 7.3 | 26.315 | 0.9954 | 0.49666
2016-08-02 13:00 | 363.7567 | 175.72 | 188.0367 | 386.6864 | 17.8565 | 29.109 | 60.9038 | 29.0962 | 31.9994 | 27.7618 | 342.1756 | 131.79 | 0.2 | 0 | 18.1878 | 492.1535 | 7.3 | 22.6798 | 1.0081 | 0.40684
2016-08-02 14:00 | 304.7433 | 160.12 | 144.6233 | 319.4715 | 17.8459 | 44.1096 | 63.0832 | 26.9168 | 47.9911 | 42.0002 | 237.4129 | 120.09 | 0.2 | 0 | 15.2372 | 372.7401 | 7 | 18.6481 | 1.0222 | 0.31244
2016-08-02 15:00 | 245.73 | 144.52 | 101.21 | 247.6966 | 17.8352 | 59.1103 | 65.8828 | 24.1172 | 63.5138 | 56.1638 | 137.9226 | 108.39 | 0.2 | 0 | 12.2865 | 258.5991 | 6.6 | 14.6812 | 1.0361 | 0.21971
2016-08-02 16:00 | 199.94 | 132.11 | 67.83 | 190.0018 | 17.8246 | 74.1109 | 69.0841 | 20.9159 | 78.584 | 70.2074 | 64.3378 | 99.0825 | 0.2 | 0 | 9.997 | 173.4173 | 4.5 | 9.9193 | 1.0528 | 0.14971
2016-08-02 17:00 | 154.15 | 119.7 | 34.45 | 114.3091 | 17.814 | 89.1115 | 72.4597 | 17.5403 | 93.2832 | 84.0653 | 11.819 | 89.775 | 0.2 | 0 | 7.7075 | 109.3015 | 4.2 | 7.6157 | 1.0608 | 0.095081
2016-08-02 18:00 | 108.36 | 107.29 | 1.07 | 4.3581 | 17.8033 | 104.1121 | 75.7873 | 14.2127 | 107.7241 | 97.6324 | 0 | 80.4675 | 0.2 | 0 | 5.418 | 85.8855 | 4.1 | 6.7839 | 1.0638 | 0.074916
2016-08-02 19:00 | 95.8033 | 80.05 | 15.7533 | 81.527 | 17.7927 | 119.1127 | 78.8587 | 11.1413 | 122.0209 | 110.7275 | 0 | 60.0375 | 0.2 | 0 | 4.7902 | 64.8277 | 3.7 | 5.7259 | 1.0675 | 0.056745
2016-08-02 20:00 | 83.2467 | 52.81 | 30.4367 | 205.584 | 17.782 | 134.1134 | 81.4861 | 8.5139 | 136.2684 | 123.0148 | 0 | 39.6075 | 0.2 | 0 | 4.1623 | 43.7698 | 3.3 | 4.6678 | 1.0712 | 0.038445
2016-08-02 21:00 | 70.69 | 25.57 | 45.12 | 399.102 | 17.7713 | 149.114 | 83.5086 | 6.4914 | 150.5285 | 133.8364 | 0 | 19.1775 | 0.2 | 0 | 3.5345 | 22.712 | 3.1 | 3.8098 | 1.0742 | 0.020005
2016-08-02 22:00 | 60.61 | 23.0533 | 37.5567 | 414.4633 | 17.7606 | 164.1146 | 84.801 | 5.199 | 164.8264 | 141.9141 | 0 | 17.29 | 0.2 | 0 | 3.0305 | 20.3205 | 3 | 3.635 | 1.0748 | 0.017909
2016-08-02 23:00 | 50.53 | 20.5367 | 29.9933 | 364.6471 | 17.7499 | 179.1153 | 85.2819 | 4.7181 | 179.1545 | 145.2725 | 0 | 15.4025 | 0.2 | 0 | 2.5265 | 17.929 | 3 | 3.5603 | 1.075 | 0.015805
2016-08-03 | 40.45 | 18.02 | 22.43 | 253.3684 | 17.7392 | -165.8841 | 84.9211 | 5.0789 | -166.5142 | 142.6153 | 0 | 13.515 | 0.2 | 0 | 2.0225 | 15.5375 | 3.1 | 3.5855 | 1.075 | 0.013696
2016-08-03 01:00 | 61.53 | 35.3333 | 26.1967 | 240.3364 | 17.7285 | -150.8834 | 83.7423 | 6.2577 | -152.2083 | 134.9965 | 0 | 26.5 | 0.2 | 0 | 3.0765 | 29.5765 | 3.5 | 4.4243 | 1.072 | 0.025999
2016-08-03 02:00 | 82.61 | 52.6467 | 29.9633 | 210.6149 | 17.7178 | -135.8828 | 81.821 | 8.179 | -137.9389 | 124.4225 | 0 | 39.485 | 0.2 | 0 | 4.1305 | 43.6155 | 3.3 | 4.663 | 1.0712 | 0.03831
2016-08-03 03:00 | 103.69 | 69.96 | 33.73 | 181.2979 | 17.7071 | -120.8821 | 79.2778 | 10.7222 | -123.6856 | 112.2667 | 0 | 52.47 | 0.2 | 0 | 5.1845 | 57.6545 | 3.8 | 5.6017 | 1.0679 | 0.050486
2016-08-03 04:00 | 123.9233 | 86.7433 | 37.18 | 156.6465 | 17.6964 | -105.8814 | 76.2698 | 13.7302 | -109.3916 | 99.2445 | 0 | 65.0575 | 0.2 | 0 | 6.1962 | 71.2537 | 3.6 | 5.8267 | 1.0671 | 0.062349
2016-08-03 05:00 | 144.1567 | 103.5267 | 40.63 | 138.8276 | 17.6856 | -90.8808 | 72.9824 | 17.0176 | -94.9663 | 85.7192 | 10.3626 | 77.645 | 0.2 | 0 | 7.2078 | 95.2155 | 3.3 | 6.2755 | 1.0655 | 0.083193
2016-08-03 06:00 | 164.39 | 120.31 | 44.08 | 126.5894 | 17.6749 | -75.8801 | 69.622 | 20.378 | -80.298 | 71.8854 | 39.359 | 90.2325 | 0.2 | 0 | 8.2195 | 137.811 | 3.4 | 7.7066 | 1.0605 | 0.11984
2016-08-03 07:00 | 195.25 | 143.7367 | 51.5133 | 128.7212 | 17.6641 | -60.8794 | 66.4097 | 23.5903 | -65.2737 | 57.8546 | 68.4885 | 107.8025 | 0.2 | 0 | 9.7625 | 186.0535 | 4 | 9.8142 | 1.0532 | 0.16067
2016-08-03 08:00 | 226.11 | 167.1633 | 58.9467 | 132.4488 | 17.6533 | -45.8787 | 63.5733 | 26.4267 | -49.8079 | 43.696 | 95.7626 | 125.3725 | 0.2 | 0 | 11.3055 | 232.4406 | 3.9 | 11.1638 | 1.0484 | 0.19983
2016-08-03 09:00 | 256.97 | 190.59 | 66.38 | 138.3723 | 17.6426 | -30.878 | 61.3329 | 28.6671 | -33.8761 | 29.4555 | 120.486 | 142.9425 | 0.2 | 0 | 12.8485 | 276.277 | 4.4 | 13.0337 | 1.0419 | 0.23604
2016-08-03 10:00 | 261.2267 | 191.48 | 69.7467 | 138.9874 | 17.6318 | -15.8774 | 59.8795 | 30.1205 | -17.5434 | 15.1693 | 134.1447 | 143.61 | 0.2 | 0 | 13.0613 | 290.816 | 5.7 | 14.788 | 1.0357 | 0.24699
2016-08-03 11:00 | 265.4833 | 192.37 | 73.1133 | 143.4066 | 17.621 | -0.87665 | 59.3473 | 30.6527 | -0.97123 | 1.0624 | 143.382 | 144.2775 | 0.2 | 0 | 13.2742 | 300.9336 | 6 | 15.4042 | 1.0336 | 0.25505
2016-08-03 12:00 | 269.74 | 193.26 | 76.48 | 151.9881 | 17.6102 | 14.1241 | 59.7882 | 30.2118 | 15.6133 | 13.4982 | 147.7898 | 144.945 | 0.2 | 0 | 13.487 | 306.2218 | 6.1 | 15.6694 | 1.0327 | 0.2593
2016-08-03 13:00 | 252.0067 | 182.6133 | 69.3933 | 143.864 | 17.5994 | 29.1248 | 61.1608 | 28.8392 | 31.9796 | 27.7897 | 127.2714 | 136.96 | 0.2 | 0 | 12.6003 | 276.8318 | 6.5 | 15.151 | 1.0345 | 0.23483
2016-08-03 14:00 | 234.2733 | 171.9667 | 62.3067 | 138.8579 | 17.5886 | 44.1255 | 63.3392 | 26.6608 | 47.957 | 42.0417 | 103.1239 | 128.975 | 0.2 | 0 | 11.7137 | 243.8125 | 6.4 | 14.0191 | 1.0384 | 0.20761
2016-08-03 15:00 | 216.54 | 161.32 | 55.22 | 136.5004 | 17.5778 | 59.1262 | 66.1376 | 23.8624 | 63.4703 | 56.2186 | 75.8977 | 120.99 | 0.2 | 0 | 10.827 | 207.7147 | 6.2 | 12.6911 | 1.0431 | 0.17766
2016-08-03 16:00 | 179.1567 | 135.6567 | 43.5 | 123.2823 | 17.5669 | 74.1269 | 69.3383 | 20.6617 | 78.5359 | 70.2767 | 41.6051 | 101.7425 | 0.2 | 0 | 8.9578 | 152.3055 | 5.6 | 10.3595 | 1.0512 | 0.13129
2016-08-03 17:00 | 141.7733 | 109.9933 | 31.78 | 106.9521 | 17.5561 | 89.1276 | 72.714 | 17.286 | 93.235 | 84.151 | 10.8992 | 82.495 | 0.2 | 0 | 7.0887 | 100.4828 | 5.9 | 9.0401 | 1.0559 | 0.086999
2016-08-03 18:00 | 104.39 | 84.33 | 20.06 | 83.1655 | 17.5452 | 104.1284 | 76.0423 | 13.9577 | 107.6797 | 97.7378 | 0 | 63.2475 | 0.2 | 0 | 5.2195 | 68.467 | 6.4 | 8.5396 | 1.0576 | 0.059377
2016-08-03 19:00 | 92.69 | 64.17 | 28.52 | 151.0272 | 17.5344 | 119.1291 | 79.1149 | 10.8851 | 121.9837 | 110.8573 | 0 | 48.1275 | 0.2 | 0 | 4.6345 | 52.762 | 4.7 | 6.3488 | 1.0653 | 0.046089
2016-08-03 20:00 | 80.99 | 44.01 | 36.98 | 257.5163 | 17.5235 | 134.1298 | 81.7436 | 8.2564 | 136.2413 | 123.1758 | 0 | 33.0075 | 0.2 | 0 | 4.0495 | 37.057 | 4.5 | 5.658 | 1.0677 | 0.032444
2016-08-03 21:00 | 69.29 | 23.85 | 45.44 | 418.5491 | 17.5126 | 149.1306 | 83.7674 | 6.2326 | 150.514 | 134.0364 | 0 | 17.8875 | 0.2 | 0 | 3.4645 | 21.352 | 4.2 | 4.8673 | 1.0705 | 0.018742
2016-08-03 22:00 | 61.1767 | 22.0367 | 39.14 | 454.5548 | 17.5018 | 164.1313 | 85.0604 | 4.9396 | 164.8262 | 142.1552 | 0 | 16.5275 | 0.2 | 0 | 3.0588 | 19.5863 | 4.1 | 4.7121 | 1.071 | 0.017201
2016-08-03 23:00 | 53.0633 | 20.2233 | 32.84 | 422.4064 | 17.4909 | 179.1321 | 85.541 | 4.459 | 179.1697 | 145.5319 | 0 | 15.1675 | 0.2 | 0 | 2.6532 | 17.8207 | 4.1 | 4.6569 | 1.0712 | 0.015653
2016-08-04 | 44.95 | 18.41 | 26.54 | 315.7965 | 17.48 | -165.8672 | 85.1791 | 4.8209 | -166.4837 | 142.8483 | 0 | 13.8075 | 0.2 | 0 | 2.2475 | 16.055 | 4.1 | 4.6017 | 1.0714 | 0.014105
2016-08-04 01:00 | 69.3033 | 36.89 | 32.4133 | 310.009 | 17.4691 | -150.8664 | 83.9984 | 6.0016 | -152.1633 | 135.1808 | 0 | 27.6675 | 0.2 | 0 | 3.4652 | 31.1327 | 4.4 | 5.3729 | 1.0687 | 0.027282
2016-08-04 02:00 | 93.6567 | 55.37 | 38.2867 | 277.6804 | 17.4582 | -135.8656 | 82.0748 | 7.9252 | -137.881 | 124.5623 | 0 | 41.5275 | 0.2 | 0 | 4.6828 | 46.2103 | 4.5 | 5.9441 | 1.0667 | 0.04042
2016-08-04 03:00 | 118.01 | 73.85 | 44.16 | 242.9948 | 17.4472 | -120.8648 | 79.5293 | 10.4707 | -123.6171 | 112.3719 | 0 | 55.3875 | 0.2 | 0 | 5.9005 | 61.288 | 4.3 | 6.2152 | 1.0657 | 0.05356
2016-08-04 04:00 | 161.5767 | 90.5633 | 71.0133 | 304.6315 | 17.4363 | -105.8641 | 76.5196 | 13.4804 | -109.3152 | 99.3232 | 0 | 67.9225 | 0.2 | 0 | 8.0788 | 76.0013 | 4.3 | 6.675 | 1.0641 | 0.066318
2016-08-04 05:00 | 205.1433 | 107.2767 | 97.8667 | 339.2176 | 17.4254 | -90.8633 | 73.2314 | 16.7686 | -94.8853 | 85.777 | 24.9795 | 80.4575 | 0.2 | 0 | 10.2572 | 115.6941 | 4.3 | 7.9154 | 1.0598 | 0.10054
2016-08-04 06:00 | 248.71 | 123.99 | 124.72 | 362.422 | 17.4144 | -75.8625 | 69.8713 | 20.1287 | -80.2159 | 71.926 | 112.4398 | 92.9925 | 0.2 | 0 | 12.4355 | 217.8678 | 4.5 | 11.3084 | 1.0479 | 0.18721
2016-08-04 07:00 | 300.4967 | 151.5467 | 148.95 | 375.9695 | 17.4035 | -60.8617 | 66.6607 | 23.3393 | -65.1947 | 57.8805 | 199.8983 | 113.66 | 0.2 | 0 | 15.0248 | 328.5831 | 4.4 | 14.6682 | 1.0362 | 0.27918
2016-08-04 08:00 | 352.2833 | 179.1033 | 173.18 | 392.6214 | 17.3925 | -45.8609 | 63.8268 | 26.1732 | -49.7367 | 43.7084 | 283.8125 | 134.3275 | 0.2 | 0 | 17.6142 | 435.7542 | 5 | 18.6173 | 1.0223 | 0.3653
2016-08-04 09:00 | 404.07 | 206.66 | 197.41 | 414.9123 | 17.3815 | -30.8601 | 61.5894 | 28.4106 | -33.8177 | 29.4551 | 361.2814 | 154.995 | 0.2 | 0 | 20.2035 | 536.4799 | 5.6 | 22.365 | 1.0092 | 0.44397
2016-08-04 10:00 | 409.6667 | 212.5467 | 197.12 | 395.903 | 17.3706 | -15.8593 | 60.1389 | 29.8611 | -17.5021 | 15.1537 | 382.1366 | 159.41 | 0.2 | 0 | 20.4833 | 562.03 | 5.5 | 23.0634 | 1.0068 | 0.46399
2016-08-04 11:00 | 415.2633 | 218.4333 | 196.83 | 389.0667 | 17.3596 | -0.85851 | 59.6087 | 30.3913 | -0.94994 | 0.90952 | 389.0177 | 163.825 | 0.2 | 0 | 20.7632 | 573.6059 | 5.8 | 23.7252 | 1.0045 | 0.47246
2016-08-04 12:00 | 420.86 | 224.32 | 196.54 | 393.6804 | 17.3486 | 14.1423 | 60.0504 | 29.9496 | 15.6142 | 13.5153 | 382.7784 | 168.24 | 0.2 | 0 | 21.043 | 572.0614 | 5.4 | 23.2769 | 1.006 | 0.47192
2016-08-04 13:00 | 380.46 | 201.8067 | 178.6533 | 373.4831 | 17.3376 | 29.1431 | 61.4227 | 28.5773 | 31.962 | 27.8227 | 330.3071 | 151.355 | 0.2 | 0 | 19.023 | 500.6851 | 5.8 | 21.4464 | 1.0124 | 0.41567
2016-08-04 14:00 | 340.06 | 179.2933 | 160.7667 | 361.5724 | 17.3266 | 44.1439 | 63.6002 | 26.3998 | 47.925 | 42.0875 | 268.3306 | 134.47 | 0.2 | 0 | 17.003 | 419.8036 | 5.8 | 18.9189 | 1.0213 | 0.35157
2016-08-04 15:00 | 299.66 | 156.78 | 142.88 | 356.8553 | 17.3156 | 59.1448 | 66.3977 | 23.6023 | 63.4287 | 56.2776 | 198.1154 | 117.585 | 0.2 | 0 | 14.983 | 330.6834 | 5.3 | 15.6339 | 1.0328 | 0.28005
2016-08-04 16:00 | 231.1033 | 135.1333 | 95.97 | 275.294 | 17.3045 | 74.1456 | 69.5977 | 20.4023 | 78.4896 | 70.3498 | 92.5748 | 101.35 | 0.2 | 0 | 11.5552 | 205.4799 | 5.1 | 11.5212 | 1.0472 | 0.17644
2016-08-04 17:00 | 162.5467 | 113.4867 | 49.06 | 167.5454 | 17.2935 | 89.1464 | 72.9734 | 17.0266 | 93.1884 | 84.2406 | 16.8134 | 85.115 | 0.2 | 0 | 8.1273 | 110.0557 | 4.7 | 8.1392 | 1.059 | 0.095571
2016-08-04 18:00 | 93.99 | 91.84 | 2.15 | 9.0795 | 17.2825 | 104.1473 | 76.3024 | 13.6976 | 107.6369 | 97.8471 | 0 | 68.88 | 0.2 | 0 | 4.6995 | 73.5795 | 5.1 | 7.3994 | 1.0616 | 0.064052
2016-08-04 19:00 | 82.4033 | 69.0567 | 13.3467 | 72.3946 | 17.2714 | 119.1481 | 79.3762 | 10.6238 | 121.9481 | 110.9911 | 0 | 51.7925 | 0.2 | 0 | 4.1202 | 55.9127 | 4.8 | 6.5473 | 1.0646 | 0.048809
2016-08-04 20:00 | 70.8167 | 46.2733 | 24.5433 | 176.4883 | 17.2603 | 134.149 | 82.0063 | 7.9937 | 136.216 | 123.3411 | 0 | 34.705 | 0.2 | 0 | 3.5408 | 38.2458 | 4.8 | 5.9952 | 1.0665 | 0.033448
2016-08-04 21:00 | 59.23 | 23.49 | 35.74 | 343.6909 | 17.2493 | 149.1498 | 84.0311 | 5.9689 | 150.5015 | 134.2412 | 0 | 17.6175 | 0.2 | 0 | 2.9615 | 20.579 | 4.3 | 4.9431 | 1.0702 | 0.018059
2016-08-04 22:00 | 49.25 | 21.5133 | 27.7367 | 340.2803 | 17.2382 | 164.1507 | 85.3246 | 4.6754 | 164.8284 | 142.4014 | 0 | 16.135 | 0.2 | 0 | 2.4625 | 18.5975 | 5 | 5.5812 | 1.068 | 0.016286
2016-08-04 23:00 | 39.27 | 19.5367 | 19.7333 | 269.752 | 17.2271 | 179.1516 | 85.8049 | 4.1951 | 179.1874 | 145.796 | 0 | 14.6525 | 0.2 | 0 | 1.9635 | 16.616 | 4.8 | 5.3193 | 1.0689 | 0.014564
2016-08-05 | 29.29 | 17.56 | 11.73 | 147.5935 | 17.216 | -165.8476 | 85.4416 | 4.5584 | -166.4503 | 143.0844 | 0 | 13.17 | 0.2 | 0 | 1.4645 | 14.6345 | 4.7 | 5.1573 | 1.0694 | 0.012834
2016-08-05 01:00 | 49.9733 | 27.14 | 22.8333 | 228.2554 | 17.2049 | -150.8467 | 84.2589 | 5.7411 | -152.1152 | 135.3664 | 0 | 20.355 | 0.2 | 0 | 2.4987 | 22.8537 | 3.2 | 3.9142 | 1.0738 | 0.020123
2016-08-05 02:00 | 70.6567 | 36.72 | 33.9367 | 254.3615 | 17.1938 | -135.8458 | 82.3328 | 7.6672 | -137.8198 | 124.7021 | 0 | 27.54 | 0.2 | 0 | 3.5328 | 31.0728 | 3.4 | 4.371 | 1.0722 | 0.027319
2016-08-05 03:00 | 91.34 | 46.3 | 45.04 | 253.9705 | 17.1827 | -120.8449 | 79.7849 | 10.2151 | -123.5453 | 112.4765 | 0 | 34.725 | 0.2 | 0 | 4.567 | 39.292 | 3.7 | 4.9279 | 1.0703 | 0.034483
2016-08-05 04:00 | 117.6 | 70.6667 | 46.9333 | 205.1261 | 17.1716 | -105.844 | 76.7734 | 13.2266 | -109.2354 | 99.401 | 0 | 53 | 0.2 | 0 | 5.88 | 58.88 | 4.2 | 6.04 | 1.0664 | 0.051486
2016-08-05 05:00 | 143.86 | 95.0333 | 48.8267 | 171.7573 | 17.1605 | -90.8432 | 73.4844 | 16.5156 | -94.8007 | 85.8337 | 12.4784 | 71.275 | 0.2 | 0 | 7.193 | 90.9464 | 4.6 | 7.4421 | 1.0615 | 0.079159
2016-08-05 06:00 | 170.12 | 119.4 | 50.72 | 149.1877 | 17.1493 | -75.8423 | 70.1247 | 19.8753 | -80.1302 | 71.9654 | 46.1871 | 89.55 | 0.2 | 0 | 8.506 | 144.2431 | 4.9 | 9.4076 | 1.0546 | 0.12473
2016-08-05 07:00 | 242.0767 | 149.9667 | 92.11 | 234.9231 | 17.1382 | -60.8414 | 66.9157 | 23.0843 | -65.1122 | 57.9052 | 124.8196 | 112.475 | 0.2 | 0 | 12.1038 | 249.3984 | 4.7 | 12.4937 | 1.0438 | 0.21346
2016-08-05 08:00 | 314.0333 | 180.5333 | 133.5 | 305.4595 | 17.127 | -45.8405 | 64.0844 | 25.9156 | -49.6621 | 43.7201 | 220.763 | 135.4 | 0.2 | 0 | 15.7017 | 371.8647 | 5.1 | 16.7208 | 1.029 | 0.31377
2016-08-05 09:00 | 385.99 | 211.1 | 174.89 | 370.7035 | 17.1159 | -30.8395 | 61.8502 | 28.1498 | -33.7559 | 29.4545 | 322.7888 | 158.325 | 0.2 | 0 | 19.2995 | 500.4133 | 5.8 | 21.4379 | 1.0125 | 0.41545
2016-08-05 10:00 | 397.5167 | 205.0667 | 192.45 | 389.6527 | 17.1047 | -15.8386 | 60.4027 | 29.5973 | -17.4577 | 15.1401 | 376.1278 | 153.8 | 0.2 | 0 | 19.8758 | 549.8036 | 6.2 | 23.3814 | 1.0057 | 0.45339
2016-08-05 11:00 | 409.0433 | 199.0333 | 210.01 | 418.4359 | 17.0935 | -0.83771 | 59.8747 | 30.1253 | -0.92575 | 0.81095 | 418.394 | 149.275 | 0.2 | 0 | 20.4522 | 588.1211 | 6 | 24.3788 | 1.0022 | 0.48331
2016-08-05 12:00 | 420.57 | 193 | 227.57 | 459.5569 | 17.0823 | 14.1632 | 60.3174 | 29.6826 | 15.6176 | 13.5401 | 446.7842 | 144.75 | 0.2 | 0 | 21.0285 | 612.5627 | 6 | 25.1426 | 0.9995 | 0.50205
2016-08-05 13:00 | 356.4267 | 195.5333 | 160.8933 | 339.2598 | 17.0711 | 29.1641 | 61.6896 | 28.3104 | 31.9468 | 27.8608 | 299.9348 | 146.65 | 0.2 | 0 | 17.8213 | 464.4061 | 6.3 | 20.8127 | 1.0147 | 0.38639
2016-08-05 14:00 | 292.2833 | 198.0667 | 94.2167 | 213.9013 | 17.0599 | 44.1651 | 63.8663 | 26.1337 | 47.8951 | 42.1378 | 158.615 | 148.55 | 0.2 | 0 | 14.6142 | 321.7792 | 5.4 | 15.4556 | 1.0334 | 0.27267
2016-08-05 15:00 | 228.14 | 200.6 | 27.54 | 69.5205 | 17.0487 | 59.166 | 66.6628 | 23.3372 | 63.3889 | 56.3405 | 38.5321 | 150.45 | 0.2 | 0 | 11.407 | 200.3891 | 5.5 | 11.7622 | 1.0463 | 0.17193
2016-08-05 16:00 | 190.0467 | 161.2833 | 28.7633 | 83.5467 | 17.0375 | 74.167 | 69.8622 | 20.1378 | 78.4449 | 70.427 | 27.9888 | 120.9625 | 0.2 | 0 | 9.5023 | 158.4537 | 5.6 | 10.5517 | 1.0506 | 0.1365
2016-08-05 17:00 | 151.9533 | 121.9667 | 29.9867 | 103.9765 | 17.0263 | 89.1679 | 73.2379 | 16.7621 | 93.1434 | 84.3341 | 10.2654 | 91.475 | 0.2 | 0 | 7.5977 | 109.338 | 4.9 | 8.3168 | 1.0584 | 0.094892
2016-08-05 18:00 | 113.86 | 82.65 | 31.21 | 134.3531 | 17.015 | 104.1689 | 76.5676 | 13.4324 | 107.5956 | 97.9603 | 0 | 61.9875 | 0.2 | 0 | 5.693 | 67.6805 | 4.7 | 6.815 | 1.0636 | 0.05903
2016-08-05 19:00 | 94.1667 | 62.95 | 31.2167 | 173.6292 | 17.0038 | 119.1698 | 79.6425 | 10.3575 | 121.9143 | 111.129 | 0 | 47.2125 | 0.2 | 0 | 4.7083 | 51.9208 | 4.8 | 6.4225 | 1.065 | 0.045343
2016-08-05 20:00 | 74.4733 | 43.25 | 31.2233 | 232.2503 | 16.9925 | 134.1708 | 82.2739 | 7.7261 | 136.1926 | 123.5107 | 0 | 32.4375 | 0.2 | 0 | 3.7237 | 36.1612 | 4.4 | 5.53 | 1.0681 | 0.031673
2016-08-05 21:00 | 54.78 | 23.55 | 31.23 | 314.4222 | 16.9813 | 149.1717 | 84.2997 | 5.7003 | 150.4911 | 134.4506 | 0 | 17.6625 | 0.2 | 0 | 2.739 | 20.4015 | 4.8 | 5.4375 | 1.0685 | 0.017875
2016-08-05 22:00 | 47.62 | 22.64 | 24.98 | 325.1265 | 16.97 | 164.1727 | 85.5935 | 4.4065 | 164.8328 | 142.6526 | 0 | 16.98 | 0.2 | 0 | 2.381 | 19.361 | 5 | 5.605 | 1.0679 | 0.016954
2016-08-05 23:00 | 40.46 | 21.73 | 18.73 | 273.5094 | 16.9587 | 179.1737 | 86.0733 | 3.9267 | 179.2078 | 146.0648 | 0 | 16.2975 | 0.2 | 0 | 2.023 | 18.3205 | 4.8 | 5.3725 | 1.0687 | 0.016055
2016-08-06 | 33.3 | 20.82 | 12.48 | 166.7793 | 16.9475 | -165.8253 | 85.7086 | 4.2914 | -166.4141 | 143.3233 | 0 | 15.615 | 0.2 | 0 | 1.665 | 17.28 | 4.7 | 5.24 | 1.0692 | 0.01515
2016-08-06 01:00 | 61.43 | 29.41 | 32.02 | 335.5143 | 16.9362 | -150.8243 | 84.5236 | 5.4764 | -152.064 | 135.553 | 0 | 22.0575 | 0.2 | 0 | 3.0715 | 25.129 | 3.9 | 4.6853 | 1.0711 | 0.022071
2016-08-06 02:00 | 89.56 | 38 | 51.56 | 400.0515 | 16.9249 | -135.8234 | 82.5949 | 7.4051 | -137.7555 | 124.8419 | 0 | 28.5 | 0.2 | 0 | 4.478 | 32.978 | 4.3 | 5.3306 | 1.0688 | 0.028904
2016-08-06 03:00 | 117.69 | 46.59 | 71.1 | 411.263 | 16.9136 | -120.8224 | 80.0446 | 9.9554 | -123.47 | 112.5805 | 0 | 34.9425 | 0.2 | 0 | 5.8845 | 40.827 | 3.7 | 4.9758 | 1.0701 | 0.035824
2016-08-06 04:00 | 149.7067 | 88.9233 | 60.7833 | 270.8447 | 16.9023 | -105.8214 | 77.0311 | 12.9689 | -109.1521 | 99.4778 | 0 | 66.6925 | 0.2 | 0 | 7.4853 | 74.1778 | 4.2 | 6.5181 | 1.0647 | 0.06476
2016-08-06 05:00 | 181.7233 | 131.2567 | 50.4667 | 180.2532 | 16.8909 | -90.8204 | 73.7412 | 16.2588 | -94.7126 | 85.8893 | 12.9212 | 98.4425 | 0.2 | 0 | 9.0862 | 120.4499 | 3.3 | 7.0641 | 1.0628 | 0.10497
2016-08-06 06:00 | 213.74 | 173.59 | 40.15 | 119.5834 | 16.8796 | -75.8194 | 70.3819 | 19.6181 | -80.041 | 72.0038 | 36.9458 | 130.1925 | 0.2 | 0 | 10.687 | 177.8253 | 3.8 | 9.357 | 1.0548 | 0.1538
2016-08-06 07:00 | 261.6467 | 180.1833 | 81.4633 | 209.998 | 16.8683 | -60.8183 | 67.1746 | 22.8254 | -65.0261 | 57.929 | 111.5025 | 135.1375 | 0.2 | 0 | 13.0823 | 259.7223 | 4 | 12.1163 | 1.0451 | 0.22258
2016-08-06 08:00 | 309.5533 | 186.7767 | 122.7767 | 283.5924 | 16.8569 | -45.8173 | 64.3461 | 25.6539 | -49.5841 | 43.7311 | 204.9215 | 140.0825 | 0.2 | 0 | 15.4777 | 360.4816 | 4.6 | 15.8651 | 1.032 | 0.30505
2016-08-06 09:00 | 357.46 | 193.37 | 164.09 | 350.8482 | 16.8456 | -30.8163 | 62.1152 | 27.8848 | -33.6909 | 29.4539 | 305.5017 | 145.0275 | 0.2 | 0 | 17.873 | 468.4022 | 5.9 | 20.5376 | 1.0156 | 0.39009
2016-08-06 10:00 | 358.49 | 194.1333 | 164.3567 | 335.541 | 16.8342 | -15.8153 | 60.6709 | 29.3291 | -17.4102 | 15.1287 | 323.9118 | 145.6 | 0.2 | 0 | 17.9245 | 487.4363 | 6.4 | 21.6324 | 1.0118 | 0.40441
2016-08-06 11:00 | 359.52 | 194.8967 | 164.6233 | 330.6997 | 16.8229 | -0.81426 | 60.1452 | 29.8548 | -0.89868 | 0.79227 | 330.6681 | 146.1725 | 0.2 | 0 | 17.976 | 494.8166 | 6.9 | 22.363 | 1.0092 | 0.40949
2016-08-06 12:00 | 360.55 | 195.66 | 164.89 | 335.7778 | 16.8115 | 14.1868 | 60.5891 | 29.4109 | 15.6237 | 13.5728 | 326.4004 | 146.745 | 0.2 | 0 | 18.0275 | 491.1729 | 6.8 | 22.1492 | 1.01 | 0.40678
2016-08-06 13:00 | 329.2 | 154.43 | 174.77 | 371.7976 | 16.8001 | 29.1878 | 61.9613 | 28.0387 | 31.9339 | 27.9042 | 328.5693 | 115.8225 | 0.2 | 0 | 16.46 | 460.8518 | 6.1 | 20.5016 | 1.0157 | 0.38385
2016-08-06 14:00 | 297.85 | 113.2 | 184.65 | 423.2989 | 16.7887 | 44.1889 | 64.1373 | 25.8627 | 47.8673 | 42.1925 | 313.619 | 84.9 | 0.2 | 0 | 14.8925 | 413.4115 | 6.1 | 19.0191 | 1.0209 | 0.34609
2016-08-06 15:00 | 266.5 | 71.97 | 194.53 | 496.4919 | 16.7773 | 59.1899 | 66.9329 | 23.0671 | 63.351 | 56.4076 | 274.6995 | 53.9775 | 0.2 | 0 | 13.325 | 342.002 | 5.7 | 16.3876 | 1.0301 | 0.2889
2016-08-06 16:00 | 195.28 | 65.0033 | 130.2767 | 383.327 | 16.7659 | 74.191 | 70.1318 | 19.8682 | 78.4019 | 70.508 | 127.9068 | 48.7525 | 0.2 | 0 | 9.764 | 186.4233 | 5.5 | 11.3257 | 1.0479 | 0.16018
2016-08-06 17:00 | 124.06 | 58.0367 | 66.0233 | 232.5662 | 16.7545 | 89.192 | 73.5075 | 16.4925 | 93.1001 | 84.4314 | 22.5676 | 43.5275 | 0.2 | 0 | 6.203 | 72.2981 | 5.9 | 8.1593 | 1.0589 | 0.062779
2016-08-06 18:00 | 52.84 | 51.07 | 1.77 | 7.7731 | 16.7431 | 104.1931 | 76.8378 | 13.1622 | 107.5561 | 98.0774 | 0 | 38.3025 | 0.2 | 0 | 2.642 | 40.9445 | 6.2 | 7.4795 | 1.0613 | 0.035633
2016-08-06 19:00 | 40.5067 | 39.3267 | 1.18 | 6.7379 | 16.7316 | 119.1941 | 79.9138 | 10.0862 | 121.8821 | 111.2709 | 0 | 29.495 | 0.2 | 0 | 2.0253 | 31.5203 | 6 | 6.985 | 1.0631 | 0.027476
2016-08-06 20:00 | 28.1733 | 27.5833 | 0.59 | 4.5481 | 16.7202 | 134.1952 | 82.5464 | 7.4536 | 136.1711 | 123.6845 | 0 | 20.6875 | 0.2 | 0 | 1.4087 | 22.0962 | 6.3 | 6.9905 | 1.063 | 0.019261
2016-08-06 21:00 | 15.84 | 15.84 | 0 | 0 | 16.7088 | 149.1963 | 84.5731 | 5.4269 | 150.4828 | 134.6647 | 0 | 11.88 | 0.2 | 0 | 0.792 | 12.672 | 6.1 | 6.496 | 1.0648 | 0.011064
2016-08-06 22:00 | 14.7567 | 14.72 | 0.036667 | 0.50877 | 16.6973 | 164.1974 | 85.8672 | 4.1328 | 164.8396 | 142.9089 | 0 | 11.04 | 0.2 | 0 | 0.73783 | 11.7778 | 6.1 | 6.4681 | 1.0649 | 0.010284
2016-08-06 23:00 | 13.6733 | 13.6 | 0.073333 | 1.1508 | 16.6859 | 179.1985 | 86.3463 | 3.6537 | 179.2307 | 146.3382 | 0 | 10.2 | 0.2 | 0 | 0.68367 | 10.8837 | 6 | 6.3401 | 1.0653 | 0.0095075
2016-08-07 | 12.59 | 12.48 | 0.11 | 1.5691 | 16.6744 | -165.8004 | 85.9799 | 4.0201 | -166.3751 | 143.5649 | 0 | 9.36 | 0.2 | 0 | 0.6295 | 9.9895 | 6 | 6.3122 | 1.0654 | 0.0087272
2016-08-07 01:00 | 23.6133 | 21.9067 | 1.7067 | 18.8038 | 16.6629 | -150.7994 | 84.7926 | 5.2074 | -152.0098 | 135.7406 | 0 | 16.43 | 0.2 | 0 | 1.1807 | 17.6107 | 5.8 | 6.3503 | 1.0653 | 0.015383
2016-08-07 02:00 | 34.6367 | 31.3333 | 3.3033 | 26.5809 | 16.6514 | -135.7983 | 82.8611 | 7.1389 | -137.6878 | 124.9816 | 0 | 23.5 | 0.2 | 0 | 1.7318 | 25.2318 | 5.7 | 6.4885 | 1.0648 | 0.022031
2016-08-07 03:00 | 45.66 | 40.76 | 4.9 | 29.1061 | 16.6399 | -120.7971 | 80.3081 | 9.6919 | -123.3914 | 112.6837 | 0 | 30.57 | 0.2 | 0 | 2.283 | 32.853 | 5.6 | 6.6267 | 1.0643 | 0.028672
2016-08-07 04:00 | 62.78 | 57.8533 | 4.9267 | 22.397 | 16.6284 | -105.796 | 77.2927 | 12.7073 | -109.0654 | 99.5536 | 0 | 43.39 | 0.2 | 0 | 3.139 | 46.529 | 5.6 | 7.054 | 1.0628 | 0.04055
2016-08-07 05:00 | 79.9 | 74.9467 | 4.9533 | 17.9725 | 16.6169 | -90.7949 | 74.0018 | 15.9982 | -94.621 | 85.9438 | 1.2713 | 56.21 | 0.2 | 0 | 3.995 | 61.4763 | 5.7 | 7.6211 | 1.0608 | 0.053477
2016-08-07 06:00 | 97.02 | 92.04 | 4.98 | 15.0247 | 16.6054 | -75.7938 | 70.643 | 19.357 | -79.9483 | 72.041 | 4.6327 | 69.03 | 0.2 | 0 | 4.851 | 78.5137 | 5.6 | 8.0536 | 1.0593 | 0.0682
2016-08-07 07:00 | 122.77 | 117.6833 | 5.0867 | 13.2571 | 16.5939 | -60.7927 | 67.4374 | 22.5626 | -64.9367 | 57.9518 | 7.0347 | 88.2625 | 0.2 | 0 | 6.1385 | 101.4357 | 5.7 | 8.8699 | 1.0565 | 0.087873
2016-08-07 08:00 | 148.52 | 143.3267 | 5.1933 | 12.1128 | 16.5824 | -45.7916 | 64.6118 | 25.3882 | -49.5027 | 43.7415 | 8.7511 | 107.495 | 0.2 | 0 | 7.426 | 123.6721 | 5.6 | 9.4648 | 1.0544 | 0.10693
2016-08-07 09:00 | 174.27 | 168.97 | 5.3 | 11.4338 | 16.5708 | -30.7904 | 62.3844 | 27.6156 | -33.6226 | 29.4534 | 9.9561 | 126.7275 | 0.2 | 0 | 8.7135 | 145.3971 | 5.6 | 10.1437 | 1.052 | 0.12542
2016-08-07 10:00 | 196.4 | 192.7333 | 3.6667 | 7.5496 | 16.5593 | -15.7893 | 60.9434 | 29.0566 | -17.3596 | 15.1198 | 7.2883 | 144.55 | 0.2 | 0 | 9.82 | 161.6583 | 5.7 | 10.7518 | 1.0499 | 0.13917
2016-08-07 11:00 | 218.53 | 216.4967 | 2.0333 | 4.1191 | 16.5477 | -0.78816 | 60.4203 | 29.5797 | -0.86874 | 0.86316 | 4.1186 | 162.3725 | 0.2 | 0 | 10.9265 | 177.4176 | 5.8 | 11.3443 | 1.0478 | 0.15244
2016-08-07 12:00 | 240.66 | 240.26 | 0.4 | 0.82159 | 16.5362 | 14.213 | 60.8655 | 29.1345 | 15.6324 | 13.6137 | 0.79851 | 180.195 | 0.2 | 0 | 12.033 | 193.0265 | 5.7 | 11.7321 | 1.0464 | 0.16563
2016-08-07 13:00 | 204.8633 | 204.5967 | 0.26667 | 0.57249 | 16.5246 | 29.2141 | 62.2378 | 27.7622 | 31.9234 | 27.9529 | 0.5057 | 153.4475 | 0.2 | 0 | 10.2432 | 164.1964 | 5.5 | 10.6311 | 1.0503 | 0.14141
2016-08-07 14:00 | 169.0667 | 168.9333 | 0.13333 | 0.30873 | 16.513 | 44.2153 | 64.4131 | 25.5869 | 47.8415 | 42.2517 | 0.22852 | 126.7 | 0.2 | 0 | 8.4533 | 135.3819 | 6.3 | 10.5307 | 1.0506 | 0.11664
2016-08-07 15:00 | 133.27 | 133.27 | 0 | 0 | 16.5015 | 59.2165 | 67.2079 | 22.7921 | 63.315 | 56.4788 | 0 | 99.9525 | 0.2 | 0 | 6.6635 | 106.616 | 5.6 | 8.9318 | 1.0562 | 0.092342
2016-08-07 16:00 | 116.22 | 114.1533 | 2.0667 | 6.1627 | 16.4899 | 74.2176 | 70.4063 | 19.5937 | 78.3607 | 70.593 | 2.0477 | 85.615 | 0.2 | 0 | 5.811 | 93.4737 | 5.9 | 8.8211 | 1.0566 | 0.080989
2016-08-07 17:00 | 99.17 | 95.0367 | 4.1333 | 14.7993 | 16.4783 | 89.2188 | 73.782 | 16.218 | 93.0584 | 84.5326 | 1.4101 | 71.2775 | 0.2 | 0 | 4.9585 | 77.6461 | 5.5 | 7.9264 | 1.0598 | 0.067475
2016-08-07 18:00 | 82.12 | 75.92 | 6.2 | 27.7989 | 16.4667 | 104.22 | 77.1129 | 12.8871 | 107.5182 | 98.1983 | 0 | 56.94 | 0.2 | 0 | 4.106 | 61.046 | 5.6 | 7.5077 | 1.0612 | 0.053122
2016-08-07 19:00 | 63.1867 | 57.7033 | 5.4833 | 32.1827 | 16.4551 | 119.2211 | 80.19 | 9.81 | 121.8517 | 111.4167 | 0 | 43.2775 | 0.2 | 0 | 3.1593 | 46.4368 | 4.6 | 6.0512 | 1.0663 | 0.040604
2016-08-07 20:00 | 44.2533 | 39.4867 | 4.7667 | 38.1567 | 16.4434 | 134.2223 | 82.8237 | 7.1763 | 136.1514 | 123.8624 | 0 | 29.615 | 0.2 | 0 | 2.2127 | 31.8277 | 4.9 | 5.8946 | 1.0669 | 0.027844
2016-08-07 21:00 | 25.32 | 21.27 | 4.05 | 45.1292 | 16.4318 | 149.2235 | 84.8512 | 5.1488 | 150.4765 | 134.8832 | 0 | 15.9525 | 0.2 | 0 | 1.266 | 17.2185 | 4.8 | 5.3381 | 1.0688 | 0.015091
2016-08-07 22:00 | 23.3333 | 20.63 | 2.7033 | 40.2134 | 16.4202 | 164.2247 | 86.1454 | 3.8546 | 164.8487 | 143.1701 | 0 | 15.4725 | 0.2 | 0 | 1.1667 | 16.6392 | 5 | 5.52 | 1.0682 | 0.014574
2016-08-07 23:00 | 21.3467 | 19.99 | 1.3567 | 23.0358 | 16.4085 | 179.2259 | 86.6237 | 3.3763 | 179.2561 | 146.6161 | 0 | 14.9925 | 0.2 | 0 | 1.0673 | 16.0598 | 4.6 | 5.1019 | 1.0696 | 0.014086
2016-08-08 | 19.36 | 19.35 | 0.01 | 0.15312 | 16.3969 | -165.7729 | 86.2555 | 3.7445 | -166.3332 | 143.8092 | 0 | 14.5125 | 0.2 | 0 | 0.968 | 15.4805 | 3.5 | 3.9838 | 1.0736 | 0.013628
2016-08-08 01:00 | 40.4667 | 38.8567 | 1.61 | 18.7178 | 16.3852 | -150.7717 | 85.0656 | 4.9344 | -151.9526 | 135.929 | 0 | 29.1425 | 0.2 | 0 | 2.0233 | 31.1658 | 3.7 | 4.6739 | 1.0711 | 0.027374
2016-08-08 02:00 | 61.5733 | 58.3633 | 3.21 | 26.8406 | 16.3735 | -135.7705 | 83.1313 | 6.8687 | -137.617 | 125.121 | 0 | 43.7725 | 0.2 | 0 | 3.0787 | 46.8512 | 3.6 | 5.0641 | 1.0698 | 0.041099
2016-08-08 03:00 | 82.68 | 77.87 | 4.81 | 29.3745 | 16.3619 | -120.7693 | 80.5755 | 9.4245 | -123.3094 | 112.7862 | 0 | 58.4025 | 0.2 | 0 | 4.134 | 62.5365 | 3.4 | 5.3543 | 1.0688 | 0.054806
2016-08-08 04:00 | 123.24 | 106.8867 | 16.3533 | 75.9029 | 16.3502 | -105.7681 | 77.558 | 12.442 | -108.9752 | 99.6284 | 0 | 80.165 | 0.2 | 0 | 6.162 | 86.327 | 4.5 | 7.1977 | 1.0623 | 0.075199
2016-08-08 05:00 | 163.8 | 135.9033 | 27.8967 | 102.8758 | 16.3385 | -90.7668 | 74.2662 | 15.7338 | -94.5259 | 85.9971 | 7.1814 | 101.9275 | 0.2 | 0 | 8.19 | 117.2989 | 4.4 | 8.0656 | 1.0593 | 0.10189
2016-08-08 06:00 | 204.36 | 164.92 | 39.44 | 120.5784 | 16.3268 | -75.7656 | 70.9077 | 19.0923 | -79.8521 | 72.0771 | 37.1064 | 123.69 | 0.2 | 0 | 10.218 | 171.0144 | 4.7 | 10.0442 | 1.0523 | 0.14757
2016-08-08 07:00 | 261.6933 | 178.1567 | 83.5367 | 220.1862 | 16.3151 | -60.7644 | 67.704 | 22.296 | -64.8437 | 57.9736 | 116.7668 | 133.6175 | 0.2 | 0 | 13.0847 | 263.469 | 5 | 13.2334 | 1.0412 | 0.22494
2016-08-08 08:00 | 319.0267 | 191.3933 | 127.6333 | 300.6726 | 16.3034 | -45.7632 | 64.8814 | 25.1186 | -49.4179 | 43.7512 | 217.1907 | 143.545 | 0.2 | 0 | 15.9513 | 376.6871 | 5 | 16.7715 | 1.0288 | 0.31778
2016-08-08 09:00 | 376.36 | 204.63 | 171.73 | 373.8895 | 16.2917 | -30.7619 | 62.6576 | 27.3424 | -33.5511 | 29.4531 | 325.5674 | 153.4725 | 0.2 | 0 | 18.818 | 497.8579 | 5.5 | 21.0581 | 1.0138 | 0.41388
2016-08-08 10:00 | 399.18 | 174.3433 | 224.8367 | 467.0027 | 16.28 | -15.7607 | 61.2201 | 28.7799 | -17.3059 | 15.1135 | 450.8495 | 130.7575 | 0.2 | 0 | 19.959 | 601.566 | 5.3 | 24.0989 | 1.0032 | 0.49484
2016-08-08 11:00 | 422 | 144.0567 | 277.9433 | 567.9417 | 16.2682 | -0.75941 | 60.6997 | 29.3003 | -0.83596 | 1.0086 | 567.8537 | 108.0425 | 0.2 | 0 | 21.1 | 696.9962 | 5.5 | 27.2811 | 0.99202 | 0.56697
2016-08-08 12:00 | 444.82 | 113.77 | 331.05 | 686.0096 | 16.2565 | 14.2418 | 61.1464 | 28.8536 | 15.6438 | 13.6629 | 666.597 | 85.3275 | 0.2 | 0 | 22.241 | 774.1655 | 6.3 | 30.4927 | 0.98078 | 0.62261
2016-08-08 13:00 | 400.5033 | 109.3833 | 291.12 | 630.8743 | 16.2447 | 29.2431 | 62.519 | 27.481 | 31.9153 | 28.0071 | 556.9921 | 82.0375 | 0.2 | 0 | 20.0252 | 659.0548 | 4.9 | 25.4955 | 0.99827 | 0.53949
2016-08-08 14:00 | 356.1867 | 104.9967 | 251.19 | 587.6393 | 16.233 | 44.2444 | 64.6938 | 25.3062 | 47.8179 | 42.3155 | 434.5293 | 78.7475 | 0.2 | 0 | 17.8093 | 531.0861 | 5.4 | 21.9964 | 1.0105 | 0.44007
2016-08-08 15:00 | 311.87 | 100.61 | 211.26 | 551.7656 | 16.2212 | 59.2456 | 67.4878 | 22.5122 | 63.2809 | 56.5542 | 304.1046 | 75.4575 | 0.2 | 0 | 15.5935 | 395.1556 | 4.7 | 17.0486 | 1.0278 | 0.33305
2016-08-08 16:00 | 264 | 85.47 | 178.53 | 539.7722 | 16.2094 | 74.2469 | 70.6857 | 19.3143 | 78.3213 | 70.6819 | 178.5636 | 64.1025 | 0.2 | 0 | 13.2 | 255.8661 | 4.8 | 12.7958 | 1.0427 | 0.21877
2016-08-08 17:00 | 216.13 | 70.33 | 145.8 | 530.9397 | 16.1977 | 89.2482 | 74.0614 | 15.9386 | 93.0184 | 84.6376 | 49.6187 | 52.7475 | 0.2 | 0 | 10.8065 | 113.1727 | 5.3 | 8.8366 | 1.0566 | 0.098052
2016-08-08 18:00 | 168.26 | 55.19 | 113.07 | 518.043 | 16.1859 | 104.2495 | 77.3929 | 12.6071 | 107.4819 | 98.323 | 0 | 41.3925 | 0.2 | 0 | 8.413 | 49.8055 | 5.2 | 6.7564 | 1.0639 | 0.043448
2016-08-08 19:00 | 125.6167 | 44.4067 | 81.21 | 490.5557 | 16.1741 | 119.2508 | 80.471 | 9.529 | 121.8231 | 111.5664 | 0 | 33.305 | 0.2 | 0 | 6.2808 | 39.5858 | 4.8 | 6.0371 | 1.0664 | 0.034615
2016-08-08 20:00 | 82.9733 | 33.6233 | 49.35 | 411.1205 | 16.1623 | 134.252 | 83.1057 | 6.8943 | 136.1337 | 124.0444 | 0 | 25.2175 | 0.2 | 0 | 4.1487 | 29.3662 | 4.5 | 5.4177 | 1.0685 | 0.025731
2016-08-08 21:00 | 40.33 | 22.84 | 17.49 | 206.1865 | 16.1505 | 149.2533 | 85.134 | 4.866 | 150.4724 | 135.1061 | 0 | 17.13 | 0.2 | 0 | 2.0165 | 19.1465 | 3.9 | 4.4983 | 1.0718 | 0.016827
2016-08-08 22:00 | 27.7867 | 15.9967 | 11.79 | 189.245 | 16.1387 | 164.2546 | 86.4281 | 3.5719 | 164.8602 | 143.4361 | 0 | 11.9975 | 0.2 | 0 | 1.3893 | 13.3868 | 4.9 | 5.3183 | 1.0689 | 0.011733
2016-08-08 23:00 | 15.2433 | 9.1533 | 6.09 | 112.8115 | 16.1268 | 179.2559 | 86.9054 | 3.0946 | 179.2842 | 146.8984 | 0 | 6.865 | 0.2 | 0 | 0.76217 | 7.6272 | 5.2 | 5.4383 | 1.0685 | 0.0066825
2016-08-09 | 2.7 | 2.31 | 0.39 | 6.4535 | 16.115 | -165.7427 | 86.5354 | 3.4646 | -166.2886 | 144.056 | 0 | 1.7325 | 0.2 | 0 | 0.135 | 1.8675 | 5.8 | 5.8584 | 1.067 | 0.0016339
2016-08-09 01:00 | 3.7733 | 3.5133 | 0.26 | 3.2022 | 16.1032 | -150.7414 | 85.3427 | 4.6573 | -151.8923 | 136.1181 | 0 | 2.635 | 0.2 | 0 | 0.18867 | 2.8237 | 5.8 | 5.8882 | 1.0669 | 0.0024703
2016-08-09 02:00 | 4.8467 | 4.7167 | 0.13 | 1.132 | 16.0913 | -135.7401 | 83.4053 | 6.5947 | -137.543 | 125.2601 | 0 | 3.5375 | 0.2 | 0 | 0.24233 | 3.7798 | 6.1 | 6.2181 | 1.0657 | 0.0033032
2016-08-09 03:00 | 5.92 | 5.92 | 0 | 0 | 16.0795 | -120.7388 | 80.8467 | 9.1533 | -123.2241 | 112.8878 | 0 | 4.44 | 0.2 | 0 | 0.296 | 4.736 | 5.9 | 6.048 | 1.0663 | 0.0041411
2016-08-09 04:00 | 11.24 | 11.24 | 0 | 0 | 16.0676 | -105.7375 | 77.827 | 12.173 | -108.8816 | 99.702 | 0 | 8.43 | 0.2 | 0 | 0.562 | 8.992 | 6 | 6.281 | 1.0655 | 0.0078565
2016-08-09 05:00 | 16.56 | 16.56 | 0 | 0 | 16.0557 | -90.7361 | 74.5342 | 15.4658 | -94.4274 | 86.0492 | 0 | 12.42 | 0.2 | 0 | 0.828 | 13.248 | 5.9 | 6.314 | 1.0654 | 0.011574
2016-08-09 06:00 | 21.88 | 21.88 | 0 | 0 | 16.0439 | -75.7348 | 71.1762 | 18.8238 | -79.7525 | 72.1121 | 0 | 16.41 | 0.2 | 0 | 1.094 | 17.504 | 5.9 | 6.447 | 1.0649 | 0.015285
2016-08-09 07:00 | 47.5733 | 46.03 | 1.5433 | 4.1153 | 16.032 | -60.7335 | 67.9744 | 22.0256 | -64.7474 | 57.9945 | 2.1811 | 34.5225 | 0.2 | 0 | 2.3787 | 39.0823 | 5.8 | 7.0213 | 1.0629 | 0.034064
2016-08-09 08:00 | 73.2667 | 70.18 | 3.0867 | 7.3463 | 16.0201 | -45.7321 | 65.1549 | 24.8451 | -49.3298 | 43.7604 | 5.3058 | 52.635 | 0.2 | 0 | 3.6633 | 61.6041 | 5.9 | 7.8251 | 1.0601 | 0.053552
2016-08-09 09:00 | 98.96 | 94.33 | 4.63 | 10.1757 | 16.0082 | -30.7308 | 62.9348 | 27.0652 | -33.4764 | 29.4531 | 8.8606 | 70.7475 | 0.2 | 0 | 4.948 | 84.5561 | 5.6 | 8.2424 | 1.0587 | 0.073403
2016-08-09 10:00 | 97.9733 | 94.88 | 3.0933 | 6.483 | 15.9963 | -15.7294 | 61.501 | 28.499 | -17.2493 | 15.1102 | 6.2589 | 71.16 | 0.2 | 0 | 4.8987 | 82.3175 | 6.2 | 8.7724 | 1.0568 | 0.071334
2016-08-09 11:00 | 96.9867 | 95.43 | 1.5567 | 3.2092 | 15.9844 | -0.72804 | 60.9834 | 29.0166 | -0.80036 | 1.2051 | 3.2085 | 71.5725 | 0.2 | 0 | 4.8493 | 79.6303 | 5.7 | 8.1884 | 1.0588 | 0.069139
2016-08-09 12:00 | 96 | 95.98 | 0.02 | 0.041823 | 15.9725 | 14.2733 | 61.4317 | 28.5683 | 15.6577 | 13.7207 | 0.04063 | 71.985 | 0.2 | 0 | 4.8 | 76.8256 | 5.6 | 8.0008 | 1.0595 | 0.066745
2016-08-09 13:00 | 87.1633 | 87.15 | 0.013333 | 0.029174 | 15.9605 | 29.2747 | 62.8047 | 27.1953 | 31.9095 | 28.0669 | 0.025743 | 65.3625 | 0.2 | 0 | 4.3582 | 69.7464 | 5.9 | 8.0796 | 1.0592 | 0.060579
2016-08-09 14:00 | 78.3267 | 78.32 | 0.0066667 | 0.015762 | 15.9486 | 44.2761 | 64.9791 | 25.0209 | 47.7964 | 42.3839 | 0.011643 | 58.74 | 0.2 | 0 | 3.9163 | 62.668 | 5.9 | 7.8584 | 1.06 | 0.054471
2016-08-09 15:00 | 69.49 | 69.49 | 0 | 0 | 15.9367 | 59.2774 | 67.7724 | 22.2276 | 63.2487 | 56.6337 | 0 | 52.1175 | 0.2 | 0 | 3.4745 | 55.592 | 5.9 | 7.6372 | 1.0608 | 0.048356
2016-08-09 16:00 | 66.5567 | 66.5433 | 0.013333 | 0.040891 | 15.9247 | 74.2788 | 70.9698 | 19.0302 | 78.2836 | 70.7747 | 0.013465 | 49.9075 | 0.2 | 0 | 3.3278 | 53.2488 | 6 | 7.664 | 1.0607 | 0.046313
2016-08-09 17:00 | 63.6233 | 63.5967 | 0.026667 | 0.098826 | 15.9128 | 89.2802 | 74.3456 | 15.6544 | 92.9801 | 84.7465 | 0.0090488 | 47.6975 | 0.2 | 0 | 3.1812 | 50.8877 | 6.2 | 7.7902 | 1.0602 | 0.044241
2016-08-09 18:00 | 60.69 | 60.65 | 0.04 | 0.18743 | 15.9008 | 104.2816 | 77.6777 | 12.3223 | 107.4474 | 98.4516 | 0 | 45.4875 | 0.2 | 0 | 3.0345 | 48.522 | 6.3 | 7.8163 | 1.0601 | 0.042181
2016-08-09 19:00 | 45.6833 | 45.6567 | 0.026667 | 0.16602 | 15.8888 | 119.283 | 80.7567 | 9.2433 | 121.7962 | 111.7199 | 0 | 34.2425 | 0.2 | 0 | 2.2842 | 36.5267 | 6 | 7.1415 | 1.0625 | 0.031824
2016-08-09 20:00 | 30.6767 | 30.6633 | 0.013333 | 0.11587 | 15.8769 | 134.2844 | 83.3924 | 6.6076 | 136.1178 | 124.2304 | 0 | 22.9975 | 0.2 | 0 | 1.5338 | 24.5313 | 5.9 | 6.6666 | 1.0642 | 0.021406
2016-08-09 21:00 | 15.67 | 15.67 | 0 | 0 | 15.8649 | 149.2858 | 85.4213 | 4.5787 | 150.4704 | 135.3335 | 0 | 11.7525 | 0.2 | 0 | 0.7835 | 12.536 | 6 | 6.3918 | 1.0651 | 0.010949
2016-08-09 22:00 | 10.7967 | 10.7567 | 0.04 | 0.69811 | 15.8529 | 164.2872 | 86.7153 | 3.2847 | 164.8739 | 143.7068 | 0 | 8.0675 | 0.2 | 0 | 0.53983 | 8.6073 | 5.6 | 5.869 | 1.067 | 0.0075306
2016-08-09 23:00 | 5.9233 | 5.8433 | 0.08 | 0 | 15.8409 | 179.2886 | 87.1915 | 2.8085 | 179.3148 | 147.185 | 0 | 4.3825 | 0.2 | 0 | 0.29617 | 4.6787 | 5.7 | 5.8462 | 1.067 | 0.0040937
2016-08-10 | 1.05 | 0.93 | 0.12 | 2.1627 | 15.8289 | -165.71 | 86.8193 | 3.1807 | -166.2411 | 144.3052 | 0 | 0.6975 | 0.2 | 0 | 0.0525 | 0.75 | 6 | 6.0234 | 1.0664 | 0.00065585
2016-08-10 01:00 | 1.7067 | 1.4767 | 0.23 | 3.0142 | 15.8169 | -150.7085 | 85.6238 | 4.3762 | -151.829 | 136.3077 | 0 | 1.1075 | 0.2 | 0 | 0.085333 | 1.1928 | 6.4 | 6.4373 | 1.065 | 0.0010417
2016-08-10 02:00 | 2.3633 | 2.0233 | 0.34 | 3.0902 | 15.8048 | -135.7071 | 83.6831 | 6.3169 | -137.4658 | 125.3987 | 0 | 1.5175 | 0.2 | 0 | 0.11817 | 1.6357 | 6.4 | 6.4511 | 1.0649 | 0.0014283
2016-08-10 03:00 | 3.02 | 2.57 | 0.45 | 2.9156 | 15.7928 | -120.7057 | 81.1215 | 8.8785 | -123.1356 | 112.9885 | 0 | 1.9275 | 0.2 | 0 | 0.151 | 2.0785 | 6.6 | 6.665 | 1.0642 | 0.0018137
2016-08-10 04:00 | 7.4533 | 7.1533 | 0.3 | 1.4548 | 15.7808 | -105.7042 | 78.0996 | 11.9004 | -108.7846 | 99.7745 | 0 | 5.365 | 0.2 | 0 | 0.37267 | 5.7377 | 6.7 | 6.8793 | 1.0634 | 0.0050033
2016-08-10 05:00 | 11.8867 | 11.7367 | 0.15 | 0.57232 | 15.7687 | -90.7028 | 74.8057 | 15.1943 | -94.3255 | 86.1002 | 0.038924 | 8.8025 | 0.2 | 0 | 0.59433 | 9.4358 | 7 | 7.2949 | 1.062 | 0.0082168
2016-08-10 06:00 | 16.32 | 16.32 | 0 | 0 | 15.7567 | -75.7013 | 71.4482 | 18.5518 | -79.6495 | 72.146 | 0 | 12.24 | 0.2 | 0 | 0.816 | 13.056 | 6.4 | 6.808 | 1.0637 | 0.011388
2016-08-10 07:00 | 41.7533 | 41.7533 | 0 | 0 | 15.7446 | -60.6999 | 68.2484 | 21.7516 | -64.6478 | 58.0144 | 0 | 31.315 | 0.2 | 0 | 2.0877 | 33.4027 | 4.8 | 5.8438 | 1.067 | 0.029227
2016-08-10 08:00 | 67.1867 | 67.1867 | 0 | 0 | 15.7326 | -45.6984 | 65.4321 | 24.5679 | -49.2385 | 43.769 | 0 | 50.39 | 0.2 | 0 | 3.3593 | 53.7493 | 4.7 | 6.3797 | 1.0652 | 0.046947
2016-08-10 09:00 | 92.62 | 92.62 | 0 | 0 | 15.7205 | -30.697 | 63.2159 | 26.7841 | -33.3986 | 29.4536 | 0 | 69.465 | 0.2 | 0 | 4.631 | 74.096 | 4.3 | 6.6155 | 1.0643 | 0.064668
2016-08-10 10:00 | 100.62 | 100.62 | 0 | 0 | 15.7084 | -15.6955 | 61.7859 | 28.2141 | -17.1896 | 15.1101 | 0 | 75.465 | 0.2 | 0 | 5.031 | 80.496 | 4.7 | 7.2155 | 1.0622 | 0.070115
2016-08-10 11:00 | 108.62 | 108.62 | 0 | 0 | 15.6963 | -0.69405 | 61.2714 | 28.7286 | -0.76196 | 1.4343 | 0 | 81.465 | 0.2 | 0 | 5.431 | 86.896 | 4.3 | 7.0155 | 1.0629 | 0.07574
2016-08-10 12:00 | 116.62 | 116.62 | 0 | 0 | 15.6842 | 14.3074 | 61.7215 | 28.2785 | 15.6742 | 13.7871 | 0 | 87.465 | 0.2 | 0 | 5.831 | 93.296 | 4.6 | 7.5155 | 1.0612 | 0.081184
2016-08-10 13:00 | 102.3633 | 102.28 | 0.083333 | 0.18416 | 15.6721 | 29.3089 | 63.095 | 26.905 | 31.9061 | 28.1323 | 0.1624 | 76.71 | 0.2 | 0 | 5.1182 | 81.9906 | 4.8 | 7.3622 | 1.0617 | 0.071383
2016-08-10 14:00 | 88.1067 | 87.94 | 0.16667 | 0.39838 | 15.66 | 44.3104 | 65.269 | 24.731 | 47.7771 | 42.457 | 0.29392 | 65.955 | 0.2 | 0 | 4.4053 | 70.6543 | 4.7 | 6.9079 | 1.0633 | 0.061605
2016-08-10 15:00 | 73.85 | 73.6 | 0.25 | 0.66915 | 15.6479 | 59.3119 | 68.0617 | 21.9383 | 63.2185 | 56.7174 | 0.36721 | 55.2 | 0.2 | 0 | 3.6925 | 59.2597 | 4.7 | 6.5519 | 1.0646 | 0.051731
2016-08-10 16:00 | 80.79 | 75.5733 | 5.2167 | 16.2363 | 15.6358 | 74.3134 | 71.2586 | 18.7414 | 78.2477 | 70.8715 | 5.3204 | 56.68 | 0.2 | 0 | 4.0395 | 66.0399 | 4.6 | 6.6637 | 1.0642 | 0.057628
2016-08-10 17:00 | 87.73 | 77.5467 | 10.1833 | 38.431 | 15.6237 | 89.3149 | 74.6344 | 15.3656 | 92.9436 | 84.8591 | 3.4436 | 58.16 | 0.2 | 0 | 4.3865 | 65.9901 | 4.8 | 6.8622 | 1.0635 | 0.057547
2016-08-10 18:00 | 94.67 | 79.52 | 15.15 | 72.6712 | 15.6115 | 104.3164 | 77.9671 | 12.0329 | 107.4146 | 98.5838 | 0 | 59.64 | 0.2 | 0 | 4.7335 | 64.3735 | 4.3 | 6.3117 | 1.0654 | 0.056239
2016-08-10 19:00 | 71.68 | 59.8667 | 11.8133 | 75.9096 | 15.5994 | 119.3179 | 81.047 | 8.953 | 121.7711 | 111.8772 | 0 | 44.9 | 0.2 | 0 | 3.584 | 48.484 | 4.2 | 5.7151 | 1.0675 | 0.04244
2016-08-10 20:00 | 48.69 | 40.2133 | 8.4767 | 77.048 | 15.5872 | 134.3194 | 83.6836 | 6.3164 | 136.1039 | 124.4203 | 0 | 30.16 | 0.2 | 0 | 2.4345 | 32.5945 | 4.3 | 5.3186 | 1.0689 | 0.028569
2016-08-10 21:00 | 25.7 | 20.56 | 5.14 | 68.7607 | 15.5751 | 149.3209 | 85.713 | 4.287 | 150.4704 | 135.565 | 0 | 15.42 | 0.2 | 0 | 1.285 | 16.705 | 3.8 | 4.322 | 1.0724 | 0.014689
2016-08-10 22:00 | 21.0967 | 17.3867 | 3.71 | 0 | 15.5629 | 164.3224 | 87.0068 | 2.9932 | 164.89 | 143.9823 | 0 | 13.04 | 0.2 | 0 | 1.0548 | 14.0948 | 3.7 | 4.1405 | 1.073 | 0.012402
2016-08-10 23:00 | 16.4933 | 14.2133 | 2.28 | 0 | 15.5507 | 179.3239 | 87.4817 | 2.5183 | 179.348 | 147.4758 | 0 | 10.66 | 0.2 | 0 | 0.82467 | 11.4847 | 3.5 | 3.8589 | 1.074 | 0.010114
2016-08-11 | 11.89 | 11.04 | 0.85 | 0 | 15.5386 | -165.6745 | 87.1073 | 2.8927 | -166.1908 | 144.5566 | 0 | 8.28 | 0.2 | 0 | 0.5945 | 8.8745 | 2.5 | 2.7773 | 1.0778 | 0.0078431
2016-08-11 01:00 | 25.8967 | 23.4133 | 2.4833 | 34.8069 | 15.5264 | -150.673 | 85.9087 | 4.0913 | -151.7627 | 136.4977 | 0 | 17.56 | 0.2 | 0 | 1.2948 | 18.8548 | 2.9 | 3.4892 | 1.0753 | 0.016625
2016-08-11 02:00 | 39.9033 | 35.7867 | 4.1167 | 39.1537 | 15.5142 | -135.6715 | 83.9647 | 6.0353 | -137.3854 | 125.5368 | 0 | 26.84 | 0.2 | 0 | 1.9952 | 28.8352 | 3.6 | 4.5011 | 1.0717 | 0.025341
2016-08-11 03:00 | 53.91 | 48.16 | 5.75 | 38.4521 | 15.502 | -120.6699 | 81.3999 | 8.6001 | -123.0437 | 113.0882 | 0 | 36.12 | 0.2 | 0 | 2.6955 | 38.8155 | 3.5 | 4.713 | 1.071 | 0.034089
2016-08-11 04:00 | 79.7633 | 74.1967 | 5.5667 | 27.6271 | 15.4898 | -105.6684 | 78.3757 | 11.6243 | -108.6843 | 99.8458 | 0 | 55.6475 | 0.2 | 0 | 3.9882 | 59.6357 | 2.7 | 4.5636 | 1.0715 | 0.052399
2016-08-11 05:00 | 105.6167 | 100.2333 | 5.3833 | 20.9096 | 15.4776 | -90.6668 | 75.0808 | 14.9192 | -94.2202 | 86.1499 | 1.404 | 75.175 | 0.2 | 0 | 5.2808 | 81.8598 | 2.4 | 4.9581 | 1.0701 | 0.071834
2016-08-11 06:00 | 131.47 | 126.27 | 5.2 | 16.5817 | 15.4653 | -75.6653 | 71.7237 | 18.2763 | -79.5432 | 72.1787 | 5.0748 | 94.7025 | 0.2 | 0 | 6.5735 | 106.3508 | 2.1 | 5.4235 | 1.0685 | 0.093183
2016-08-11 07:00 | 165.2033 | 155.6233 | 9.58 | 26.1691 | 15.4531 | -60.6637 | 68.5259 | 21.4741 | -64.5449 | 58.0335 | 13.8545 | 116.7175 | 0.2 | 0 | 8.2602 | 138.8322 | 2.7 | 7.0385 | 1.0629 | 0.121
2016-08-11 08:00 | 198.9367 | 184.9767 | 13.96 | 33.9405 | 15.4409 | -45.6622 | 65.713 | 24.287 | -49.144 | 43.7773 | 24.5062 | 138.7325 | 0.2 | 0 | 9.9468 | 173.1855 | 2.7 | 8.112 | 1.0591 | 0.15041
2016-08-11 09:00 | 232.67 | 214.33 | 18.34 | 41.104 | 15.4286 | -30.6606 | 63.5008 | 26.4992 | -33.3177 | 29.4545 | 35.7912 | 160.7475 | 0.2 | 0 | 11.6335 | 208.1722 | 2.9 | 9.4054 | 1.0546 | 0.18002
2016-08-11 10:00 | 266.2267 | 229.5033 | 36.7233 | 78.4153 | 15.4164 | -15.659 | 62.0748 | 27.9252 | -17.127 | 15.1134 | 75.7031 | 172.1275 | 0.2 | 0 | 13.3113 | 261.1419 | 2.9 | 11.0607 | 1.0488 | 0.22458
2016-08-11 11:00 | 299.7833 | 244.6767 | 55.1067 | 115.7253 | 15.4041 | -0.65745 | 61.5635 | 28.4365 | -0.72081 | 1.6853 | 115.6753 | 183.5075 | 0.2 | 0 | 14.9892 | 314.1719 | 3.2 | 13.0179 | 1.0419 | 0.26842
2016-08-11 12:00 | 333.34 | 259.85 | 73.49 | 156.6174 | 15.3919 | 14.3441 | 62.0155 | 27.9845 | 15.6932 | 13.8624 | 152.0557 | 194.8875 | 0.2 | 0 | 16.667 | 363.6102 | 3.3 | 14.6628 | 1.0362 | 0.30895
2016-08-11 13:00 | 298.28 | 239.2433 | 59.0367 | 131.8017 | 15.3796 | 29.3457 | 63.3897 | 26.6103 | 31.905 | 28.2034 | 116.1536 | 179.4325 | 0.2 | 0 | 14.914 | 310.5001 | 3.3 | 13.0031 | 1.042 | 0.2653
2016-08-11 14:00 | 263.22 | 218.6367 | 44.5833 | 107.7713 | 15.3673 | 44.3473 | 65.5635 | 24.4365 | 47.7598 | 42.5347 | 79.4132 | 163.9775 | 0.2 | 0 | 13.161 | 256.5517 | 3.2 | 11.2172 | 1.0482 | 0.22052
2016-08-11 15:00 | 228.16 | 198.03 | 30.13 | 81.6875 | 15.355 | 59.3489 | 68.3556 | 21.6444 | 63.1902 | 56.8053 | 44.7227 | 148.5225 | 0.2 | 0 | 11.408 | 204.6532 | 4 | 10.3954 | 1.0511 | 0.17639
2016-08-11 16:00 | 179.7633 | 153.8867 | 25.8767 | 81.7738 | 15.3427 | 74.3505 | 71.5521 | 18.4479 | 78.2136 | 70.9722 | 26.6605 | 115.415 | 0.2 | 0 | 8.9882 | 151.0637 | 3.9 | 8.6207 | 1.0573 | 0.13097
2016-08-11 17:00 | 131.3667 | 109.7433 | 21.6233 | 83.1558 | 15.3304 | 89.3521 | 74.9279 | 15.0721 | 92.9087 | 84.9755 | 7.283 | 82.3075 | 0.2 | 0 | 6.5683 | 96.1588 | 4.1 | 7.105 | 1.0626 | 0.083789
2016-08-11 18:00 | 82.97 | 65.6 | 17.37 | 85.3766 | 15.3181 | 104.3537 | 78.2611 | 11.7389 | 107.3835 | 98.7198 | 0 | 49.2 | 0.2 | 0 | 4.1485 | 53.3485 | 4.3 | 5.9671 | 1.0666 | 0.04666
2016-08-11 19:00 | 60.99 | 49.2467 | 11.7433 | 78.0091 | 15.3058 | 119.3553 | 81.3419 | 8.6581 | 121.7478 | 112.0382 | 0 | 36.935 | 0.2 | 0 | 3.0495 | 39.9845 | 3.9 | 5.1495 | 1.0695 | 0.035065
2016-08-11 20:00 | 39.01 | 32.8933 | 6.1167 | 58.3168 | 15.2935 | 134.3569 | 83.9794 | 6.0206 | 136.0919 | 124.6141 | 0 | 24.67 | 0.2 | 0 | 1.9505 | 26.6205 | 3.9 | 4.7319 | 1.0709 | 0.023377
2016-08-11 21:00 | 17.03 | 16.54 | 0.49 | 7.0405 | 15.2812 | 149.3586 | 86.0091 | 3.9909 | 150.4726 | 135.8008 | 0 | 12.405 | 0.2 | 0 | 0.8515 | 13.2565 | 3.8 | 4.2143 | 1.0728 | 0.011661
2016-08-11 22:00 | 15.89 | 15.2133 | 0.67667 | 0 | 15.2688 | 164.3602 | 87.3025 | 2.6975 | 164.9085 | 144.2623 | 0 | 11.41 | 0.2 | 0 | 0.7945 | 12.2045 | 3.6 | 3.9814 | 1.0736 | 0.010744
2016-08-11 23:00 | 14.75 | 13.8867 | 0.86333 | 0 | 15.2565 | 179.3618 | 87.7761 | 2.2239 | 179.3838 | 147.7707 | 0 | 10.415 | 0.2 | 0 | 0.7375 | 11.1525 | 2.8 | 3.1485 | 1.0765 | 0.0098445
2016-08-12 | 13.61 | 12.56 | 1.05 | 0 | 15.2442 | -165.6366 | 87.3991 | 2.6009 | -166.1377 | 144.8101 | 0 | 9.42 | 0.2 | 0 | 0.6805 | 10.1005 | 3.6 | 3.9156 | 1.0738 | 0.0088936
2016-08-12 01:00 | 32.8667 | 28.4967 | 4.37 | 65.8933 | 15.2318 | -150.6349 | 86.1974 | 3.8026 | -151.6934 | 136.6881 | 0 | 21.3725 | 0.2 | 0 | 1.6433 | 23.0158 | 2.6 | 3.3192 | 1.0759 | 0.020305
2016-08-12 02:00 | 52.1233 | 44.4333 | 7.69 | 76.7539 | 15.2194 | -135.6333 | 84.2499 | 5.7501 | -137.3018 | 125.6742 | 0 | 33.325 | 0.2 | 0 | 2.6062 | 35.9312 | 2.5 | 3.6228 | 1.0748 | 0.031668
2016-08-12 03:00 | 71.38 | 60.37 | 11.01 | 76.1045 | 15.2071 | -120.6316 | 81.6819 | 8.3181 | -122.9486 | 113.1867 | 0 | 45.2775 | 0.2 | 0 | 3.569 | 48.8465 | 3.1 | 4.6265 | 1.0713 | 0.04291
2016-08-12 04:00 | 112.7533 | 92.8567 | 19.8967 | 101.1461 | 15.1947 | -105.63 | 78.6552 | 11.3448 | -108.5807 | 99.9159 | 0 | 69.6425 | 0.2 | 0 | 5.6377 | 75.2802 | 2.5 | 4.8525 | 1.0705 | 0.066083
2016-08-12 05:00 | 154.1267 | 125.3433 | 28.7833 | 113.877 | 15.1823 | -90.6283 | 75.3592 | 14.6408 | -94.1116 | 86.1984 | 7.5502 | 94.0075 | 0.2 | 0 | 7.7063 | 109.264 | 2 | 5.4145 | 1.0685 | 0.095738
2016-08-12 06:00 | 195.5 | 157.83 | 37.67 | 121.92 | 15.1699 | -75.6267 | 72.0026 | 17.9974 | -79.4336 | 72.2103 | 37.2495 | 118.3725 | 0.2 | 0 | 9.775 | 165.397 | 2.7 | 7.8687 | 1.06 | 0.14376
2016-08-12 07:00 | 237.3733 | 168.7267 | 68.6467 | 189.888 | 15.1575 | -60.625 | 68.807 | 21.193 | -64.4387 | 58.0517 | 100.4799 | 126.545 | 0.2 | 0 | 11.8687 | 238.8935 | 3.2 | 10.6654 | 1.0502 | 0.20572
2016-08-12 08:00 | 279.2467 | 179.6233 | 99.6233 | 244.9087 | 15.1451 | -45.6233 | 65.9974 | 24.0026 | -49.0463 | 43.7852 | 176.8092 | 134.7175 | 0.2 | 0 | 13.9623 | 325.4891 | 3.3 | 13.4715 | 1.0403 | 0.27767
2016-08-12 09:00 | 321.12 | 190.52 | 130.6 | 295.6955 | 15.1327 | -30.6216 | 63.7895 | 26.2105 | -33.2338 | 29.4562 | 257.4716 | 142.89 | 0.2 | 0 | 16.056 | 416.4176 | 3.7 | 16.7131 | 1.029 | 0.35137
2016-08-12 10:00 | 291.5267 | 198.2767 | 93.25 | 201.0577 | 15.1203 | -15.62 | 62.3676 | 27.6324 | -17.0615 | 15.1204 | 194.0971 | 148.7075 | 0.2 | 0 | 14.5763 | 357.3809 | 4.8 | 15.9682 | 1.0316 | 0.30232
2016-08-12 11:00 | 261.9333 | 206.0333 | 55.9 | 118.5242 | 15.1079 | -0.61828 | 61.8596 | 28.1404 | -0.67693 | 1.9514 | 118.4555 | 154.525 | 0.2 | 0 | 13.0967 | 286.0771 | 4.7 | 13.6399 | 1.0398 | 0.24391
2016-08-12 12:00 | 232.34 | 213.79 | 18.55 | 39.9242 | 15.0954 | 14.3834 | 62.3137 | 27.6863 | 15.7148 | 13.9466 | 38.7473 | 160.3425 | 0.2 | 0 | 11.617 | 210.7068 | 5.5 | 12.0846 | 1.0452 | 0.18059
2016-08-12 13:00 | 194.85 | 182.1133 | 12.7367 | 28.7348 | 15.083 | 29.3851 | 63.6887 | 26.3113 | 31.9062 | 28.2803 | 25.3051 | 136.585 | 0.2 | 0 | 9.7425 | 171.6326 | 5.4 | 10.7635 | 1.0498 | 0.14775
2016-08-12 14:00 | 157.36 | 150.4367 | 6.9233 | 16.9304 | 15.0706 | 44.3868 | 65.8624 | 24.1376 | 47.7447 | 42.6171 | 12.459 | 112.8275 | 0.2 | 0 | 7.868 | 133.1545 | 4.9 | 9.0611 | 1.0558 | 0.11528
2016-08-12 15:00 | 119.87 | 118.76 | 1.11 | 3.0495 | 15.0581 | 59.3885 | 68.654 | 21.346 | 63.1638 | 56.8974 | 1.6654 | 89.07 | 0.2 | 0 | 5.9935 | 96.7289 | 4.8 | 7.8228 | 1.0601 | 0.084086
2016-08-12 16:00 | 85.72 | 84.8967 | 0.82333 | 2.6431 | 15.0457 | 74.3902 | 71.8501 | 18.1499 | 78.1814 | 71.0767 | 0.85716 | 63.6725 | 0.2 | 0 | 4.286 | 68.8157 | 4.6 | 6.7505 | 1.0639 | 0.060033
2016-08-12 17:00 | 51.57 | 51.0333 | 0.53667 | 2.1045 | 15.0332 | 89.3919 | 75.2259 | 14.7741 | 92.8756 | 85.0956 | 0.17992 | 38.275 | 0.2 | 0 | 2.5785 | 41.0334 | 4.2 | 5.4823 | 1.0683 | 0.035946
2016-08-12 18:00 | 17.42 | 17.17 | 0.25 | 1.2604 | 15.0207 | 104.3936 | 78.5597 | 11.4403 | 107.3542 | 98.8594 | 0 | 12.8775 | 0.2 | 0 | 0.871 | 13.7485 | 3.8 | 4.2296 | 1.0727 | 0.012093
2016-08-12 19:00 | 12.98 | 12.8133 | 0.16667 | 1.1465 | 15.0082 | 119.3953 | 81.6412 | 8.3588 | 121.7263 | 112.2029 | 0 | 9.61 | 0.2 | 0 | 0.649 | 10.259 | 3.8 | 4.1206 | 1.0731 | 0.0090271
2016-08-12 20:00 | 8.54 | 8.4567 | 0.083333 | 0.83604 | 14.9958 | 134.3971 | 84.2794 | 5.7206 | 136.0818 | 124.8116 | 0 | 6.3425 | 0.2 | 0 | 0.427 | 6.7695 | 3.3 | 3.5115 | 1.0752 | 0.0059685
2016-08-12 21:00 | 4.1 | 4.1 | 0 | 0 | 14.9833 | 149.3988 | 86.3096 | 3.6904 | 150.4769 | 136.0407 | 0 | 3.075 | 0.2 | 0 | 0.205 | 3.28 | 4 | 4.1025 | 1.0731 | 0.0028863
2016-08-12 22:00 | 5.6767 | 5.5567 | 0.12 | 0 | 14.9708 | 164.4005 | 87.6024 | 2.3976 | 164.9293 | 144.5469 | 0 | 4.1675 | 0.2 | 0 | 0.28383 | 4.4513 | 3.9 | 4.0391 | 1.0734 | 0.0039179
2016-08-12 23:00 | 7.2533 | 7.0133 | 0.24 | 0 | 14.9583 | 179.4023 | 88.0744 | 1.9256 | 179.4222 | 148.0696 | 0 | 5.26 | 0.2 | 0 | 0.36267 | 5.6227 | 3.8 | 3.9757 | 1.0736 | 0.0049499
2016-08-13 | 8.83 | 8.47 | 0.36 | 0 | 14.9457 | -165.596 | 87.6949 | 2.3051 | -166.0818 | 145.0656 | 0 | 6.3525 | 0.2 | 0 | 0.4415 | 6.794 | 3.9 | 4.1123 | 1.0731 | 0.0059784
2016-08-13 01:00 | 23.0033 | 21.3433 | 1.66 | 27.1123 | 14.9332 | -150.5942 | 86.4898 | 3.5102 | -151.6211 | 136.8786 | 0 | 16.0075 | 0.2 | 0 | 1.1502 | 17.1577 | 3.4 | 3.9362 | 1.0737 | 0.015107
2016-08-13 02:00 | 37.1767 | 34.2167 | 2.96 | 31.1005 | 14.9207 | -135.5925 | 84.5386 | 5.4614 | -137.2152 | 125.8109 | 0 | 25.6625 | 0.2 | 0 | 1.8588 | 27.5213 | 3.4 | 4.26 | 1.0726 | 0.024206
2016-08-13 03:00 | 51.35 | 47.09 | 4.26 | 30.4853 | 14.9082 | -120.5907 | 81.9672 | 8.0328 | -122.8503 | 113.2842 | 0 | 35.3175 | 0.2 | 0 | 2.5675 | 37.885 | 3.3 | 4.4839 | 1.0718 | 0.033296
2016-08-13 04:00 | 83.3267 | 72.7733 | 10.5533 | 55.0028 | 14.8956 | -105.589 | 78.9381 | 11.0619 | -108.4739 | 99.9848 | 0 | 54.58 | 0.2 | 0 | 4.1663 | 58.7463 | 3 | 4.8358 | 1.0706 | 0.051572
2016-08-13 05:00 | 115.3033 | 98.4567 | 16.8467 | 67.9309 | 14.8831 | -90.5872 | 75.641 | 14.359 | -93.9998 | 86.2457 | 4.448 | 73.8425 | 0.2 | 0 | 5.7652 | 84.0557 | 3.5 | 6.1267 | 1.0661 | 0.073479
2016-08-13 06:00 | 147.28 | 124.14 | 23.14 | 76.0474 | 14.8705 | -75.5855 | 72.2849 | 17.7151 | -79.3207 | 72.2408 | 23.1957 | 93.105 | 0.2 | 0 | 7.364 | 123.6647 | 4.8 | 8.6645 | 1.0572 | 0.1072
2016-08-13 07:00 | 196.0567 | 154.1267 | 41.93 | 117.4911 | 14.858 | -60.5837 | 69.0914 | 20.9086 | -64.3293 | 58.0691 | 62.1405 | 115.595 | 0.2 | 0 | 9.8028 | 187.5383 | 4.8 | 10.6606 | 1.0502 | 0.1615
2016-08-13 08:00 | 244.8333 | 184.1133 | 60.72 | 150.977 | 14.8454 | -45.5819 | 66.2854 | 23.7146 | -48.9455 | 43.7928 | 108.9824 | 138.085 | 0.2 | 0 | 12.2417 | 259.309 | 4.4 | 12.5034 | 1.0437 | 0.22193
2016-08-13 09:00 | 293.61 | 214.1 | 79.51 | 181.9086 | 14.8328 | -30.5801 | 64.0818 | 25.9182 | -33.1468 | 29.4586 | 158.3899 | 160.575 | 0.2 | 0 | 14.6805 | 333.6454 | 4.5 | 14.9264 | 1.0353 | 0.28324
2016-08-13 10:00 | 295.1333 | 221.79 | 73.3433 | 159.7182 | 14.8202 | -15.5783 | 62.6642 | 27.3358 | -16.9932 | 15.1313 | 154.1808 | 166.3425 | 0.2 | 0 | 14.7567 | 335.28 | 4.9 | 15.3775 | 1.0337 | 0.28419
2016-08-13 11:00 | 296.6567 | 229.48 | 67.1767 | 143.8447 | 14.8077 | -0.57655 | 62.1597 | 27.8403 | -0.63036 | 2.2291 | 143.7358 | 172.11 | 0.2 | 0 | 14.8328 | 330.6787 | 4.5 | 14.8337 | 1.0356 | 0.2808
2016-08-13 12:00 | 298.18 | 237.17 | 61.01 | 132.6446 | 14.7951 | 14.4252 | 62.6161 | 27.3839 | 15.7388 | 14.0398 | 128.6821 | 177.8775 | 0.2 | 0 | 14.909 | 321.4686 | 5.5 | 15.5459 | 1.0331 | 0.27233
2016-08-13 13:00 | 258.85 | 205.7033 | 53.1467 | 121.2017 | 14.7825 | 29.427 | 63.9919 | 26.0081 | 31.9097 | 28.363 | 106.6521 | 154.2775 | 0.2 | 0 | 12.9425 | 273.8721 | 5.8 | 14.3585 | 1.0372 | 0.23294
2016-08-13 14:00 | 219.52 | 174.2367 | 45.2833 | 112.061 | 14.7699 | 44.4288 | 66.1656 | 23.8344 | 47.7316 | 42.7043 | 82.3496 | 130.6775 | 0.2 | 0 | 10.976 | 224.0031 | 5.2 | 12.2001 | 1.0448 | 0.19191
2016-08-13 15:00 | 180.19 | 142.77 | 37.42 | 104.2128 | 14.7572 | 59.4307 | 68.9567 | 21.0433 | 63.1393 | 56.9937 | 56.7679 | 107.0775 | 0.2 | 0 | 9.0095 | 172.8549 | 5.1 | 10.5017 | 1.0507 | 0.14893
2016-08-13 16:00 | 150.79 | 122.9533 | 27.8367 | 90.8256 | 14.7446 | 74.4325 | 72.1525 | 17.8475 | 78.1509 | 71.1852 | 29.2922 | 92.215 | 0.2 | 0 | 7.5395 | 129.0467 | 4.9 | 8.9327 | 1.0562 | 0.11177
2016-08-13 17:00 | 121.39 | 103.1367 | 18.2533 | 73.0424 | 14.732 | 89.4343 | 75.5284 | 14.4716 | 92.8442 | 85.2193 | 6.0875 | 77.3525 | 0.2 | 0 | 6.0695 | 89.5095 | 4.4 | 7.1972 | 1.0623 | 0.077971
2016-08-13 18:00 | 91.99 | 83.32 | 8.67 | 44.8844 | 14.7194 | 104.4361 | 78.8626 | 11.1374 | 107.3265 | 99.0025 | 0 | 62.49 | 0.2 | 0 | 4.5995 | 67.0895 | 5.7 | 7.7965 | 1.0602 | 0.058326
2016-08-13 19:00 | 68.6833 | 60.9 | 7.7833 | 55.5456 | 14.7067 | 119.4379 | 81.9449 | 8.0551 | 121.7066 | 112.3711 | 0 | 45.675 | 0.2 | 0 | 3.4342 | 49.1092 | 4.3 | 5.8347 | 1.0671 | 0.042971
2016-08-13 20:00 | 45.3767 | 38.48 | 6.8967 | 73.0662 | 14.6941 | 134.4398 | 84.5838 | 5.4162 | 136.0737 | 125.0129 | 0 | 28.86 | 0.2 | 0 | 2.2688 | 31.1288 | 4.1 | 5.0728 | 1.0697 | 0.027306
2016-08-13 21:00 | 22.07 | 16.06 | 6.01 | 101.7613 | 14.6814 | 149.4416 | 86.6142 | 3.3858 | 150.4833 | 136.2845 | 0 | 12.045 | 0.2 | 0 | 1.1035 | 13.1485 | 4.2 | 4.6109 | 1.0714 | 0.011551
2016-08-13 22:00 | 16.74 | 12.7233 | 4.0167 | 0 | 14.6688 | 164.4434 | 87.9064 | 2.0936 | 164.9524 | 144.8359 | 0 | 9.5425 | 0.2 | 0 | 0.837 | 10.3795 | 4.3 | 4.6244 | 1.0713 | 0.0091182
2016-08-13 23:00 | 11.41 | 9.3867 | 2.0233 | 0 | 14.6561 | 179.4453 | 88.3767 | 1.6233 | 179.4631 | 148.3725 | 0 | 7.04 | 0.2 | 0 | 0.5705 | 7.6105 | 4.1 | 4.3378 | 1.0723 | 0.0066919
2016-08-14 | 6.08 | 6.05 | 0.03 | 0 | 14.6434 | -165.5529 | 87.9944 | 2.0056 | -166.0231 | 145.3229 | 0 | 4.5375 | 0.2 | 0 | 0.304 | 4.8415 | 3.8 | 3.9513 | 1.0737 | 0.0042625
2016-08-14 01:00 | 17.7467 | 17.5433 | 0.20333 | 3.6264 | 14.6307 | -150.551 | 86.7858 | 3.2142 | -151.5458 | 137.0691 | 0 | 13.1575 | 0.2 | 0 | 0.88733 | 14.0448 | 3.7 | 4.1389 | 1.073 | 0.012358
2016-08-14 02:00 | 29.4133 | 29.0367 | 0.37667 | 4.1807 | 14.618 | -135.5492 | 84.8308 | 5.1692 | -137.1255 | 125.9467 | 0 | 21.7775 | 0.2 | 0 | 1.4707 | 23.2482 | 3.7 | 4.4265 | 1.072 | 0.020436
2016-08-14 03:00 | 41.08 | 40.53 | 0.55 | 4.0817 | 14.6054 | -120.5473 | 82.2559 | 7.7441 | -122.7488 | 113.3805 | 0 | 30.3975 | 0.2 | 0 | 2.054 | 32.4515 | 4.6 | 5.6141 | 1.0679 | 0.028416
2016-08-14 04:00 | 67.15 | 64.12 | 3.03 | 16.2062 | 14.5927 | -105.5455 | 79.2243 | 10.7757 | -108.3638 | 100.0523 | 0 | 48.09 | 0.2 | 0 | 3.3575 | 51.4475 | 4.9 | 6.5077 | 1.0647 | 0.044917
2016-08-14 05:00 | 93.22 | 87.71 | 5.51 | 22.6586 | 14.5799 | -90.5436 | 75.926 | 14.074 | -93.8847 | 86.2917 | 1.4655 | 65.7825 | 0.2 | 0 | 4.661 | 71.909 | 4.9 | 7.1472 | 1.0625 | 0.06265
2016-08-14 06:00 | 119.29 | 111.3 | 7.99 | 26.6749 | 14.5672 | -75.5417 | 72.5705 | 17.4295 | -79.2046 | 72.2703 | 8.1232 | 83.475 | 0.2 | 0 | 5.9645 | 97.5627 | 5.6 | 8.6488 | 1.0572 | 0.08458
2016-08-14 07:00 | 179.1733 | 122.7333 | 56.44 | 160.2582 | 14.5545 | -60.5398 | 69.3792 | 20.6208 | -64.2168 | 58.0858 | 84.7204 | 92.05 | 0.2 | 0 | 8.9587 | 185.729 | 5.9 | 11.704 | 1.0465 | 0.15939
2016-08-14 08:00 | 239.0567 | 134.1667 | 104.89 | 263.862 | 14.5418 | -45.538 | 66.5769 | 23.4231 | -48.8416 | 43.8001 | 190.4447 | 100.625 | 0.2 | 0 | 11.9528 | 303.0225 | 6 | 15.4695 | 1.0334 | 0.25677
2016-08-14 09:00 | 298.94 | 145.6 | 153.34 | 354.5949 | 14.5291 | -30.5361 | 64.3777 | 25.6223 | -33.0569 | 29.4619 | 308.7398 | 109.2 | 0.2 | 0 | 14.947 | 432.8868 | 6.1 | 19.6277 | 1.0188 | 0.36164
2016-08-14 10:00 | 288.44 | 156.6367 | 131.8033 | 289.9695 | 14.5163 | -15.5342 | 62.9645 | 27.0355 | -16.922 | 15.1463 | 279.8965 | 117.4775 | 0.2 | 0 | 14.422 | 411.796 | 6.3 | 19.1686 | 1.0204 | 0.34456
2016-08-14 11:00 | 277.94 | 167.6733 | 110.2667 | 238.5122 | 14.5036 | -0.53229 | 62.4637 | 27.5363 | -0.58116 | 2.5158 | 238.2823 | 125.755 | 0.2 | 0 | 13.897 | 377.9343 | 6.1 | 17.9104 | 1.0248 | 0.3176
2016-08-14 12:00 | 267.44 | 178.71 | 88.73 | 194.9268 | 14.4908 | 14.4696 | 62.9224 | 27.0776 | 15.7653 | 14.1421 | 189.0191 | 134.0325 | 0.2 | 0 | 13.372 | 336.4236 | 6.6 | 17.1132 | 1.0276 | 0.28348
2016-08-14 13:00 | 221.06 | 160.78 | 60.28 | 138.9998 | 14.4781 | 29.4715 | 64.2993 | 25.7007 | 31.9154 | 28.4516 | 122.2114 | 120.585 | 0.2 | 0 | 11.053 | 253.8494 | 6.2 | 14.1328 | 1.038 | 0.21607
2016-08-14 14:00 | 174.68 | 142.85 | 31.83 | 79.7383 | 14.4653 | 44.4734 | 66.473 | 23.527 | 47.7206 | 42.7963 | 58.5099 | 107.1375 | 0.2 | 0 | 8.734 | 174.3814 | 5.6 | 11.0494 | 1.0488 | 0.14997
2016-08-14 15:00 | 128.3 | 124.92 | 3.38 | 9.5462 | 14.4525 | 59.4753 | 69.2638 | 20.7362 | 63.1168 | 57.0942 | 5.1861 | 93.69 | 0.2 | 0 | 6.415 | 105.2911 | 6.4 | 9.6903 | 1.0536 | 0.090965
2016-08-14 16:00 | 106.8333 | 101.3367 | 5.4967 | 18.2381 | 14.4397 | 74.4773 | 72.4592 | 17.5408 | 78.1222 | 71.2975 | 5.8481 | 76.0025 | 0.2 | 0 | 5.3417 | 87.1923 | 5.6 | 8.3248 | 1.0584 | 0.075671
2016-08-14 17:00 | 85.3667 | 77.7533 | 7.6133 | 31.1113 | 14.4269 | 89.4792 | 75.8352 | 14.1648 | 92.8145 | 85.3468 | 2.5239 | 58.315 | 0.2 | 0 | 4.2683 | 65.1072 | 6 | 8.0346 | 1.0594 | 0.056558
2016-08-14 18:00 | 63.9 | 54.17 | 9.73 | 51.7833 | 14.4142 | 104.4811 | 79.1698 | 10.8302 | 107.3006 | 99.1492 | 0 | 40.6275 | 0.2 | 0 | 3.195 | 43.8225 | 5.1 | 6.4695 | 1.0649 | 0.038265
2016-08-14 19:00 | 46.3133 | 39.73 | 6.5833 | 48.8374 | 14.4014 | 119.483 | 82.2529 | 7.7471 | 121.6887 | 112.5428 | 0 | 29.7975 | 0.2 | 0 | 2.3157 | 32.1132 | 5.3 | 6.3035 | 1.0654 | 0.028056
2016-08-14 20:00 | 28.7267 | 25.29 | 3.4367 | 38.6029 | 14.3885 | 134.485 | 84.8924 | 5.1076 | 136.0675 | 125.2177 | 0 | 18.9675 | 0.2 | 0 | 1.4363 | 20.4038 | 4.8 | 5.4376 | 1.0685 | 0.017877
2016-08-14 21:00 | 11.14 | 10.85 | 0.29 | 5.4023 | 14.3757 | 149.4869 | 86.9229 | 3.0771 | 150.4918 | 136.5323 | 0 | 8.1375 | 0.2 | 0 | 0.557 | 8.6945 | 4.6 | 4.8717 | 1.0704 | 0.0076318
2016-08-14 22:00 | 8.7433 | 8.48 | 0.26333 | 0 | 14.3629 | 164.4888 | 88.2143 | 1.7857 | 164.9778 | 145.1292 | 0 | 6.36 | 0.2 | 0 | 0.43717 | 6.7972 | 4.5 | 4.7124 | 1.071 | 0.0059694
2016-08-14 23:00 | 6.3467 | 6.11 | 0.23667 | 0 | 14.3501 | 179.4908 | 88.6828 | 1.3172 | 179.5065 | 148.6792 | 0 | 4.5825 | 0.2 | 0 | 0.31733 | 4.8998 | 4.2 | 4.3531 | 1.0723 | 0.0043082
2016-08-15 | 3.95 | 3.74 | 0.21 | 0 | 14.3373 | -165.5073 | 88.2976 | 1.7024 | -165.9617 | 145.582 | 0 | 2.805 | 0.2 | 0 | 0.1975 | 3.0025 | 4.4 | 4.4938 | 1.0718 | 0.0026388
2016-08-15 01:00 | 12.6633 | 12.37 | 0.29333 | 0 | 14.3244 | -150.5053 | 87.0853 | 2.9147 | -151.4677 | 137.2595 | 0 | 9.2775 | 0.2 | 0 | 0.63317 | 9.9107 | 4.4 | 4.7097 | 1.071 | 0.0087039
2016-08-15 02:00 | 21.3767 | 21 | 0.37667 | 4.4335 | 14.3116 | -135.5034 | 85.1263 | 4.8737 | -137.0327 | 126.0816 | 0 | 15.75 | 0.2 | 0 | 1.0688 | 16.8188 | 4.4 | 4.9256 | 1.0703 | 0.01476
2016-08-15 03:00 | 30.09 | 29.63 | 0.46 | 3.5467 | 14.2987 | -120.5014 | 82.5479 | 7.4521 | -122.6441 | 113.4755 | 0 | 22.2225 | 0.2 | 0 | 1.5045 | 23.727 | 5 | 5.7415 | 1.0674 | 0.020768
2016-08-15 04:00 | 41.7633 | 40.6667 | 1.0967 | 6.0256 | 14.2859 | -105.4994 | 79.5136 | 10.4864 | -108.2506 | 100.1185 | 0 | 30.5 | 0.2 | 0 | 2.0882 | 32.5882 | 5.1 | 6.1184 | 1.0661 | 0.028488
2016-08-15 05:00 | 53.4367 | 51.7033 | 1.7333 | 7.2739 | 14.273 | -90.4974 | 76.2141 | 13.7859 | -93.7664 | 86.3365 | 0.46478 | 38.7775 | 0.2 | 0 | 2.6718 | 41.9141 | 4.8 | 6.1098 | 1.0661 | 0.036642
2016-08-15 06:00 | 65.11 | 62.74 | 2.37 | 8.0415 | 14.2601 | -75.4955 | 72.8592 | 17.1408 | -79.0854 | 72.2987 | 2.4451 | 47.055 | 0.2 | 0 | 3.2555 | 52.7556 | 5 | 6.6486 | 1.0642 | 0.046038
2016-08-15 07:00 | 93.1233 | 86.6667 | 6.4567 | 18.5844 | 14.2472 | -60.4935 | 69.6702 | 20.3298 | -64.1012 | 58.1017 | 9.8203 | 65 | 0.2 | 0 | 4.6562 | 79.4764 | 5.1 | 7.5836 | 1.061 | 0.069143
2016-08-15 08:00 | 121.1367 | 110.5933 | 10.5433 | 26.842 | 14.2344 | -45.4915 | 66.8717 | 23.1283 | -48.7348 | 43.8073 | 19.3711 | 82.945 | 0.2 | 0 | 6.0568 | 108.3729 | 5.3 | 8.6867 | 1.0571 | 0.09394
2016-08-15 09:00 | 149.15 | 134.52 | 14.63 | 34.2046 | 14.2215 | -30.4895 | 64.677 | 25.323 | -32.9642 | 29.4662 | 29.7801 | 100.89 | 0.2 | 0 | 7.4575 | 138.1276 | 4.4 | 8.7165 | 1.057 | 0.11972
2016-08-15 10:00 | 138.8067 | 128.99 | 9.8167 | 21.824 | 14.2086 | -15.4875 | 63.2685 | 26.7315 | -16.8482 | 15.1657 | 21.064 | 96.7425 | 0.2 | 0 | 6.9403 | 124.7468 | 5 | 8.8983 | 1.0564 | 0.10806
2016-08-15 11:00 | 128.4633 | 123.46 | 5.0033 | 10.9353 | 14.1957 | -0.48553 | 62.7715 | 27.2285 | -0.52936 | 2.8102 | 10.9221 | 92.595 | 0.2 | 0 | 6.4232 | 109.9403 | 5.2 | 8.6356 | 1.0573 | 0.095314
2016-08-15 12:00 | 118.12 | 117.93 | 0.19 | 0.42188 | 14.1828 | 14.5165 | 63.2327 | 26.7673 | 15.7943 | 14.2535 | 0.40889 | 88.4475 | 0.2 | 0 | 5.906 | 94.7624 | 4.9 | 7.8613 | 1.06 | 0.082366
2016-08-15 13:00 | 109.02 | 108.8267 | 0.19333 | 0.45091 | 14.1698 | 29.5185 | 64.6108 | 25.3892 | 31.9234 | 28.5461 | 0.39609 | 81.62 | 0.2 | 0 | 5.451 | 87.4671 | 5.1 | 7.8333 | 1.0601 | 0.076032
2016-08-15 14:00 | 99.92 | 99.7233 | 0.19667 | 0.49892 | 14.1569 | 44.5205 | 66.7846 | 23.2154 | 47.7117 | 42.893 | 0.36552 | 74.7925 | 0.2 | 0 | 4.996 | 80.154 | 5.6 | 8.1048 | 1.0591 | 0.069613
2016-08-15 15:00 | 90.82 | 90.62 | 0.2 | 0.5731 | 14.144 | 59.5225 | 69.5751 | 20.4249 | 63.0961 | 57.1989 | 0.31046 | 67.965 | 0.2 | 0 | 4.541 | 72.8165 | 5.7 | 7.9755 | 1.0596 | 0.063267
2016-08-15 16:00 | 76.4467 | 76.3133 | 0.13333 | 0.45014 | 14.1311 | 74.5245 | 72.7702 | 17.2298 | 78.0953 | 71.4137 | 0.14347 | 57.235 | 0.2 | 0 | 3.8223 | 61.2008 | 6.1 | 8.0125 | 1.0595 | 0.053168
2016-08-15 17:00 | 62.0733 | 62.0067 | 0.066667 | 0.27842 | 14.1181 | 89.5266 | 76.1462 | 13.8538 | 92.7866 | 85.4778 | 0.021952 | 46.505 | 0.2 | 0 | 3.1037 | 49.6306 | 6.1 | 7.651 | 1.0607 | 0.043168
2016-08-15 18:00 | 47.7 | 47.7 | 0 | 0 | 14.1052 | 104.5286 | 79.4813 | 10.5187 | 107.2764 | 99.2994 | 0 | 35.775 | 0.2 | 0 | 2.385 | 38.16 | 5.4 | 6.5925 | 1.0644 | 0.033307
2016-08-15 19:00 | 34.5533 | 34.5533 | 0 | 0 | 14.0922 | 119.5306 | 82.565 | 7.435 | 121.6726 | 112.718 | 0 | 25.915 | 0.2 | 0 | 1.7277 | 27.6427 | 5.5 | 6.3638 | 1.0652 | 0.024145
2016-08-15 20:00 | 21.4067 | 21.4067 | 0 | 0 | 14.0793 | 134.5326 | 85.2051 | 4.7949 | 136.0631 | 125.4261 | 0 | 16.055 | 0.2 | 0 | 1.0703 | 17.1253 | 5.7 | 6.2352 | 1.0657 | 0.014965
2016-08-15 21:00 | 8.26 | 8.26 | 0 | 0 | 14.0663 | 149.5347 | 87.2356 | 2.7644 | 150.5024 | 136.7839 | 0 | 6.195 | 0.2 | 0 | 0.413 | 6.608 | 5.7 | 5.9065 | 1.0668 | 0.0057807
2016-08-15 22:00 | 6.8667 | 6.8667 | 0 | 0 | 14.0533 | 164.5367 | 88.5262 | 1.4738 | 165.0055 | 145.4267 | 0 | 5.15 | 0.2 | 0 | 0.34333 | 5.4933 | 5.8 | 5.9717 | 1.0666 | 0.0048045
2016-08-15 23:00 | 5.4733 | 5.4733 | 0 | 0 | 14.0403 | 179.5388 | 88.9926 | 1.0074 | 179.5525 | 148.9897 | 0 | 4.105 | 0.2 | 0 | 0.27367 | 4.3787 | 5.8 | 5.9368 | 1.0667 | 0.0038301
2016-08-16 | 4.08 | 4.08 | 0 | 0 | 14.0273 | -165.4592 | 88.6044 | 1.3956 | -165.8976 | 145.8426 | 0 | 3.06 | 0.2 | 0 | 0.204 | 3.264 | 5.9 | 6.002 | 1.0665 | 0.0028544
2016-08-16 01:00 | 17.4367 | 17.4 | 0.036667 | 0 | 14.0144 | -150.4571 | 87.3882 | 2.6118 | -151.3867 | 137.4498 | 0 | 13.05 | 0.2 | 0 | 0.87183 | 13.9218 | 6.2 | 6.6351 | 1.0643 | 0.01215
2016-08-16 02:00 | 30.7933 | 30.72 | 0.073333 | 0.91942 | 14.0014 | -135.455 | 85.4252 | 4.5748 | -136.9369 | 126.2155 | 0 | 23.04 | 0.2 | 0 | 1.5397 | 24.5797 | 6.5 | 7.2681 | 1.0621 | 0.021406
2016-08-16 03:00 | 44.15 | 44.04 | 0.11 | 0.88291 | 13.9884 | -120.453 | 82.8431 | 7.1569 | -122.5364 | 113.5692 | 0 | 33.03 | 0.2 | 0 | 2.2075 | 35.2375 | 6.2 | 7.3012 | 1.0619 | 0.030685
2016-08-16 04:00 | 71.36 | 70.4533 | 0.90667 | 5.123 | 13.9753 | -105.4509 | 79.8061 | 10.1939 | -108.1342 | 100.1834 | 0 | 52.84 | 0.2 | 0 | 3.568 | 56.408 | 6 | 7.7627 | 1.0603 | 0.049045
2016-08-16 05:00 | 98.57 | 96.8667 | 1.7033 | 7.2994 | 13.9623 | -90.4488 | 76.5054 | 13.4946 | -93.6451 | 86.38 | 0.46087 | 72.65 | 0.2 | 0 | 4.9285 | 78.0394 | 6.6 | 9.0387 | 1.0559 | 0.067567
2016-08-16 06:00 | 125.78 | 123.28 | 2.5 | 8.6252 | 13.9493 | -75.4468 | 73.151 | 16.849 | -78.9631 | 72.326 | 2.6186 | 92.46 | 0.2 | 0 | 6.289 | 101.3676 | 4.9 | 8.0677 | 1.0593 | 0.088047
2016-08-16 07:00 | 182.6833 | 153.5167 | 29.1667 | 85.1324 | 13.9363 | -60.4447 | 69.9644 | 20.0356 | -63.9826 | 58.1169 | 44.9659 | 115.1375 | 0.2 | 0 | 9.1342 | 169.2376 | 5 | 10.2887 | 1.0515 | 0.14592
2016-08-16 08:00 | 239.5867 | 183.7533 | 55.8333 | 143.8993 | 13.9232 | -45.4426 | 67.1697 | 22.8303 | -48.625 | 43.8145 | 103.8356 | 137.815 | 0.2 | 0 | 11.9793 | 253.63 | 4.1 | 12.0259 | 1.0454 | 0.21742
2016-08-16 09:00 | 296.49 | 213.99 | 82.5 | 195.0644 | 13.9102 | -30.4405 | 64.9798 | 25.0202 | -32.8686 | 29.4716 | 169.823 | 160.4925 | 0.2 | 0 | 14.8245 | 345.14 | 5.7 | 16.4856 | 1.0298 | 0.29145
2016-08-16 10:00 | 318.82 | 201.0667 | 117.7533 | 264.6084 | 13.8971 | -15.4384 | 63.576 | 26.424 | -16.7716 | 15.1898 | 255.3639 | 150.8 | 0.2 | 0 | 15.941 | 422.1049 | 4.6 | 17.7908 | 1.0252 | 0.35486
2016-08-16 11:00 | 341.15 | 188.1433 | 153.0067 | 337.9873 | 13.8841 | -0.4363 | 63.083 | 26.917 | -0.47501 | 3.1111 | 337.4892 | 141.1075 | 0.2 | 0 | 17.0575 | 495.6542 | 4.3 | 19.7892 | 1.0182 | 0.41385
2016-08-16 12:00 | 363.48 | 175.22 | 188.26 | 422.614 | 13.871 | 14.5658 | 63.5469 | 26.4531 | 15.8256 | 14.3741 | 409.3844 | 131.415 | 0.2 | 0 | 18.174 | 558.9734 | 5.9 | 23.3679 | 1.0057 | 0.46098
2016-08-16 13:00 | 284.27 | 158.3233 | 125.9467 | 297.1947 | 13.8579 | 29.5679 | 64.9262 | 25.0738 | 31.9337 | 28.6466 | 260.8162 | 118.7425 | 0.2 | 0 | 14.2135 | 393.7722 | 5.4 | 17.7054 | 1.0255 | 0.33114
2016-08-16 14:00 | 205.06 | 141.4267 | 63.6333 | 163.5316 | 13.8449 | 44.57 | 67.1003 | 22.8997 | 47.7049 | 42.9945 | 119.6102 | 106.07 | 0.2 | 0 | 10.253 | 235.9332 | 6.3 | 13.6729 | 1.0396 | 0.20114
2016-08-16 15:00 | 125.85 | 124.53 | 1.32 | 3.8393 | 13.8318 | 59.5721 | 69.8905 | 20.1095 | 63.0774 | 57.3077 | 2.0737 | 93.3975 | 0.2 | 0 | 6.2925 | 101.7637 | 4.7 | 7.8801 | 1.0599 | 0.088446
2016-08-16 16:00 | 103.3133 | 102.4333 | 0.88 | 3.0246 | 13.8187 | 74.5743 | 73.0854 | 16.9146 | 78.0701 | 71.5336 | 0.95804 | 76.825 | 0.2 | 0 | 5.1657 | 82.9487 | 3.9 | 6.4921 | 1.0648 | 0.072424
2016-08-16 17:00 | 80.7767 | 80.3367 | 0.44 | 1.8795 | 13.8056 | 89.5764 | 76.4614 | 13.5386 | 92.7603 | 85.6124 | 0.14379 | 60.2525 | 0.2 | 0 | 4.0388 | 64.4351 | 5.8 | 7.8136 | 1.0602 | 0.056015
2016-08-16 18:00 | 58.24 | 58.24 | 0 | 0 | 13.7925 | 104.5785 | 79.7969 | 10.2031 | 107.2539 | 99.453 | 0 | 43.68 | 0.2 | 0 | 2.912 | 46.592 | 5 | 6.456 | 1.0649 | 0.040685
2016-08-16 19:00 | 41.7867 | 41.7867 | 0 | 0 | 13.7794 | 119.5807 | 82.8813 | 7.1187 | 121.6582 | 112.8965 | 0 | 31.34 | 0.2 | 0 | 2.0893 | 33.4293 | 4.4 | 5.4447 | 1.0684 | 0.029288
2016-08-16 20:00 | 25.3333 | 25.3333 | 0 | 0 | 13.7663 | 134.5828 | 85.5218 | 4.4782 | 136.0607 | 125.6379 | 0 | 19 | 0.2 | 0 | 1.2667 | 20.2667 | 4.6 | 5.2333 | 1.0692 | 0.017768
2016-08-16 21:00 | 8.88 | 8.88 | 0 | 0 | 13.7532 | 149.5849 | 87.5522 | 2.4478 | 150.5151 | 137.0392 | 0 | 6.66 | 0.2 | 0 | 0.444 | 7.104 | 4.8 | 5.022 | 1.0699 | 0.0062326
2016-08-16 22:00 | 6.25 | 6.18 | 0.07 | 0 | 13.7401 | 164.5871 | 88.8418 | 1.1582 | 165.0355 | 145.7284 | 0 | 4.635 | 0.2 | 0 | 0.3125 | 4.9475 | 4.1 | 4.2546 | 1.0726 | 0.0043515
2016-08-16 23:00 | 3.62 | 3.48 | 0.14 | 0 | 13.7269 | 179.5892 | 89.3061 | 0.69391 | 179.6009 | 149.3037 | 0 | 2.61 | 0.2 | 0 | 0.181 | 2.791 | 5.4 | 5.4872 | 1.0683 | 0.0024449
2016-08-17 | 0.99 | 0.78 | 0.21 | 0 | 13.7138 | -165.4086 | 88.9146 | 1.0854 | -165.8308 | 146.1046 | 0 | 0.585 | 0.2 | 0 | 0.0495 | 0.6345 | 3.7 | 3.7198 | 1.0745 | 0.00055904
2016-08-17 01:00 | 5.2733 | 3.8567 | 1.4167 | 0 | 13.7006 | -150.4065 | 87.6945 | 2.3055 | -151.3028 | 137.6397 | 0 | 2.8925 | 0.2 | 0 | 0.26367 | 3.1562 | 4.4 | 4.4986 | 1.0718 | 0.0027738
2016-08-17 02:00 | 9.5567 | 6.9333 | 2.6233 | 35.2105 | 13.6875 | -135.4043 | 85.7273 | 4.2727 | -136.8381 | 126.3483 | 0 | 5.2 | 0.2 | 0 | 0.47783 | 5.6778 | 6.5 | 6.6774 | 1.0641 | 0.0049544
2016-08-17 03:00 | 13.84 | 10.01 | 3.83 | 32.0714 | 13.6743 | -120.4021 | 83.1413 | 6.8587 | -122.4256 | 113.6615 | 0 | 7.5075 | 0.2 | 0 | 0.692 | 8.1995 | 6.1 | 6.3562 | 1.0653 | 0.0071623
2016-08-17 04:00 | 19.0067 | 16.1067 | 2.9 | 16.8701 | 13.6612 | -105.4 | 80.1016 | 9.8984 | -108.0147 | 100.2469 | 0 | 12.08 | 0.2 | 0 | 0.95033 | 13.0303 | 6.7 | 7.1072 | 1.0626 | 0.011354
2016-08-17 05:00 | 24.1733 | 22.2033 | 1.97 | 8.6269 | 13.648 | -90.3978 | 76.7997 | 13.2003 | -93.5206 | 86.4223 | 0.53834 | 16.6525 | 0.2 | 0 | 1.2087 | 18.3995 | 6.1 | 6.675 | 1.0641 | 0.016055
2016-08-17 06:00 | 29.34 | 28.3 | 1.04 | 3.6501 | 13.6348 | -75.3956 | 73.4459 | 16.5541 | -78.8378 | 72.3523 | 1.1066 | 21.225 | 0.2 | 0 | 1.467 | 23.7986 | 6.4 | 7.1437 | 1.0625 | 0.020734
2016-08-17 07:00 | 46.44 | 44.5333 | 1.9067 | 5.6456 | 13.6217 | -60.3934 | 70.2617 | 19.7383 | -63.8611 | 58.1315 | 2.9807 | 33.4 | 0.2 | 0 | 2.322 | 38.7027 | 4 | 5.2095 | 1.0693 | 0.033935
2016-08-17 08:00 | 63.54 | 60.7667 | 2.7733 | 7.2382 | 13.6085 | -45.3912 | 67.471 | 22.529 | -48.5124 | 43.8216 | 5.2224 | 45.575 | 0.2 | 0 | 3.177 | 53.9744 | 4.8 | 6.4867 | 1.0648 | 0.047127
2016-08-17 09:00 | 80.64 | 77 | 3.64 | 8.7063 | 13.5953 | -30.389 | 65.286 | 24.714 | -32.7703 | 29.4783 | 7.5792 | 57.75 | 0.2 | 0 | 4.032 | 69.3612 | 4.7 | 6.8675 | 1.0635 | 0.060486
2016-08-17 10:00 | 86.33 | 83.1767 | 3.1533 | 7.1644 | 13.5821 | -15.3868 | 63.887 | 26.113 | -16.6924 | 15.2187 | 6.9131 | 62.3825 | 0.2 | 0 | 4.3165 | 73.6121 | 6.8 | 9.1004 | 1.0556 | 0.063721
2016-08-17 11:00 | 92.02 | 89.3533 | 2.6667 | 5.9552 | 13.5689 | -0.38464 | 63.3981 | 26.6019 | -0.41818 | 3.418 | 5.9446 | 67.015 | 0.2 | 0 | 4.601 | 77.5606 | 6.5 | 8.9238 | 1.0563 | 0.067178
2016-08-17 12:00 | 97.71 | 95.53 | 2.18 | 4.949 | 13.5557 | 14.6176 | 63.8648 | 26.1352 | 15.8593 | 14.5037 | 4.7913 | 71.6475 | 0.2 | 0 | 4.8855 | 81.3243 | 6.6 | 9.1414 | 1.0555 | 0.070387
2016-08-17 13:00 | 114.54 | 87.74 | 26.8 | 64.003 | 13.5424 | 29.6198 | 65.2455 | 24.7545 | 31.9461 | 28.753 | 56.1115 | 65.805 | 0.2 | 0 | 5.727 | 127.6435 | 6.3 | 10.2889 | 1.0515 | 0.11006
2016-08-17 14:00 | 131.37 | 79.95 | 51.42 | 133.9152 | 13.5292 | 44.622 | 67.4199 | 22.5801 | 47.7001 | 43.1007 | 97.7787 | 59.9625 | 0.2 | 0 | 6.5685 | 164.3097 | 6.5 | 11.6347 | 1.0468 | 0.14104
2016-08-17 15:00 | 148.2 | 72.16 | 76.04 | 224.5883 | 13.516 | 59.6242 | 70.2099 | 19.7901 | 63.0605 | 57.4207 | 120.9334 | 54.12 | 0.2 | 0 | 7.41 | 182.4634 | 6.7 | 12.402 | 1.0441 | 0.15622
2016-08-17 16:00 | 137.0067 | 59.3533 | 77.6533 | 271.8841 | 13.5028 | 74.6264 | 73.4046 | 16.5954 | 78.0468 | 71.6573 | 85.5619 | 44.515 | 0.2 | 0 | 6.8503 | 136.9272 | 6.5 | 10.779 | 1.0498 | 0.11787
2016-08-17 17:00 | 125.8133 | 46.5467 | 79.2667 | 346.6278 | 13.4895 | 89.6286 | 76.7807 | 13.2193 | 92.7358 | 85.7505 | 25.6848 | 34.91 | 0.2 | 0 | 6.2907 | 66.8855 | 6.7 | 8.7902 | 1.0567 | 0.057958
2016-08-17 18:00 | 114.62 | 33.74 | 80.88 | 471.2085 | 13.4763 | 104.6309 | 80.1166 | 9.8834 | 107.2331 | 99.6099 | 0 | 25.305 | 0.2 | 0 | 5.731 | 31.036 | 6.9 | 7.8699 | 1.06 | 0.026975
2016-08-17 19:00 | 80.6567 | 24.7567 | 55.9 | 472.216 | 13.463 | 119.6331 | 83.2015 | 6.7985 | 121.6456 | 113.0783 | 0 | 18.5675 | 0.2 | 0 | 4.0328 | 22.6003 | 7.1 | 7.8063 | 1.0602 | 0.019648
2016-08-17 20:00 | 46.6933 | 15.7733 | 30.92 | 426.4883 | 13.4497 | 134.6353 | 85.8425 | 4.1575 | 136.0601 | 125.853 | 0 | 11.83 | 0.2 | 0 | 2.3347 | 14.1647 | 6.9 | 7.3426 | 1.0618 | 0.012333
2016-08-17 21:00 | 12.73 | 6.79 | 5.94 | 0 | 13.4365 | 149.6376 | 87.8727 | 2.1273 | 150.5298 | 137.2981 | 0 | 5.0925 | 0.2 | 0 | 0.6365 | 5.729 | 6.7 | 6.879 | 1.0634 | 0.0049957
2016-08-17 22:00 | 9.4733 | 5.2167 | 4.2567 | 0 | 13.4232 | 164.6398 | 89.1612 | 0.83884 | 165.0677 | 146.0342 | 0 | 3.9125 | 0.2 | 0 | 0.47367 | 4.3862 | 6.4 | 6.5371 | 1.0646 | 0.0038291
2016-08-17 23:00 | 6.2167 | 3.6433 | 2.5733 | 0 | 13.4099 | 179.6421 | 89.6232 | 0.37684 | 179.6518 | 149.6213 | 0 | 2.7325 | 0.2 | 0 | 0.31083 | 3.0433 | 6.5 | 6.5951 | 1.0644 | 0.0026563
2016-08-18 | 2.96 | 2.07 | 0.89 | 0 | 13.3966 | -165.3557 | 89.2283 | 0.77167 | -165.7614 | 146.3679 | 0 | 1.5525 | 0.2 | 0 | 0.148 | 1.7005 | 6.7 | 6.7531 | 1.0639 | 0.0014835
2016-08-18 01:00 | 25.2567 | 10.8967 | 14.36 | 0 | 13.3834 | -150.3534 | 88.004 | 1.996 | -151.2161 | 137.8291 | 0 | 8.1725 | 0.2 | 0 | 1.2628 | 9.4353 | 6.4 | 6.6949 | 1.0641 | 0.0082327
2016-08-18 02:00 | 47.5533 | 19.7233 | 27.83 | 402.2169 | 13.3701 | -135.3511 | 86.0324 | 3.9676 | -136.7364 | 126.4798 | 0 | 14.7925 | 0.2 | 0 | 2.3777 | 17.1702 | 5.3 | 5.8366 | 1.0671 | 0.015024
2016-08-18 03:00 | 69.85 | 28.55 | 41.3 | 361.6504 | 13.3568 | -120.3489 | 83.4426 | 6.5574 | -122.3119 | 113.7525 | 0 | 21.4125 | 0.2 | 0 | 3.4925 | 24.905 | 5.4 | 6.1783 | 1.0659 | 0.021767
2016-08-18 04:00 | 98.5767 | 61.3733 | 37.2033 | 223.0835 | 13.3435 | -105.3466 | 80.4 | 9.6 | -107.8923 | 100.309 | 0 | 46.03 | 0.2 | 0 | 4.9288 | 50.9588 | 5.2 | 6.7925 | 1.0637 | 0.044449
2016-08-18 05:00 | 127.3033 | 94.1967 | 33.1067 | 148.2587 | 13.3301 | -90.3443 | 77.0969 | 12.9031 | -93.3932 | 86.4633 | 9.1458 | 70.6475 | 0.2 | 0 | 6.3652 | 86.1585 | 5.3 | 7.9925 | 1.0595 | 0.074855
2016-08-18 06:00 | 156.03 | 127.02 | 29.01 | 103.6315 | 13.3168 | -75.3421 | 73.7437 | 16.2563 | -78.7095 | 72.3777 | 31.3736 | 95.265 | 0.2 | 0 | 7.8015 | 134.4401 | 5.8 | 10.0013 | 1.0525 | 0.11603
2016-08-18 07:00 | 132.8533 | 111.91 | 20.9433 | 62.9335 | 13.3035 | -60.3398 | 70.5621 | 19.4379 | -63.7366 | 58.1455 | 33.2141 | 83.9325 | 0.2 | 0 | 6.6427 | 123.7892 | 6.1 | 9.9684 | 1.0526 | 0.10685
2016-08-18 08:00 | 109.6767 | 96.8 | 12.8767 | 34.0438 | 13.2902 | -45.3375 | 67.7754 | 22.2246 | -48.397 | 43.8289 | 24.5596 | 72.6 | 0.2 | 0 | 5.4838 | 102.6434 | 6.4 | 9.6076 | 1.0539 | 0.088702
2016-08-18 09:00 | 86.5 | 81.69 | 4.81 | 11.6415 | 13.2768 | -30.3352 | 65.5953 | 24.4047 | -32.6693 | 29.4865 | 10.1336 | 61.2675 | 0.2 | 0 | 4.325 | 75.7261 | 7 | 9.3664 | 1.0547 | 0.065493
2016-08-18 10:00 | 96.3667 | 90.17 | 6.1967 | 14.2384 | 13.2635 | -15.3329 | 64.2015 | 25.7985 | -16.6106 | 15.2526 | 13.7368 | 67.6275 | 0.2 | 0 | 4.8183 | 86.1827 | 7.5 | 10.1932 | 1.0518 | 0.074332
2016-08-18 11:00 | 106.2333 | 98.65 | 7.5833 | 17.1255 | 13.2501 | -0.3306 | 63.7168 | 26.2832 | -0.3589 | 3.7302 | 17.0892 | 73.9875 | 0.2 | 0 | 5.3117 | 96.3884 | 8.1 | 11.1121 | 1.0486 | 0.08288
2016-08-18 12:00 | 116.1 | 107.13 | 8.97 | 20.5996 | 13.2368 | 14.6717 | 64.1864 | 25.8136 | 15.8953 | 14.6424 | 19.9306 | 80.3475 | 0.2 | 0 | 5.805 | 106.0831 | 8 | 11.3151 | 1.0479 | 0.091155
2016-08-18 13:00 | 117.36 | 95.58 | 21.78 | 52.6592 | 13.2234 | 29.674 | 65.5686 | 24.4314 | 31.9606 | 28.8653 | 46.1166 | 71.685 | 0.2 | 0 | 5.868 | 123.6696 | 7.1 | 10.9647 | 1.0491 | 0.10639
2016-08-18 14:00 | 118.62 | 84.03 | 34.59 | 91.3256 | 13.21 | 44.6763 | 67.7434 | 22.2566 | 47.6972 | 43.2117 | 66.5607 | 63.0225 | 0.2 | 0 | 5.931 | 135.5142 | 6.4 | 10.6348 | 1.0503 | 0.11671
2016-08-18 15:00 | 119.88 | 72.48 | 47.4 | 142.2317 | 13.1967 | 59.6786 | 70.5333 | 19.4667 | 63.0455 | 57.5378 | 76.342 | 54.36 | 0.2 | 0 | 5.994 | 136.696 | 6.7 | 10.9717 | 1.0491 | 0.11759
2016-08-18 16:00 | 110.27 | 58.2267 | 52.0433 | 185.7352 | 13.1833 | 74.681 | 73.7278 | 16.2722 | 78.0251 | 71.7847 | 58.0586 | 43.67 | 0.2 | 0 | 5.5135 | 107.2421 | 6.8 | 10.1513 | 1.052 | 0.092509
2016-08-18 17:00 | 100.66 | 43.9733 | 56.6867 | 253.991 | 13.1699 | 89.6833 | 77.1039 | 12.8961 | 92.7129 | 85.8921 | 18.1947 | 32.98 | 0.2 | 0 | 5.033 | 56.2077 | 6.3 | 8.0565 | 1.0593 | 0.048824
2016-08-18 18:00 | 91.05 | 29.72 | 61.33 | 369.2871 | 13.1565 | 104.6856 | 80.4402 | 9.5598 | 107.214 | 99.7701 | 0 | 22.29 | 0.2 | 0 | 4.5525 | 26.8425 | 6.2 | 7.0388 | 1.0629 | 0.023395
2016-08-18 19:00 | 62.62 | 21.1 | 41.52 | 368.2201 | 13.1431 | 119.6879 | 83.5256 | 6.4744 | 121.6347 | 113.2632 | 0 | 15.825 | 0.2 | 0 | 3.131 | 18.956 | 6.1 | 6.6924 | 1.0641 | 0.01654
2016-08-18 20:00 | 34.19 | 12.48 | 21.71 | 324.7585 | 13.1297 | 134.6903 | 86.1669 | 3.8331 | 136.0615 | 126.0713 | 0 | 9.36 | 0.2 | 0 | 1.7095 | 11.0695 | 6.3 | 6.6459 | 1.0642 | 0.0096601
2016-08-18 21:00 | 5.76 | 3.86 | 1.9 | 0 | 13.1163 | 149.6926 | 88.1969 | 1.8031 | 150.5465 | 137.5605 | 0 | 2.895 | 0.2 | 0 | 0.288 | 3.183 | 6.5 | 6.5995 | 1.0644 | 0.0027782
2016-08-18 22:00 | 4.39 | 2.95 | 1.44 | 0 | 13.1029 | 164.695 | 89.4841 | 0.51588 | 165.1022 | 146.3439 | 0 | 2.2125 | 0.2 | 0 | 0.2195 | 2.432 | 6.6 | 6.676 | 1.0641 | 0.0021221
2016-08-18 23:00 | 3.02 | 2.04 | 0.98 | 0 | 13.0895 | 179.6973 | 89.9437 | 0.0563 | 179.7052 | 149.9424 | 0 | 1.53 | 0.2 | 0 | 0.151 | 1.681 | 6.6 | 6.6525 | 1.0642 | 0.0014669
2016-08-19 | 1.65 | 1.13 | 0.52 | 0 | 13.076 | -165.3003 | 89.5453 | 0.45466 | -165.6893 | 146.6323 | 0 | 0.8475 | 0.2 | 0 | 0.0825 | 0.93 | 6.5 | 6.5291 | 1.0646 | 0.0008119
2016-08-19 01:00 | 22.2433 | 8.51 | 13.7333 | 0 | 13.0626 | -150.298 | 88.3168 | 1.6832 | -151.1266 | 138.0179 | 0 | 6.3825 | 0.2 | 0 | 1.1122 | 7.4947 | 7 | 7.2342 | 1.0622 | 0.0065278
2016-08-19 02:00 | 42.8367 | 15.89 | 26.9467 | 422.2048 | 13.0492 | -135.2956 | 86.3407 | 3.6593 | -136.6318 | 126.6102 | 0 | 11.9175 | 0.2 | 0 | 2.1418 | 14.0593 | 6.2 | 6.6394 | 1.0643 | 0.01227
2016-08-19 03:00 | 63.43 | 23.27 | 40.16 | 368.7035 | 13.0357 | -120.2933 | 83.7468 | 6.2532 | -122.1952 | 113.842 | 0 | 17.4525 | 0.2 | 0 | 3.1715 | 20.624 | 7.4 | 8.0445 | 1.0593 | 0.017915
2016-08-19 04:00 | 75.03 | 38.1767 | 36.8533 | 228.0798 | 13.0223 | -105.2909 | 80.7013 | 9.2987 | -107.7668 | 100.3697 | 0 | 28.6325 | 0.2 | 0 | 3.7515 | 32.384 | 7.6 | 8.612 | 1.0574 | 0.028078
2016-08-19 05:00 | 86.63 | 53.0833 | 33.5467 | 153.7459 | 13.0088 | -90.2885 | 77.3969 | 12.6031 | -93.2628 | 86.5031 | 9.3777 | 39.8125 | 0.2 | 0 | 4.3315 | 53.5217 | 7.7 | 9.3726 | 1.0547 | 0.046288
2016-08-19 06:00 | 98.23 | 67.99 | 30.24 | 110.007 | 12.9953 | -75.2861 | 74.0444 | 15.9556 | -78.5784 | 72.402 | 33.2591 | 50.9925 | 0.2 | 0 | 4.9115 | 89.1631 | 7.4 | 10.1863 | 1.0518 | 0.076904
2016-08-19 07:00 | 117.88 | 90.6733 | 27.2067 | 83.0006 | 12.9819 | -60.2838 | 70.8654 | 19.1346 | -63.6094 | 58.1589 | 43.7882 | 68.005 | 0.2 | 0 | 5.894 | 117.6872 | 6.5 | 10.1777 | 1.0519 | 0.10151
2016-08-19 08:00 | 137.53 | 113.3567 | 24.1733 | 64.7618 | 12.9684 | -45.2814 | 68.0829 | 21.9171 | -48.2789 | 43.8363 | 46.7141 | 85.0175 | 0.2 | 0 | 6.8765 | 138.6081 | 5.9 | 10.2315 | 1.0517 | 0.11953
2016-08-19 09:00 | 157.18 | 136.04 | 21.14 | 51.7877 | 12.9549 | -30.279 | 65.9079 | 24.0921 | -32.5656 | 29.4961 | 45.0755 | 102.03 | 0.2 | 0 | 7.859 | 154.9645 | 6.3 | 11.1426 | 1.0485 | 0.13323
2016-08-19 10:00 | 169.4433 | 147.0233 | 22.42 | 52.1142 | 12.9414 | -15.2766 | 64.5192 | 25.4808 | -16.5263 | 15.2919 | 50.2691 | 110.2675 | 0.2 | 0 | 8.4722 | 169.0088 | 7 | 12.2815 | 1.0445 | 0.14476
2016-08-19 11:00 | 181.7067 | 158.0067 | 23.7 | 54.1391 | 12.9279 | -0.2742 | 64.0389 | 25.9611 | -0.29725 | 4.0474 | 54.0041 | 118.505 | 0.2 | 0 | 9.0853 | 181.5944 | 6.6 | 12.2748 | 1.0445 | 0.15554
2016-08-19 12:00 | 193.97 | 168.99 | 24.98 | 58.0486 | 12.9144 | 14.7282 | 64.5115 | 25.4885 | 15.9335 | 14.79 | 56.1253 | 126.7425 | 0.2 | 0 | 9.6985 | 192.5663 | 6.3 | 12.3177 | 1.0444 | 0.16491
2016-08-19 13:00 | 177.9333 | 136.2233 | 41.71 | 102.1294 | 12.9009 | 29.7306 | 65.8954 | 24.1046 | 31.9773 | 28.9837 | 89.3385 | 102.1675 | 0.2 | 0 | 8.8967 | 200.4026 | 6.1 | 12.3626 | 1.0442 | 0.1716
2016-08-19 14:00 | 161.8967 | 103.4567 | 58.44 | 156.4819 | 12.8874 | 44.733 | 68.0707 | 21.9293 | 47.6963 | 43.3275 | 113.8318 | 77.5925 | 0.2 | 0 | 8.0948 | 199.5191 | 6.3 | 12.535 | 1.0436 | 0.17074
2016-08-19 15:00 | 145.86 | 70.69 | 75.17 | 229.2683 | 12.8739 | 59.7354 | 70.8605 | 19.1395 | 63.0323 | 57.6589 | 122.6489 | 53.0175 | 0.2 | 0 | 7.293 | 182.9594 | 6 | 11.7175 | 1.0465 | 0.157
2016-08-19 16:00 | 115.1667 | 56.55 | 58.6167 | 213.3705 | 12.8604 | 74.7378 | 74.0548 | 15.9452 | 78.0052 | 71.9158 | 66.2332 | 42.4125 | 0.2 | 0 | 5.7583 | 114.404 | 6.4 | 9.9751 | 1.0526 | 0.098745
2016-08-19 17:00 | 84.4733 | 42.41 | 42.0633 | 193.2924 | 12.8469 | 89.7403 | 77.431 | 12.569 | 92.6917 | 86.037 | 13.3587 | 31.8075 | 0.2 | 0 | 4.2237 | 49.3899 | 6 | 7.5434 | 1.0611 | 0.042974
2016-08-19 18:00 | 53.78 | 28.27 | 25.51 | 159.0022 | 12.8333 | 104.7427 | 80.7677 | 9.2323 | 107.1966 | 99.9335 | 0 | 21.2025 | 0.2 | 0 | 2.689 | 23.8915 | 5.7 | 6.4466 | 1.0649 | 0.020863
2016-08-19 19:00 | 37.02 | 19.81 | 17.21 | 160.7367 | 12.8198 | 119.7451 | 83.8536 | 6.1464 | 121.6256 | 113.4513 | 0 | 14.8575 | 0.2 | 0 | 1.851 | 16.7085 | 5.7 | 6.2221 | 1.0657 | 0.014601
2016-08-19 20:00 | 20.26 | 11.35 | 8.91 | 145.7479 | 12.8063 | 134.7475 | 86.4952 | 3.5048 | 136.0646 | 126.2928 | 0 | 8.5125 | 0.2 | 0 | 1.013 | 9.5255 | 5 | 5.2977 | 1.069 | 0.0083495
2016-08-19 21:00 | 3.5 | 2.89 | 0.61 | 0 | 12.7927 | 149.75 | 88.5247 | 1.4753 | 150.5652 | 137.8263 | 0 | 2.1675 | 0.2 | 0 | 0.175 | 2.3425 | 5.2 | 5.2732 | 1.069 | 0.0020535
2016-08-19 22:00 | 2.65 | 2.2433 | 0.40667 | 0 | 12.7791 | 164.7524 | 89.8106 | 0.18939 | 165.1388 | 146.6575 | 0 | 1.6825 | 0.2 | 0 | 0.1325 | 1.815 | 5.3 | 5.3567 | 1.0688 | 0.0015906
2016-08-19 23:00 | 1.8 | 1.5967 | 0.20333 | 0 | 12.7656 | 179.7549 | 90.2676 | -0.26763 | 179.7609 | 150.2668 | 0 | 1.1975 | 0.2 | 0 | 0.09 | 1.2875 | 5.4 | 5.4402 | 1.0685 | 0.001128
2016-08-20 | 0.95 | 0.95 | 0 | 0 | 12.752 | -165.2427 | 89.8656 | 0.1344 | -165.6146 | 146.8978 | 0 | 0.7125 | 0.2 | 0 | 0.0475 | 0.76 | 5.4 | 5.4238 | 1.0685 | 0.0006659
2016-08-20 01:00 | 15.7767 | 10.5167 | 5.26 | 0 | 12.7384 | -150.2402 | 88.6326 | 1.3674 | -151.0344 | 138.2061 | 0 | 7.8875 | 0.2 | 0 | 0.78883 | 8.6763 | 5.2 | 5.4711 | 1.0684 | 0.0076009
2016-08-20 02:00 | 30.6033 | 20.0833 | 10.52 | 180.1297 | 12.7249 | -135.2378 | 86.6519 | 3.3481 | -136.5244 | 126.7391 | 0 | 15.0625 | 0.2 | 0 | 1.5302 | 16.5927 | 4.6 | 5.1185 | 1.0696 | 0.014553
2016-08-20 03:00 | 45.43 | 29.65 | 15.78 | 152.327 | 12.7113 | -120.2353 | 84.0539 | 5.9461 | -122.0755 | 113.93 | 0 | 22.2375 | 0.2 | 0 | 2.2715 | 24.509 | 4.7 | 5.4659 | 1.0684 | 0.021471
2016-08-20 04:00 | 74.4667 | 52.4167 | 22.05 | 141.0384 | 12.6977 | -105.2329 | 81.0055 | 8.9945 | -107.6385 | 100.429 | 0 | 39.3125 | 0.2 | 0 | 3.7233 | 43.0358 | 4.3 | 5.6449 | 1.0677 | 0.03768
2016-08-20 05:00 | 103.5033 | 75.1833 | 28.32 | 132.9364 | 12.6841 | -90.2304 | 77.6998 | 12.3002 | -93.1295 | 86.5416 | 8.0191 | 56.3875 | 0.2 | 0 | 5.1752 | 69.5818 | 4.2 | 6.3744 | 1.0652 | 0.060777
2016-08-20 06:00 | 132.54 | 97.95 | 34.59 | 128.2088 | 12.6705 | -75.2279 | 74.348 | 15.652 | -78.4444 | 72.4255 | 38.7121 | 73.4625 | 0.2 | 0 | 6.627 | 118.8016 | 5.4 | 9.1125 | 1.0556 | 0.10283
2016-08-20 07:00 | 156.77 | 106.4633 | 50.3067 | 155.8757 | 12.6569 | -60.2255 | 71.1715 | 18.8285 | -63.4794 | 58.1719 | 82.2046 | 79.8475 | 0.2 | 0 | 7.8385 | 169.8906 | 5.8 | 11.1091 | 1.0486 | 0.14608
2016-08-20 08:00 | 181 | 114.9767 | 66.0233 | 179.2975 | 12.6433 | -45.223 | 68.3933 | 21.6067 | -48.1581 | 43.8439 | 129.3146 | 86.2325 | 0.2 | 0 | 9.05 | 224.5971 | 5.3 | 12.3187 | 1.0444 | 0.19234
2016-08-20 09:00 | 205.23 | 123.49 | 81.74 | 202.7435 | 12.6297 | -30.2205 | 66.2235 | 23.7765 | -32.4595 | 29.5074 | 176.4461 | 92.6175 | 0.2 | 0 | 10.2615 | 279.3251 | 6.4 | 15.1289 | 1.0345 | 0.23696
2016-08-20 10:00 | 222.5433 | 139.6367 | 82.9067 | 195.0077 | 12.616 | -15.218 | 64.8401 | 25.1599 | -16.4396 | 15.3366 | 188.0632 | 104.7275 | 0.2 | 0 | 11.1272 | 303.9179 | 6.2 | 15.6974 | 1.0326 | 0.25733
2016-08-20 11:00 | 239.8567 | 155.7833 | 84.0733 | 194.3234 | 12.6024 | -0.21551 | 64.3644 | 25.6356 | -0.23328 | 4.3692 | 193.7586 | 116.8375 | 0.2 | 0 | 11.9928 | 322.589 | 5.7 | 15.7809 | 1.0323 | 0.27306
2016-08-20 12:00 | 257.17 | 171.93 | 85.24 | 200.4966 | 12.5888 | 14.787 | 64.8402 | 25.1598 | 15.9739 | 14.9466 | 193.7132 | 128.9475 | 0.2 | 0 | 12.8585 | 335.5192 | 6.1 | 16.585 | 1.0295 | 0.28323
2016-08-20 13:00 | 215.5767 | 134.0467 | 81.53 | 202.2409 | 12.5751 | 29.7895 | 66.2258 | 23.7742 | 31.996 | 29.108 | 176.6988 | 100.535 | 0.2 | 0 | 10.7788 | 288.0126 | 6.6 | 15.6004 | 1.0329 | 0.24394
2016-08-20 14:00 | 173.9833 | 96.1633 | 77.82 | 211.4119 | 12.5615 | 44.792 | 68.4017 | 21.5983 | 47.6973 | 43.448 | 153.4848 | 72.1225 | 0.2 | 0 | 8.6992 | 234.3065 | 6.1 | 13.4221 | 1.0405 | 0.19992
2016-08-20 15:00 | 132.39 | 58.28 | 74.11 | 229.8651 | 12.5478 | 59.7945 | 71.1915 | 18.8085 | 63.0209 | 57.7842 | 122.5434 | 43.71 | 0.2 | 0 | 6.6195 | 172.8729 | 5.6 | 11.0023 | 1.049 | 0.1487
2016-08-20 16:00 | 98.8567 | 47.63 | 51.2267 | 190.3196 | 12.5342 | 74.797 | 74.3856 | 15.6144 | 77.987 | 72.0505 | 58.6523 | 35.7225 | 0.2 | 0 | 4.9428 | 99.3176 | 5.4 | 8.5037 | 1.0577 | 0.086143
2016-08-20 17:00 | 65.3233 | 36.98 | 28.3433 | 133.711 | 12.5205 | 89.7995 | 77.7619 | 12.2381 | 92.6722 | 86.1853 | 8.8957 | 27.735 | 0.2 | 0 | 3.2662 | 39.8969 | 5.7 | 6.9468 | 1.0632 | 0.034783
2016-08-20 18:00 | 31.79 | 26.33 | 5.46 | 35.2875 | 12.5068 | 104.802 | 81.0989 | 8.9011 | 107.1807 | 100.1 | 0 | 19.7475 | 0.2 | 0 | 1.5895 | 21.337 | 5.3 | 5.9668 | 1.0666 | 0.018662
2016-08-20 19:00 | 22.4267 | 18.4567 | 3.97 | 39.1857 | 12.4932 | 119.8046 | 84.1853 | 5.8147 | 121.6181 | 113.6423 | 0 | 13.8425 | 0.2 | 0 | 1.1213 | 14.9638 | 5.6 | 6.0676 | 1.0663 | 0.013083
2016-08-20 20:00 | 13.0633 | 10.5833 | 2.48 | 44.8052 | 12.4795 | 134.8071 | 86.827 | 3.173 | 136.0696 | 126.5173 | 0 | 7.9375 | 0.2 | 0 | 0.65317 | 8.5907 | 5.6 | 5.8685 | 1.067 | 0.007516
2016-08-20 21:00 | 3.7 | 2.71 | 0.99 | 0 | 12.4658 | 149.8096 | 88.8561 | 1.1439 | 150.5859 | 138.0953 | 0 | 2.0325 | 0.2 | 0 | 0.185 | 2.2175 | 5.7 | 5.7693 | 1.0673 | 0.0019407
2016-08-20 22:00 | 2.7133 | 1.9967 | 0.71667 | 0 | 12.4521 | 164.8121 | 90.1405 | -0.14053 | 165.1777 | 146.9748 | 0 | 1.4975 | 0.2 | 0 | 0.13567 | 1.6332 | 5.8 | 5.851 | 1.067 | 0.001429
2016-08-20 23:00 | 1.7267 | 1.2833 | 0.44333 | 0 | 12.4384 | 179.8147 | 90.5949 | -0.59487 | 179.819 | 150.5944 | 0 | 0.9625 | 0.2 | 0 | 0.086333 | 1.0488 | 5.4 | 5.4328 | 1.0685 | 0.00091894
2016-08-21 | 0.74 | 0.57 | 0.17 | 0 | 12.4247 | -165.1828 | 90.189 | -0.18902 | -165.5374 | 147.1641 | 0 | 0.4275 | 0.2 | 0 | 0.037 | 0.4645 | 4.9 | 4.9145 | 1.0703 | 0.00040767
2016-08-21 01:00 | 12.9033 | 8.92 | 3.9833 | 0 | 12.411 | -150.1802 | 88.9514 | 1.0486 | -150.9394 | 138.3934 | 0 | 6.69 | 0.2 | 0 | 0.64517 | 7.3352 | 5.4 | 5.6292 | 1.0678 | 0.0064226
2016-08-21 02:00 | 25.0667 | 17.27 | 7.7967 | 147.304 | 12.3973 | -135.1777 | 86.966 | 3.034 | -136.4142 | 126.8667 | 0 | 12.9525 | 0.2 | 0 | 1.2533 | 14.2058 | 5 | 5.4439 | 1.0684 | 0.012446
2016-08-21 03:00 | 37.23 | 25.62 | 11.61 | 118.2133 | 12.3836 | -120.1751 | 84.3638 | 5.6362 | -121.9531 | 114.0165 | 0 | 19.215 | 0.2 | 0 | 1.8615 | 21.0765 | 5 | 5.6586 | 1.0677 | 0.018453
2016-08-21 04:00 | 64.32 | 47.9633 | 16.3567 | 108.2875 | 12.3698 | -105.1726 | 81.3123 | 8.6877 | -107.5073 | 100.4869 | 0 | 35.9725 | 0.2 | 0 | 3.216 | 39.1885 | 5.3 | 6.5246 | 1.0647 | 0.034213
2016-08-21 05:00 | 91.41 | 70.3067 | 21.1033 | 101.5459 | 12.3561 | -90.17 | 78.0053 | 11.9947 | -92.9935 | 86.579 | 6.0595 | 52.73 | 0.2 | 0 | 4.5705 | 63.36 | 5.2 | 7.18 | 1.0624 | 0.055196
2016-08-21 06:00 | 118.5 | 92.65 | 25.85 | 97.6786 | 12.3424 | -75.1674 | 74.6542 | 15.3458 | -78.3077 | 72.4481 | 29.4569 | 69.4875 | 0.2 | 0 | 5.925 | 104.8694 | 4.9 | 8.1772 | 1.0589 | 0.091056
2016-08-21 07:00 | 187.01 | 108.3067 | 78.7033 | 247.7854 | 12.3286 | -60.1649 | 71.4805 | 18.5195 | -63.3468 | 58.1845 | 130.629 | 81.23 | 0.2 | 0 | 9.3505 | 221.2095 | 5.5 | 12.4128 | 1.0441 | 0.18938
2016-08-21 08:00 | 255.52 | 123.9633 | 131.5567 | 362.2718 | 12.3149 | -45.1623 | 68.7066 | 21.2934 | -48.0347 | 43.8519 | 261.246 | 92.9725 | 0.2 | 0 | 12.776 | 366.9945 | 5.6 | 17.0686 | 1.0278 | 0.30929
2016-08-21 09:00 | 324.03 | 139.62 | 184.41 | 463.2562 | 12.3011 | -30.1597 | 66.5422 | 23.4578 | -32.3508 | 29.5205 | 403.116 | 104.715 | 0.2 | 0 | 16.2015 | 524.0325 | 5.6 | 21.976 | 1.0106 | 0.43425
2016-08-21 10:00 | 340.45 | 123.9233 | 216.5267 | 515.5166 | 12.2874 | -15.1572 | 65.1642 | 24.8358 | -16.3506 | 15.387 | 497.0382 | 92.9425 | 0.2 | 0 | 17.0225 | 607.0032 | 5.8 | 24.7689 | 1.0008 | 0.49815
2016-08-21 11:00 | 356.87 | 108.2267 | 248.6433 | 581.6676 | 12.2736 | -0.15457 | 64.6931 | 25.3069 | -0.16707 | 4.6955 | 579.7155 | 81.17 | 0.2 | 0 | 17.8435 | 678.729 | 5.8 | 27.0103 | 0.99296 | 0.55264
2016-08-21 12:00 | 373.29 | 92.53 | 280.76 | 668.6492 | 12.2598 | 14.848 | 65.1723 | 24.8277 | 16.0165 | 15.112 | 645.5262 | 69.3975 | 0.2 | 0 | 18.6645 | 733.5882 | 5.9 | 28.8246 | 0.98661 | 0.59349
2016-08-21 13:00 | 329.9867 | 88.3167 | 241.67 | 607.5271 | 12.246 | 29.8506 | 66.5597 | 23.4403 | 32.0167 | 29.2383 | 530.1258 | 66.2375 | 0.2 | 0 | 16.4993 | 612.8626 | 6 | 25.152 | 0.99947 | 0.50228
2016-08-21 14:00 | 286.6833 | 84.1033 | 202.58 | 558.5938 | 12.2323 | 44.8532 | 68.7363 | 21.2637 | 47.7002 | 43.5732 | 404.6981 | 63.0775 | 0.2 | 0 | 14.3342 | 482.1098 | 5.4 | 20.4659 | 1.0159 | 0.4016
2016-08-21 15:00 | 243.38 | 79.89 | 163.49 | 515.9485 | 12.2185 | 59.8558 | 71.5261 | 18.4739 | 63.0112 | 57.9134 | 274.0718 | 59.9175 | 0.2 | 0 | 12.169 | 346.1583 | 5.2 | 16.0174 | 1.0314 | 0.29277
2016-08-21 16:00 | 193.82 | 64.37 | 129.45 | 491.2082 | 12.2047 | 74.8584 | 74.7201 | 15.2799 | 77.9704 | 72.1888 | 150.2511 | 48.2775 | 0.2 | 0 | 9.691 | 208.2196 | 5.2 | 11.7069 | 1.0465 | 0.17868
2016-08-21 17:00 | 144.26 | 48.85 | 95.41 | 462.5622 | 12.1909 | 89.861 | 78.0965 | 11.9035 | 92.6542 | 86.3369 | 29.5532 | 36.6375 | 0.2 | 0 | 7.213 | 73.4037 | 5.6 | 7.8939 | 1.0599 | 0.063795
2016-08-21 18:00 | 94.7 | 33.33 | 61.37 | 412.012 | 12.1771 | 104.8636 | 81.4338 | 8.5662 | 107.1665 | 100.2696 | 0 | 24.9975 | 0.2 | 0 | 4.735 | 29.7325 | 5.4 | 6.3291 | 1.0653 | 0.025974
2016-08-21 19:00 | 65.16 | 23.4033 | 41.7567 | 437.2934 | 12.1633 | 119.8662 | 84.5205 | 5.4795 | 121.6123 | 113.8363 | 0 | 17.5525 | 0.2 | 0 | 3.258 | 20.8105 | 5.2 | 5.8503 | 1.067 | 0.018208
2016-08-21 20:00 | 35.62 | 13.4767 | 22.1433 | 0 | 12.1495 | 134.8689 | 87.1624 | 2.8376 | 136.0763 | 126.7447 | 0 | 10.1075 | 0.2 | 0 | 1.781 | 11.8885 | 3.8 | 4.1715 | 1.0729 | 0.010459
2016-08-21 21:00 | 6.08 | 3.55 | 2.53 | 0 | 12.1356 | 149.8715 | 89.191 | 0.809 | 150.6086 | 138.3676 | 0 | 2.6625 | 0.2 | 0 | 0.304 | 2.9665 | 4.8 | 4.8927 | 1.0704 | 0.0026037
2016-08-21 22:00 | 4.2567 | 2.4667 | 1.79 | 0 | 12.1218 | 164.8741 | 90.4738 | -0.4738 | 165.2186 | 147.2958 | 0 | 1.85 | 0.2 | 0 | 0.21283 | 2.0628 | 3.7 | 3.7645 | 1.0743 | 0.0018172
2016-08-21 23:00 | 2.4333 | 1.3833 | 1.05 | 0 | 12.108 | 179.8767 | 90.9253 | -0.92532 | 179.8795 | 150.9251 | 0 | 1.0375 | 0.2 | 0 | 0.12167 | 1.1592 | 2.5 | 2.5362 | 1.0786 | 0.0010252
2016-08-22 | 0.61 | 0.3 | 0.31 | 0 | 12.0942 | -165.1206 | 90.5155 | -0.5155 | -165.4577 | 147.4311 | 0 | 0.225 | 0.2 | 0 | 0.0305 | 0.2555 | 2.1 | 2.108 | 1.0801 | 0.0002263
2016-08-22 01:00 | 18.7133 | 7.41 | 11.3033 | 0 | 12.0803 | -150.118 | 89.2732 | 0.72683 | -150.8419 | 138.5798 | 0 | 5.5575 | 0.2 | 0 | 0.93567 | 6.4932 | 2.1005 | 2.3034 | 1.0794 | 0.0057474
2016-08-22 02:00 | 36.8167 | 14.52 | 22.2967 | 0 | 12.0665 | -135.1154 | 87.2829 | 2.7171 | -136.3012 | 126.9928 | 0 | 10.89 | 0.2 | 0 | 1.8408 | 12.7308 | 2.1009 | 2.4987 | 1.0788 | 0.011261
2016-08-22 03:00 | 54.92 | 21.63 | 33.29 | 358.7987 | 12.0526 | -120.1127 | 84.6763 | 5.3237 | -121.8279 | 114.1015 | 0 | 16.2225 | 0.2 | 0 | 2.746 | 18.9685 | 2.1014 | 2.6941 | 1.0781 | 0.016768
2016-08-22 04:00 | 100.2733 | 38.9067 | 61.3667 | 421.1664 | 12.0388 | -105.1101 | 81.6218 | 8.3782 | -107.3734 | 100.5434 | 0 | 29.18 | 0.2 | 0 | 5.0137 | 34.1937 | 2.1018 | 3.1704 | 1.0764 | 0.030181
2016-08-22 05:00 | 145.6267 | 56.1833 | 89.4433 | 441.5729 | 12.0249 | -90.1074 | 78.3135 | 11.6865 | -92.8546 | 86.6152 | 26.0714 | 42.1375 | 0.2 | 0 | 7.2813 | 75.4902 | 2.1023 | 4.4613 | 1.0719 | 0.066352
2016-08-22 06:00 | 190.98 | 73.46 | 117.52 | 452.9758 | 12.011 | -75.1048 | 74.9632 | 15.0368 | -78.1682 | 72.4698 | 136.4401 | 55.095 | 0.2 | 0 | 9.549 | 201.0841 | 2.1027 | 8.3866 | 1.0581 | 0.17448
2016-08-22 07:00 | 244.6 | 86.41 | 158.19 | 506.2667 | 11.9972 | -60.1021 | 71.7922 | 18.2078 | -63.2115 | 58.1967 | 266.8049 | 64.8075 | 0.2 | 0 | 12.23 | 343.8424 | 2.1032 | 12.8483 | 1.0425 | 0.29394
2016-08-22 08:00 | 298.22 | 99.36 | 198.86 | 555.48 | 11.9833 | -45.0994 | 69.0228 | 20.9772 | -47.9089 | 43.8604 | 400.5181 | 74.52 | 0.2 | 0 | 14.911 | 489.9491 | 2.1036 | 17.4145 | 1.0265 | 0.41242
2016-08-22 09:00 | 351.84 | 112.31 | 239.53 | 609.6184 | 11.9694 | -30.0968 | 66.8638 | 23.1362 | -32.2398 | 29.5355 | 530.3986 | 84.2325 | 0.2 | 0 | 17.592 | 632.2231 | 2.1041 | 21.8611 | 1.011 | 0.52412
2016-08-22 10:00 | 356.8067 | 121.3433 | 235.4633 | 567.6142 | 11.9555 | -15.0941 | 65.4914 | 24.5086 | -16.2592 | 15.4433 | 547.1203 | 91.0075 | 0.2 | 0 | 17.8403 | 655.9681 | 2.1045 | 22.6035 | 1.0084 | 0.54241
2016-08-22 11:00 | 361.7733 | 130.3767 | 231.3967 | 548.0457 | 11.9416 | -0.091425 | 65.0251 | 24.9749 | -0.098673 | 5.0258 | 545.9386 | 97.7825 | 0.2 | 0 | 18.0887 | 661.8098 | 2.105 | 22.7865 | 1.0077 | 0.54689
2016-08-22 12:00 | 366.74 | 139.41 | 227.33 | 548.3492 | 11.9277 | 14.9113 | 65.5077 | 24.4923 | 16.0611 | 15.286 | 528.9496 | 104.5575 | 0.2 | 0 | 18.337 | 651.8441 | 2.1054 | 22.4756 | 1.0088 | 0.53923
2016-08-22 13:00 | 338.65 | 104.6733 | 233.9767 | 596.2944 | 11.9138 | 29.9139 | 66.8971 | 23.1029 | 32.0394 | 29.3744 | 519.6305 | 78.505 | 0.2 | 0 | 16.9325 | 615.068 | 2.1059 | 21.3268 | 1.0129 | 0.51084
2016-08-22 14:00 | 310.56 | 69.9367 | 240.6233 | 673.7217 | 11.8999 | 44.9166 | 69.0744 | 20.9256 | 47.7049 | 43.7031 | 487.0539 | 52.4525 | 0.2 | 0 | 15.528 | 555.0344 | 2.1063 | 19.4512 | 1.0194 | 0.46397
2016-08-22 15:00 | 282.47 | 35.2 | 247.27 | 794.3931 | 11.886 | 59.9193 | 71.8643 | 18.1357 | 63.0033 | 58.0467 | 420.4154 | 26.4 | 0.2 | 0 | 14.1235 | 460.9389 | 2.1068 | 16.5111 | 1.0297 | 0.3892
2016-08-22 16:00 | 216.8267 | 39.3167 | 177.51 | 688.4583 | 11.872 | 74.922 | 75.0582 | 14.9418 | 77.9555 | 72.3307 | 208.9632 | 29.4875 | 0.2 | 0 | 10.8413 | 249.292 | 2.1073 | 9.8976 | 1.0529 | 0.21522
2016-08-22 17:00 | 151.1833 | 43.4333 | 107.75 | 537.4458 | 11.8581 | 89.9247 | 78.4347 | 11.5653 | 92.6378 | 86.4916 | 32.889 | 32.575 | 0.2 | 0 | 7.5592 | 73.0232 | 2.1077 | 4.3897 | 1.0721 | 0.064198
2016-08-22 18:00 | 85.54 | 47.55 | 37.99 | 265.4639 | 11.8442 | 104.9274 | 81.7723 | 8.2277 | 107.1539 | 100.4421 | 0 | 35.6625 | 0.2 | 0 | 4.277 | 39.9395 | 2.1082 | 3.3563 | 1.0758 | 0.035231
2016-08-22 19:00 | 58.6533 | 32.6933 | 25.96 | 289.7293 | 11.8302 | 119.9301 | 84.8594 | 5.1406 | 121.6082 | 114.0331 | 0 | 24.52 | 0.2 | 0 | 2.9327 | 27.4527 | 2.1086 | 2.9665 | 1.0771 | 0.024247
2016-08-22 20:00 | 31.7667 | 17.8367 | 13.93 | 0 | 11.8163 | 134.9328 | 87.5013 | 2.4987 | 136.0848 | 126.9749 | 0 | 13.3775 | 0.2 | 0 | 1.5883 | 14.9658 | 2.1091 | 2.5768 | 1.0785 | 0.013235
2016-08-22 21:00 | 4.88 | 2.98 | 1.9 | 0 | 11.8024 | 149.9355 | 89.5292 | 0.47076 | 150.6331 | 138.6429 | 0 | 2.235 | 0.2 | 0 | 0.244 | 2.479 | 2.1095 | 2.187 | 1.0798 | 0.0021951
2016-08-22 22:00 | 3.3467 | 2.0333 | 1.3133 | 0 | 11.7884 | 164.9382 | 90.8103 | -0.81033 | 165.2617 | 147.6204 | 0 | 1.525 | 0.2 | 0 | 0.16733 | 1.6923 | 2.11 | 2.1629 | 1.0799 | 0.0014986
2016-08-22 23:00 | 1.8133 | 1.0867 | 0.72667 | 0 | 11.7744 | 179.941 | 91.2589 | -1.2589 | 179.9422 | 151.2588 | 0 | 0.815 | 0.2 | 0 | 0.090667 | 0.90567 | 2.1104 | 2.1387 | 1.08 | 0.00080207
2016-08-23 | 0.28 | 0.14 | 0.14 | 0 | 11.7605 | -165.0563 | 90.845 | -0.84496 | -165.3755 | 147.6987 | 0 | 0.105 | 0.2 | 0 | 0.014 | 0.119 | 2.1109 | 2.1146 | 1.0801 | 0.0001054
2016-08-23 01:00 | 16.6267 | 7.0933 | 9.5333 | 0 | 11.7465 | -150.0536 | 89.5978 | 0.40224 | -150.7417 | 138.7651 | 0 | 5.32 | 0.2 | 0 | 0.83133 | 6.1513 | 2.1113 | 2.3036 | 1.0794 | 0.0054448
2016-08-23 02:00 | 32.9733 | 14.0467 | 18.9267 | 0 | 11.7325 | -135.0509 | 87.6025 | 2.3975 | -136.1856 | 127.1173 | 0 | 10.535 | 0.2 | 0 | 1.6487 | 12.1837 | 2.1118 | 2.4925 | 1.0788 | 0.010778
2016-08-23 03:00 | 49.32 | 21 | 28.32 | 324.388 | 11.7186 | -120.0481 | 84.9915 | 5.0085 | -121.6999 | 114.1848 | 0 | 15.75 | 0.2 | 0 | 2.466 | 18.216 | 2.1122 | 2.6815 | 1.0781 | 0.016104
2016-08-23 04:00 | 102.7133 | 28.58 | 74.1333 | 528.3324 | 11.7046 | -105.0454 | 81.9339 | 8.0661 | -107.2367 | 100.5984 | 0 | 21.435 | 0.2 | 0 | 5.1357 | 26.5707 | 2.1127 | 2.943 | 1.0772 | 0.02347
2016-08-23 05:00 | 156.1067 | 36.16 | 119.9467 | 608.1194 | 11.6906 | -90.0427 | 78.6243 | 11.3757 | -92.7132 | 86.6502 | 35.5337 | 27.12 | 0.2 | 0 | 7.8053 | 70.459 | 2.1132 | 4.315 | 1.0724 | 0.061959
2016-08-23 06:00 | 209.5 | 43.74 | 165.76 | 652.1231 | 11.6766 | -75.0399 | 75.2747 | 14.7253 | -78.0262 | 72.4907 | 196.1979 | 32.805 | 0.2 | 0 | 10.475 | 239.4779 | 2.1136 | 9.5973 | 1.0539 | 0.20696
2016-08-23 07:00 | 249.39 | 56.1 | 193.29 | 629.1027 | 11.6626 | -60.0372 | 72.1066 | 17.8934 | -63.0738 | 58.2086 | 331.4287 | 42.075 | 0.2 | 0 | 12.4695 | 385.9732 | 2.1141 | 14.1757 | 1.0379 | 0.32849
2016-08-23 08:00 | 289.28 | 68.46 | 220.82 | 625.9176 | 11.6486 | -45.0344 | 69.3417 | 20.6583 | -47.7807 | 43.8693 | 451.2379 | 51.345 | 0.2 | 0 | 14.464 | 517.0469 | 2.1145 | 18.2722 | 1.0235 | 0.43396
2016-08-23 09:00 | 329.17 | 80.82 | 248.35 | 640.566 | 11.6346 | -30.0317 | 67.1883 | 22.8117 | -32.1265 | 29.5526 | 557.2306 | 60.615 | 0.2 | 0 | 16.4585 | 634.3041 | 2.115 | 21.937 | 1.0107 | 0.52571
2016-08-23 10:00 | 342.1 | 85.61 | 256.49 | 626.227 | 11.6205 | -15.0289 | 65.8216 | 24.1784 | -16.1657 | 15.5056 | 603.4352 | 64.2075 | 0.2 | 0 | 17.105 | 684.7477 | 2.1154 | 23.5138 | 1.0052 | 0.56441
2016-08-23 11:00 | 355.03 | 90.4 | 264.63 | 634.7365 | 11.6065 | -0.026139 | 65.3601 | 24.6399 | -0.028169 | 5.3602 | 631.9609 | 67.8 | 0.2 | 0 | 17.7515 | 717.5124 | 2.1159 | 24.5381 | 1.0016 | 0.58931
2016-08-23 12:00 | 367.96 | 95.19 | 272.77 | 666.6156 | 11.5925 | 14.9766 | 65.8463 | 24.1537 | 16.1077 | 15.4686 | 642.4687 | 71.3925 | 0.2 | 0 | 18.398 | 732.2592 | 2.1163 | 24.9994 | 1 | 0.60045
2016-08-23 13:00 | 326.05 | 90.7667 | 235.2833 | 608.1105 | 11.5785 | 29.9794 | 67.2377 | 22.7623 | 32.0639 | 29.5165 | 529.1863 | 68.075 | 0.2 | 0 | 16.3025 | 613.5638 | 2.1168 | 21.2906 | 1.013 | 0.50965
2016-08-23 14:00 | 284.14 | 86.3433 | 197.7967 | 562.5904 | 11.5644 | 44.9822 | 69.4159 | 20.5841 | 47.7115 | 43.8376 | 405.8001 | 64.7575 | 0.2 | 0 | 14.207 | 484.7646 | 2.1172 | 17.2661 | 1.0271 | 0.40827
2016-08-23 15:00 | 242.23 | 81.92 | 160.31 | 524.5796 | 11.5504 | 59.9849 | 72.2059 | 17.7941 | 62.997 | 58.1838 | 276.5561 | 61.44 | 0.2 | 0 | 12.1115 | 350.1076 | 2.1177 | 13.0586 | 1.0418 | 0.29909
2016-08-23 16:00 | 186.65 | 68.63 | 118.02 | 468.1991 | 11.5363 | 74.9877 | 75.3998 | 14.6002 | 77.9421 | 72.4759 | 140.9779 | 51.4725 | 0.2 | 0 | 9.3325 | 201.7829 | 2.1181 | 8.4239 | 1.058 | 0.17506
2016-08-23 17:00 | 131.07 | 55.34 | 75.73 | 389.0777 | 11.5223 | 89.9905 | 78.7763 | 11.2237 | 92.623 | 86.6494 | 22.7396 | 41.505 | 0.2 | 0 | 6.5535 | 70.7981 | 2.1186 | 4.331 | 1.0723 | 0.062254
2016-08-23 18:00 | 75.49 | 42.05 | 33.44 | 243.7335 | 11.5082 | 104.9933 | 82.1142 | 7.8858 | 107.1428 | 100.6175 | 0 | 31.5375 | 0.2 | 0 | 3.7745 | 35.312 | 2.119 | 3.2225 | 1.0762 | 0.031163
2016-08-23 19:00 | 51.42 | 28.8333 | 22.5867 | 270.0136 | 11.4942 | 119.9961 | 85.2016 | 4.7984 | 121.6056 | 114.2326 | 0 | 21.625 | 0.2 | 0 | 2.571 | 24.196 | 2.1195 | 2.8756 | 1.0774 | 0.021377
2016-08-23 20:00 | 27.35 | 15.6167 | 11.7333 | 0 | 11.4801 | 134.9989 | 87.8435 | 2.1565 | 136.095 | 127.2078 | 0 | 11.7125 | 0.2 | 0 | 1.3675 | 13.08 | 2.12 | 2.5287 | 1.0786 | 0.011569
2016-08-23 21:00 | 3.28 | 2.4 | 0.88 | 0 | 11.466 | 150.0017 | 89.8707 | 0.12925 | 150.6596 | 138.9211 | 0 | 1.8 | 0.2 | 0 | 0.164 | 1.964 | 2.1204 | 2.1818 | 1.0799 | 0.0017391
2016-08-23 22:00 | 2.21 | 1.6233 | 0.58667 | 0 | 11.4519 | 165.0045 | 91.15 | -1.15 | 165.3068 | 147.9484 | 0 | 1.2175 | 0.2 | 0 | 0.1105 | 1.328 | 2.1209 | 2.1624 | 1.0799 | 0.001176
2016-08-23 23:00 | 1.14 | 0.84667 | 0.29333 | 0 | 11.4378 | 180.0073 | 91.5955 | -1.5955 | -179.9929 | 151.5955 | 0 | 0.635 | 0.2 | 0 | 0.057 | 0.692 | 2.1213 | 2.1429 | 1.08 | 0.00061284
2016-08-24 | 0.07 | 0.07 | 0 | 0 | 11.4238 | -164.9899 | 91.1773 | -1.1773 | -165.2909 | 147.9667 | 0 | 0.0525 | 0.2 | 0 | 0.0035 | 0.056 | 2.1218 | 2.1235 | 1.0801 | 4.9597e-05
2016-08-24 01:00 | 10.94 | 10.51 | 0.43 | 0 | 11.4097 | -149.9871 | 89.9251 | 0.074879 | -150.639 | 138.9493 | 0 | 7.8825 | 0.2 | 0 | 0.547 | 8.4295 | 2.1222 | 2.3856 | 1.0792 | 0.0074593
2016-08-24 02:00 | 21.81 | 20.95 | 0.86 | 0 | 11.3956 | -134.9843 | 87.9247 | 2.0753 | -136.0673 | 127.2402 | 0 | 15.7125 | 0.2 | 0 | 1.0905 | 16.803 | 2.1227 | 2.6478 | 1.0782 | 0.014856
2016-08-24 03:00 | 32.68 | 31.39 | 1.29 | 15.7746 | 11.3815 | -119.9815 | 85.3093 | 4.6907 | -121.5693 | 114.2666 | 0 | 23.5425 | 0.2 | 0 | 1.634 | 25.1765 | 2.1231 | 2.9099 | 1.0773 | 0.022241
2016-08-24 04:00 | 70.73 | 66.2067 | 4.5233 | 33.5366 | 11.3673 | -104.9786 | 82.2485 | 7.7515 | -107.0974 | 100.652 | 0 | 49.655 | 0.2 | 0 | 3.5365 | 53.1915 | 2.1236 | 3.7858 | 1.0742 | 0.046856
2016-08-24 05:00 | 108.78 | 101.0233 | 7.7567 | 40.4247 | 11.3532 | -89.9758 | 78.9375 | 11.0625 | -92.5691 | 86.684 | 2.3382 | 75.7675 | 0.2 | 0 | 5.439 | 83.5447 | 2.124 | 4.7348 | 1.0709 | 0.073366
2016-08-24 06:00 | 146.83 | 135.84 | 10.99 | 44.1578 | 11.3391 | -74.973 | 75.5887 | 14.4113 | -77.8817 | 72.5109 | 13.2705 | 101.88 | 0.2 | 0 | 7.3415 | 122.492 | 2.1245 | 5.9524 | 1.0667 | 0.10714
2016-08-24 07:00 | 187.73 | 165.4967 | 22.2333 | 73.6256 | 11.325 | -59.9701 | 72.4235 | 17.5765 | -62.9336 | 58.2204 | 38.7752 | 124.1225 | 0.2 | 0 | 9.3865 | 172.2842 | 2.1249 | 7.5088 | 1.0612 | 0.14992
2016-08-24 08:00 | 228.63 | 195.1533 | 33.4767 | 96.3256 | 11.3109 | -44.9673 | 69.6633 | 20.3367 | -47.6501 | 43.8789 | 69.4321 | 146.365 | 0.2 | 0 | 11.4315 | 227.2286 | 2.1254 | 9.2263 | 1.0552 | 0.19661
2016-08-24 09:00 | 269.53 | 224.81 | 44.72 | 116.9356 | 11.2967 | -29.9645 | 67.5156 | 22.4844 | -32.0109 | 29.5718 | 101.7033 | 168.6075 | 0.2 | 0 | 13.4765 | 283.7873 | 2.1259 | 10.9942 | 1.049 | 0.24411
2016-08-24 10:00 | 265.9967 | 222.97 | 43.0267 | 106.4305 | 11.2826 | -14.9616 | 66.1546 | 23.8454 | -16.07 | 15.574 | 102.5229 | 167.2275 | 0.2 | 0 | 13.2998 | 283.0502 | 2.1263 | 10.9716 | 1.0491 | 0.2435
2016-08-24 11:00 | 262.4633 | 221.13 | 41.3333 | 100.4352 | 11.2684 | 0.041234 | 65.6982 | 24.3018 | 0.04437 | 5.6984 | 99.9389 | 165.8475 | 0.2 | 0 | 13.1232 | 278.9095 | 2.1268 | 10.8427 | 1.0496 | 0.24004
2016-08-24 12:00 | 258.93 | 219.29 | 39.64 | 98.1828 | 11.2543 | 15.0441 | 66.188 | 23.812 | 16.1562 | 15.6595 | 94.5385 | 164.4675 | 0.2 | 0 | 12.9465 | 271.9525 | 2.1272 | 10.6257 | 1.0503 | 0.23422
2016-08-24 13:00 | 233.06 | 179.7633 | 53.2967 | 139.7515 | 11.2401 | 30.0469 | 67.5816 | 22.4184 | 32.0903 | 29.6644 | 121.4356 | 134.8225 | 0.2 | 0 | 11.653 | 267.9111 | 2.1277 | 10.4999 | 1.0508 | 0.23084
2016-08-24 14:00 | 207.19 | 140.2367 | 66.9533 | 193.5392 | 11.226 | 45.0498 | 69.7607 | 20.2393 | 47.7197 | 43.9766 | 139.2753 | 105.1775 | 0.2 | 0 | 10.3595 | 254.8123 | 2.1281 | 10.091 | 1.0522 | 0.21985
2016-08-24 15:00 | 181.32 | 100.71 | 80.61 | 268.827 | 11.2118 | 60.0527 | 72.5509 | 17.4491 | 62.9923 | 58.3248 | 141.1618 | 75.5325 | 0.2 | 0 | 9.066 | 225.7603 | 2.1286 | 9.1836 | 1.0554 | 0.19537
2016-08-24 16:00 | 141.9433 | 79.6533 | 62.29 | 252.9634 | 11.1976 | 75.0555 | 75.7448 | 14.2552 | 77.9303 | 72.6246 | 75.5428 | 59.74 | 0.2 | 0 | 7.0972 | 142.38 | 2.129 | 6.5784 | 1.0645 | 0.12428
2016-08-24 17:00 | 102.5667 | 58.5967 | 43.97 | 232.9794 | 11.1835 | 90.0584 | 79.1214 | 10.8786 | 92.6097 | 86.8103 | 12.9633 | 43.9475 | 0.2 | 0 | 5.1283 | 62.0392 | 2.1295 | 4.0682 | 1.0733 | 0.054599
2016-08-24 18:00 | 63.19 | 37.54 | 25.65 | 195.4631 | 11.1693 | 105.0613 | 82.4595 | 7.5405 | 107.1333 | 100.7957 | 0 | 28.155 | 0.2 | 0 | 3.1595 | 31.3145 | 2.1299 | 3.1085 | 1.0766 | 0.027645
2016-08-24 19:00 | 42.7767 | 25.58 | 17.1967 | 221.497 | 11.1551 | 120.0641 | 85.5472 | 4.4528 | 121.6046 | 114.4347 | 0 | 19.185 | 0.2 | 0 | 2.1388 | 21.3238 | 2.1304 | 2.7968 | 1.0777 | 0.018844
2016-08-24 20:00 | 22.3633 | 13.62 | 8.7433 | 0 | 11.1409 | 135.067 | 88.1891 | 1.8109 | 136.1069 | 127.4432 | 0 | 10.215 | 0.2 | 0 | 1.1182 | 11.3332 | 2.1308 | 2.485 | 1.0788 | 0.010026
2016-08-24 21:00 | 1.95 | 1.66 | 0.29 | 0 | 11.1267 | 150.0699 | 90.2154 | -0.21544 | 150.6878 | 139.2021 | 0 | 1.245 | 0.2 | 0 | 0.0975 | 1.3425 | 2.1313 | 2.1732 | 1.0799 | 0.0011888
2016-08-24 22:00 | 1.3 | 1.1067 | 0.19333 | 0 | 11.1125 | 165.0728 | 91.4928 | -1.4928 | 165.3539 | 148.2798 | 0 | 0.83 | 0.2 | 0 | 0.065 | 0.895 | 2.1317 | 2.1597 | 1.0799 | 0.00079257
2016-08-24 23:00 | 0.65 | 0.55333 | 0.096667 | 0 | 11.0983 | 180.0757 | 91.935 | -1.935 | -179.9257 | 151.9349 | 0 | 0.415 | 0.2 | 0 | 0.0325 | 0.4475 | 2.1322 | 2.1462 | 1.08 | 0.0003963
2016-08-25 | 0 | 0 | 0 | 0 | 11.0841 | -164.9214 | 91.5125 | -1.5125 | -165.2039 | 148.235 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1327 | 2.1327 | 1.08 | 0
2016-08-25 01:00 | 7.5667 | 7.5233 | 0.043333 | 0 | 11.0699 | -149.9185 | 90.2552 | -0.25516 | -150.5338 | 139.1322 | 0 | 5.6425 | 0.2 | 0 | 0.37833 | 6.0208 | 2.1331 | 2.3213 | 1.0794 | 0.005329
2016-08-25 02:00 | 15.1333 | 15.0467 | 0.086667 | 0 | 11.0556 | -134.9156 | 88.2495 | 1.7505 | -135.9465 | 127.3614 | 0 | 11.285 | 0.2 | 0 | 0.75667 | 12.0417 | 2.1336 | 2.5099 | 1.0787 | 0.010651
2016-08-25 03:00 | 22.7 | 22.57 | 0.13 | 1.7059 | 11.0414 | -119.9127 | 85.6295 | 4.3705 | -121.4361 | 114.3467 | 0 | 16.9275 | 0.2 | 0 | 1.135 | 18.0625 | 2.134 | 2.6985 | 1.0781 | 0.015967
2016-08-25 04:00 | 52.4033 | 47.9567 | 4.4467 | 34.3655 | 11.0272 | -104.9098 | 82.5655 | 7.4345 | -106.9555 | 100.7042 | 0 | 35.9675 | 0.2 | 0 | 2.6202 | 38.5877 | 2.1345 | 3.3403 | 1.0758 | 0.034041
2016-08-25 05:00 | 82.1067 | 73.3433 | 8.7633 | 46.9961 | 11.0129 | -89.9069 | 79.2532 | 10.7468 | -92.4225 | 86.7168 | 2.6915 | 55.0075 | 0.2 | 0 | 4.1053 | 61.8044 | 2.1349 | 4.0663 | 1.0733 | 0.054393
2016-08-25 06:00 | 111.81 | 98.73 | 13.08 | 53.7108 | 10.9987 | -74.904 | 75.9052 | 14.0948 | -77.7348 | 72.5304 | 16.124 | 74.0475 | 0.2 | 0 | 5.5905 | 95.762 | 2.1354 | 5.1279 | 1.0696 | 0.083986
2016-08-25 07:00 | 158.25 | 116.44 | 41.81 | 140.9366 | 10.9845 | -59.9011 | 72.743 | 17.257 | -62.7911 | 58.2319 | 74.2006 | 87.33 | 0.2 | 0 | 7.9125 | 169.4431 | 2.1358 | 7.4309 | 1.0615 | 0.14749
2016-08-25 08:00 | 204.69 | 134.15 | 70.54 | 206.1214 | 10.9702 | -44.8982 | 69.9875 | 20.0125 | -47.5173 | 43.8892 | 148.5479 | 100.6125 | 0.2 | 0 | 10.2345 | 259.3949 | 2.1363 | 10.2424 | 1.0517 | 0.22369
2016-08-25 09:00 | 251.13 | 151.86 | 99.27 | 263.2424 | 10.956 | -29.8952 | 67.8455 | 22.1545 | -31.8932 | 29.5934 | 228.9029 | 113.895 | 0.2 | 0 | 12.5565 | 355.3544 | 2.1367 | 13.2416 | 1.0412 | 0.30338
2016-08-25 10:00 | 265.48 | 148.9233 | 116.5567 | 292.1944 | 10.9417 | -14.8923 | 66.4905 | 23.5095 | -15.9722 | 15.6489 | 281.3636 | 111.6925 | 0.2 | 0 | 13.274 | 406.3301 | 2.1372 | 14.835 | 1.0356 | 0.34504
2016-08-25 11:00 | 279.83 | 145.9867 | 133.8433 | 329.5737 | 10.9274 | 0.11063 | 66.0393 | 23.9607 | 0.11887 | 6.0402 | 327.744 | 109.49 | 0.2 | 0 | 13.9915 | 451.2255 | 2.1376 | 16.2384 | 1.0307 | 0.38135
2016-08-25 12:00 | 294.18 | 143.05 | 151.13 | 379.5101 | 10.9132 | 15.1136 | 66.5328 | 23.4672 | 16.2067 | 15.8587 | 365.0654 | 107.2875 | 0.2 | 0 | 14.709 | 487.0619 | 2.1381 | 17.3588 | 1.0267 | 0.41007
2016-08-25 13:00 | 238.56 | 135.3067 | 103.2533 | 274.7843 | 10.8989 | 30.1165 | 67.9286 | 22.0714 | 32.1185 | 29.818 | 238.4054 | 101.48 | 0.2 | 0 | 11.928 | 351.8134 | 2.1385 | 13.1327 | 1.0415 | 0.30047
2016-08-25 14:00 | 182.94 | 127.5633 | 55.3767 | 162.7593 | 10.8846 | 45.1194 | 70.1087 | 19.8913 | 47.7296 | 44.1203 | 116.8417 | 95.6725 | 0.2 | 0 | 9.147 | 221.6612 | 2.139 | 9.0659 | 1.0558 | 0.1919
2016-08-25 15:00 | 127.32 | 119.82 | 7.5 | 25.5055 | 10.8703 | 60.1224 | 72.8992 | 17.1008 | 62.9893 | 58.4697 | 13.3381 | 89.865 | 0.2 | 0 | 6.366 | 109.5691 | 2.1395 | 5.5635 | 1.068 | 0.095959
2016-08-25 16:00 | 99.1733 | 91.8367 | 7.3367 | 30.5255 | 10.856 | 75.1253 | 76.0931 | 13.9069 | 77.92 | 72.7765 | 9.0386 | 68.8775 | 0.2 | 0 | 4.9587 | 82.8747 | 2.1399 | 4.7297 | 1.0709 | 0.072779
2016-08-25 17:00 | 71.0267 | 63.8533 | 7.1733 | 39.2511 | 10.8417 | 90.1283 | 79.4697 | 10.5303 | 92.5978 | 86.9742 | 2.0719 | 47.89 | 0.2 | 0 | 3.5513 | 53.5132 | 2.1404 | 3.8127 | 1.0742 | 0.047135
2016-08-25 18:00 | 42.88 | 35.87 | 7.01 | 55.9935 | 10.8274 | 105.1312 | 82.8081 | 7.1919 | 107.1251 | 100.9765 | 0 | 26.9025 | 0.2 | 0 | 2.144 | 29.0465 | 2.1408 | 3.0485 | 1.0768 | 0.025648
2016-08-25 19:00 | 28.9767 | 24.2733 | 4.7033 | 65.7188 | 10.8131 | 120.1342 | 85.896 | 4.104 | 121.6052 | 114.6393 | 0 | 18.205 | 0.2 | 0 | 1.4488 | 19.6538 | 2.1413 | 2.7555 | 1.0779 | 0.017371
2016-08-25 20:00 | 15.0733 | 12.6767 | 2.3967 | 0 | 10.7988 | 135.1372 | 88.5377 | 1.4623 | 136.1204 | 127.6811 | 0 | 9.5075 | 0.2 | 0 | 0.75367 | 10.2612 | 2.1417 | 2.4624 | 1.0789 | 0.0090779
2016-08-25 21:00 | 1.17 | 1.08 | 0.09 | 0 | 10.7845 | 150.1401 | 90.5632 | -0.56321 | 150.7179 | 139.4858 | 0 | 0.81 | 0.2 | 0 | 0.0585 | 0.8685 | 2.1422 | 2.1693 | 1.0799 | 0.00076908
2016-08-25 22:00 | 0.78 | 0.72 | 0.06 | 0 | 10.7702 | 165.1431 | 91.8385 | -1.8385 | 165.403 | 148.6144 | 0 | 0.54 | 0.2 | 0 | 0.039 | 0.579 | 2.1426 | 2.1607 | 1.0799 | 0.00051273
2016-08-25 23:00 | 0.39 | 0.36 | 0.03 | 0 | 10.7559 | 180.1461 | 92.2774 | -2.2774 | -179.8564 | 152.2771 | 0 | 0.27 | 0.2 | 0 | 0.0195 | 0.2895 | 2.1431 | 2.1521 | 1.08 | 0.00025637
2016-08-26 | 0 | 0 | 0 | 0 | 10.7415 | -164.851 | 91.8504 | -1.8504 | -165.1146 | 148.5034 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1435 | 2.1435 | 1.08 | 0
2016-08-26 01:00 | 9.1767 | 7.69 | 1.4867 | 0 | 10.7272 | -149.848 | 90.5878 | -0.58778 | -150.4262 | 139.3137 | 0 | 5.7675 | 0.2 | 0 | 0.45883 | 6.2263 | 2.144 | 2.3386 | 1.0793 | 0.0055105
2016-08-26 02:00 | 18.3533 | 15.38 | 2.9733 | 0 | 10.7129 | -134.845 | 88.5768 | 1.4232 | -135.8232 | 127.4809 | 0 | 11.535 | 0.2 | 0 | 0.91767 | 12.4527 | 2.1444 | 2.5336 | 1.0786 | 0.011014
2016-08-26 03:00 | 27.53 | 23.07 | 4.46 | 63.1822 | 10.6985 | -119.842 | 85.9522 | 4.0478 | -121.3004 | 114.4252 | 0 | 17.3025 | 0.2 | 0 | 1.3765 | 18.679 | 2.1449 | 2.7286 | 1.0779 | 0.016511
2016-08-26 04:00 | 64.16 | 50.0633 | 14.0967 | 113.8074 | 10.6842 | -104.839 | 82.8848 | 7.1152 | -106.8112 | 100.755 | 0 | 37.5475 | 0.2 | 0 | 3.208 | 40.7555 | 2.1454 | 3.419 | 1.0755 | 0.035944
2016-08-26 05:00 | 100.79 | 77.0567 | 23.7333 | 131.1137 | 10.6698 | -89.836 | 79.5712 | 10.4288 | -92.2735 | 86.7485 | 7.4367 | 57.7925 | 0.2 | 0 | 5.0395 | 70.2687 | 2.1458 | 4.3417 | 1.0723 | 0.061786
2016-08-26 06:00 | 137.42 | 104.05 | 33.37 | 140.1366 | 10.6555 | -74.833 | 76.2241 | 13.7759 | -77.5855 | 72.5492 | 42.0252 | 78.0375 | 0.2 | 0 | 6.871 | 126.9337 | 2.1463 | 6.1129 | 1.0661 | 0.11097
2016-08-26 07:00 | 178.7367 | 102.9867 | 75.75 | 260.0519 | 10.6411 | -59.83 | 73.0649 | 16.9351 | -62.6463 | 58.2434 | 136.8683 | 77.24 | 0.2 | 0 | 8.9368 | 223.0451 | 2.1467 | 9.1169 | 1.0556 | 0.19306
2016-08-26 08:00 | 220.0533 | 101.9233 | 118.13 | 350.6778 | 10.6267 | -44.827 | 70.3142 | 19.6858 | -47.3823 | 43.9003 | 252.6801 | 76.4425 | 0.2 | 0 | 11.0027 | 340.1252 | 2.1472 | 12.7761 | 1.0428 | 0.29084
2016-08-26 09:00 | 261.37 | 100.86 | 160.51 | 431.801 | 10.6123 | -29.824 | 68.1781 | 21.8219 | -31.7735 | 29.6174 | 375.384 | 75.645 | 0.2 | 0 | 13.0685 | 464.0975 | 2.1476 | 16.6507 | 1.0292 | 0.39168
2016-08-26 10:00 | 267.9167 | 113.7833 | 154.1333 | 391.7238 | 10.598 | -14.821 | 66.8291 | 23.1709 | -15.8726 | 15.7302 | 377.0534 | 85.3375 | 0.2 | 0 | 13.3958 | 475.7867 | 2.1481 | 17.0164 | 1.0279 | 0.40105
2016-08-26 11:00 | 274.4633 | 126.7067 | 147.7567 | 368.8213 | 10.5836 | 0.18199 | 66.3831 | 23.6169 | 0.19525 | 6.3855 | 366.5332 | 95.03 | 0.2 | 0 | 13.7232 | 475.2863 | 2.1485 | 17.0012 | 1.028 | 0.40065
2016-08-26 12:00 | 281.01 | 139.63 | 141.38 | 360.0669 | 10.5692 | 15.185 | 66.8806 | 23.1194 | 16.2589 | 16.0659 | 346.0042 | 104.7225 | 0.2 | 0 | 14.0505 | 464.7772 | 2.149 | 16.6733 | 1.0291 | 0.39222
2016-08-26 13:00 | 239.5933 | 132.7933 | 106.8 | 288.5768 | 10.5548 | 30.188 | 68.2787 | 21.7213 | 32.1484 | 29.9774 | 249.9717 | 99.595 | 0.2 | 0 | 11.9797 | 361.5464 | 2.1494 | 13.4478 | 1.0404 | 0.30846
2016-08-26 14:00 | 198.1767 | 125.9567 | 72.22 | 215.9254 | 10.5404 | 45.191 | 70.4598 | 19.5402 | 47.7412 | 44.2684 | 154.6194 | 94.4675 | 0.2 | 0 | 9.9088 | 258.9958 | 2.1499 | 10.2435 | 1.0516 | 0.22335
2016-08-26 15:00 | 156.76 | 119.12 | 37.64 | 130.61 | 10.526 | 60.1941 | 73.2506 | 16.7494 | 62.9878 | 58.6182 | 68.0135 | 89.34 | 0.2 | 0 | 7.838 | 165.1915 | 2.1503 | 7.3126 | 1.0619 | 0.14384
2016-08-26 16:00 | 123.44 | 90.5433 | 32.8967 | 140.3521 | 10.5116 | 75.1971 | 76.4445 | 13.5555 | 77.9112 | 72.9318 | 41.1948 | 67.9075 | 0.2 | 0 | 6.172 | 115.2743 | 2.1508 | 5.7531 | 1.0674 | 0.10089
2016-08-26 17:00 | 90.12 | 61.9667 | 28.1533 | 159.3108 | 10.4972 | 90.2001 | 79.8213 | 10.1787 | 92.5874 | 87.1409 | 7.9464 | 46.475 | 0.2 | 0 | 4.506 | 58.9274 | 2.1512 | 3.9927 | 1.0735 | 0.051873
2016-08-26 18:00 | 56.8 | 33.39 | 23.41 | 196.5578 | 10.4828 | 105.2032 | 83.1598 | 6.8402 | 107.1185 | 101.16 | 0 | 25.0425 | 0.2 | 0 | 2.84 | 27.8825 | 2.1517 | 3.023 | 1.0769 | 0.024622
2016-08-26 19:00 | 38.1967 | 22.51 | 15.6867 | 239.7128 | 10.4684 | 120.2062 | 86.2479 | 3.7521 | 121.6072 | 114.8463 | 0 | 16.8825 | 0.2 | 0 | 1.9098 | 18.7923 | 2.1522 | 2.7394 | 1.0779 | 0.01661
2016-08-26 20:00 | 19.5933 | 11.63 | 7.9633 | 0 | 10.4539 | 135.2092 | 88.8895 | 1.1105 | 136.1355 | 127.9214 | 0 | 8.7225 | 0.2 | 0 | 0.97967 | 9.7022 | 2.1526 | 2.4558 | 1.0789 | 0.0085835
2016-08-26 21:00 | 0.99 | 0.75 | 0.24 | 0 | 10.4395 | 150.2123 | 90.914 | -0.91398 | 150.7496 | 139.772 | 0 | 0.5625 | 0.2 | 0 | 0.0495 | 0.612 | 2.1531 | 2.1722 | 1.0799 | 0.00054194
2016-08-26 22:00 | 0.66 | 0.5 | 0.16 | 0 | 10.4251 | 165.2153 | 92.1872 | -2.1872 | 165.454 | 148.9522 | 0 | 0.375 | 0.2 | 0 | 0.033 | 0.408 | 2.1535 | 2.1663 | 1.0799 | 0.0003613
2016-08-26 23:00 | 0.33 | 0.25 | 0.08 | 0 | 10.4106 | 180.2184 | 92.6226 | -2.6226 | -179.785 | 152.6218 | 0 | 0.1875 | 0.2 | 0 | 0.0165 | 0.204 | 2.154 | 2.1603 | 1.0799 | 0.00018065
2016-08-27 | 0 | 0 | 0 | 0 | 10.3962 | -164.7786 | 92.1909 | -2.1909 | -165.0231 | 148.7718 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1544 | 2.1544 | 1.08 | 0
2016-08-27 01:00 | 9.5033 | 6.6067 | 2.8967 | 0 | 10.3817 | -149.7755 | 90.9229 | -0.92292 | -150.3162 | 139.4937 | 0 | 4.955 | 0.2 | 0 | 0.47517 | 5.4302 | 2.1549 | 2.3246 | 1.0794 | 0.0048061
2016-08-27 02:00 | 19.0067 | 13.2133 | 5.7933 | 0 | 10.3673 | -134.7724 | 88.9065 | 1.0935 | -135.6975 | 127.5986 | 0 | 9.91 | 0.2 | 0 | 0.95033 | 10.8603 | 2.1553 | 2.4947 | 1.0788 | 0.0096069
2016-08-27 03:00 | 28.51 | 19.82 | 8.69 | 133.8345 | 10.3528 | -119.7694 | 86.2771 | 3.7229 | -121.1623 | 114.5021 | 0 | 14.865 | 0.2 | 0 | 1.4255 | 16.2905 | 2.1558 | 2.6649 | 1.0782 | 0.014402
2016-08-27 04:00 | 67.5733 | 44.8167 | 22.7567 | 192.3774 | 10.3384 | -104.7663 | 83.2065 | 6.7935 | -106.6644 | 100.8044 | 0 | 33.6125 | 0.2 | 0 | 3.3787 | 36.9912 | 2.1562 | 3.3122 | 1.0759 | 0.032635
2016-08-27 05:00 | 106.6367 | 69.8133 | 36.8233 | 209.8043 | 10.3239 | -89.7632 | 79.8915 | 10.1085 | -92.1221 | 86.7791 | 11.7879 | 52.36 | 0.2 | 0 | 5.3318 | 69.4798 | 2.1567 | 4.3279 | 1.0724 | 0.061096
2016-08-27 06:00 | 145.7 | 94.81 | 50.89 | 218.7157 | 10.3094 | -74.7602 | 76.5453 | 13.4547 | -77.4339 | 72.5674 | 65.5238 | 71.1075 | 0.2 | 0 | 7.285 | 143.9163 | 2.1571 | 6.6545 | 1.0642 | 0.12559
2016-08-27 07:00 | 187.43 | 100.25 | 87.18 | 304.9648 | 10.295 | -59.7571 | 73.3892 | 16.6108 | -62.4994 | 58.2549 | 160.4545 | 75.1875 | 0.2 | 0 | 9.3715 | 245.0135 | 2.1576 | 9.8143 | 1.0532 | 0.21159
2016-08-27 08:00 | 229.16 | 105.69 | 123.47 | 372.5183 | 10.2805 | -44.754 | 70.6434 | 19.3566 | -47.2453 | 43.9123 | 268.363 | 79.2675 | 0.2 | 0 | 11.458 | 359.0885 | 2.158 | 13.3796 | 1.0407 | 0.30643
2016-08-27 09:00 | 270.89 | 111.13 | 159.76 | 436.1628 | 10.266 | -29.7509 | 68.5133 | 21.4867 | -31.6518 | 29.644 | 379.0758 | 83.3475 | 0.2 | 0 | 13.5445 | 475.9678 | 2.1585 | 17.0325 | 1.0279 | 0.40118
2016-08-27 10:00 | 284.4933 | 101.6067 | 182.8867 | 471.3678 | 10.2515 | -14.7478 | 67.1704 | 22.8296 | -15.771 | 15.818 | 453.5181 | 76.205 | 0.2 | 0 | 14.2247 | 543.9478 | 2.159 | 19.1573 | 1.0204 | 0.45516
2016-08-27 11:00 | 298.0967 | 92.0833 | 206.0133 | 521.4632 | 10.237 | 0.25524 | 66.7298 | 23.2702 | 0.27342 | 6.7342 | 517.8655 | 69.0625 | 0.2 | 0 | 14.9048 | 601.8329 | 2.1594 | 20.9667 | 1.0141 | 0.50047
2016-08-27 12:00 | 311.7 | 82.56 | 229.14 | 592.0716 | 10.2225 | 15.2583 | 67.2312 | 22.7688 | 16.3129 | 16.2809 | 568.3289 | 61.92 | 0.2 | 0 | 15.585 | 645.8339 | 2.1599 | 22.3422 | 1.0093 | 0.53451
2016-08-27 13:00 | 269.7233 | 76.7567 | 192.9667 | 529.6027 | 10.208 | 30.2614 | 68.6317 | 21.3683 | 32.1799 | 30.1424 | 457.9897 | 57.5675 | 0.2 | 0 | 13.4862 | 529.0433 | 2.1603 | 18.6929 | 1.0221 | 0.44339
2016-08-27 14:00 | 227.7467 | 70.9533 | 156.7933 | 477.1035 | 10.1935 | 45.2645 | 70.814 | 19.186 | 47.7543 | 44.4209 | 340.7556 | 53.215 | 0.2 | 0 | 11.3873 | 405.3579 | 2.1608 | 14.8282 | 1.0356 | 0.34423
2016-08-27 15:00 | 185.77 | 65.15 | 120.62 | 427.3423 | 10.179 | 60.2676 | 73.6051 | 16.3949 | 62.9877 | 58.7705 | 221.563 | 48.8625 | 0.2 | 0 | 9.2885 | 279.714 | 2.1612 | 10.9023 | 1.0493 | 0.24068
2016-08-27 16:00 | 136.75 | 55.64 | 81.11 | 355.1745 | 10.1645 | 75.2707 | 76.7991 | 13.2009 | 77.9038 | 73.0901 | 103.3084 | 41.73 | 0.2 | 0 | 6.8375 | 151.8759 | 2.1617 | 6.9078 | 1.0633 | 0.13242
2016-08-27 17:00 | 87.73 | 46.13 | 41.6 | 243.8108 | 10.1499 | 90.2738 | 80.1759 | 9.8241 | 92.5783 | 87.3104 | 11.4409 | 34.5975 | 0.2 | 0 | 4.3865 | 50.4249 | 2.1621 | 3.7379 | 1.0744 | 0.044425
2016-08-27 18:00 | 38.71 | 36.62 | 2.09 | 18.504 | 10.1354 | 105.277 | 83.5147 | 6.4853 | 107.1132 | 101.3459 | 0 | 27.465 | 0.2 | 0 | 1.9355 | 29.4005 | 2.1626 | 3.0814 | 1.0767 | 0.025958
2016-08-27 19:00 | 25.9533 | 24.56 | 1.3933 | 23.5138 | 10.1209 | 120.2801 | 86.6029 | 3.3971 | 121.6106 | 115.0555 | 0 | 18.42 | 0.2 | 0 | 1.2977 | 19.7177 | 2.163 | 2.7792 | 1.0778 | 0.017426
2016-08-27 20:00 | 13.1967 | 12.5 | 0.69667 | 0 | 10.1063 | 135.2832 | 89.2442 | 0.75578 | 136.1521 | 128.1638 | 0 | 9.375 | 0.2 | 0 | 0.65983 | 10.0348 | 2.1635 | 2.4771 | 1.0788 | 0.0088772
2016-08-27 21:00 | 0.44 | 0.44 | 0 | 0 | 10.0918 | 150.2863 | 91.2677 | -1.2677 | 150.7831 | 140.0607 | 0 | 0.33 | 0.2 | 0 | 0.022 | 0.352 | 2.1639 | 2.1749 | 1.0799 | 0.0003117
2016-08-27 22:00 | 0.29333 | 0.29333 | 0 | 0 | 10.0773 | 165.2894 | 92.5386 | -2.5386 | 165.5068 | 149.293 | 0 | 0.22 | 0.2 | 0 | 0.014667 | 0.23467 | 2.1644 | 2.1717 | 1.0799 | 0.0002078
2016-08-27 23:00 | 0.14667 | 0.14667 | 0 | 0 | 10.0627 | 180.2926 | 92.9705 | -2.9705 | -179.7116 | 152.9691 | 0 | 0.11 | 0.2 | 0 | 0.0073333 | 0.11733 | 2.1649 | 2.1685 | 1.0799 | 0.0001039
2016-08-28 | 0 | 0 | 0 | 0 | 10.0482 | -164.7043 | 92.534 | -2.534 | -164.9294 | 149.0401 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1653 | 2.1653 | 1.0799 | 0
2016-08-28 01:00 | 3.8567 | 3.4033 | 0.45333 | 0 | 10.0336 | -149.7012 | 91.2605 | -1.2605 | -150.204 | 139.6721 | 0 | 2.5525 | 0.2 | 0 | 0.19283 | 2.7453 | 2.1658 | 2.2516 | 1.0796 | 0.0024304
2016-08-28 02:00 | 7.7133 | 6.8067 | 0.90667 | 0 | 10.019 | -134.698 | 89.2385 | 0.76148 | -135.5694 | 127.7145 | 0 | 5.105 | 0.2 | 0 | 0.38567 | 5.4907 | 2.1662 | 2.3378 | 1.0793 | 0.0048595
2016-08-28 03:00 | 11.57 | 10.21 | 1.36 | 22.9609 | 10.0045 | -119.6949 | 86.6043 | 3.3957 | -121.0218 | 114.5772 | 0 | 7.6575 | 0.2 | 0 | 0.5785 | 8.236 | 2.1667 | 2.424 | 1.079 | 0.0072872
2016-08-28 04:00 | 21.25 | 20.1833 | 1.0667 | 9.4666 | 9.9899 | -104.6918 | 83.5303 | 6.4697 | -106.5153 | 100.8524 | 0 | 15.1375 | 0.2 | 0 | 1.0625 | 16.2 | 2.1671 | 2.6734 | 1.0781 | 0.014322
2016-08-28 05:00 | 30.93 | 30.1567 | 0.77333 | 4.5499 | 9.9753 | -89.6886 | 80.214 | 9.786 | -91.9685 | 86.8088 | 0.25329 | 22.6175 | 0.2 | 0 | 1.5465 | 24.4173 | 2.1676 | 2.9306 | 1.0772 | 0.021569
2016-08-28 06:00 | 40.61 | 40.13 | 0.48 | 2.1128 | 9.9607 | -74.6855 | 76.8687 | 13.1313 | -77.2802 | 72.585 | 0.63235 | 30.0975 | 0.2 | 0 | 2.0305 | 32.7604 | 2.168 | 3.1918 | 1.0763 | 0.028914
2016-08-28 07:00 | 31.3033 | 30.9833 | 0.32 | 1.1412 | 9.9462 | -59.6823 | 73.7158 | 16.2842 | -62.3504 | 58.2665 | 0.60025 | 23.2375 | 0.2 | 0 | 1.5652 | 25.4029 | 2.1685 | 2.9623 | 1.0771 | 0.022437
2016-08-28 08:00 | 21.9967 | 21.8367 | 0.16 | 0.49083 | 9.9316 | -44.6792 | 70.975 | 19.025 | -47.1063 | 43.9253 | 0.35351 | 16.3775 | 0.2 | 0 | 1.0998 | 17.8308 | 2.1689 | 2.7261 | 1.078 | 0.015761
2016-08-28 09:00 | 12.69 | 12.69 | 0 | 0 | 9.917 | -29.676 | 68.8509 | 21.1491 | -31.5282 | 29.6733 | 0 | 9.5175 | 0.2 | 0 | 0.6345 | 10.152 | 2.1694 | 2.4866 | 1.0788 | 0.0089806
2016-08-28 10:00 | 14.0567 | 14.0567 | 0 | 0 | 9.9024 | -14.6728 | 67.5143 | 22.4857 | -15.6677 | 15.9126 | 0 | 10.5425 | 0.2 | 0 | 0.70283 | 11.2453 | 2.1698 | 2.5213 | 1.0787 | 0.0099467
2016-08-28 11:00 | 15.4233 | 15.4233 | 0 | 0 | 9.8878 | 0.33032 | 67.0791 | 22.9209 | 0.35331 | 7.0862 | 0 | 11.5675 | 0.2 | 0 | 0.77117 | 12.3387 | 2.1703 | 2.5559 | 1.0786 | 0.010912
2016-08-28 12:00 | 16.79 | 16.79 | 0 | 0 | 9.8732 | 15.3335 | 67.5846 | 22.4154 | 16.3685 | 16.5035 | 0 | 12.5925 | 0.2 | 0 | 0.8395 | 13.432 | 2.1707 | 2.5905 | 1.0784 | 0.011878
2016-08-28 13:00 | 32.56 | 32.56 | 0 | 0 | 9.8585 | 30.3367 | 68.9876 | 21.0124 | 32.2131 | 30.313 | 0 | 24.42 | 0.2 | 0 | 1.628 | 26.048 | 2.1712 | 2.9852 | 1.0771 | 0.023005
2016-08-28 14:00 | 48.33 | 48.33 | 0 | 0 | 9.8439 | 45.3398 | 71.1711 | 18.8289 | 47.7689 | 44.5778 | 0 | 36.2475 | 0.2 | 0 | 2.4165 | 38.664 | 2.1717 | 3.3799 | 1.0757 | 0.034104
2016-08-28 15:00 | 64.1 | 64.1 | 0 | 0 | 9.8293 | 60.343 | 73.9626 | 16.0374 | 62.9891 | 58.9264 | 0 | 48.075 | 0.2 | 0 | 3.205 | 51.28 | 2.1721 | 3.7746 | 1.0743 | 0.045173
2016-08-28 16:00 | 50.3733 | 50.13 | 0.24333 | 1.0947 | 9.8147 | 75.3462 | 77.1566 | 12.8434 | 77.8977 | 73.2516 | 0.31545 | 37.5975 | 0.2 | 0 | 2.5187 | 40.4316 | 2.1726 | 3.4361 | 1.0755 | 0.035656
2016-08-28 17:00 | 36.6467 | 36.16 | 0.48667 | 2.959 | 9.8001 | 90.3494 | 80.5335 | 9.4665 | 92.5706 | 87.4826 | 0.12997 | 27.12 | 0.2 | 0 | 1.8323 | 29.0823 | 2.173 | 3.0818 | 1.0767 | 0.025677
2016-08-28 18:00 | 22.92 | 22.19 | 0.73 | 6.839 | 9.7854 | 105.3526 | 83.8725 | 6.1275 | 107.1092 | 101.5342 | 0 | 16.6425 | 0.2 | 0 | 1.146 | 17.7885 | 2.1735 | 2.7294 | 1.0779 | 0.015724
2016-08-28 19:00 | 15.34 | 14.8533 | 0.48667 | 9.1791 | 9.7708 | 120.3557 | 86.9608 | 3.0392 | 121.6155 | 115.267 | 0 | 11.14 | 0.2 | 0 | 0.767 | 11.907 | 2.1739 | 2.546 | 1.0786 | 0.010531
2016-08-28 20:00 | 7.76 | 7.5167 | 0.24333 | 0 | 9.7561 | 135.3589 | 89.6018 | 0.39816 | 136.1702 | 128.4083 | 0 | 5.6375 | 0.2 | 0 | 0.388 | 6.0255 | 2.1744 | 2.3627 | 1.0792 | 0.0053324
2016-08-28 21:00 | 0.18 | 0.18 | 0 | 0 | 9.7415 | 150.3621 | 91.6241 | -1.6241 | 150.8182 | 140.3516 | 0 | 0.135 | 0.2 | 0 | 0.009 | 0.144 | 2.1748 | 2.1793 | 1.0799 | 0.00012751
2016-08-28 22:00 | 0.12 | 0.12 | 0 | 0 | 9.7268 | 165.3653 | 92.8927 | -2.8927 | 165.5615 | 149.6366 | 0 | 0.09 | 0.2 | 0 | 0.006 | 0.096 | 2.1753 | 2.1783 | 1.0799 | 8.5008e-05
2016-08-28 23:00 | 0.06 | 0.06 | 0 | 0 | 9.7122 | 180.3685 | 93.3209 | -3.3209 | -179.6361 | 153.3187 | 0 | 0.045 | 0.2 | 0 | 0.003 | 0.048 | 2.1757 | 2.1772 | 1.0799 | 4.2504e-05
2016-08-29 | 0 | 0 | 0 | 0 | 9.6975 | -164.6283 | 92.8795 | -2.8795 | -164.8336 | 149.3081 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1762 | 2.1762 | 1.0799 | 0
2016-08-29 01:00 | 1.1333 | 0.99667 | 0.13667 | 0 | 9.6829 | -149.6251 | 91.6004 | -1.6004 | -150.0895 | 139.8489 | 0 | 0.7475 | 0.2 | 0 | 0.056667 | 0.80417 | 2.1766 | 2.2018 | 1.0798 | 0.00071203
2016-08-29 02:00 | 2.2667 | 1.9933 | 0.27333 | 0 | 9.6682 | -134.6219 | 89.5728 | 0.42721 | -135.439 | 127.8286 | 0 | 1.495 | 0.2 | 0 | 0.11333 | 1.6083 | 2.1771 | 2.2274 | 1.0797 | 0.0014239
2016-08-29 03:00 | 3.4 | 2.99 | 0.41 | 7.6648 | 9.6535 | -119.6186 | 86.9337 | 3.0663 | -120.879 | 114.6507 | 0 | 2.2425 | 0.2 | 0 | 0.17 | 2.4125 | 2.1776 | 2.2529 | 1.0796 | 0.0021357
2016-08-29 04:00 | 7.6067 | 7.3333 | 0.27333 | 2.554 | 9.6388 | -104.6154 | 83.8563 | 6.1437 | -106.3639 | 100.8991 | 0 | 5.5 | 0.2 | 0 | 0.38033 | 5.8803 | 2.178 | 2.3618 | 1.0792 | 0.0052039
2016-08-29 05:00 | 11.8133 | 11.6767 | 0.13667 | 0.8314 | 9.6241 | -89.6122 | 80.5386 | 9.4614 | -91.8127 | 86.8374 | 0.045868 | 8.7575 | 0.2 | 0 | 0.59067 | 9.394 | 2.1785 | 2.472 | 1.0788 | 0.0083105
2016-08-29 06:00 | 16.02 | 16.02 | 0 | 0 | 9.6095 | -74.609 | 77.1943 | 12.8057 | -77.1243 | 72.6022 | 0 | 12.015 | 0.2 | 0 | 0.801 | 12.816 | 2.1789 | 2.5794 | 1.0785 | 0.011334
2016-08-29 07:00 | 40.3467 | 39.2033 | 1.1433 | 4.1593 | 9.5948 | -59.6058 | 74.0446 | 15.9554 | -62.1994 | 58.2782 | 2.1869 | 29.4025 | 0.2 | 0 | 2.0173 | 33.6068 | 2.1794 | 3.2296 | 1.0762 | 0.029657
2016-08-29 08:00 | 64.6733 | 62.3867 | 2.2867 | 7.1354 | 9.5801 | -44.6025 | 71.3088 | 18.6912 | -46.9654 | 43.9395 | 5.138 | 46.79 | 0.2 | 0 | 3.2337 | 55.1617 | 2.1798 | 3.9036 | 1.0738 | 0.048572
2016-08-29 09:00 | 89 | 85.57 | 3.43 | 9.6551 | 9.5654 | -29.5993 | 69.191 | 20.809 | -31.4029 | 29.7054 | 8.3862 | 64.1775 | 0.2 | 0 | 4.45 | 77.0137 | 2.1803 | 4.587 | 1.0714 | 0.067663
2016-08-29 10:00 | 82.7867 | 80.4833 | 2.3033 | 6.1119 | 9.5507 | -14.5961 | 67.8607 | 22.1393 | -15.5626 | 16.014 | 5.8747 | 60.3625 | 0.2 | 0 | 4.1393 | 70.3766 | 2.1807 | 4.38 | 1.0722 | 0.061874
2016-08-29 11:00 | 76.5733 | 75.3967 | 1.1767 | 3.0659 | 9.536 | 0.40716 | 67.4311 | 22.5689 | 0.43483 | 7.4413 | 3.0401 | 56.5475 | 0.2 | 0 | 3.8287 | 63.4162 | 2.1812 | 4.1629 | 1.0729 | 0.055794
2016-08-29 12:00 | 70.36 | 70.31 | 0.05 | 0.13313 | 9.5212 | 15.4104 | 67.9406 | 22.0594 | 16.4256 | 16.7335 | 0.12749 | 52.7325 | 0.2 | 0 | 3.518 | 56.378 | 2.1816 | 3.9434 | 1.0737 | 0.049637
2016-08-29 13:00 | 80.96 | 79.15 | 1.81 | 5.1316 | 9.5065 | 30.4136 | 69.3463 | 20.6537 | 32.2477 | 30.4891 | 4.422 | 59.3625 | 0.2 | 0 | 4.048 | 67.8325 | 2.1821 | 4.3019 | 1.0724 | 0.059652
2016-08-29 14:00 | 91.56 | 87.99 | 3.57 | 11.2692 | 9.4918 | 45.4169 | 71.531 | 18.469 | 47.7849 | 44.7389 | 8.0048 | 65.9925 | 0.2 | 0 | 4.578 | 78.5753 | 2.1825 | 4.638 | 1.0713 | 0.069024
2016-08-29 15:00 | 102.16 | 96.83 | 5.33 | 19.725 | 9.4771 | 60.4201 | 74.3229 | 15.6771 | 62.9919 | 59.0857 | 10.1338 | 72.6225 | 0.2 | 0 | 5.108 | 87.8643 | 2.183 | 4.9288 | 1.0702 | 0.07711
2016-08-29 16:00 | 77.6533 | 73.69 | 3.9633 | 18.3361 | 9.4623 | 75.4234 | 77.517 | 12.483 | 77.893 | 73.4161 | 5.2335 | 55.2675 | 0.2 | 0 | 3.8827 | 64.3836 | 2.1834 | 4.1954 | 1.0728 | 0.056639
2016-08-29 17:00 | 53.1467 | 50.55 | 2.5967 | 16.4075 | 9.4476 | 90.4266 | 80.894 | 9.106 | 92.5641 | 87.6574 | 0.67066 | 37.9125 | 0.2 | 0 | 2.6573 | 41.2405 | 2.1839 | 3.4727 | 1.0753 | 0.036365
2016-08-29 18:00 | 28.64 | 27.41 | 1.23 | 12.2412 | 9.4329 | 105.4299 | 84.2332 | 5.7668 | 107.1065 | 101.7248 | 0 | 20.5575 | 0.2 | 0 | 1.432 | 21.9895 | 2.1844 | 2.8715 | 1.0774 | 0.019428
2016-08-29 19:00 | 19.11 | 18.29 | 0.82 | 0 | 9.4181 | 120.4331 | 87.3216 | 2.6784 | 121.6217 | 115.4804 | 0 | 13.7175 | 0.2 | 0 | 0.9555 | 14.673 | 2.1848 | 2.6433 | 1.0782 | 0.012973
2016-08-29 20:00 | 9.58 | 9.17 | 0.41 | 0 | 9.4034 | 135.4364 | 89.9622 | 0.037767 | 136.1898 | 128.6548 | 0 | 6.8775 | 0.2 | 0 | 0.479 | 7.3565 | 2.1853 | 2.4152 | 1.079 | 0.0065092
2016-08-29 21:00 | 0.05 | 0.05 | 0 | 0 | 9.3886 | 150.4397 | 91.9833 | -1.9833 | 150.8549 | 140.6447 | 0 | 0.0375 | 0.2 | 0 | 0.0025 | 0.04 | 2.1857 | 2.187 | 1.0798 | 3.5419e-05
2016-08-29 22:00 | 0.033333 | 0.033333 | 0 | 0 | 9.3739 | 165.4429 | 93.2495 | -3.2495 | 165.6179 | 149.9831 | 0 | 0.025 | 0.2 | 0 | 0.0016667 | 0.026667 | 2.1862 | 2.187 | 1.0798 | 2.3613e-05
2016-08-29 23:00 | 0.016667 | 0.016667 | 0 | 0 | 9.3591 | 180.4462 | 93.6738 | -3.6738 | -179.5588 | 153.6705 | 0 | 0.0125 | 0.2 | 0 | 0.00083333 | 0.013333 | 2.1866 | 2.187 | 1.0798 | 1.1806e-05
2016-08-30 | 0 | 0 | 0 | 0 | 9.3444 | -164.5505 | 93.2274 | -3.2274 | -164.7357 | 149.5756 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1871 | 2.1871 | 1.0798 | 0
2016-08-30 01:00 | 4.6267 | 4.17 | 0.45667 | 0 | 9.3296 | -149.5472 | 91.9426 | -1.9426 | -149.9728 | 140.0239 | 0 | 3.1275 | 0.2 | 0 | 0.23133 | 3.3588 | 2.1875 | 2.2925 | 1.0795 | 0.0029731
2016-08-30 02:00 | 9.2533 | 8.34 | 0.91333 | 0 | 9.3148 | -134.544 | 89.9092 | 0.090769 | -135.3064 | 127.9407 | 0 | 6.255 | 0.2 | 0 | 0.46267 | 6.7177 | 2.188 | 2.3979 | 1.0791 | 0.0059442
2016-08-30 03:00 | 13.88 | 12.51 | 1.37 | 0 | 9.3 | -119.5407 | 87.2652 | 2.7348 | -120.734 | 114.7225 | 0 | 9.3825 | 0.2 | 0 | 0.694 | 10.0765 | 2.1884 | 2.5033 | 1.0787 | 0.0089133
2016-08-30 04:00 | 38.1433 | 34.1967 | 3.9467 | 38.9497 | 9.2853 | -104.5374 | 84.1844 | 5.8156 | -106.2104 | 100.9444 | 0 | 25.6475 | 0.2 | 0 | 1.9072 | 27.5547 | 2.1889 | 3.05 | 1.0768 | 0.024331
2016-08-30 05:00 | 62.4067 | 55.8833 | 6.5233 | 41.0906 | 9.2705 | -89.5341 | 80.8654 | 9.1346 | -91.6548 | 86.8652 | 2.2471 | 41.9125 | 0.2 | 0 | 3.1203 | 47.2799 | 2.1893 | 3.6668 | 1.0747 | 0.041664
2016-08-30 06:00 | 86.67 | 77.57 | 9.1 | 42.1172 | 9.2557 | -74.5308 | 77.522 | 12.478 | -76.9665 | 72.6189 | 12.5815 | 58.1775 | 0.2 | 0 | 4.3335 | 75.0925 | 2.1898 | 4.5364 | 1.0716 | 0.065986
2016-08-30 07:00 | 114.36 | 100.1367 | 14.2233 | 52.8101 | 9.2409 | -59.5275 | 74.3756 | 15.6244 | -62.0465 | 58.2902 | 27.7579 | 75.1025 | 0.2 | 0 | 5.718 | 108.5784 | 2.1902 | 5.5833 | 1.068 | 0.095085
2016-08-30 08:00 | 142.05 | 122.7033 | 19.3467 | 61.4367 | 9.2261 | -44.5242 | 71.645 | 18.355 | -46.8228 | 43.9548 | 44.2275 | 92.0275 | 0.2 | 0 | 7.1025 | 143.3575 | 2.1907 | 6.6706 | 1.0642 | 0.12509
2016-08-30 09:00 | 169.74 | 145.27 | 24.47 | 69.982 | 9.2113 | -29.5209 | 69.5334 | 20.4666 | -31.2758 | 29.7405 | 60.764 | 108.9525 | 0.2 | 0 | 8.487 | 178.2035 | 2.1912 | 7.76 | 1.0603 | 0.15494
2016-08-30 10:00 | 164.9567 | 148.6433 | 16.3133 | 43.9459 | 9.1965 | -14.5176 | 68.2095 | 21.7905 | -15.456 | 16.1223 | 42.2175 | 111.4825 | 0.2 | 0 | 8.2478 | 161.9479 | 2.1916 | 7.2525 | 1.0621 | 0.14105
2016-08-30 11:00 | 160.1733 | 152.0167 | 8.1567 | 21.5742 | 9.1817 | 0.48567 | 67.7855 | 22.2145 | 0.51789 | 7.7993 | 21.3746 | 114.0125 | 0.2 | 0 | 8.0087 | 143.3958 | 2.1921 | 6.6732 | 1.0641 | 0.12513
2016-08-30 12:00 | 155.39 | 155.39 | 0 | 0 | 9.1668 | 15.489 | 68.2993 | 21.7007 | 16.4843 | 16.9706 | 0 | 116.5425 | 0.2 | 0 | 7.7695 | 124.312 | 2.1925 | 6.0773 | 1.0662 | 0.10869
2016-08-30 13:00 | 127.2933 | 127.2933 | 0 | 0 | 9.152 | 30.4923 | 69.7076 | 20.2924 | 32.2838 | 30.6706 | 0 | 95.47 | 0.2 | 0 | 6.3647 | 101.8347 | 2.193 | 5.3753 | 1.0687 | 0.08924
2016-08-30 14:00 | 99.1967 | 99.1967 | 0 | 0 | 9.1372 | 45.4956 | 71.8936 | 18.1064 | 47.8023 | 44.9043 | 0 | 74.3975 | 0.2 | 0 | 4.9598 | 79.3573 | 2.1934 | 4.6733 | 1.0711 | 0.069703
2016-08-30 15:00 | 71.1 | 71.1 | 0 | 0 | 9.1224 | 60.4989 | 74.686 | 15.314 | 62.9959 | 59.2486 | 0 | 53.325 | 0.2 | 0 | 3.555 | 56.88 | 2.1939 | 3.9714 | 1.0736 | 0.050074
2016-08-30 16:00 | 52.91 | 52.91 | 0 | 0 | 9.1075 | 75.5022 | 77.8803 | 12.1197 | 77.8895 | 73.5835 | 0 | 39.6825 | 0.2 | 0 | 2.6455 | 42.328 | 2.1943 | 3.5171 | 1.0752 | 0.037319
2016-08-30 17:00 | 34.72 | 34.72 | 0 | 0 | 9.0927 | 90.5056 | 81.2574 | 8.7426 | 92.5589 | 87.8347 | 0 | 26.04 | 0.2 | 0 | 1.736 | 27.776 | 2.1948 | 3.0628 | 1.0768 | 0.024525
2016-08-30 18:00 | 16.53 | 16.53 | 0 | 0 | 9.0779 | 105.5089 | 84.5966 | 5.4034 | 107.1051 | 101.9176 | 0 | 12.3975 | 0.2 | 0 | 0.8265 | 13.224 | 2.1952 | 2.6085 | 1.0784 | 0.011694
2016-08-30 19:00 | 11.03 | 11.03 | 0 | 0 | 9.063 | 120.5122 | 87.6851 | 2.3149 | 121.6291 | 115.6958 | 0 | 8.2725 | 0.2 | 0 | 0.5515 | 8.824 | 2.1957 | 2.4714 | 1.0788 | 0.0078062
2016-08-30 20:00 | 5.53 | 5.53 | 0 | 0 | 9.0482 | 135.5155 | 90.3253 | -0.32532 | 136.2108 | 128.903 | 0 | 4.1475 | 0.2 | 0 | 0.2765 | 4.424 | 2.1961 | 2.3344 | 1.0793 | 0.0039155
2016-08-30 21:00 | 0.03 | 0.03 | 0 | 0 | 9.0333 | 150.5189 | 92.3451 | -2.3451 | 150.8931 | 140.9397 | 0 | 0.0225 | 0.2 | 0 | 0.0015 | 0.024 | 2.1966 | 2.1973 | 1.0798 | 2.1251e-05
2016-08-30 22:00 | 0.02 | 0.02 | 0 | 0 | 9.0185 | 165.5222 | 93.6087 | -3.6087 | 165.676 | 150.3322 | 0 | 0.015 | 0.2 | 0 | 0.001 | 0.016 | 2.1971 | 2.1976 | 1.0798 | 1.4167e-05
2016-08-30 23:00 | 0.01 | 0.01 | 0 | 0 | 9.0036 | 180.5255 | 94.0292 | -4.0292 | -179.4797 | 154.0245 | 0 | 0.0075 | 0.2 | 0 | 0.0005 | 0.008 | 2.1975 | 2.1978 | 1.0798 | 7.0835e-06
2016-08-31 | 0 | 0 | 0 | 0 | 8.9887 | -164.4711 | 93.5777 | -3.5777 | -164.6359 | 149.8426 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.198 | 2.198 | 1.0798 | 0
2016-08-31 01:00 | 4.9633 | 4.9433 | 0.02 | 0 | 8.9739 | -149.4678 | 92.287 | -2.287 | -149.854 | 140.197 | 0 | 3.7075 | 0.2 | 0 | 0.24817 | 3.9557 | 2.1984 | 2.322 | 1.0794 | 0.0035011
2016-08-31 02:00 | 9.9267 | 9.8867 | 0.04 | 0 | 8.959 | -134.4644 | 90.2478 | -0.24777 | -135.1717 | 128.0509 | 0 | 7.415 | 0.2 | 0 | 0.49633 | 7.9113 | 2.1989 | 2.4461 | 1.0789 | 0.0069994
2016-08-31 03:00 | 14.89 | 14.83 | 0.06 | 0 | 8.9441 | -119.4611 | 87.5987 | 2.4013 | -120.5869 | 114.7927 | 0 | 11.1225 | 0.2 | 0 | 0.7445 | 11.867 | 2.1993 | 2.5702 | 1.0785 | 0.010495
2016-08-31 04:00 | 44.8067 | 43.46 | 1.3467 | 14.0873 | 8.9292 | -104.4577 | 84.5145 | 5.4855 | -106.0548 | 100.9884 | 0 | 32.595 | 0.2 | 0 | 2.2403 | 34.8353 | 2.1998 | 3.2884 | 1.076 | 0.030736
2016-08-31 05:00 | 74.7233 | 72.09 | 2.6333 | 17.2015 | 8.9144 | -89.4544 | 81.1941 | 8.8059 | -91.4949 | 86.8921 | 0.93262 | 54.0675 | 0.2 | 0 | 3.7362 | 58.7363 | 2.2002 | 4.0357 | 1.0734 | 0.051698
2016-08-31 06:00 | 104.64 | 100.72 | 3.92 | 18.6275 | 8.8995 | -74.451 | 77.8518 | 12.1482 | -76.8068 | 72.6353 | 5.5594 | 75.54 | 0.2 | 0 | 5.232 | 86.3314 | 2.2007 | 4.8985 | 1.0704 | 0.075772
2016-08-31 07:00 | 145.28 | 117.8467 | 27.4333 | 104.0218 | 8.8846 | -59.4477 | 74.7087 | 15.2913 | -61.8918 | 58.3024 | 54.6568 | 88.385 | 0.2 | 0 | 7.264 | 150.3058 | 2.2011 | 6.8982 | 1.0634 | 0.13106
2016-08-31 08:00 | 185.92 | 134.9733 | 50.9467 | 164.7189 | 8.8697 | -44.4443 | 71.9833 | 18.0167 | -46.6785 | 43.9715 | 118.5458 | 101.23 | 0.2 | 0 | 9.296 | 229.0718 | 2.2016 | 9.3601 | 1.0547 | 0.19812
2016-08-31 09:00 | 226.56 | 152.1 | 74.46 | 216.4411 | 8.8548 | -29.4409 | 69.878 | 20.122 | -31.1472 | 29.7787 | 187.86 | 114.075 | 0.2 | 0 | 11.328 | 313.263 | 2.202 | 11.9915 | 1.0455 | 0.26857
2016-08-31 10:00 | 207.8467 | 152.63 | 55.2167 | 151.0647 | 8.8399 | -14.4376 | 68.5606 | 21.4394 | -15.3478 | 16.2375 | 145.0388 | 114.4725 | 0.2 | 0 | 10.3923 | 269.9037 | 2.2025 | 10.637 | 1.0503 | 0.23245
2016-08-31 11:00 | 189.1333 | 153.16 | 35.9733 | 96.6242 | 8.825 | 0.56579 | 68.1424 | 21.8576 | 0.6024 | 8.1603 | 95.6458 | 114.87 | 0.2 | 0 | 9.4567 | 219.9725 | 2.2029 | 9.0771 | 1.0557 | 0.19043
2016-08-31 12:00 | 170.42 | 153.69 | 16.73 | 45.975 | 8.8101 | 15.5692 | 68.6605 | 21.3395 | 16.5444 | 17.2147 | 43.9154 | 115.2675 | 0.2 | 0 | 8.521 | 167.7039 | 2.2034 | 7.4441 | 1.0614 | 0.14597
2016-08-31 13:00 | 147.1733 | 135.44 | 11.7333 | 34.424 | 8.7951 | 30.5725 | 70.0715 | 19.9285 | 32.3212 | 30.8573 | 29.5512 | 101.58 | 0.2 | 0 | 7.3587 | 138.4898 | 2.2039 | 6.5317 | 1.0646 | 0.1209
2016-08-31 14:00 | 123.9267 | 117.19 | 6.7367 | 22.108 | 8.7802 | 45.5759 | 72.2589 | 17.7411 | 47.8211 | 45.0738 | 15.6125 | 87.8925 | 0.2 | 0 | 6.1963 | 109.7014 | 2.2043 | 5.6325 | 1.0678 | 0.096053
2016-08-31 15:00 | 100.68 | 98.94 | 1.74 | 6.7456 | 8.7653 | 60.5793 | 75.0518 | 14.9482 | 63.0012 | 59.4148 | 3.4323 | 74.205 | 0.2 | 0 | 5.034 | 82.6713 | 2.2048 | 4.7882 | 1.0707 | 0.072586
2016-08-31 16:00 | 77.0333 | 74.11 | 2.9233 | 14.3507 | 8.7504 | 75.5827 | 78.2462 | 11.7538 | 77.8872 | 73.7537 | 4.0148 | 55.5825 | 0.2 | 0 | 3.8517 | 63.449 | 2.2052 | 4.188 | 1.0728 | 0.055818
2016-08-31 17:00 | 53.3867 | 49.28 | 4.1067 | 28.1897 | 8.7354 | 90.5861 | 81.6234 | 8.3766 | 92.5548 | 88.0144 | 0.97674 | 36.96 | 0.2 | 0 | 2.6693 | 40.6061 | 2.2057 | 3.4746 | 1.0753 | 0.035806
2016-08-31 18:00 | 29.74 | 24.45 | 5.29 | 60.2484 | 8.7205 | 105.5895 | 84.9628 | 5.0372 | 107.1048 | 102.1124 | 0 | 18.3375 | 0.2 | 0 | 1.487 | 19.8245 | 2.2061 | 2.8256 | 1.0776 | 0.017518
2016-08-31 19:00 | 19.8267 | 16.3 | 3.5267 | 0 | 8.7056 | 120.5928 | 88.0512 | 1.9488 | 121.6378 | 115.913 | 0 | 12.225 | 0.2 | 0 | 0.99133 | 13.2163 | 2.2066 | 2.6196 | 1.0783 | 0.011686
2016-08-31 20:00 | 9.9133 | 8.15 | 1.7633 | 0 | 8.6906 | 135.5962 | 90.691 | -0.69099 | 136.233 | 129.1529 | 0 | 6.1125 | 0.2 | 0 | 0.49567 | 6.6082 | 2.207 | 2.4135 | 1.0791 | 0.0058471
2016-08-31 21:00 | 0 | 0 | 0 | 0 | 8.6757 | 150.5996 | 92.7094 | -2.7094 | 150.9328 | 141.2367 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2075 | 2.2075 | 1.0798 | 0
2016-08-31 22:00 | 0 | 0 | 0 | 0 | 8.6607 | 165.603 | 93.9704 | -3.9704 | 165.7357 | 150.6839 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2079 | 2.2079 | 1.0798 | 0
2016-08-31 23:00 | 0 | 0 | 0 | 0 | 8.6458 | 180.6064 | 94.3869 | -4.3869 | -179.3987 | 154.3806 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2084 | 2.2084 | 1.0798 | 0
2016-09-01 | 0 | 0 | 0 | 0 | 8.6308 | -164.3902 | 93.9301 | -3.9301 | -164.5341 | 150.1088 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2088 | 2.2088 | 1.0798 | 0
2016-09-01 01:00 | 4.7733 | 3.8633 | 0.91 | 0 | 8.6158 | -149.3868 | 92.6335 | -2.6335 | -149.7333 | 140.3682 | 0 | 2.8975 | 0.2 | 0 | 0.23867 | 3.1362 | 2.2093 | 2.3073 | 1.0794 | 0.0027759
2016-09-01 02:00 | 9.5467 | 7.7267 | 1.82 | 0 | 8.6009 | -134.3833 | 90.5883 | -0.58833 | -135.0349 | 128.1591 | 0 | 5.795 | 0.2 | 0 | 0.47733 | 6.2723 | 2.2098 | 2.4058 | 1.0791 | 0.00555
2016-09-01 03:00 | 14.32 | 11.59 | 2.73 | 0 | 8.5859 | -119.3799 | 87.9342 | 2.0658 | -120.4377 | 114.8612 | 0 | 8.6925 | 0.2 | 0 | 0.716 | 9.4085 | 2.2102 | 2.5042 | 1.0787 | 0.0083224
2016-09-01 04:00 | 48.41 | 32.8533 | 15.5567 | 173.1887 | 8.5709 | -104.3765 | 84.8465 | 5.1535 | -105.8972 | 101.0312 | 0 | 24.64 | 0.2 | 0 | 2.4205 | 27.0605 | 2.2107 | 3.0563 | 1.0768 | 0.023894
2016-09-01 05:00 | 82.5 | 54.1167 | 28.3833 | 192.5832 | 8.5559 | -89.3731 | 81.5247 | 8.4753 | -91.3331 | 86.9181 | 10.3539 | 40.5875 | 0.2 | 0 | 4.125 | 55.0664 | 2.2111 | 3.9319 | 1.0737 | 0.048484
2016-09-01 06:00 | 116.59 | 75.38 | 41.21 | 201.2427 | 8.5409 | -74.3697 | 78.1835 | 11.8165 | -76.6453 | 72.6515 | 60.0073 | 56.535 | 0.2 | 0 | 5.8295 | 122.3718 | 2.2116 | 6.0357 | 1.0664 | 0.10701
2016-09-01 07:00 | 146.39 | 105.9167 | 40.4733 | 156.8244 | 8.526 | -59.3663 | 75.0438 | 14.9562 | -61.7355 | 58.3151 | 82.3717 | 79.4375 | 0.2 | 0 | 7.3195 | 169.1287 | 2.212 | 7.4973 | 1.0613 | 0.14718
2016-09-01 08:00 | 176.19 | 136.4533 | 39.7367 | 130.868 | 8.511 | -44.3628 | 72.3237 | 17.6763 | -46.5326 | 43.9895 | 94.1552 | 102.34 | 0.2 | 0 | 8.8095 | 205.3047 | 2.2125 | 8.6282 | 1.0573 | 0.178
2016-09-01 09:00 | 205.99 | 166.99 | 39 | 115.2722 | 8.496 | -29.3594 | 70.2249 | 19.7751 | -31.0171 | 29.8201 | 100.0091 | 125.2425 | 0.2 | 0 | 10.2995 | 235.5511 | 2.2129 | 9.5739 | 1.054 | 0.20358
2016-09-01 10:00 | 211.03 | 170.4 | 40.63 | 112.9337 | 8.481 | -14.356 | 68.914 | 21.086 | -15.2383 | 16.3597 | 108.3613 | 127.8 | 0.2 | 0 | 10.5515 | 246.7128 | 2.2134 | 9.9232 | 1.0528 | 0.21298
2016-09-01 11:00 | 216.07 | 173.81 | 42.26 | 115.3146 | 8.466 | 0.64744 | 68.5016 | 21.4984 | 0.68827 | 8.5241 | 114.0408 | 130.3575 | 0.2 | 0 | 10.8035 | 255.2018 | 2.2138 | 10.1889 | 1.0518 | 0.22011
2016-09-01 12:00 | 221.11 | 177.22 | 43.89 | 122.6061 | 8.451 | 15.6509 | 69.0241 | 20.9759 | 16.6057 | 17.4656 | 116.9537 | 132.915 | 0.2 | 0 | 11.0555 | 260.9242 | 2.2143 | 10.3682 | 1.0512 | 0.22491
2016-09-01 13:00 | 190.5 | 151.04 | 39.46 | 117.8511 | 8.436 | 30.6543 | 70.4378 | 19.5622 | 32.3599 | 31.0493 | 100.9659 | 113.28 | 0.2 | 0 | 9.525 | 223.7709 | 2.2147 | 9.2076 | 1.0553 | 0.19363
2016-09-01 14:00 | 159.89 | 124.86 | 35.03 | 117.3154 | 8.4209 | 45.6578 | 72.6267 | 17.3733 | 47.841 | 45.2473 | 82.5957 | 93.645 | 0.2 | 0 | 7.9945 | 184.2352 | 2.2152 | 7.9725 | 1.0596 | 0.16008
2016-09-01 15:00 | 129.28 | 98.68 | 30.6 | 121.5588 | 8.4059 | 60.6612 | 75.4201 | 14.5799 | 63.0077 | 59.5842 | 61.5417 | 74.01 | 0.2 | 0 | 6.464 | 142.0157 | 2.2156 | 6.6536 | 1.0642 | 0.12393
2016-09-01 16:00 | 96.73 | 74.2733 | 22.4567 | 113.7585 | 8.3909 | 75.6646 | 78.6147 | 11.3853 | 77.886 | 73.9266 | 31.4962 | 55.705 | 0.2 | 0 | 4.8365 | 92.0377 | 2.2161 | 5.0923 | 1.0697 | 0.080729
2016-09-01 17:00 | 64.18 | 49.8667 | 14.3133 | 102.7427 | 8.3759 | 90.6681 | 81.9919 | 8.0081 | 92.5518 | 88.1964 | 3.2337 | 37.4 | 0.2 | 0 | 3.209 | 43.8427 | 2.2166 | 3.5866 | 1.0749 | 0.038645
2016-09-01 18:00 | 31.63 | 25.46 | 6.17 | 75.8068 | 8.3608 | 105.6715 | 85.3315 | 4.6685 | 107.1056 | 102.3092 | 0 | 19.095 | 0.2 | 0 | 1.5815 | 20.6765 | 2.217 | 2.8631 | 1.0775 | 0.018268
2016-09-01 19:00 | 21.0867 | 16.9733 | 4.1133 | 0 | 8.3458 | 120.675 | 88.4199 | 1.5801 | 121.6477 | 116.1319 | 0 | 12.73 | 0.2 | 0 | 1.0543 | 13.7843 | 2.2175 | 2.6482 | 1.0782 | 0.012187
2016-09-01 20:00 | 10.5433 | 8.4867 | 2.0567 | 0 | 8.3308 | 135.6784 | 91.0592 | -1.0592 | 136.2566 | 129.4044 | 0 | 6.365 | 0.2 | 0 | 0.52717 | 6.8922 | 2.2179 | 2.4333 | 1.079 | 0.006098
2016-09-01 21:00 | 0 | 0 | 0 | 0 | 8.3157 | 150.6819 | 93.0761 | -3.0761 | 150.9738 | 141.5353 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2184 | 2.2184 | 1.0797 | 0
2016-09-01 22:00 | 0 | 0 | 0 | 0 | 8.3007 | 165.6854 | 94.3344 | -4.3344 | 165.797 | 151.038 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2188 | 2.2188 | 1.0797 | 0
2016-09-01 23:00 | 0 | 0 | 0 | 0 | 8.2856 | 180.6888 | 94.7468 | -4.7468 | -179.316 | 154.7385 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2193 | 2.2193 | 1.0797 | 0
2016-09-02 | 0 | 0 | 0 | 0 | 8.2706 | -164.3077 | 94.2847 | -4.2847 | -164.4305 | 150.3741 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2197 | 2.2197 | 1.0797 | 0
2016-09-02 01:00 | 5.0433 | 3.1867 | 1.8567 | 0 | 8.2555 | -149.3043 | 92.982 | -2.982 | -149.6106 | 140.5374 | 0 | 2.39 | 0.2 | 0 | 0.25217 | 2.6422 | 2.2202 | 2.3027 | 1.0794 | 0.0023387
2016-09-02 02:00 | 10.0867 | 6.3733 | 3.7133 | 0 | 8.2405 | -134.3008 | 90.9308 | -0.93084 | -134.8961 | 128.2653 | 0 | 4.78 | 0.2 | 0 | 0.50433 | 5.2843 | 2.2206 | 2.3858 | 1.0791 | 0.0046761
2016-09-02 03:00 | 15.13 | 9.56 | 5.57 | 0 | 8.2254 | -119.2973 | 88.2716 | 1.7284 | -120.2866 | 114.928 | 0 | 7.17 | 0.2 | 0 | 0.7565 | 7.9265 | 2.2211 | 2.4688 | 1.0789 | 0.0070123
2016-09-02 04:00 | 51.98 | 26.4567 | 25.5233 | 303.7771 | 8.2103 | -104.2938 | 85.1803 | 4.8197 | -105.7377 | 101.0727 | 0 | 19.8425 | 0.2 | 0 | 2.599 | 22.4415 | 2.2215 | 2.9228 | 1.0773 | 0.019824
2016-09-02 05:00 | 88.83 | 43.3533 | 45.4767 | 321.0737 | 8.1953 | -89.2904 | 81.8573 | 8.1427 | -91.1695 | 86.9434 | 17.1204 | 32.515 | 0.2 | 0 | 4.4415 | 54.0769 | 2.222 | 3.9119 | 1.0738 | 0.047616
2016-09-02 06:00 | 125.68 | 60.25 | 65.43 | 328.6708 | 8.1802 | -74.2869 | 78.5172 | 11.4828 | -76.482 | 72.6673 | 97.9173 | 45.1875 | 0.2 | 0 | 6.284 | 149.3888 | 2.2224 | 6.8908 | 1.0634 | 0.13026
2016-09-02 07:00 | 169.1267 | 68.2833 | 100.8433 | 399.55 | 8.1651 | -59.2834 | 75.3809 | 14.6191 | -61.5775 | 58.3282 | 209.7846 | 51.2125 | 0.2 | 0 | 8.4563 | 269.4535 | 2.2229 | 10.6433 | 1.0502 | 0.23205
2016-09-02 08:00 | 212.5733 | 76.3167 | 136.2567 | 457.3301 | 8.15 | -44.2799 | 72.6661 | 17.3339 | -46.3852 | 44.0091 | 328.9252 | 57.2375 | 0.2 | 0 | 10.6287 | 396.7913 | 2.2234 | 14.6231 | 1.0363 | 0.33719
2016-09-02 09:00 | 256.02 | 84.35 | 171.67 | 516.1569 | 8.1349 | -29.2764 | 70.5738 | 19.4262 | -30.8857 | 29.8648 | 447.6127 | 63.2625 | 0.2 | 0 | 12.801 | 523.6762 | 2.2238 | 18.5887 | 1.0224 | 0.43905
2016-09-02 10:00 | 261 | 87.0767 | 173.9233 | 491.3491 | 8.1198 | -14.273 | 69.2696 | 20.7304 | -15.1274 | 16.4889 | 471.1422 | 65.3075 | 0.2 | 0 | 13.05 | 549.4997 | 2.2243 | 19.3961 | 1.0196 | 0.45943
2016-09-02 11:00 | 265.98 | 89.8033 | 176.1767 | 488.5672 | 8.1047 | 0.73053 | 68.863 | 21.137 | 0.77541 | 8.8905 | 482.6973 | 67.3525 | 0.2 | 0 | 13.299 | 563.3488 | 2.2247 | 19.8294 | 1.0181 | 0.47031
2016-09-02 12:00 | 270.96 | 92.53 | 178.43 | 506.8961 | 8.0896 | 15.734 | 69.39 | 20.61 | 16.6684 | 17.7228 | 482.8389 | 69.3975 | 0.2 | 0 | 13.548 | 565.7844 | 2.2252 | 19.9059 | 1.0178 | 0.47221
2016-09-02 13:00 | 232.49 | 85.4733 | 147.0167 | 447.1882 | 8.0745 | 30.7375 | 70.8066 | 19.1934 | 32.3997 | 31.2463 | 382.3215 | 64.105 | 0.2 | 0 | 11.6245 | 458.051 | 2.2256 | 16.5397 | 1.0296 | 0.38672
2016-09-02 14:00 | 194.02 | 78.4167 | 115.6033 | 395.3282 | 8.0594 | 45.741 | 72.9969 | 17.0031 | 47.8621 | 45.4247 | 277.4595 | 58.8125 | 0.2 | 0 | 9.701 | 345.973 | 2.2261 | 13.0377 | 1.0419 | 0.29558
2016-09-02 15:00 | 155.55 | 71.36 | 84.19 | 342.9866 | 8.0443 | 60.7445 | 75.7909 | 14.2091 | 63.0152 | 59.7569 | 172.7523 | 53.52 | 0.2 | 0 | 7.7775 | 234.0498 | 2.2265 | 9.5406 | 1.0541 | 0.20231
2016-09-02 16:00 | 112.5567 | 53.8033 | 58.7533 | 307.5204 | 8.0292 | 75.748 | 78.9856 | 11.0144 | 77.8859 | 74.1021 | 84.237 | 40.3525 | 0.2 | 0 | 5.6278 | 130.2173 | 2.227 | 6.2963 | 1.0655 | 0.11377
2016-09-02 17:00 | 69.5633 | 36.2467 | 33.3167 | 250.6968 | 8.0141 | 90.7515 | 82.363 | 7.637 | 92.5499 | 88.3805 | 7.085 | 27.185 | 0.2 | 0 | 3.4782 | 37.7482 | 2.2274 | 3.4071 | 1.0756 | 0.033293
2016-09-02 18:00 | 26.57 | 18.69 | 7.88 | 105.161 | 7.999 | 105.755 | 85.7026 | 4.2974 | 107.1075 | 102.5078 | 0 | 14.0175 | 0.2 | 0 | 1.3285 | 15.346 | 2.2279 | 2.7075 | 1.078 | 0.013566
2016-09-02 19:00 | 17.7133 | 12.46 | 5.2533 | 0 | 7.9839 | 120.7585 | 88.791 | 1.209 | 121.6586 | 116.3523 | 0 | 9.345 | 0.2 | 0 | 0.88567 | 10.2307 | 2.2283 | 2.5481 | 1.0786 | 0.0090484
2016-09-02 20:00 | 8.8567 | 6.23 | 2.6267 | 0 | 7.9687 | 135.7621 | 91.4297 | -1.4297 | 136.2813 | 129.6572 | 0 | 4.6725 | 0.2 | 0 | 0.44283 | 5.1153 | 2.2288 | 2.3887 | 1.0791 | 0.0045265
2016-09-02 21:00 | 0 | 0 | 0 | 0 | 7.9536 | 150.7656 | 93.4452 | -3.4452 | 151.0162 | 141.8355 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2293 | 2.2293 | 1.0797 | 0
2016-09-02 22:00 | 0 | 0 | 0 | 0 | 7.9385 | 165.7691 | 94.7007 | -4.7007 | 165.8597 | 151.3944 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2297 | 2.2297 | 1.0797 | 0
2016-09-02 23:00 | 0 | 0 | 0 | 0 | 7.9233 | 180.7726 | 95.1088 | -5.1088 | -179.2317 | 155.0983 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2302 | 2.2302 | 1.0797 | 0
2016-09-03 | 0 | 0 | 0 | 0 | 7.9082 | -164.2239 | 94.6413 | -4.6413 | -164.3251 | 150.6384 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2306 | 2.2306 | 1.0797 | 0
2016-09-03 01:00 | 3.6367 | 3.4733 | 0.16333 | 0 | 7.893 | -149.2204 | 93.3325 | -3.3325 | -149.4861 | 140.7044 | 0 | 2.605 | 0.2 | 0 | 0.18183 | 2.7868 | 2.2311 | 2.3182 | 1.0794 | 0.0024666
2016-09-03 02:00 | 7.2733 | 6.9467 | 0.32667 | 0 | 7.8779 | -134.2168 | 91.2752 | -1.2752 | -134.7555 | 128.3695 | 0 | 5.21 | 0.2 | 0 | 0.36367 | 5.5737 | 2.2315 | 2.4057 | 1.0791 | 0.0049318
2016-09-03 03:00 | 10.91 | 10.42 | 0.49 | 0 | 7.8627 | -119.2133 | 88.6108 | 1.3892 | -120.1336 | 114.9932 | 0 | 7.815 | 0.2 | 0 | 0.5455 | 8.3605 | 2.232 | 2.4932 | 1.0788 | 0.0073957
2016-09-03 04:00 | 39.64 | 38.5233 | 1.1167 | 14.2831 | 7.8476 | -104.2098 | 85.516 | 4.484 | -105.5764 | 101.1131 | 0 | 28.8925 | 0.2 | 0 | 1.982 | 30.8745 | 2.2324 | 3.1973 | 1.0763 | 0.027249
2016-09-03 05:00 | 68.37 | 66.6267 | 1.7433 | 12.8318 | 7.8324 | -89.2062 | 82.1916 | 7.8084 | -91.0041 | 86.968 | 0.67873 | 49.97 | 0.2 | 0 | 3.4185 | 54.0672 | 2.2329 | 3.9225 | 1.0738 | 0.047606
2016-09-03 06:00 | 97.1 | 94.73 | 2.37 | 12.2586 | 7.8173 | -74.2027 | 78.8526 | 11.1474 | -76.3172 | 72.6831 | 3.6489 | 71.0475 | 0.2 | 0 | 4.855 | 79.5514 | 2.2333 | 4.7193 | 1.071 | 0.069862
2016-09-03 07:00 | 137.9467 | 120.67 | 17.2767 | 70.0415 | 7.8021 | -59.1992 | 75.7199 | 14.2801 | -61.4181 | 58.342 | 36.7612 | 90.5025 | 0.2 | 0 | 6.8973 | 134.161 | 2.2338 | 6.4263 | 1.065 | 0.11716
2016-09-03 08:00 | 178.7933 | 146.61 | 32.1833 | 110.1429 | 7.7869 | -44.1956 | 73.0105 | 16.9895 | -46.2364 | 44.0303 | 79.1897 | 109.9575 | 0.2 | 0 | 8.9397 | 198.0868 | 2.2342 | 8.4245 | 1.058 | 0.17185
2016-09-03 09:00 | 219.64 | 172.55 | 47.09 | 144.09 | 7.7717 | -29.1921 | 70.9247 | 19.0753 | -30.7529 | 29.913 | 124.8949 | 129.4125 | 0.2 | 0 | 10.982 | 265.2894 | 2.2347 | 10.525 | 1.0507 | 0.22856
2016-09-03 10:00 | 220.34 | 178.1067 | 42.2333 | 121.3164 | 7.7566 | -14.1886 | 69.6273 | 20.3727 | -15.0153 | 16.6251 | 116.245 | 133.58 | 0.2 | 0 | 11.017 | 260.842 | 2.2351 | 10.3865 | 1.0511 | 0.22483
2016-09-03 11:00 | 221.04 | 183.6633 | 37.3767 | 105.3838 | 7.7414 | 0.81499 | 69.2267 | 20.7733 | 0.86372 | 9.2595 | 104.0106 | 137.7475 | 0.2 | 0 | 11.052 | 252.8101 | 2.2356 | 10.1359 | 1.052 | 0.21809
2016-09-03 12:00 | 221.74 | 189.22 | 32.52 | 93.9929 | 7.7262 | 15.8185 | 69.7581 | 20.2419 | 16.7321 | 17.9864 | 89.3994 | 141.915 | 0.2 | 0 | 11.087 | 242.4014 | 2.2361 | 9.8111 | 1.0532 | 0.20934
2016-09-03 13:00 | 183.7367 | 160.1033 | 23.6333 | 73.251 | 7.711 | 30.8221 | 71.1776 | 18.8224 | 32.4407 | 31.4482 | 62.4913 | 120.0775 | 0.2 | 0 | 9.1868 | 191.7556 | 2.2365 | 8.2289 | 1.0587 | 0.16647
2016-09-03 14:00 | 145.7333 | 130.9867 | 14.7467 | 51.5258 | 7.6958 | 45.8256 | 73.3694 | 16.6306 | 47.8843 | 45.606 | 36.0469 | 98.24 | 0.2 | 0 | 7.2867 | 141.5736 | 2.237 | 6.6611 | 1.0642 | 0.12354
2016-09-03 15:00 | 107.73 | 101.87 | 5.86 | 24.5042 | 7.6806 | 60.8292 | 76.1641 | 13.8359 | 63.0238 | 59.9326 | 12.2771 | 76.4025 | 0.2 | 0 | 5.3865 | 94.0661 | 2.2374 | 5.177 | 1.0694 | 0.082486
2016-09-03 16:00 | 81.5033 | 73.7433 | 7.76 | 42.0243 | 7.6654 | 75.8327 | 79.359 | 10.641 | 77.8868 | 74.2802 | 11.3858 | 55.3075 | 0.2 | 0 | 4.0752 | 70.7684 | 2.2379 | 4.4494 | 1.0719 | 0.062204
2016-09-03 17:00 | 55.2767 | 45.6167 | 9.66 | 76.4039 | 7.6502 | 90.8363 | 82.7365 | 7.2635 | 92.5489 | 88.5668 | 1.911 | 34.2125 | 0.2 | 0 | 2.7638 | 38.8873 | 2.2383 | 3.4536 | 1.0754 | 0.034292
2016-09-03 18:00 | 29.05 | 17.49 | 11.56 | 168.9316 | 7.635 | 105.8399 | 86.0762 | 3.9238 | 107.1104 | 102.7081 | 0 | 13.1175 | 0.2 | 0 | 1.4525 | 14.57 | 2.2388 | 2.6941 | 1.0781 | 0.01288
2016-09-03 19:00 | 19.3667 | 11.66 | 7.7067 | 0 | 7.6198 | 120.8434 | 89.1645 | 0.83554 | 121.6706 | 116.5741 | 0 | 8.745 | 0.2 | 0 | 0.96833 | 9.7133 | 2.2392 | 2.5428 | 1.0786 | 0.008591
2016-09-03 20:00 | 9.6833 | 5.83 | 3.8533 | 0 | 7.6046 | 135.847 | 91.8026 | -1.8026 | 136.3071 | 129.9113 | 0 | 4.3725 | 0.2 | 0 | 0.48417 | 4.8567 | 2.2397 | 2.3915 | 1.0791 | 0.0042976
2016-09-03 21:00 | 0 | 0 | 0 | 0 | 7.5894 | 150.8506 | 93.8165 | -3.8165 | 151.0599 | 142.137 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2401 | 2.2401 | 1.0797 | 0
2016-09-03 22:00 | 0 | 0 | 0 | 0 | 7.5741 | 165.8541 | 95.0691 | -5.0691 | 165.9239 | 151.753 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2406 | 2.2406 | 1.0797 | 0
2016-09-03 23:00 | 0 | 0 | 0 | 0 | 7.5589 | 180.8577 | 95.473 | -5.473 | -179.1459 | 155.4597 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.241 | 2.241 | 1.0797 | 0
2016-09-04 | 0 | 0 | 0 | 0 | 7.5437 | -164.1387 | 94.9999 | -4.9999 | -164.218 | 150.9015 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2415 | 2.2415 | 1.0797 | 0
2016-09-04 01:00 | 2.86 | 2.6667 | 0.19333 | 0 | 7.5285 | -149.1351 | 93.6848 | -3.6848 | -149.3597 | 140.8693 | 0 | 2 | 0.2 | 0 | 0.143 | 2.143 | 2.242 | 2.3089 | 1.0794 | 0.0018968
2016-09-04 02:00 | 5.72 | 5.3333 | 0.38667 | 0 | 7.5132 | -134.1316 | 91.6214 | -1.6214 | -134.6131 | 128.4716 | 0 | 4 | 0.2 | 0 | 0.286 | 4.286 | 2.2424 | 2.3763 | 1.0792 | 0.0037928
2016-09-04 03:00 | 8.58 | 8 | 0.58 | 0 | 7.498 | -119.128 | 88.9517 | 1.0483 | -119.9788 | 115.0567 | 0 | 6 | 0.2 | 0 | 0.429 | 6.429 | 2.2429 | 2.4438 | 1.0789 | 0.005688
2016-09-04 04:00 | 34.07 | 30.8533 | 3.2167 | 44.4851 | 7.4828 | -104.1244 | 85.8534 | 4.1466 | -105.4134 | 101.1522 | 0 | 23.14 | 0.2 | 0 | 1.7035 | 24.8435 | 2.2433 | 3.0197 | 1.0769 | 0.021939
2016-09-04 05:00 | 59.56 | 53.7067 | 5.8533 | 45.0094 | 7.4675 | -89.1208 | 82.5277 | 7.4723 | -90.8372 | 86.9919 | 2.362 | 40.28 | 0.2 | 0 | 2.978 | 45.62 | 2.2438 | 3.6694 | 1.0747 | 0.040201
2016-09-04 06:00 | 85.05 | 76.56 | 8.49 | 45.2667 | 7.4523 | -74.1172 | 79.1899 | 10.8101 | -76.1509 | 72.6987 | 13.4621 | 57.42 | 0.2 | 0 | 4.2525 | 75.1346 | 2.2442 | 4.5922 | 1.0714 | 0.066011
2016-09-04 07:00 | 116.9333 | 102.1833 | 14.75 | 61.2301 | 7.437 | -59.1136 | 76.0607 | 13.9393 | -61.2573 | 58.3563 | 32.1235 | 76.6375 | 0.2 | 0 | 5.8467 | 114.6076 | 2.2447 | 5.8262 | 1.0671 | 0.10028
2016-09-04 08:00 | 148.8167 | 127.8067 | 21.01 | 73.3562 | 7.4218 | -44.1101 | 73.3568 | 16.6432 | -46.0864 | 44.0533 | 52.7206 | 95.855 | 0.2 | 0 | 7.4408 | 156.0165 | 2.2451 | 7.1206 | 1.0626 | 0.13594
2016-09-04 09:00 | 180.7 | 153.43 | 27.27 | 84.958 | 7.4065 | -29.1065 | 71.2777 | 18.7223 | -30.619 | 29.9647 | 73.6019 | 115.0725 | 0.2 | 0 | 9.035 | 197.7094 | 2.2456 | 8.424 | 1.058 | 0.17153
2016-09-04 10:00 | 180.9833 | 157.3067 | 23.6767 | 69.1828 | 7.3912 | -14.1029 | 69.987 | 20.013 | -14.9021 | 16.7684 | 66.2411 | 117.98 | 0.2 | 0 | 9.0492 | 193.2703 | 2.246 | 8.2857 | 1.0585 | 0.16775
2016-09-04 11:00 | 181.2667 | 161.1833 | 20.0833 | 57.5954 | 7.376 | 0.90072 | 69.5924 | 20.4076 | 0.9531 | 9.6309 | 56.7837 | 120.8875 | 0.2 | 0 | 9.0633 | 186.7345 | 2.2465 | 8.0819 | 1.0592 | 0.16219
2016-09-04 12:00 | 181.55 | 165.06 | 16.49 | 48.5124 | 7.3607 | 15.9043 | 70.1284 | 19.8716 | 16.7969 | 18.2559 | 46.0707 | 123.795 | 0.2 | 0 | 9.0775 | 178.9432 | 2.2469 | 7.8389 | 1.0601 | 0.15555
2016-09-04 13:00 | 152.5967 | 140.6967 | 11.9 | 37.6032 | 7.3454 | 30.9079 | 71.5509 | 18.4491 | 32.4828 | 31.655 | 32.0087 | 105.5225 | 0.2 | 0 | 7.6298 | 145.1611 | 2.2474 | 6.7837 | 1.0638 | 0.12662
2016-09-04 14:00 | 123.6433 | 116.3333 | 7.31 | 26.1141 | 7.3302 | 45.9115 | 73.7442 | 16.2558 | 47.9074 | 45.791 | 18.2088 | 87.25 | 0.2 | 0 | 6.1822 | 111.6409 | 2.2478 | 5.7366 | 1.0674 | 0.097718
2016-09-04 15:00 | 94.69 | 91.97 | 2.72 | 11.6851 | 7.3149 | 60.9151 | 76.5395 | 13.4605 | 63.0334 | 60.1113 | 5.8229 | 68.9775 | 0.2 | 0 | 4.7345 | 79.5349 | 2.2483 | 4.7338 | 1.0709 | 0.069845
2016-09-04 16:00 | 69.4267 | 66.8033 | 2.6233 | 14.7207 | 7.2996 | 75.9187 | 79.7346 | 10.2654 | 77.8886 | 74.4607 | 3.9437 | 50.1025 | 0.2 | 0 | 3.4713 | 57.5175 | 2.2488 | 4.0462 | 1.0733 | 0.050623
2016-09-04 17:00 | 44.1633 | 41.6367 | 2.5267 | 21.0686 | 7.2843 | 90.9223 | 83.1122 | 6.8878 | 92.5488 | 88.755 | 0.45777 | 31.2275 | 0.2 | 0 | 2.2082 | 33.8934 | 2.2492 | 3.3084 | 1.0759 | 0.029903
2016-09-04 18:00 | 18.9 | 16.47 | 2.43 | 39.2663 | 7.269 | 105.926 | 86.452 | 3.548 | 107.1141 | 102.91 | 0 | 12.3525 | 0.2 | 0 | 0.945 | 13.2975 | 2.2497 | 2.6652 | 1.0782 | 0.011756
2016-09-04 19:00 | 12.6 | 10.98 | 1.62 | 0 | 7.2537 | 120.9296 | 89.5401 | 0.45985 | 121.6835 | 116.7971 | 0 | 8.235 | 0.2 | 0 | 0.63 | 8.865 | 2.2501 | 2.5271 | 1.0787 | 0.0078411
2016-09-04 20:00 | 6.3 | 5.49 | 0.81 | 0 | 7.2384 | 135.9332 | 92.1776 | -2.1776 | 136.3341 | 130.1664 | 0 | 4.1175 | 0.2 | 0 | 0.315 | 4.4325 | 2.2506 | 2.3891 | 1.0791 | 0.0039223
2016-09-04 21:00 | 0 | 0 | 0 | 0 | 7.2231 | 150.9368 | 94.1899 | -4.1899 | 151.1047 | 142.4399 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.251 | 2.251 | 1.0796 | 0
2016-09-04 22:00 | 0 | 0 | 0 | 0 | 7.2078 | 165.9404 | 95.4396 | -5.4396 | 165.9894 | 152.1136 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2515 | 2.2515 | 1.0796 | 0
2016-09-04 23:00 | 0 | 0 | 0 | 0 | 7.1925 | 180.944 | 95.8391 | -5.8391 | -179.0585 | 155.8228 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2519 | 2.2519 | 1.0796 | 0
2016-09-05 | 0 | 0 | 0 | 0 | 7.1772 | -164.0523 | 95.3603 | -5.3603 | -164.1093 | 151.1633 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2524 | 2.2524 | 1.0796 | 0
2016-09-05 01:00 | 3.06 | 2.2933 | 0.76667 | 0 | 7.1619 | -149.0487 | 94.0389 | -4.0389 | -149.2317 | 141.0319 | 0 | 1.72 | 0.2 | 0 | 0.153 | 1.873 | 2.2528 | 2.3114 | 1.0794 | 0.0016578
2016-09-05 02:00 | 6.12 | 4.5867 | 1.5333 | 0 | 7.1466 | -134.0451 | 91.9693 | -1.9693 | -134.4689 | 128.5717 | 0 | 3.44 | 0.2 | 0 | 0.306 | 3.746 | 2.2533 | 2.3704 | 1.0792 | 0.003315
2016-09-05 03:00 | 9.18 | 6.88 | 2.3 | 0 | 7.1313 | -119.0415 | 89.2943 | 0.70566 | -119.8224 | 115.1187 | 0 | 5.16 | 0.2 | 0 | 0.459 | 5.619 | 2.2537 | 2.4293 | 1.079 | 0.0049716
2016-09-05 04:00 | 40.0733 | 26.6167 | 13.4567 | 202.6438 | 7.1159 | -104.0378 | 86.1924 | 3.8076 | -105.2488 | 101.1903 | 0 | 19.9625 | 0.2 | 0 | 2.0037 | 21.9662 | 2.2542 | 2.9406 | 1.0772 | 0.019403
2016-09-05 05:00 | 70.9667 | 46.3533 | 24.6133 | 198.1752 | 7.1006 | -89.0342 | 82.8654 | 7.1346 | -90.6687 | 87.0152 | 10.3191 | 34.765 | 0.2 | 0 | 3.5483 | 48.6324 | 2.2546 | 3.7744 | 1.0743 | 0.042841
2016-09-05 06:00 | 101.86 | 66.09 | 35.77 | 196.8188 | 7.0853 | -74.0306 | 79.5288 | 10.4712 | -75.9832 | 72.7144 | 58.4817 | 49.5675 | 0.2 | 0 | 5.093 | 113.1422 | 2.2551 | 5.7908 | 1.0672 | 0.099014
2016-09-05 07:00 | 134.52 | 88.2167 | 46.3033 | 196.9622 | 7.07 | -59.0269 | 76.4032 | 13.5968 | -61.0952 | 58.3715 | 103.289 | 66.1625 | 0.2 | 0 | 6.726 | 176.1775 | 2.2556 | 7.7611 | 1.0603 | 0.15318
2016-09-05 08:00 | 167.18 | 110.3433 | 56.8367 | 202.5654 | 7.0546 | -44.0233 | 73.7049 | 16.2951 | -45.9352 | 44.078 | 145.5216 | 82.7575 | 0.2 | 0 | 8.359 | 236.6381 | 2.256 | 9.6509 | 1.0537 | 0.20447
2016-09-05 09:00 | 199.84 | 132.47 | 67.37 | 213.7976 | 7.0393 | -29.0196 | 71.6325 | 18.3675 | -30.484 | 30.0201 | 185.1166 | 99.3525 | 0.2 | 0 | 9.992 | 294.4611 | 2.2565 | 11.4584 | 1.0474 | 0.2529
2016-09-05 10:00 | 208.5233 | 131.62 | 76.9033 | 228.6778 | 7.0239 | -14.016 | 70.3487 | 19.6513 | -14.7879 | 16.9187 | 218.7803 | 98.715 | 0.2 | 0 | 10.4262 | 327.9215 | 2.2569 | 12.5045 | 1.0437 | 0.28066
2016-09-05 11:00 | 217.2067 | 130.77 | 86.4367 | 252.2414 | 7.0086 | 0.98765 | 69.9601 | 20.0399 | 1.0435 | 10.0047 | 248.4057 | 98.0775 | 0.2 | 0 | 10.8603 | 357.3435 | 2.2574 | 13.4244 | 1.0405 | 0.30489
2016-09-05 12:00 | 225.89 | 129.92 | 95.97 | 287.5126 | 6.9932 | 15.9913 | 70.5008 | 19.4992 | 16.8627 | 18.5311 | 272.6054 | 97.44 | 0.2 | 0 | 11.2945 | 381.3399 | 2.2578 | 14.1747 | 1.0379 | 0.32455
2016-09-05 13:00 | 187.29 | 116.0833 | 71.2067 | 229.52 | 6.9779 | 30.9949 | 71.9262 | 18.0738 | 32.5257 | 31.8665 | 194.927 | 87.0625 | 0.2 | 0 | 9.3645 | 291.354 | 2.2583 | 11.3631 | 1.0477 | 0.25031
2016-09-05 14:00 | 148.69 | 102.2467 | 46.4433 | 169.7465 | 6.9625 | 45.9986 | 74.1212 | 15.8788 | 47.9315 | 45.9796 | 117.9592 | 76.685 | 0.2 | 0 | 7.4345 | 202.0787 | 2.2587 | 8.5737 | 1.0575 | 0.17523
2016-09-05 15:00 | 110.09 | 88.41 | 21.68 | 95.7762 | 6.9472 | 61.0022 | 76.9171 | 13.0829 | 63.0438 | 60.2928 | 47.4635 | 66.3075 | 0.2 | 0 | 5.5045 | 119.2755 | 2.2592 | 5.9865 | 1.0665 | 0.10431
2016-09-05 16:00 | 80.1233 | 63.6767 | 16.4467 | 95.7786 | 6.9318 | 76.0059 | 80.1124 | 9.8876 | 77.8912 | 74.6435 | 25.3645 | 47.7575 | 0.2 | 0 | 4.0062 | 77.1282 | 2.2596 | 4.6699 | 1.0712 | 0.067745
2016-09-05 17:00 | 50.1567 | 38.9433 | 11.2133 | 98.9047 | 6.9164 | 91.0096 | 83.4901 | 6.5099 | 92.5496 | 88.9451 | 1.821 | 29.2075 | 0.2 | 0 | 2.5078 | 33.5363 | 2.2601 | 3.3081 | 1.0759 | 0.029588
2016-09-05 18:00 | 20.19 | 14.21 | 5.98 | 108.1379 | 6.9011 | 106.0132 | 86.8299 | 3.1701 | 107.1188 | 103.1133 | 0 | 10.6575 | 0.2 | 0 | 1.0095 | 11.667 | 2.2605 | 2.6251 | 1.0783 | 0.010316
2016-09-05 19:00 | 13.46 | 9.4733 | 3.9867 | 0 | 6.8857 | 121.0169 | 89.918 | 0.082028 | 121.6974 | 117.0213 | 0 | 7.105 | 0.2 | 0 | 0.673 | 7.778 | 2.261 | 2.5041 | 1.0787 | 0.0068801
2016-09-05 20:00 | 6.73 | 4.7367 | 1.9933 | 0 | 6.8703 | 136.0205 | 92.5547 | -2.5547 | 136.362 | 130.4225 | 0 | 3.5525 | 0.2 | 0 | 0.3365 | 3.889 | 2.2615 | 2.383 | 1.0792 | 0.0034414
2016-09-05 21:00 | 0 | 0 | 0 | 0 | 6.855 | 151.0242 | 94.5654 | -4.5654 | 151.1507 | 142.7437 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2619 | 2.2619 | 1.0796 | 0
2016-09-05 22:00 | 0 | 0 | 0 | 0 | 6.8396 | 166.0279 | 95.8121 | -5.8121 | 166.0562 | 152.4761 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2624 | 2.2624 | 1.0796 | 0
2016-09-05 23:00 | 0 | 0 | 0 | 0 | 6.8242 | 181.0315 | 96.2071 | -6.2071 | -178.9697 | 156.1873 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2628 | 2.2628 | 1.0796 | 0
2016-09-06 | 0 | 0 | 0 | 0 | 6.8088 | -163.9648 | 95.7226 | -5.7226 | -163.999 | 151.4236 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2633 | 2.2633 | 1.0796 | 0
2016-09-06 01:00 | 2.68 | 2.1133 | 0.56667 | 0 | 6.7934 | -148.9611 | 94.3948 | -4.3948 | -149.1021 | 141.1921 | 0 | 1.585 | 0.2 | 0 | 0.134 | 1.719 | 2.2637 | 2.3174 | 1.0794 | 0.0015215
2016-09-06 02:00 | 5.36 | 4.2267 | 1.1333 | 0 | 6.778 | -133.9575 | 92.3189 | -2.3189 | -134.3232 | 128.6698 | 0 | 3.17 | 0.2 | 0 | 0.268 | 3.438 | 2.2642 | 2.3716 | 1.0792 | 0.0030424
2016-09-06 03:00 | 8.04 | 6.34 | 1.7 | 0 | 6.7626 | -118.9538 | 89.6386 | 0.36143 | -119.6643 | 115.1791 | 0 | 4.755 | 0.2 | 0 | 0.402 | 5.157 | 2.2646 | 2.4258 | 1.079 | 0.0045629
2016-09-06 04:00 | 40.2167 | 25.7067 | 14.51 | 239.9459 | 6.7472 | -103.9501 | 86.5331 | 3.4669 | -105.0826 | 101.2273 | 0 | 19.28 | 0.2 | 0 | 2.0108 | 21.2908 | 2.2651 | 2.9304 | 1.0772 | 0.018807
2016-09-06 05:00 | 72.3933 | 45.0733 | 27.32 | 230.8982 | 6.7318 | -88.9464 | 83.2048 | 6.7952 | -90.4989 | 87.038 | 11.9312 | 33.805 | 0.2 | 0 | 3.6197 | 49.3559 | 2.2655 | 3.8079 | 1.0742 | 0.043474
2016-09-06 06:00 | 104.57 | 64.44 | 40.13 | 228.1514 | 6.7164 | -73.9427 | 79.8694 | 10.1306 | -75.8141 | 72.7301 | 67.7319 | 48.33 | 0.2 | 0 | 5.2285 | 121.2904 | 2.266 | 6.0563 | 1.0663 | 0.10605
2016-09-06 07:00 | 135.0267 | 96.42 | 38.6067 | 168.4093 | 6.701 | -58.9391 | 76.7475 | 13.2525 | -60.932 | 58.3874 | 88.2756 | 72.315 | 0.2 | 0 | 6.7513 | 167.3419 | 2.2664 | 7.4959 | 1.0613 | 0.14563
2016-09-06 08:00 | 165.4833 | 128.4 | 37.0833 | 134.9869 | 6.6856 | -43.9354 | 74.0548 | 15.9452 | -45.783 | 44.1047 | 96.9299 | 96.3 | 0.2 | 0 | 8.2742 | 201.5041 | 2.2669 | 8.5639 | 1.0575 | 0.17474
2016-09-06 09:00 | 195.94 | 160.38 | 35.56 | 115.0072 | 6.6702 | -28.9317 | 71.9891 | 18.0109 | -30.348 | 30.0792 | 99.5195 | 120.285 | 0.2 | 0 | 9.797 | 229.6015 | 2.2673 | 9.4424 | 1.0545 | 0.19853
2016-09-06 10:00 | 196.7667 | 169.1467 | 27.62 | 83.6175 | 6.6548 | -13.928 | 70.7122 | 19.2878 | -14.6728 | 17.076 | 79.9313 | 126.86 | 0.2 | 0 | 9.8383 | 216.6296 | 2.2678 | 9.0375 | 1.0559 | 0.18756
2016-09-06 11:00 | 197.5933 | 177.9133 | 19.68 | 58.4659 | 6.6393 | 1.0757 | 70.3297 | 19.6703 | 1.1347 | 10.3807 | 57.5089 | 133.435 | 0.2 | 0 | 9.8797 | 200.8236 | 2.2683 | 8.544 | 1.0576 | 0.17416
2016-09-06 12:00 | 198.42 | 186.68 | 11.74 | 35.8332 | 6.6239 | 16.0794 | 70.8751 | 19.1249 | 16.9293 | 18.8118 | 33.9191 | 140.01 | 0.2 | 0 | 9.921 | 183.8501 | 2.2687 | 8.014 | 1.0595 | 0.15972
2016-09-06 13:00 | 162.8133 | 149.3267 | 13.4867 | 44.3678 | 6.6085 | 31.0831 | 72.3035 | 17.6965 | 32.5696 | 32.0825 | 37.5922 | 111.995 | 0.2 | 0 | 8.1407 | 157.7278 | 2.2692 | 7.1982 | 1.0623 | 0.1374
2016-09-06 14:00 | 127.2067 | 111.9733 | 15.2333 | 57.0032 | 6.593 | 46.0868 | 74.5001 | 15.4999 | 47.9564 | 46.1718 | 39.4746 | 83.98 | 0.2 | 0 | 6.3603 | 129.815 | 2.2696 | 6.3263 | 1.0654 | 0.11341
2016-09-06 15:00 | 91.6 | 74.62 | 16.98 | 77.2161 | 6.5776 | 61.0905 | 77.2967 | 12.7033 | 63.0551 | 60.4772 | 38.0498 | 55.965 | 0.2 | 0 | 4.58 | 98.5948 | 2.2701 | 5.3512 | 1.0688 | 0.086408
2016-09-06 16:00 | 66.1667 | 53.6633 | 12.5033 | 75.6951 | 6.5622 | 76.0941 | 80.4923 | 9.5077 | 77.8946 | 74.8285 | 19.8101 | 40.2475 | 0.2 | 0 | 3.3083 | 63.366 | 2.2705 | 4.2507 | 1.0726 | 0.055734
2016-09-06 17:00 | 40.7333 | 32.7067 | 8.0267 | 75.1675 | 6.5467 | 91.0978 | 83.8701 | 6.1299 | 92.5511 | 89.1368 | 1.1324 | 24.53 | 0.2 | 0 | 2.0367 | 27.699 | 2.271 | 3.1366 | 1.0765 | 0.024451
2016-09-06 18:00 | 15.3 | 11.75 | 3.55 | 0 | 6.5313 | 106.1015 | 87.21 | 2.79 | 107.1242 | 103.318 | 0 | 8.8125 | 0.2 | 0 | 0.765 | 9.5775 | 2.2714 | 2.5707 | 1.0785 | 0.0084701
2016-09-06 19:00 | 10.2 | 7.8333 | 2.3667 | 0 | 6.5158 | 121.1053 | 90.2978 | -0.29783 | 121.7121 | 117.2465 | 0 | 5.875 | 0.2 | 0 | 0.51 | 6.385 | 2.2719 | 2.4714 | 1.0789 | 0.0056485
2016-09-06 20:00 | 5.1 | 3.9167 | 1.1833 | 0 | 6.5004 | 136.109 | 92.9339 | -2.9339 | 136.3908 | 130.6793 | 0 | 2.9375 | 0.2 | 0 | 0.255 | 3.1925 | 2.2723 | 2.3721 | 1.0792 | 0.0028252
2016-09-06 21:00 | 0 | 0 | 0 | 0 | 6.4849 | 151.1127 | 94.9428 | -4.9428 | 151.1977 | 143.0485 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2728 | 2.2728 | 1.0795 | 0
2016-09-06 22:00 | 0 | 0 | 0 | 0 | 6.4695 | 166.1164 | 96.1864 | -6.1864 | 166.1241 | 152.8404 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2732 | 2.2732 | 1.0795 | 0
2016-09-06 23:00 | 0 | 0 | 0 | 0 | 6.454 | 181.1201 | 96.5768 | -6.5768 | -178.8796 | 156.5531 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2737 | 2.2737 | 1.0795 | 0
2016-09-07 | 0 | 0 | 0 | 0 | 6.4386 | -163.8762 | 96.0866 | -6.0866 | -163.8874 | 151.6824 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2741 | 2.2741 | 1.0795 | 0
2016-09-07 01:00 | 2.2967 | 1.8533 | 0.44333 | 0 | 6.4231 | -148.8725 | 94.7523 | -4.7523 | -148.971 | 141.35 | 0 | 1.39 | 0.2 | 0 | 0.11483 | 1.5048 | 2.2746 | 2.3216 | 1.0794 | 0.0013319
2016-09-07 02:00 | 4.5933 | 3.7067 | 0.88667 | 0 | 6.4076 | -133.8688 | 92.67 | -2.67 | -134.1759 | 128.7658 | 0 | 2.78 | 0.2 | 0 | 0.22967 | 3.0097 | 2.2751 | 2.3691 | 1.0792 | 0.0026634
2016-09-07 03:00 | 6.89 | 5.56 | 1.33 | 0 | 6.3922 | -118.8651 | 89.9843 | 0.015657 | -119.5048 | 115.2379 | 0 | 4.17 | 0.2 | 0 | 0.3445 | 4.5145 | 2.2755 | 2.4166 | 1.079 | 0.0039945
2016-09-07 04:00 | 37.5367 | 26.5233 | 11.0133 | 202.0439 | 6.3767 | -103.8613 | 86.8753 | 3.1247 | -104.9151 | 101.2633 | 0 | 19.8925 | 0.2 | 0 | 1.8768 | 21.7693 | 2.276 | 2.9563 | 1.0772 | 0.019228
2016-09-07 05:00 | 68.1833 | 47.4867 | 20.6967 | 184.1172 | 6.3612 | -88.8576 | 83.5457 | 6.4543 | -90.3277 | 87.0604 | 9.4422 | 35.615 | 0.2 | 0 | 3.4092 | 48.4664 | 2.2764 | 3.791 | 1.0742 | 0.042693
2016-09-07 06:00 | 98.83 | 68.45 | 30.38 | 178.6957 | 6.3457 | -73.8539 | 80.2116 | 9.7884 | -75.6439 | 72.746 | 53.0025 | 51.3375 | 0.2 | 0 | 4.9415 | 109.2815 | 2.2769 | 5.6919 | 1.0676 | 0.095667
2016-09-07 07:00 | 141.0467 | 83.59 | 57.4567 | 257.2349 | 6.3302 | -58.8502 | 77.0934 | 12.9066 | -60.7677 | 58.4043 | 134.7709 | 62.6925 | 0.2 | 0 | 7.0523 | 204.5157 | 2.2773 | 8.6684 | 1.0572 | 0.17729
2016-09-07 08:00 | 183.2633 | 98.73 | 84.5333 | 314.4686 | 6.3148 | -43.8465 | 74.4063 | 15.5937 | -45.6298 | 44.1335 | 225.7004 | 74.0475 | 0.2 | 0 | 9.1632 | 308.911 | 2.2778 | 11.9312 | 1.0457 | 0.26489
2016-09-07 09:00 | 225.48 | 113.87 | 111.61 | 368.0533 | 6.2993 | -28.8427 | 72.3474 | 17.6526 | -30.2112 | 30.1423 | 318.2856 | 85.4025 | 0.2 | 0 | 11.274 | 414.9621 | 2.2782 | 15.2458 | 1.0341 | 0.35189
2016-09-07 10:00 | 231.7967 | 119.9867 | 111.81 | 344.7849 | 6.2838 | -13.839 | 71.0775 | 18.9225 | -14.5568 | 17.2403 | 329.2938 | 89.99 | 0.2 | 0 | 11.5898 | 430.8736 | 2.2787 | 15.7435 | 1.0324 | 0.36476
2016-09-07 11:00 | 238.1133 | 126.1033 | 112.01 | 338.9162 | 6.2683 | 1.1647 | 70.7012 | 19.2988 | 1.2267 | 10.7588 | 332.9586 | 94.5775 | 0.2 | 0 | 11.9057 | 439.4418 | 2.2791 | 16.0117 | 1.0315 | 0.37168
2016-09-07 12:00 | 244.43 | 132.22 | 112.21 | 349.1083 | 6.2528 | 16.1685 | 71.2512 | 18.7488 | 16.9967 | 19.0978 | 329.8939 | 99.165 | 0.2 | 0 | 12.2215 | 441.2804 | 2.2796 | 16.0696 | 1.0313 | 0.37316
2016-09-07 13:00 | 205.7467 | 110.19 | 95.5567 | 321.0243 | 6.2373 | 31.1722 | 72.6828 | 17.3172 | 32.6142 | 32.3029 | 271.3409 | 82.6425 | 0.2 | 0 | 10.2873 | 364.2708 | 2.28 | 13.6635 | 1.0397 | 0.31055
2016-09-07 14:00 | 167.0633 | 88.16 | 78.9033 | 302.5149 | 6.2218 | 46.1759 | 74.881 | 15.119 | 47.9821 | 46.3673 | 208.7452 | 66.12 | 0.2 | 0 | 8.3532 | 283.2183 | 2.2805 | 11.1311 | 1.0485 | 0.24351
2016-09-07 15:00 | 128.38 | 66.13 | 62.25 | 291.7053 | 6.2063 | 61.1797 | 77.6783 | 12.3217 | 63.0671 | 60.6641 | 142.9146 | 49.5975 | 0.2 | 0 | 6.419 | 198.9311 | 2.281 | 8.4976 | 1.0578 | 0.17255
2016-09-07 16:00 | 90.81 | 48.0467 | 42.7633 | 269.6233 | 6.1908 | 76.1834 | 80.8741 | 9.1259 | 77.8987 | 75.0155 | 69.7131 | 36.035 | 0.2 | 0 | 4.5405 | 110.2886 | 2.2814 | 5.7279 | 1.0675 | 0.096537
2016-09-07 17:00 | 53.24 | 29.9633 | 23.2767 | 232.4096 | 6.1752 | 91.1871 | 84.252 | 5.748 | 92.5534 | 89.3302 | 2.7167 | 22.4725 | 0.2 | 0 | 2.662 | 27.8512 | 2.2819 | 3.1522 | 1.0765 | 0.024584
2016-09-07 18:00 | 15.67 | 11.88 | 3.79 | 0 | 6.1597 | 106.1909 | 87.5919 | 2.4081 | 107.1302 | 103.5238 | 0 | 8.91 | 0.2 | 0 | 0.7835 | 9.6935 | 2.2823 | 2.5852 | 1.0785 | 0.0085723
2016-09-07 19:00 | 10.4467 | 7.92 | 2.5267 | 0 | 6.1442 | 121.1946 | 90.6796 | -0.67961 | 121.7275 | 117.4726 | 0 | 5.94 | 0.2 | 0 | 0.52233 | 6.4623 | 2.2828 | 2.4847 | 1.0788 | 0.0057167
2016-09-07 20:00 | 5.2233 | 3.96 | 1.2633 | 0 | 6.1287 | 136.1984 | 93.3149 | -3.3149 | 136.4204 | 130.9368 | 0 | 2.97 | 0.2 | 0 | 0.26117 | 3.2312 | 2.2832 | 2.3842 | 1.0792 | 0.0028593
2016-09-07 21:00 | 0 | 0 | 0 | 0 | 6.1132 | 151.2021 | 95.322 | -5.322 | 151.2456 | 143.3541 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2837 | 2.2837 | 1.0795 | 0
2016-09-07 22:00 | 0 | 0 | 0 | 0 | 6.0976 | 166.2058 | 96.5625 | -6.5625 | 166.1932 | 153.2063 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2841 | 2.2841 | 1.0795 | 0
2016-09-07 23:00 | 0 | 0 | 0 | 0 | 6.0821 | 181.2096 | 96.9483 | -6.9483 | -178.7883 | 156.9202 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2846 | 2.2846 | 1.0795 | 0
2016-09-08 | 0 | 0 | 0 | 0 | 6.0666 | -163.7867 | 96.4522 | -6.4522 | -163.7744 | 151.9394 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.285 | 2.285 | 1.0795 | 0
2016-09-08 01:00 | 1.83 | 1.4967 | 0.33333 | 0 | 6.051 | -148.7829 | 95.1114 | -5.1114 | -148.8385 | 141.5055 | 0 | 1.1225 | 0.2 | 0 | 0.0915 | 1.214 | 2.2855 | 2.3234 | 1.0794 | 0.0010745
2016-09-08 02:00 | 3.66 | 2.9933 | 0.66667 | 0 | 6.0355 | -133.7792 | 93.0226 | -3.0226 | -134.0272 | 128.8597 | 0 | 2.245 | 0.2 | 0 | 0.183 | 2.428 | 2.2859 | 2.3618 | 1.0792 | 0.0021487
2016-09-08 03:00 | 5.49 | 4.49 | 1 | 0 | 6.02 | -118.7754 | 90.3316 | -0.33159 | -119.3439 | 115.2952 | 0 | 3.3675 | 0.2 | 0 | 0.2745 | 3.642 | 2.2864 | 2.4002 | 1.0791 | 0.0032227
2016-09-08 04:00 | 35.2267 | 22.22 | 13.0067 | 0 | 6.0044 | -103.7716 | 87.2189 | 2.7811 | -104.7462 | 101.2983 | 0 | 16.665 | 0.2 | 0 | 1.7613 | 18.4263 | 2.2868 | 2.8627 | 1.0775 | 0.01628
2016-09-08 05:00 | 64.9633 | 39.95 | 25.0133 | 234.9326 | 5.9889 | -88.7679 | 83.8881 | 6.1119 | -90.1553 | 87.0823 | 11.9583 | 29.9625 | 0.2 | 0 | 3.2482 | 45.169 | 2.2873 | 3.6988 | 1.0746 | 0.0398
2016-09-08 06:00 | 94.7 | 57.68 | 37.02 | 225.6007 | 5.9733 | -73.7641 | 80.5553 | 9.4447 | -75.4726 | 72.7622 | 66.8542 | 43.26 | 0.2 | 0 | 4.735 | 114.8492 | 2.2878 | 5.8768 | 1.0669 | 0.10048
2016-09-08 07:00 | 116.6933 | 87.3133 | 29.38 | 135.1131 | 5.9578 | -58.7604 | 77.4408 | 12.5592 | -60.6024 | 58.4222 | 70.7527 | 65.485 | 0.2 | 0 | 5.8347 | 142.0723 | 2.2882 | 6.728 | 1.064 | 0.12395
2016-09-08 08:00 | 138.6867 | 116.9467 | 21.74 | 82.7021 | 5.9422 | -43.7566 | 74.7595 | 15.2405 | -45.4758 | 44.1643 | 59.3259 | 87.71 | 0.2 | 0 | 6.9343 | 153.9703 | 2.2887 | 7.1002 | 1.0626 | 0.13417
2016-09-08 09:00 | 160.68 | 146.58 | 14.1 | 47.4347 | 5.9267 | -28.7528 | 72.7075 | 17.2925 | -30.0736 | 30.2093 | 40.9928 | 109.935 | 0.2 | 0 | 8.034 | 158.9618 | 2.2891 | 7.2567 | 1.0621 | 0.13844
2016-09-08 10:00 | 169.0533 | 151.9 | 17.1533 | 53.9035 | 5.9111 | -13.7491 | 71.4445 | 18.5555 | -14.4402 | 17.4115 | 51.4336 | 113.925 | 0.2 | 0 | 8.4527 | 173.8113 | 2.2896 | 7.7212 | 1.0605 | 0.15114
2016-09-08 11:00 | 177.4267 | 157.22 | 20.2067 | 62.3009 | 5.8955 | 1.2547 | 71.0744 | 18.9256 | 1.3194 | 11.139 | 61.1272 | 117.915 | 0.2 | 0 | 8.8713 | 187.9135 | 2.29 | 8.1623 | 1.0589 | 0.16317
2016-09-08 12:00 | 185.8 | 162.54 | 23.26 | 73.8025 | 5.88 | 16.2584 | 71.6292 | 18.3708 | 17.0648 | 19.3888 | 69.617 | 121.905 | 0.2 | 0 | 9.29 | 200.812 | 2.2905 | 8.5659 | 1.0575 | 0.17414
2016-09-08 13:00 | 157.6633 | 136.8567 | 20.8067 | 71.4254 | 5.8644 | 31.2622 | 73.0638 | 16.9362 | 32.6594 | 32.5276 | 60.2211 | 102.6425 | 0.2 | 0 | 7.8832 | 170.7468 | 2.2909 | 7.6268 | 1.0608 | 0.14853
2016-09-08 14:00 | 129.5267 | 111.1733 | 18.3533 | 72.152 | 5.8488 | 46.266 | 75.2637 | 14.7363 | 48.0084 | 46.5661 | 49.6057 | 83.38 | 0.2 | 0 | 6.4763 | 139.4621 | 2.2914 | 6.6496 | 1.0642 | 0.1217
2016-09-08 15:00 | 101.39 | 85.49 | 15.9 | 76.8646 | 5.8332 | 61.2698 | 78.0618 | 11.9382 | 63.0797 | 60.8537 | 37.4363 | 64.1175 | 0.2 | 0 | 5.0695 | 106.6233 | 2.2918 | 5.6238 | 1.0678 | 0.09336
2016-09-08 16:00 | 71.9533 | 60.6133 | 11.34 | 74.6109 | 5.8177 | 76.2735 | 81.2578 | 8.7422 | 77.9035 | 75.2045 | 19.0533 | 45.46 | 0.2 | 0 | 3.5977 | 68.111 | 2.2923 | 4.4208 | 1.072 | 0.059874
2016-09-08 17:00 | 42.5167 | 35.7367 | 6.78 | 72.5236 | 5.8021 | 91.2773 | 84.6358 | 5.3642 | 92.5562 | 89.5251 | 0.60111 | 26.8025 | 0.2 | 0 | 2.1258 | 29.5294 | 2.2927 | 3.2155 | 1.0762 | 0.02606
2016-09-08 18:00 | 13.08 | 10.86 | 2.22 | 0 | 5.7865 | 106.2811 | 87.9757 | 2.0243 | 107.137 | 103.7308 | 0 | 8.145 | 0.2 | 0 | 0.654 | 8.799 | 2.2932 | 2.5682 | 1.0785 | 0.0077817
2016-09-08 19:00 | 8.72 | 7.24 | 1.48 | 0 | 5.7709 | 121.2849 | 91.0632 | -1.0632 | 121.7436 | 117.6993 | 0 | 5.43 | 0.2 | 0 | 0.436 | 5.866 | 2.2937 | 2.477 | 1.0788 | 0.0051893
2016-09-08 20:00 | 4.36 | 3.62 | 0.74 | 0 | 5.7553 | 136.2886 | 93.6977 | -3.6977 | 136.4508 | 131.1947 | 0 | 2.715 | 0.2 | 0 | 0.218 | 2.933 | 2.2941 | 2.3858 | 1.0791 | 0.0025954
2016-09-08 21:00 | 0 | 0 | 0 | 0 | 5.7397 | 151.2924 | 95.7031 | -5.7031 | 151.2944 | 143.6602 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2946 | 2.2946 | 1.0795 | 0
2016-09-08 22:00 | 0 | 0 | 0 | 0 | 5.7241 | 166.2962 | 96.9404 | -6.9404 | 166.2632 | 153.5738 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.295 | 2.295 | 1.0795 | 0
2016-09-08 23:00 | 0 | 0 | 0 | 0 | 5.7085 | 181.3 | 97.3215 | -7.3215 | -178.6958 | 157.2884 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2955 | 2.2955 | 1.0795 | 0
2016-09-09 | 0 | 0 | 0 | 0 | 5.6929 | -163.6962 | 96.8194 | -6.8194 | -163.6601 | 152.1946 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2959 | 2.2959 | 1.0795 | 0
2016-09-09 01:00 | 1.7333 | 1.31 | 0.42333 | 0 | 5.6773 | -148.6925 | 95.4719 | -5.4719 | -148.7046 | 141.6584 | 0 | 0.9825 | 0.2 | 0 | 0.086667 | 1.0692 | 2.2964 | 2.3298 | 1.0793 | 0.00094628
2016-09-09 02:00 | 3.4667 | 2.62 | 0.84667 | 0 | 5.6617 | -133.6887 | 93.3767 | -3.3767 | -133.8771 | 128.9515 | 0 | 1.965 | 0.2 | 0 | 0.17333 | 2.1383 | 2.2968 | 2.3636 | 1.0792 | 0.0018924
2016-09-09 03:00 | 5.2 | 3.93 | 1.27 | 0 | 5.6461 | -118.6849 | 90.6802 | -0.68024 | -119.1816 | 115.351 | 0 | 2.9475 | 0.2 | 0 | 0.26 | 3.2075 | 2.2973 | 2.3975 | 1.0791 | 0.0028382
2016-09-09 04:00 | 35.7833 | 22.18 | 13.6033 | 0 | 5.6305 | -103.6811 | 87.564 | 2.436 | -104.5761 | 101.3324 | 0 | 16.635 | 0.2 | 0 | 1.7892 | 18.4242 | 2.2977 | 2.8735 | 1.0774 | 0.016278
2016-09-09 05:00 | 66.3667 | 40.43 | 25.9367 | 258.0716 | 5.6149 | -88.6773 | 84.2319 | 5.7681 | -89.9818 | 87.1039 | 13.0389 | 30.3225 | 0.2 | 0 | 3.3183 | 46.6798 | 2.2982 | 3.7569 | 1.0744 | 0.041123
2016-09-09 06:00 | 96.95 | 58.68 | 38.27 | 241.9858 | 5.5993 | -73.6735 | 80.9005 | 9.0995 | -75.3004 | 72.7786 | 71.6435 | 44.01 | 0.2 | 0 | 4.8475 | 120.501 | 2.2986 | 6.0643 | 1.0663 | 0.10536
2016-09-09 07:00 | 141.1967 | 74.4233 | 66.7733 | 315.715 | 5.5837 | -58.6697 | 77.7898 | 12.2102 | -60.4363 | 58.4413 | 165.2365 | 55.8175 | 0.2 | 0 | 7.0598 | 228.1138 | 2.2991 | 9.4277 | 1.0545 | 0.19725
2016-09-09 08:00 | 185.4433 | 90.1667 | 95.2767 | 370.8807 | 5.568 | -43.6659 | 75.1142 | 14.8858 | -45.321 | 44.1974 | 265.9 | 67.625 | 0.2 | 0 | 9.2722 | 342.7972 | 2.2995 | 13.012 | 1.042 | 0.29289
2016-09-09 09:00 | 229.69 | 105.91 | 123.78 | 425.0411 | 5.5524 | -28.6621 | 73.0691 | 16.9309 | -29.9354 | 30.2803 | 367.0522 | 79.4325 | 0.2 | 0 | 11.4845 | 457.9692 | 2.3 | 16.6115 | 1.0294 | 0.38656
2016-09-09 10:00 | 229.5367 | 115.2167 | 114.32 | 366.2726 | 5.5368 | -13.6583 | 71.8131 | 18.1869 | -14.323 | 17.5895 | 349.1479 | 86.4125 | 0.2 | 0 | 11.4768 | 447.0372 | 2.6 | 16.5699 | 1.0295 | 0.37739
2016-09-09 11:00 | 229.3833 | 124.5233 | 104.86 | 329.5987 | 5.5212 | 1.3455 | 71.4493 | 18.5507 | 1.4126 | 11.5211 | 322.9578 | 93.3925 | 0.2 | 0 | 11.4692 | 427.8194 | 2.7 | 16.0694 | 1.0313 | 0.36178
2016-09-09 12:00 | 229.23 | 133.83 | 95.4 | 308.8672 | 5.5055 | 16.3493 | 72.0088 | 17.9912 | 17.1334 | 19.6845 | 290.8176 | 100.3725 | 0.2 | 0 | 11.4615 | 402.6516 | 2.6 | 15.1829 | 1.0344 | 0.34152
2016-09-09 13:00 | 189.4333 | 119.4067 | 70.0267 | 245.7859 | 5.4899 | 31.3531 | 73.4466 | 16.5534 | 32.7053 | 32.7564 | 206.7008 | 89.555 | 0.2 | 0 | 9.4717 | 305.7274 | 3.3 | 12.854 | 1.0425 | 0.26135
2016-09-09 14:00 | 149.6367 | 104.9833 | 44.6533 | 180.1443 | 5.4742 | 46.3569 | 75.6482 | 14.3518 | 48.0353 | 46.7681 | 123.3904 | 78.7375 | 0.2 | 0 | 7.4818 | 209.6097 | 2.9 | 9.4503 | 1.0544 | 0.18123
2016-09-09 15:00 | 109.84 | 90.56 | 19.28 | 96.2675 | 5.4586 | 61.3607 | 78.4469 | 11.5531 | 63.0929 | 61.0456 | 46.6044 | 67.92 | 0.2 | 0 | 5.492 | 120.0164 | 2.9 | 6.6505 | 1.0642 | 0.10473
2016-09-09 16:00 | 77.7133 | 63.5667 | 14.1467 | 97.3376 | 5.443 | 76.3645 | 81.6433 | 8.3567 | 77.9088 | 75.3954 | 24.5434 | 47.675 | 0.2 | 0 | 3.8857 | 76.1041 | 2.4 | 4.7783 | 1.0708 | 0.066822
2016-09-09 17:00 | 45.5867 | 36.5733 | 9.0133 | 103.8577 | 5.4273 | 91.3683 | 85.0213 | 4.9787 | 92.5596 | 89.7213 | 0.50512 | 27.43 | 0.2 | 0 | 2.2793 | 30.2145 | 1.8 | 2.7442 | 1.0779 | 0.026706
2016-09-09 18:00 | 13.46 | 9.58 | 3.88 | 0 | 5.4117 | 106.3721 | 88.3613 | 1.6387 | 107.1442 | 103.9386 | 0 | 7.185 | 0.2 | 0 | 0.673 | 7.858 | 1.1 | 1.3456 | 1.0828 | 0.006977
2016-09-09 19:00 | 8.9733 | 6.3867 | 2.5867 | 0 | 5.396 | 121.3759 | 91.4485 | -1.4485 | 121.7602 | 117.9266 | 0 | 4.79 | 0.2 | 0 | 0.44867 | 5.2387 | 0.8 | 0.96371 | 1.0841 | 0.0046571
2016-09-09 20:00 | 4.4867 | 3.1933 | 1.2933 | 0 | 5.3804 | 136.3797 | 94.0822 | -4.0822 | 136.4819 | 131.453 | 0 | 2.395 | 0.2 | 0 | 0.22433 | 2.6193 | 1.7 | 1.7819 | 1.0813 | 0.0023224
2016-09-09 21:00 | 0 | 0 | 0 | 0 | 5.3647 | 151.3835 | 96.0857 | -6.0857 | 151.3441 | 143.9667 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-09-09 22:00 | 0 | 0 | 0 | 0 | 5.349 | 166.3873 | 97.3198 | -7.3198 | 166.3342 | 153.9426 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-09-09 23:00 | 0 | 0 | 0 | 0 | 5.3334 | 181.3911 | 97.6961 | -7.6961 | -178.6023 | 157.6576 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-09-10 | 0 | 0 | 0 | 0 | 5.3177 | -163.605 | 97.188 | -7.188 | -163.5446 | 152.4477 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0816 | 0
2016-09-10 01:00 | 1.1867 | 0.97333 | 0.21333 | 0 | 5.3021 | -148.6012 | 95.8339 | -5.8339 | -148.5696 | 141.8088 | 0 | 0.73 | 0.2 | 0 | 0.059333 | 0.78933 | 1.5 | 1.5247 | 1.0822 | 0.00070043
2016-09-10 02:00 | 2.3733 | 1.9467 | 0.42667 | 0 | 5.2864 | -133.5974 | 93.7321 | -3.7321 | -133.7259 | 129.0413 | 0 | 1.46 | 0.2 | 0 | 0.11867 | 1.5787 | 1.6 | 1.6493 | 1.0817 | 0.0014003
2016-09-10 03:00 | 3.56 | 2.92 | 0.64 | 0 | 5.2707 | -118.5936 | 91.0302 | -1.0302 | -119.0182 | 115.4054 | 0 | 2.19 | 0.2 | 0 | 0.178 | 2.368 | 1.8 | 1.874 | 1.0809 | 0.0020989
2016-09-10 04:00 | 29.1967 | 18.8167 | 10.38 | 0 | 5.255 | -103.5898 | 87.9104 | 2.0896 | -104.405 | 101.3657 | 0 | 14.1125 | 0.2 | 0 | 1.4598 | 15.5723 | 1.4 | 1.8866 | 1.0809 | 0.013802
2016-09-10 05:00 | 54.8333 | 34.7133 | 20.12 | 212.8961 | 5.2394 | -88.5859 | 84.5771 | 5.4229 | -89.8073 | 87.1253 | 10.6772 | 26.035 | 0.2 | 0 | 2.7417 | 39.4539 | 1.8 | 3.0329 | 1.0769 | 0.03484
2016-09-10 06:00 | 80.47 | 50.61 | 29.86 | 196.222 | 5.2237 | -73.5821 | 81.247 | 8.753 | -75.1272 | 72.7954 | 58.0393 | 37.9575 | 0.2 | 0 | 4.0235 | 100.0203 | 2 | 5.1256 | 1.0696 | 0.087722
2016-09-10 07:00 | 101.9233 | 80.2133 | 21.71 | 105.6357 | 5.208 | -58.5783 | 78.1402 | 11.8598 | -60.2695 | 58.4615 | 55.255 | 60.16 | 0.2 | 0 | 5.0962 | 120.5112 | 2.1 | 5.866 | 1.067 | 0.10544
2016-09-10 08:00 | 123.3767 | 109.8167 | 13.56 | 54.0497 | 5.1923 | -43.5745 | 75.4704 | 14.5296 | -45.1657 | 44.2328 | 38.7272 | 82.3625 | 0.2 | 0 | 6.1688 | 127.2586 | 2.3 | 6.2768 | 1.0655 | 0.11119
2016-09-10 09:00 | 144.83 | 139.42 | 5.41 | 18.9725 | 5.1766 | -28.5707 | 73.4322 | 16.5678 | -29.7966 | 30.3555 | 16.3714 | 104.565 | 0.2 | 0 | 7.2415 | 128.1779 | 2.6 | 6.6056 | 1.0644 | 0.11187
2016-09-10 10:00 | 143.1367 | 136.62 | 6.5167 | 21.2982 | 5.1609 | -13.5668 | 72.1833 | 17.8167 | -14.2053 | 17.7743 | 20.2816 | 102.465 | 0.2 | 0 | 7.1568 | 129.9034 | 2.8 | 6.8595 | 1.0635 | 0.11328
2016-09-10 11:00 | 141.4433 | 133.82 | 7.6233 | 24.4409 | 5.1452 | 1.437 | 71.8257 | 18.1743 | 1.5064 | 11.9049 | 23.9152 | 100.365 | 0.2 | 0 | 7.0722 | 131.3524 | 2.2 | 6.3048 | 1.0654 | 0.11476
2016-09-10 12:00 | 139.75 | 131.02 | 8.73 | 28.8561 | 5.1295 | 16.4408 | 72.39 | 17.61 | 17.2026 | 19.9848 | 27.1185 | 98.265 | 0.2 | 0 | 6.9875 | 132.371 | 2.2 | 6.3366 | 1.0653 | 0.11563
2016-09-10 13:00 | 125.8833 | 107.8167 | 18.0667 | 64.8778 | 5.1139 | 31.4447 | 73.8309 | 16.1691 | 32.7516 | 32.9891 | 54.4178 | 80.8625 | 0.2 | 0 | 6.2942 | 141.5744 | 2.1 | 6.5242 | 1.0647 | 0.1236
2016-09-10 14:00 | 112.0167 | 84.6133 | 27.4033 | 113.5458 | 5.0982 | 46.4485 | 76.0343 | 13.9657 | 48.0627 | 46.9731 | 77.477 | 63.46 | 0.2 | 0 | 5.6008 | 146.5379 | 1.9 | 6.4793 | 1.0648 | 0.12795
2016-09-10 15:00 | 98.15 | 61.41 | 36.74 | 189.7178 | 5.0824 | 61.4523 | 78.8338 | 11.1662 | 63.1065 | 61.2398 | 91.2816 | 46.0575 | 0.2 | 0 | 4.9075 | 142.2466 | 1.9 | 6.3452 | 1.0653 | 0.12426
2016-09-10 16:00 | 68.62 | 43.4867 | 25.1333 | 181.2736 | 5.0667 | 76.4561 | 82.0303 | 7.9697 | 77.9145 | 75.588 | 45.1178 | 32.615 | 0.2 | 0 | 3.431 | 81.1638 | 1.8 | 4.3364 | 1.0723 | 0.071368
2016-09-10 17:00 | 39.09 | 25.5633 | 13.5267 | 168.9747 | 5.051 | 91.46 | 85.4085 | 4.5915 | 92.5634 | 89.9188 | 0.23948 | 19.1725 | 0.2 | 0 | 1.9545 | 21.3665 | 1.2 | 1.8677 | 1.081 | 0.018939
2016-09-10 18:00 | 9.56 | 7.64 | 1.92 | 0 | 5.0353 | 106.4638 | 88.7485 | 1.2515 | 107.152 | 104.1473 | 0 | 5.73 | 0.2 | 0 | 0.478 | 6.208 | 1 | 1.194 | 1.0833 | 0.0055147
2016-09-10 19:00 | 6.3733 | 5.0933 | 1.28 | 0 | 5.0196 | 121.4676 | 91.8355 | -1.8355 | 121.7774 | 118.1543 | 0 | 3.82 | 0.2 | 0 | 0.31867 | 4.1387 | 1.1 | 1.2293 | 1.0832 | 0.0036761
2016-09-10 20:00 | 3.1867 | 2.5467 | 0.64 | 0 | 5.0039 | 136.4715 | 94.4683 | -4.4683 | 136.5136 | 131.7114 | 0 | 1.91 | 0.2 | 0 | 0.15933 | 2.0693 | 1.3 | 1.3647 | 1.0827 | 0.0018372
2016-09-10 21:00 | 0 | 0 | 0 | 0 | 4.9882 | 151.4753 | 96.4699 | -6.4699 | 151.3944 | 144.2735 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0837 | 0
2016-09-10 22:00 | 0 | 0 | 0 | 0 | 4.9725 | 166.4792 | 97.7007 | -7.7007 | 166.4061 | 154.3126 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0826 | 0
2016-09-10 23:00 | 0 | 0 | 0 | 0 | 4.9567 | 181.483 | 98.0722 | -8.0722 | -178.5078 | 158.0277 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0833 | 0
2016-09-11 | 0 | 0 | 0 | 0 | 4.941 | -163.5132 | 97.5581 | -7.5581 | -163.4281 | 152.6987 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.083 | 0
2016-09-11 01:00 | 0.41333 | 0.41333 | 0 | 0 | 4.9253 | -148.5093 | 96.1971 | -6.1971 | -148.4333 | 141.9566 | 0 | 0.31 | 0.2 | 0 | 0.020667 | 0.33067 | 1.8 | 1.8103 | 1.0812 | 0.00029315
2016-09-11 02:00 | 0.82667 | 0.82667 | 0 | 0 | 4.9096 | -133.5055 | 94.0889 | -4.0889 | -133.5734 | 129.1291 | 0 | 0.62 | 0.2 | 0 | 0.041333 | 0.66133 | 1.7 | 1.7207 | 1.0815 | 0.00058648
2016-09-11 03:00 | 1.24 | 1.24 | 0 | 0 | 4.8938 | -118.5016 | 91.3815 | -1.3815 | -118.8537 | 115.4584 | 0 | 0.93 | 0.2 | 0 | 0.062 | 0.992 | 1.5 | 1.531 | 1.0821 | 0.00088026
2016-09-11 04:00 | 10.5833 | 10.14 | 0.44333 | 0 | 4.8781 | -103.4978 | 88.258 | 1.742 | -104.2328 | 101.3981 | 0 | 7.605 | 0.2 | 0 | 0.52917 | 8.1342 | 2.2 | 2.4542 | 1.0789 | 0.0071963
2016-09-11 05:00 | 19.9267 | 19.04 | 0.88667 | 10.0206 | 4.8624 | -88.4939 | 84.9236 | 5.0764 | -89.632 | 87.1465 | 0.49886 | 14.28 | 0.2 | 0 | 0.99633 | 15.7752 | 2.5 | 2.993 | 1.077 | 0.013932
2016-09-11 06:00 | 29.27 | 27.94 | 1.33 | 9.0989 | 4.8466 | -73.4901 | 81.5949 | 8.4051 | -74.9534 | 72.8128 | 2.6887 | 20.955 | 0.2 | 0 | 1.4635 | 25.1072 | 1.8 | 2.5846 | 1.0785 | 0.022203
2016-09-11 07:00 | 35.7667 | 34.88 | 0.88667 | 4.4443 | 4.8309 | -58.4862 | 78.492 | 11.508 | -60.102 | 58.483 | 2.3233 | 26.16 | 0.2 | 0 | 1.7883 | 30.2716 | 2.2 | 3.146 | 1.0765 | 0.026721
2016-09-11 08:00 | 42.2633 | 41.82 | 0.44333 | 1.8108 | 4.8151 | -43.4824 | 75.828 | 14.172 | -45.0098 | 44.2706 | 1.2966 | 31.365 | 0.2 | 0 | 2.1132 | 34.7748 | 2.2 | 3.2867 | 1.076 | 0.030682
2016-09-11 09:00 | 48.76 | 48.76 | 0 | 0 | 4.7994 | -28.4785 | 73.7967 | 16.2033 | -29.6574 | 30.435 | 0 | 36.57 | 0.2 | 0 | 2.438 | 39.008 | 1.9 | 3.119 | 1.0766 | 0.034436
2016-09-11 10:00 | 41.29 | 41.2867 | 0.0033333 | 0.011119 | 4.7836 | -13.4747 | 72.5549 | 17.4451 | -14.0873 | 17.9657 | 0.010577 | 30.965 | 0.2 | 0 | 2.0645 | 33.0401 | 2.4 | 3.4325 | 1.0755 | 0.029138
2016-09-11 11:00 | 33.82 | 33.8133 | 0.0066667 | 0.021812 | 4.7679 | 1.5292 | 72.2036 | 17.7964 | 1.6005 | 12.2905 | 0.021313 | 25.36 | 0.2 | 0 | 1.691 | 27.0723 | 2.5 | 3.346 | 1.0758 | 0.023882
2016-09-11 12:00 | 26.35 | 26.34 | 0.01 | 0.033765 | 4.7521 | 16.533 | 72.7728 | 17.2272 | 17.2721 | 20.2893 | 0.03167 | 19.755 | 0.2 | 0 | 1.3175 | 21.1042 | 1.9 | 2.5595 | 1.0785 | 0.018665
2016-09-11 13:00 | 30.89 | 25.55 | 5.34 | 19.6325 | 4.7364 | 31.5369 | 74.2168 | 15.7832 | 32.7983 | 33.2257 | 16.423 | 19.1625 | 0.2 | 0 | 1.5445 | 37.13 | 1.7 | 2.8603 | 1.0775 | 0.032806
2016-09-11 14:00 | 35.43 | 24.76 | 10.67 | 45.4485 | 4.7206 | 46.5407 | 76.4219 | 13.5781 | 48.0905 | 47.181 | 30.8907 | 18.57 | 0.2 | 0 | 1.7715 | 51.2322 | 1.7 | 3.301 | 1.0759 | 0.045201
2016-09-11 15:00 | 39.97 | 23.97 | 16 | 85.5607 | 4.7049 | 61.5446 | 79.2221 | 10.7779 | 63.1206 | 61.4363 | 40.9097 | 17.9775 | 0.2 | 0 | 1.9985 | 60.8857 | 2.1 | 4.0027 | 1.0735 | 0.053595
2016-09-11 16:00 | 28.2 | 17.0567 | 11.1433 | 84.4652 | 4.6891 | 76.5484 | 82.419 | 7.581 | 77.9207 | 75.7822 | 20.7454 | 12.7925 | 0.2 | 0 | 1.41 | 34.9479 | 1.8 | 2.8921 | 1.0774 | 0.030875
2016-09-11 17:00 | 16.43 | 10.1433 | 6.2867 | 85.7814 | 4.6733 | 91.5523 | 85.7972 | 4.2028 | 92.5676 | 90.1174 | 0 | 7.6075 | 0.2 | 0 | 0.8215 | 8.429 | 1.6 | 1.8634 | 1.081 | 0.0074715
2016-09-11 18:00 | 4.66 | 3.23 | 1.43 | 0 | 4.6576 | 106.5561 | 89.1372 | 0.86282 | 107.1601 | 104.3566 | 0 | 2.4225 | 0.2 | 0 | 0.233 | 2.6555 | 1.5 | 1.583 | 1.082 | 0.002356
2016-09-11 19:00 | 3.1067 | 2.1533 | 0.95333 | 0 | 4.6418 | 121.56 | 92.224 | -2.224 | 121.7951 | 118.3823 | 0 | 1.615 | 0.2 | 0 | 0.15533 | 1.7703 | 1.7 | 1.7553 | 1.0814 | 0.0015698
2016-09-11 20:00 | 1.5533 | 1.0767 | 0.47667 | 0 | 4.626 | 136.5639 | 94.8559 | -4.8559 | 136.5458 | 131.9697 | 0 | 0.8075 | 0.2 | 0 | 0.077667 | 0.88517 | 1.6 | 1.6277 | 1.0818 | 0.00078521
2016-09-11 21:00 | 0 | 0 | 0 | 0 | 4.6103 | 151.5677 | 96.8556 | -6.8556 | 151.4453 | 144.5803 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.084 | 0
2016-09-11 22:00 | 0 | 0 | 0 | 0 | 4.5945 | 166.5716 | 98.083 | -8.083 | 166.4787 | 154.6837 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0843 | 0
2016-09-11 23:00 | 0 | 0 | 0 | 0 | 4.5787 | 181.5754 | 98.4497 | -8.4497 | -178.4123 | 158.3985 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.084 | 0
2016-09-12 | 0 | 0 | 0 | 0 | 4.5629 | -163.4207 | 97.9294 | -7.9294 | -163.3106 | 152.9474 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.0822 | 0
2016-09-12 01:00 | 0.92333 | 0.62333 | 0.3 | 0 | 4.5471 | -148.4168 | 96.5617 | -6.5617 | -148.2961 | 142.1018 | 0 | 0.4675 | 0.2 | 0 | 0.046167 | 0.51367 | 1.9 | 1.9161 | 1.0808 | 0.00045524
2016-09-12 02:00 | 1.8467 | 1.2467 | 0.6 | 0 | 4.5313 | -133.413 | 94.4468 | -4.4468 | -133.42 | 129.2148 | 0 | 0.935 | 0.2 | 0 | 0.092333 | 1.0273 | 2 | 2.0321 | 1.0804 | 0.00091013
2016-09-12 03:00 | 2.77 | 1.87 | 0.9 | 0 | 4.5156 | -118.4091 | 91.734 | -1.734 | -118.6883 | 115.51 | 0 | 1.4025 | 0.2 | 0 | 0.1385 | 1.541 | 1.7 | 1.7482 | 1.0814 | 0.0013665
2016-09-12 04:00 | 33.56 | 14.6233 | 18.9367 | 0 | 4.4998 | -103.4052 | 88.6069 | 1.3931 | -104.0597 | 101.4299 | 0 | 10.9675 | 0.2 | 0 | 1.678 | 12.6455 | 2.7 | 3.0952 | 1.0767 | 0.011164
2016-09-12 05:00 | 64.35 | 27.3767 | 36.9733 | 448.4959 | 4.484 | -88.4014 | 85.2713 | 4.7287 | -89.4558 | 87.1675 | 22.1629 | 20.5325 | 0.2 | 0 | 3.2175 | 45.9129 | 2.7 | 4.1348 | 1.073 | 0.040398
2016-09-12 06:00 | 95.14 | 40.13 | 55.01 | 392.536 | 4.4682 | -73.3975 | 81.9441 | 8.0559 | -74.7789 | 72.8306 | 115.8755 | 30.0975 | 0.2 | 0 | 4.757 | 150.73 | 3.3 | 8.0103 | 1.0595 | 0.13095
2016-09-12 07:00 | 114.8733 | 66.9833 | 47.89 | 247.54 | 4.4524 | -58.3936 | 78.845 | 11.155 | -59.934 | 58.5059 | 129.3176 | 50.2375 | 0.2 | 0 | 5.7437 | 185.2988 | 3.5 | 9.2906 | 1.055 | 0.1603
2016-09-12 08:00 | 134.6067 | 93.8367 | 40.77 | 170.7607 | 4.4366 | -43.3898 | 76.1869 | 13.8131 | -44.8535 | 44.311 | 122.1893 | 70.3775 | 0.2 | 0 | 6.7303 | 199.2971 | 2.6 | 8.828 | 1.0566 | 0.17267
2016-09-12 09:00 | 154.34 | 120.69 | 33.65 | 123.3018 | 4.4208 | -28.3859 | 74.1626 | 15.8374 | -29.5179 | 30.5187 | 106.22 | 90.5175 | 0.2 | 0 | 7.717 | 204.4545 | 2.7 | 9.0892 | 1.0557 | 0.17699
2016-09-12 10:00 | 155.6533 | 123.1233 | 32.53 | 110.8069 | 4.405 | -13.382 | 72.928 | 17.072 | -13.9689 | 18.1637 | 105.2853 | 92.3425 | 0.2 | 0 | 7.7827 | 205.4105 | 3.3 | 9.7191 | 1.0535 | 0.17745
2016-09-12 11:00 | 156.9667 | 125.5567 | 31.41 | 104.9359 | 4.3892 | 1.6219 | 72.5829 | 17.4171 | 1.6948 | 12.6776 | 102.3776 | 94.1675 | 0.2 | 0 | 7.8483 | 204.3934 | 3.7 | 10.0873 | 1.0522 | 0.17635
2016-09-12 12:00 | 158.28 | 127.99 | 30.29 | 104.5377 | 4.3734 | 16.6257 | 73.1569 | 16.8431 | 17.3419 | 20.5979 | 97.8549 | 95.9925 | 0.2 | 0 | 7.914 | 201.7614 | 3.7 | 10.005 | 1.0525 | 0.17413
2016-09-12 13:00 | 149.8233 | 99.29 | 50.5333 | 190.3423 | 4.3576 | 31.6296 | 74.6041 | 15.3959 | 32.8453 | 33.4659 | 158.7863 | 74.4675 | 0.2 | 0 | 7.4912 | 240.7449 | 4.1 | 11.6233 | 1.0468 | 0.20665
2016-09-12 14:00 | 141.3667 | 70.59 | 70.7767 | 310.1989 | 4.3417 | 46.6335 | 76.8109 | 13.1891 | 48.1186 | 47.3917 | 209.9994 | 52.9425 | 0.2 | 0 | 7.0683 | 270.0102 | 3.9 | 12.3378 | 1.0443 | 0.23122
2016-09-12 15:00 | 132.91 | 41.89 | 91.02 | 504.7858 | 4.3259 | 61.6373 | 79.6119 | 10.3881 | 63.135 | 61.6347 | 239.8193 | 31.4175 | 0.2 | 0 | 6.6455 | 277.8823 | 4.2 | 12.8838 | 1.0424 | 0.23753
2016-09-12 16:00 | 91.6167 | 29.9867 | 61.63 | 492.3437 | 4.3101 | 76.6412 | 82.809 | 7.191 | 77.9271 | 75.9778 | 119.2938 | 22.49 | 0.2 | 0 | 4.5808 | 146.3646 | 3.3 | 7.8739 | 1.0599 | 0.12721
2016-09-12 17:00 | 50.3233 | 18.0833 | 32.24 | 484.8529 | 4.2943 | 91.6451 | 86.1873 | 3.8127 | 92.5721 | 90.3169 | 0 | 13.5625 | 0.2 | 0 | 2.5162 | 16.0787 | 3.1 | 3.6025 | 1.0749 | 0.014172
2016-09-12 18:00 | 9.03 | 6.18 | 2.85 | 0 | 4.2785 | 106.649 | 89.5273 | 0.47268 | 107.1685 | 104.5665 | 0 | 4.635 | 0.2 | 0 | 0.4515 | 5.0865 | 2 | 2.159 | 1.0799 | 0.0045044
2016-09-12 19:00 | 6.02 | 4.12 | 1.9 | 0 | 4.2627 | 121.6529 | 92.6138 | -2.6138 | 121.8131 | 118.6104 | 0 | 3.09 | 0.2 | 0 | 0.301 | 3.391 | 1.7 | 1.806 | 1.0812 | 0.0030063
2016-09-12 20:00 | 3.01 | 2.06 | 0.95 | 0 | 4.2468 | 136.6567 | 95.2449 | -5.2449 | 136.5784 | 132.2279 | 0 | 1.545 | 0.2 | 0 | 0.1505 | 1.6955 | 1.2 | 1.253 | 1.0831 | 0.0015059
2016-09-12 21:00 | 0 | 0 | 0 | 0 | 4.231 | 151.6606 | 97.2427 | -7.2427 | 151.4968 | 144.8869 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0819 | 0
2016-09-12 22:00 | 0 | 0 | 0 | 0 | 4.2152 | 166.6645 | 98.4667 | -8.4667 | 166.552 | 155.0557 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0826 | 0
2016-09-12 23:00 | 0 | 0 | 0 | 0 | 4.1993 | 181.6684 | 98.8285 | -8.8285 | -178.3162 | 158.7699 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-09-13 | 0 | 0 | 0 | 0 | 4.1835 | -163.3277 | 98.302 | -8.302 | -163.1922 | 153.1937 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.0788 | 0
2016-09-13 01:00 | 0.56333 | 0.37667 | 0.18667 | 0 | 4.1677 | -148.3239 | 96.9274 | -6.9274 | -148.1579 | 142.2443 | 0 | 0.2825 | 0.2 | 0 | 0.028167 | 0.31067 | 0.8 | 0.80971 | 1.0847 | 0.00027632
2016-09-13 02:00 | 1.1267 | 0.75333 | 0.37333 | 0 | 4.1518 | -133.32 | 94.8059 | -4.8059 | -133.2656 | 129.2985 | 0 | 0.565 | 0.2 | 0 | 0.056333 | 0.62133 | 0.7 | 0.71942 | 1.085 | 0.00055279
2016-09-13 03:00 | 1.69 | 1.13 | 0.56 | 0 | 4.136 | -118.3161 | 92.0876 | -2.0876 | -118.5219 | 115.5603 | 0 | 0.8475 | 0.2 | 0 | 0.0845 | 0.932 | 0.5 | 0.52912 | 1.0856 | 0.0008297
2016-09-13 04:00 | 9.9133 | 9.01 | 0.90333 | 0 | 4.1201 | -103.3122 | 88.9569 | 1.0431 | -103.8859 | 101.4609 | 0 | 6.7575 | 0.2 | 0 | 0.49567 | 7.2532 | 1 | 1.2267 | 1.0832 | 0.0064425
2016-09-13 05:00 | 18.1367 | 16.89 | 1.2467 | 16.3243 | 4.1043 | -88.3083 | 85.6201 | 4.3799 | -89.2791 | 87.1885 | 0.8007 | 12.6675 | 0.2 | 0 | 0.90683 | 14.375 | 1.4 | 1.8492 | 1.081 | 0.012743
2016-09-13 06:00 | 26.36 | 24.77 | 1.59 | 11.8583 | 4.0885 | -73.3044 | 82.2944 | 7.7056 | -74.6038 | 72.8492 | 3.4969 | 18.5775 | 0.2 | 0 | 1.318 | 23.3924 | 1.4 | 2.131 | 1.08 | 0.020717
2016-09-13 07:00 | 32.7033 | 31.6433 | 1.06 | 5.6566 | 4.0726 | -58.3006 | 79.1993 | 10.8007 | -59.7656 | 58.5303 | 2.953 | 23.7325 | 0.2 | 0 | 1.6352 | 28.3207 | 1.6 | 2.485 | 1.0788 | 0.025053
2016-09-13 08:00 | 39.0467 | 38.5167 | 0.53 | 2.2781 | 4.0568 | -43.2967 | 76.5471 | 13.4529 | -44.6969 | 44.354 | 1.629 | 28.8875 | 0.2 | 0 | 1.9523 | 32.4688 | 2.2 | 3.2146 | 1.0762 | 0.028654
2016-09-13 09:00 | 45.39 | 45.39 | 0 | 0 | 4.0409 | -28.2928 | 74.5298 | 15.4702 | -29.3782 | 30.6068 | 0 | 34.0425 | 0.2 | 0 | 2.2695 | 36.312 | 2 | 3.1347 | 1.0765 | 0.032055
2016-09-13 10:00 | 38.4967 | 38.4967 | 0 | 0 | 4.025 | -13.2889 | 73.3023 | 16.6977 | -13.8504 | 18.3682 | 0 | 28.8725 | 0.2 | 0 | 1.9248 | 30.7973 | 2 | 2.9624 | 1.0771 | 0.027202
2016-09-13 11:00 | 31.6033 | 31.6033 | 0 | 0 | 4.0092 | 1.715 | 72.9635 | 17.0365 | 1.7893 | 13.0662 | 0 | 23.7025 | 0.2 | 0 | 1.5802 | 25.2827 | 2.7 | 3.4901 | 1.0753 | 0.022293
2016-09-13 12:00 | 24.71 | 24.71 | 0 | 0 | 3.9933 | 16.7189 | 73.5423 | 16.4577 | 17.4118 | 20.9103 | 0 | 18.5325 | 0.2 | 0 | 1.2355 | 19.768 | 2.3 | 2.9177 | 1.0773 | 0.017463
2016-09-13 13:00 | 20.2433 | 20.2433 | 0 | 0 | 3.9775 | 31.7228 | 74.9927 | 15.0073 | 32.8926 | 33.7096 | 0 | 15.1825 | 0.2 | 0 | 1.0122 | 16.1947 | 3.5 | 4.0061 | 1.0735 | 0.014255
2016-09-13 14:00 | 15.7767 | 15.7767 | 0 | 0 | 3.9616 | 46.7267 | 77.2013 | 12.7987 | 48.147 | 47.605 | 0 | 11.8325 | 0.2 | 0 | 0.78883 | 12.6213 | 3.3 | 3.6944 | 1.0746 | 0.011121
2016-09-13 15:00 | 11.31 | 11.31 | 0 | 0 | 3.9457 | 61.7306 | 80.0031 | 9.9969 | 63.1495 | 61.8351 | 0 | 8.4825 | 0.2 | 0 | 0.5655 | 9.048 | 3.6 | 3.8828 | 1.0739 | 0.0079677
2016-09-13 16:00 | 7.9567 | 7.9567 | 0 | 0 | 3.9299 | 76.7344 | 83.2004 | 6.7996 | 77.9338 | 76.1748 | 0 | 5.9675 | 0.2 | 0 | 0.39783 | 6.3653 | 3.8 | 3.9989 | 1.0735 | 0.0056032
2016-09-13 17:00 | 4.6033 | 4.6033 | 0 | 0 | 3.914 | 91.7383 | 86.5788 | 3.4212 | 92.5768 | 90.5173 | 0 | 3.4525 | 0.2 | 0 | 0.23017 | 3.6827 | 4.7 | 4.8151 | 1.0706 | 0.0032331
2016-09-13 18:00 | 1.25 | 1.25 | 0 | 0 | 3.8981 | 106.7422 | 89.9188 | 0.081227 | 107.1772 | 104.7767 | 0 | 0.9375 | 0.2 | 0 | 0.0625 | 1 | 5.3 | 5.3312 | 1.0688 | 0.00087645
2016-09-13 19:00 | 0.83333 | 0.83333 | 0 | 0 | 3.8823 | 121.7461 | 93.005 | -3.005 | 121.8313 | 118.8385 | 0 | 0.625 | 0.2 | 0 | 0.041667 | 0.66667 | 6.6 | 6.6208 | 1.0643 | 0.00058183
2016-09-13 20:00 | 0.41667 | 0.41667 | 0 | 0 | 3.8664 | 136.75 | 95.6352 | -5.6352 | 136.6114 | 132.4857 | 0 | 0.3125 | 0.2 | 0 | 0.020833 | 0.33333 | 6.7 | 6.7104 | 1.064 | 0.00029083
2016-09-13 21:00 | 0 | 0 | 0 | 0 | 3.8505 | 151.7539 | 97.631 | -7.631 | 151.5488 | 145.1933 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6.5 | 6.5 | 1.0648 | 0
2016-09-13 22:00 | 0 | 0 | 0 | 0 | 3.8346 | 166.7578 | 98.8516 | -8.8516 | 166.6258 | 155.4284 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6.8 | 6.8 | 1.0637 | 0
2016-09-13 23:00 | 0 | 0 | 0 | 0 | 3.8187 | 181.7617 | 99.2084 | -9.2084 | -178.2193 | 159.1419 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6.9 | 6.9 | 1.0634 | 0
2016-09-14 | 0 | 0 | 0 | 0 | 3.8029 | -163.2344 | 98.6757 | -8.6757 | -163.073 | 153.4375 | 0 | 0 | 0.2 | 0 | 0 | 0 | 7.2 | 7.2 | 1.0623 | 0
2016-09-14 01:00 | 0.50333 | 0.32333 | 0.18 | 0 | 3.787 | -148.2305 | 97.2942 | -7.2942 | -148.0189 | 142.3841 | 0 | 0.2425 | 0.2 | 0 | 0.025167 | 0.26767 | 6.4 | 6.4084 | 1.0651 | 0.00023377
2016-09-14 02:00 | 1.0067 | 0.64667 | 0.36 | 0 | 3.7711 | -133.2266 | 95.1661 | -5.1661 | -133.1104 | 129.3803 | 0 | 0.485 | 0.2 | 0 | 0.050333 | 0.53533 | 6.5 | 6.5167 | 1.0647 | 0.00046737
2016-09-14 03:00 | 1.51 | 0.97 | 0.54 | 0 | 3.7552 | -118.2227 | 92.4422 | -2.4422 | -118.3548 | 115.6094 | 0 | 0.7275 | 0.2 | 0 | 0.0755 | 0.803 | 7 | 7.0251 | 1.0629 | 0.00069989
2016-09-14 04:00 | 26.0167 | 12.05 | 13.9667 | 0 | 3.7393 | -103.2188 | 89.308 | 0.692 | -103.7113 | 101.4914 | 0 | 9.0375 | 0.2 | 0 | 1.3008 | 10.3383 | 7.2 | 7.5231 | 1.0612 | 0.008996
2016-09-14 05:00 | 50.5233 | 23.13 | 27.3933 | 389.7886 | 3.7234 | -88.2149 | 85.9701 | 4.0299 | -89.1017 | 87.2096 | 18.9758 | 17.3475 | 0.2 | 0 | 2.5262 | 38.8494 | 6.6 | 7.814 | 1.0602 | 0.033773
2016-09-14 06:00 | 75.03 | 34.21 | 40.82 | 318.9024 | 3.7075 | -73.211 | 82.6459 | 7.3541 | -74.4284 | 72.8684 | 93.9381 | 25.6575 | 0.2 | 0 | 3.7515 | 123.3471 | 7.2 | 11.0546 | 1.0488 | 0.10608
2016-09-14 07:00 | 85.1067 | 54.1733 | 30.9333 | 170.6239 | 3.6916 | -58.2071 | 79.5548 | 10.4452 | -59.597 | 58.5562 | 89.008 | 40.63 | 0.2 | 0 | 4.2553 | 133.8934 | 6.8 | 10.9842 | 1.0491 | 0.11518
2016-09-14 08:00 | 95.1833 | 74.1367 | 21.0467 | 92.9185 | 3.6757 | -43.2032 | 76.9085 | 13.0915 | -44.5402 | 44.3996 | 66.3882 | 55.6025 | 0.2 | 0 | 4.7592 | 126.7498 | 6.4 | 10.3609 | 1.0512 | 0.10926
2016-09-14 09:00 | 105.26 | 94.1 | 11.16 | 42.8351 | 3.6598 | -28.1993 | 74.8983 | 15.1017 | -29.2384 | 30.6994 | 36.8321 | 70.575 | 0.2 | 0 | 5.263 | 112.6701 | 5.8 | 9.3209 | 1.0549 | 0.09746
2016-09-14 10:00 | 122.6367 | 98.8733 | 23.7633 | 84.5556 | 3.6439 | -13.1954 | 73.6778 | 16.3222 | -13.7319 | 18.5791 | 80.1489 | 74.155 | 0.2 | 0 | 6.1318 | 160.4358 | 5.8 | 10.8136 | 1.0497 | 0.13809
2016-09-14 11:00 | 140.0133 | 103.6467 | 36.3667 | 126.889 | 3.628 | 1.8085 | 73.3454 | 16.6546 | 1.8839 | 13.4562 | 123.4056 | 77.735 | 0.2 | 0 | 7.0007 | 208.1413 | 5.7 | 12.2044 | 1.0448 | 0.17832
2016-09-14 12:00 | 157.39 | 108.42 | 48.97 | 176.8967 | 3.6121 | 16.8124 | 73.929 | 16.071 | 17.4819 | 21.2262 | 164.8957 | 81.315 | 0.2 | 0 | 7.8695 | 254.0802 | 5.4 | 13.34 | 1.0408 | 0.21685
2016-09-14 13:00 | 134.23 | 89.5967 | 44.6333 | 176.8613 | 3.5962 | 31.8163 | 75.3826 | 14.6174 | 32.9399 | 33.9566 | 146.6996 | 67.1975 | 0.2 | 0 | 6.7115 | 220.6086 | 5.3 | 12.194 | 1.0448 | 0.18901
2016-09-14 14:00 | 111.07 | 70.7733 | 40.2967 | 187.551 | 3.5803 | 46.8202 | 77.5929 | 12.4071 | 48.1754 | 47.8208 | 125.9315 | 53.08 | 0.2 | 0 | 5.5535 | 184.565 | 5.2 | 10.9677 | 1.0491 | 0.15878
2016-09-14 15:00 | 87.91 | 51.95 | 35.96 | 215.526 | 3.5644 | 61.8241 | 80.3954 | 9.6046 | 63.1643 | 62.0373 | 101.0595 | 38.9625 | 0.2 | 0 | 4.3955 | 144.4175 | 5.2 | 9.713 | 1.0535 | 0.12476
2016-09-14 16:00 | 60.15 | 35.8533 | 24.2967 | 217.7318 | 3.5485 | 76.828 | 83.593 | 6.407 | 77.9406 | 76.373 | 51.2977 | 26.89 | 0.2 | 0 | 3.0075 | 81.1952 | 5 | 7.5374 | 1.0611 | 0.070649
2016-09-14 17:00 | 32.39 | 19.7567 | 12.6333 | 239.1187 | 3.5326 | 91.8319 | 86.9715 | 3.0285 | 92.5816 | 90.7183 | 0 | 14.8175 | 0.2 | 0 | 1.6195 | 16.437 | 4.9 | 5.4137 | 1.0686 | 0.014402
2016-09-14 18:00 | 4.63 | 3.66 | 0.97 | 0 | 3.5166 | 106.8358 | 90.3114 | -0.31143 | 107.186 | 104.9872 | 0 | 2.745 | 0.2 | 0 | 0.2315 | 2.9765 | 4.7 | 4.793 | 1.0707 | 0.0026133
2016-09-14 19:00 | 3.0867 | 2.44 | 0.64667 | 0 | 3.5007 | 121.8397 | 93.3974 | -3.3974 | 121.8497 | 119.0664 | 0 | 1.83 | 0.2 | 0 | 0.15433 | 1.9843 | 5.2 | 5.262 | 1.0691 | 0.0017396
2016-09-14 20:00 | 1.5433 | 1.22 | 0.32333 | 0 | 3.4848 | 136.8436 | 96.0266 | -6.0266 | 136.6446 | 132.7429 | 0 | 0.915 | 0.2 | 0 | 0.077167 | 0.99217 | 4.1 | 4.131 | 1.073 | 0.000873
2016-09-14 21:00 | 0 | 0 | 0 | 0 | 3.4689 | 151.8475 | 98.0204 | -8.0204 | 151.6011 | 145.4991 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.0735 | 0
2016-09-14 22:00 | 0 | 0 | 0 | 0 | 3.4529 | 166.8514 | 99.2376 | -9.2376 | 166.7001 | 155.8017 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5 | 4.5 | 1.0717 | 0
2016-09-14 23:00 | 0 | 0 | 0 | 0 | 3.437 | 181.8553 | 99.5895 | -9.5895 | -178.1218 | 159.5142 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0714 | 0
2016-09-15 | 0 | 0 | 0 | 0 | 3.4211 | -163.1408 | 99.0504 | -9.0504 | -162.9531 | 153.6786 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.4 | 4.4 | 1.0721 | 0
2016-09-15 01:00 | 0.34333 | 0.23333 | 0.11 | 0 | 3.4052 | -148.1369 | 97.6621 | -7.6621 | -147.8791 | 142.5212 | 0 | 0.175 | 0.2 | 0 | 0.017167 | 0.19217 | 4.3 | 4.306 | 1.0724 | 0.00016899
2016-09-15 02:00 | 0.68667 | 0.46667 | 0.22 | 0 | 3.3892 | -133.133 | 95.5273 | -5.5273 | -132.9545 | 129.4601 | 0 | 0.35 | 0.2 | 0 | 0.034333 | 0.38433 | 4.2 | 4.212 | 1.0728 | 0.00033808
2016-09-15 03:00 | 1.03 | 0.7 | 0.33 | 0 | 3.3733 | -118.1291 | 92.7979 | -2.7979 | -118.187 | 115.6573 | 0 | 0.525 | 0.2 | 0 | 0.0515 | 0.5765 | 4.2 | 4.218 | 1.0727 | 0.00050711
2016-09-15 04:00 | 26.1667 | 12.1233 | 14.0433 | 0 | 3.3574 | -103.1252 | 89.6601 | 0.33989 | -103.5363 | 101.5213 | 0 | 9.0925 | 0.2 | 0 | 1.3083 | 10.4008 | 4.1 | 4.425 | 1.072 | 0.0091429
2016-09-15 05:00 | 51.3033 | 23.5467 | 27.7567 | 432.5821 | 3.3414 | -88.1213 | 86.3211 | 3.6789 | -88.9239 | 87.2308 | 20.8993 | 17.66 | 0.2 | 0 | 2.5652 | 41.1244 | 3.8 | 5.0851 | 1.0697 | 0.036073
2016-09-15 06:00 | 76.44 | 34.97 | 41.47 | 340.2066 | 3.3255 | -73.1173 | 82.9984 | 7.0016 | -74.2526 | 72.8885 | 100.0997 | 26.2275 | 0.2 | 0 | 3.822 | 130.1492 | 3.9 | 7.9672 | 1.0596 | 0.11308
2016-09-15 07:00 | 111 | 46.2967 | 64.7033 | 369.3709 | 3.3095 | -58.1134 | 79.9113 | 10.0887 | -59.4282 | 58.5838 | 192.5351 | 34.7225 | 0.2 | 0 | 5.55 | 232.8076 | 3.7 | 10.9752 | 1.0491 | 0.20027
2016-09-15 08:00 | 145.56 | 57.6233 | 87.9367 | 399.0964 | 3.2936 | -43.1095 | 77.271 | 12.729 | -44.3834 | 44.4481 | 284.909 | 43.2175 | 0.2 | 0 | 7.278 | 335.4045 | 3.9 | 14.3814 | 1.0372 | 0.28525
2016-09-15 09:00 | 180.12 | 68.95 | 111.17 | 437.1587 | 3.2776 | -28.1056 | 75.2678 | 14.7322 | -29.0987 | 30.7964 | 375.5159 | 51.7125 | 0.2 | 0 | 9.006 | 436.2344 | 4.3 | 17.9323 | 1.0247 | 0.36656
2016-09-15 10:00 | 184.9133 | 70.7133 | 114.2 | 415.692 | 3.2617 | -13.1017 | 74.0545 | 15.9455 | -13.6134 | 18.7961 | 393.5236 | 53.035 | 0.2 | 0 | 9.2457 | 455.8043 | 5.1 | 19.3439 | 1.0198 | 0.38116
2016-09-15 11:00 | 189.7067 | 72.4767 | 117.23 | 418.3913 | 3.2458 | 1.9022 | 73.7283 | 16.2717 | 1.9784 | 13.8475 | 406.2313 | 54.3575 | 0.2 | 0 | 9.4853 | 470.0742 | 3.9 | 18.5898 | 1.0224 | 0.39411
2016-09-15 12:00 | 194.5 | 74.24 | 120.26 | 444.883 | 3.2298 | 16.9061 | 74.3168 | 15.6832 | 17.5519 | 21.5456 | 413.7972 | 55.68 | 0.2 | 0 | 9.725 | 479.2022 | 3.7 | 18.6751 | 1.0221 | 0.40164
2016-09-15 13:00 | 158.11 | 63.71 | 94.4 | 384.1224 | 3.2138 | 31.91 | 75.7735 | 14.2265 | 32.9873 | 34.2067 | 317.6749 | 47.7825 | 0.2 | 0 | 7.9055 | 373.3629 | 3.6 | 15.2676 | 1.0341 | 0.31659
2016-09-15 14:00 | 121.72 | 53.18 | 68.54 | 329.2686 | 3.1979 | 46.9139 | 77.9856 | 12.0144 | 48.2039 | 48.0389 | 220.1575 | 39.885 | 0.2 | 0 | 6.086 | 266.1285 | 3.9 | 12.2165 | 1.0447 | 0.22799
2016-09-15 15:00 | 85.33 | 42.65 | 42.68 | 266.6286 | 3.1819 | 61.9178 | 80.7889 | 9.2111 | 63.179 | 62.2411 | 124.1828 | 31.9875 | 0.2 | 0 | 4.2665 | 160.4368 | 3.8 | 8.8136 | 1.0567 | 0.13901
2016-09-15 16:00 | 58.31 | 29.4667 | 28.8433 | 275.3314 | 3.166 | 76.9217 | 83.9867 | 6.0133 | 77.9474 | 76.5723 | 63.9372 | 22.1 | 0.2 | 0 | 2.9155 | 88.9527 | 3.8 | 6.5798 | 1.0645 | 0.077644
2016-09-15 17:00 | 31.29 | 16.2833 | 15.0067 | 0 | 3.15 | 91.9257 | 87.3653 | 2.6347 | 92.5865 | 90.92 | 0 | 12.2125 | 0.2 | 0 | 1.5645 | 13.777 | 3.4 | 3.8305 | 1.0741 | 0.012134
2016-09-15 18:00 | 4.27 | 3.1 | 1.17 | 0 | 3.1341 | 106.9296 | 90.7052 | -0.70519 | 107.1948 | 105.1977 | 0 | 2.325 | 0.2 | 0 | 0.2135 | 2.5385 | 2.9 | 2.9793 | 1.0771 | 0.002242
2016-09-15 19:00 | 2.8467 | 2.0667 | 0.78 | 0 | 3.1181 | 121.9335 | 93.7909 | -3.7909 | 121.8682 | 119.2939 | 0 | 1.55 | 0.2 | 0 | 0.14233 | 1.6923 | 2.5 | 2.5529 | 1.0786 | 0.0014967
2016-09-15 20:00 | 1.4233 | 1.0333 | 0.39 | 0 | 3.1021 | 136.9374 | 96.4192 | -6.4192 | 136.678 | 132.9995 | 0 | 0.775 | 0.2 | 0 | 0.071167 | 0.84617 | 2.4 | 2.4264 | 1.079 | 0.00074868
2016-09-15 21:00 | 0 | 0 | 0 | 0 | 3.0862 | 151.9413 | 98.411 | -8.411 | 151.6536 | 145.8042 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0801 | 0
2016-09-15 22:00 | 0 | 0 | 0 | 0 | 3.0702 | 166.9452 | 99.6247 | -9.6247 | 166.7748 | 156.1755 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-09-15 23:00 | 0 | 0 | 0 | 0 | 3.0542 | 181.9491 | 99.9715 | -9.9715 | -178.0238 | 159.8868 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.078 | 0
2016-09-16 | 0 | 0 | 0 | 0 | 3.0383 | -163.047 | 99.4262 | -9.4262 | -162.8327 | 153.9169 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-09-16 01:00 | 0.2 | 0.15333 | 0.046667 | 0 | 3.0223 | -148.0431 | 98.0309 | -8.0309 | -147.7388 | 142.6555 | 0 | 0.115 | 0.2 | 0 | 0.01 | 0.125 | 2.7 | 2.7039 | 1.078 | 0.0001105
2016-09-16 02:00 | 0.4 | 0.30667 | 0.093333 | 0 | 3.0063 | -133.0391 | 95.8894 | -5.8894 | -132.7979 | 129.5379 | 0 | 0.23 | 0.2 | 0 | 0.02 | 0.25 | 2.3 | 2.3078 | 1.0794 | 0.00022128
2016-09-16 03:00 | 0.6 | 0.46 | 0.14 | 0 | 2.9903 | -118.0352 | 93.1545 | -3.1545 | -118.0187 | 115.704 | 0 | 0.345 | 0.2 | 0 | 0.03 | 0.375 | 2.8 | 2.8117 | 1.0777 | 0.00033138
2016-09-16 04:00 | 18.07 | 13.43 | 4.64 | 0 | 2.9744 | -103.0313 | 90.0132 | -0.013164 | -103.3607 | 101.5508 | 0 | 10.0725 | 0.2 | 0 | 0.9035 | 10.976 | 2.3 | 2.643 | 1.0782 | 0.0097046
2016-09-16 05:00 | 35.54 | 26.4 | 9.14 | 157.4958 | 2.9584 | -88.0274 | 86.6731 | 3.3269 | -88.7458 | 87.2522 | 7.5504 | 19.8 | 0.2 | 0 | 1.777 | 29.1274 | 2.7 | 3.6102 | 1.0749 | 0.025673
2016-09-16 06:00 | 53.01 | 39.37 | 13.64 | 117.8204 | 2.9424 | -73.0235 | 83.352 | 6.648 | -74.0766 | 72.9095 | 34.6253 | 29.5275 | 0.2 | 0 | 2.6505 | 66.8033 | 2.8 | 4.8876 | 1.0704 | 0.058635
2016-09-16 07:00 | 81.0633 | 61.1967 | 19.8667 | 117.538 | 2.9264 | -58.0196 | 80.269 | 9.731 | -59.2593 | 58.6131 | 61.2155 | 45.8975 | 0.2 | 0 | 4.0532 | 111.1662 | 2.7 | 6.1739 | 1.0659 | 0.097163
2016-09-16 08:00 | 109.1167 | 83.0233 | 26.0933 | 121.8487 | 2.9104 | -43.0157 | 77.6346 | 12.3654 | -44.2267 | 44.4994 | 86.9095 | 62.2675 | 0.2 | 0 | 5.4558 | 154.6328 | 2.9 | 7.7323 | 1.0604 | 0.13446
2016-09-16 09:00 | 137.17 | 104.85 | 32.32 | 130.3015 | 2.8944 | -28.0118 | 75.6384 | 14.3616 | -28.9591 | 30.898 | 111.8095 | 78.6375 | 0.2 | 0 | 6.8585 | 197.3055 | 4.1 | 10.2658 | 1.0516 | 0.17013
2016-09-16 10:00 | 148.4633 | 111.5033 | 36.96 | 137.7165 | 2.8785 | -13.0079 | 74.4323 | 15.5677 | -13.4951 | 19.0192 | 130.1984 | 83.6275 | 0.2 | 0 | 7.4232 | 221.2491 | 3.7 | 10.614 | 1.0504 | 0.19056
2016-09-16 11:00 | 159.7567 | 118.1567 | 41.6 | 151.9623 | 2.8625 | 1.9961 | 74.1123 | 15.8877 | 2.0728 | 14.2398 | 147.2932 | 88.6175 | 0.2 | 0 | 7.9878 | 243.8985 | 3.1 | 10.7218 | 1.05 | 0.20999
2016-09-16 12:00 | 171.05 | 124.81 | 46.24 | 175.2986 | 2.8465 | 17 | 74.7056 | 15.2944 | 17.6218 | 21.868 | 162.6849 | 93.6075 | 0.2 | 0 | 8.5525 | 264.8449 | 4.5 | 12.7764 | 1.0428 | 0.22646
2016-09-16 13:00 | 138.14 | 106.7133 | 31.4267 | 131.4276 | 2.8305 | 32.0039 | 76.1655 | 13.8345 | 33.0345 | 34.4599 | 108.365 | 80.035 | 0.2 | 0 | 6.907 | 195.307 | 2.8 | 8.9033 | 1.0563 | 0.16917
2016-09-16 14:00 | 105.23 | 88.6167 | 16.6133 | 82.476 | 2.8145 | 47.0078 | 78.3793 | 11.6207 | 48.2324 | 48.2593 | 54.9093 | 66.4625 | 0.2 | 0 | 5.2615 | 126.6333 | 2.9 | 6.8573 | 1.0635 | 0.11043
2016-09-16 15:00 | 72.32 | 70.52 | 1.8 | 11.7437 | 2.7985 | 62.0117 | 81.1833 | 8.8167 | 63.1938 | 62.4465 | 5.4324 | 52.89 | 0.2 | 0 | 3.616 | 61.9384 | 4.2 | 6.1356 | 1.066 | 0.054143
2016-09-16 16:00 | 49.34 | 47.9567 | 1.3833 | 14.1293 | 2.7825 | 77.0156 | 84.3815 | 5.6185 | 77.9542 | 76.7725 | 3.2331 | 35.9675 | 0.2 | 0 | 2.467 | 41.6676 | 2.8 | 4.1021 | 1.0731 | 0.036666
2016-09-16 17:00 | 26.36 | 25.3933 | 0.96667 | 0 | 2.7665 | 92.0195 | 87.7601 | 2.2399 | 92.5913 | 91.1221 | 0 | 19.045 | 0.2 | 0 | 1.318 | 20.363 | 2.8 | 3.4363 | 1.0755 | 0.017958
2016-09-16 18:00 | 3.38 | 2.83 | 0.55 | 0 | 2.7505 | 107.0234 | 91.0999 | -1.0999 | 107.2037 | 105.4082 | 0 | 2.1225 | 0.2 | 0 | 0.169 | 2.2915 | 3 | 3.0716 | 1.0767 | 0.0020232
2016-09-16 19:00 | 2.2533 | 1.8867 | 0.36667 | 0 | 2.7345 | 122.0274 | 94.1853 | -4.1853 | 121.8867 | 119.521 | 0 | 1.415 | 0.2 | 0 | 0.11267 | 1.5277 | 4.8 | 4.8477 | 1.0705 | 0.001341
2016-09-16 20:00 | 1.1267 | 0.94333 | 0.18333 | 0 | 2.7185 | 137.0313 | 96.8127 | -6.8127 | 136.7114 | 133.2552 | 0 | 0.7075 | 0.2 | 0 | 0.056333 | 0.76383 | 2.5 | 2.5239 | 1.0787 | 0.00067562
2016-09-16 21:00 | 0 | 0 | 0 | 0 | 2.7025 | 152.0352 | 98.8025 | -8.8025 | 151.7064 | 146.1084 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.8 | 4.8 | 1.0707 | 0
2016-09-16 22:00 | 0 | 0 | 0 | 0 | 2.6865 | 167.0391 | 100.0128 | -10.0128 | 166.8498 | 156.5496 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0714 | 0
2016-09-16 23:00 | 0 | 0 | 0 | 0 | 2.6705 | 182.043 | 100.3545 | -10.3545 | -177.9254 | 160.2596 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6 | 6 | 1.0665 | 0
2016-09-17 | 0 | 0 | 0 | 0 | 2.6545 | -162.9531 | 99.8029 | -9.8029 | -162.7117 | 154.1523 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.8 | 5.8 | 1.0672 | 0
2016-09-17 01:00 | 0.07 | 0.046667 | 0.023333 | 0 | 2.6385 | -147.9492 | 98.4006 | -8.4006 | -147.5979 | 142.7871 | 0 | 0.035 | 0.2 | 0 | 0.0035 | 0.0385 | 6.3 | 6.3012 | 1.0654 | 3.3636e-05
2016-09-17 02:00 | 0.14 | 0.093333 | 0.046667 | 0 | 2.6224 | -132.9452 | 96.2524 | -6.2524 | -132.6409 | 129.6139 | 0 | 0.07 | 0.2 | 0 | 0.007 | 0.077 | 6.7 | 6.7024 | 1.064 | 6.7184e-05
2016-09-17 03:00 | 0.21 | 0.14 | 0.07 | 0 | 2.6064 | -117.9413 | 93.512 | -3.512 | -117.8499 | 115.7496 | 0 | 0.105 | 0.2 | 0 | 0.0105 | 0.1155 | 6.6 | 6.6036 | 1.0644 | 0.00010081
2016-09-17 04:00 | 9.2967 | 6.8267 | 2.47 | 0 | 2.5904 | -102.9374 | 90.3671 | -0.36711 | -103.1849 | 101.5799 | 0 | 5.12 | 0.2 | 0 | 0.46483 | 5.5848 | 6.8 | 6.9745 | 1.0631 | 0.0048685
2016-09-17 05:00 | 18.3833 | 13.5133 | 4.87 | 0 | 2.5744 | -87.9335 | 87.026 | 2.974 | -88.5675 | 87.2739 | 0 | 10.135 | 0.2 | 0 | 0.91917 | 11.0542 | 7.6 | 7.9454 | 1.0597 | 0.0096055
2016-09-17 06:00 | 27.47 | 20.2 | 7.27 | 66.3191 | 2.5584 | -72.9296 | 83.7065 | 6.2935 | -73.9006 | 72.9314 | 19.4657 | 15.15 | 0.2 | 0 | 1.3735 | 35.9892 | 8.3 | 9.4247 | 1.0545 | 0.03112
2016-09-17 07:00 | 36.0733 | 30.6467 | 5.4267 | 33.3228 | 2.5424 | -57.9257 | 80.6275 | 9.3725 | -59.0905 | 58.6442 | 17.3395 | 22.985 | 0.2 | 0 | 1.8037 | 42.1282 | 8.1 | 9.4165 | 1.0545 | 0.036429
2016-09-17 08:00 | 44.6767 | 41.0933 | 3.5833 | 17.2337 | 2.5263 | -42.9218 | 77.9992 | 12.0008 | -44.0702 | 44.5537 | 12.2806 | 30.82 | 0.2 | 0 | 2.2338 | 45.3345 | 6.5 | 7.9167 | 1.0598 | 0.039397
2016-09-17 09:00 | 53.28 | 51.54 | 1.74 | 7.1975 | 2.5103 | -27.9179 | 76.01 | 13.99 | -28.8197 | 31.0041 | 6.1692 | 38.655 | 0.2 | 0 | 2.664 | 47.4882 | 6.5 | 7.984 | 1.0596 | 0.041259
2016-09-17 10:00 | 47.85 | 46.69 | 1.16 | 4.4274 | 2.4943 | -12.9139 | 74.811 | 15.189 | -13.377 | 19.2483 | 4.1799 | 35.0175 | 0.2 | 0 | 2.3925 | 41.5899 | 8.2 | 9.4997 | 1.0543 | 0.035954
2016-09-17 11:00 | 42.42 | 41.84 | 0.58 | 2.17 | 2.4783 | 2.09 | 74.4973 | 15.5027 | 2.1669 | 14.6333 | 2.0996 | 31.38 | 0.2 | 0 | 2.121 | 35.6006 | 7.9 | 9.0125 | 1.056 | 0.030826
2016-09-17 12:00 | 36.99 | 36.99 | 0 | 0 | 2.4622 | 17.0939 | 75.0954 | 14.9046 | 17.6915 | 22.1933 | 0 | 27.7425 | 0.2 | 0 | 1.8495 | 29.592 | 9 | 9.9247 | 1.0528 | 0.025546
2016-09-17 13:00 | 26.8533 | 26.8533 | 0 | 0 | 2.4462 | 32.0978 | 76.5584 | 13.4416 | 33.0816 | 34.7158 | 0 | 20.14 | 0.2 | 0 | 1.3427 | 21.4827 | 8.8 | 9.4713 | 1.0544 | 0.018573
2016-09-17 14:00 | 16.7167 | 16.7167 | 0 | 0 | 2.4302 | 47.1017 | 78.7739 | 11.2261 | 48.2607 | 48.4817 | 0 | 12.5375 | 0.2 | 0 | 0.83583 | 13.3733 | 7.5 | 7.9179 | 1.0598 | 0.011622
2016-09-17 15:00 | 6.58 | 6.58 | 0 | 0 | 2.4142 | 62.1056 | 81.5787 | 8.4213 | 63.2084 | 62.6532 | 0 | 4.935 | 0.2 | 0 | 0.329 | 5.264 | 6.7 | 6.8645 | 1.0635 | 0.0045905
2016-09-17 16:00 | 4.46 | 4.46 | 0 | 0 | 2.3981 | 77.1095 | 84.7771 | 5.2229 | 77.9608 | 76.9735 | 0 | 3.345 | 0.2 | 0 | 0.223 | 3.568 | 6.8 | 6.9115 | 1.0633 | 0.003111
2016-09-17 17:00 | 2.34 | 2.34 | 0 | 0 | 2.3821 | 92.1134 | 88.1557 | 1.8443 | 92.596 | 91.3244 | 0 | 1.755 | 0.2 | 0 | 0.117 | 1.872 | 6.7 | 6.7585 | 1.0638 | 0.001633
2016-09-17 18:00 | 0.22 | 0.22 | 0 | 0 | 2.366 | 107.1173 | 91.4956 | -1.4956 | 107.2124 | 105.6186 | 0 | 0.165 | 0.2 | 0 | 0.011 | 0.176 | 6.8 | 6.8055 | 1.0637 | 0.00015351
2016-09-17 19:00 | 0.14667 | 0.14667 | 0 | 0 | 2.35 | 122.1213 | 94.5806 | -4.5806 | 121.9052 | 119.7474 | 0 | 0.11 | 0.2 | 0 | 0.0073333 | 0.11733 | 7 | 7.0037 | 1.063 | 0.00010227
2016-09-17 20:00 | 0.073333 | 0.073333 | 0 | 0 | 2.334 | 137.1252 | 97.2071 | -7.2071 | 136.7448 | 133.5098 | 0 | 0.055 | 0.2 | 0 | 0.0036667 | 0.058667 | 6 | 6.0018 | 1.0665 | 5.1305e-05
2016-09-17 21:00 | 0 | 0 | 0 | 0 | 2.3179 | 152.1291 | 99.1949 | -9.1949 | 151.7592 | 146.4115 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.3 | 5.3 | 1.069 | 0
2016-09-17 22:00 | 0 | 0 | 0 | 0 | 2.3019 | 167.133 | 100.4017 | -10.4017 | 166.925 | 156.9238 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.2 | 5.2 | 1.0693 | 0
2016-09-17 23:00 | 0 | 0 | 0 | 0 | 2.2858 | 182.1369 | 100.7383 | -10.7383 | -177.8267 | 160.6323 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.1 | 5.1 | 1.0696 | 0
2016-09-18 | 0 | 0 | 0 | 0 | 2.2698 | -162.8592 | 100.1803 | -10.1803 | -162.5904 | 154.3847 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.4 | 5.4 | 1.0686 | 0
2016-09-18 01:00 | 0.046667 | 0.023333 | 0.023333 | 0 | 2.2538 | -147.8553 | 98.7711 | -8.7711 | -147.4566 | 142.9159 | 0 | 0.0175 | 0.2 | 0 | 0.0023333 | 0.019833 | 5.2 | 5.2006 | 1.0693 | 1.739e-05
2016-09-18 02:00 | 0.093333 | 0.046667 | 0.046667 | 0 | 2.2377 | -132.8514 | 96.6162 | -6.6162 | -132.4834 | 129.688 | 0 | 0.035 | 0.2 | 0 | 0.0046667 | 0.039667 | 5.6 | 5.6012 | 1.0679 | 3.4735e-05
2016-09-18 03:00 | 0.14 | 0.07 | 0.07 | 0 | 2.2217 | -117.8475 | 93.8703 | -3.8703 | -117.6808 | 115.7942 | 0 | 0.0525 | 0.2 | 0 | 0.007 | 0.0595 | 5.6 | 5.6019 | 1.0679 | 5.2103e-05
2016-09-18 04:00 | 6.1167 | 5.79 | 0.32667 | 0 | 2.2056 | -102.8436 | 90.7219 | -0.72188 | -103.0088 | 101.6087 | 0 | 4.3425 | 0.2 | 0 | 0.30583 | 4.6483 | 5.6 | 5.7453 | 1.0674 | 0.0040685
2016-09-18 05:00 | 12.0933 | 11.51 | 0.58333 | 0 | 2.1896 | -87.8396 | 87.3797 | 2.6203 | -88.3891 | 87.2959 | 0 | 8.6325 | 0.2 | 0 | 0.60467 | 9.2372 | 6 | 6.2887 | 1.0655 | 0.0080705
2016-09-18 06:00 | 18.07 | 17.23 | 0.84 | 8.1195 | 2.1735 | -72.8357 | 84.0619 | 5.9381 | -73.7246 | 72.9545 | 2.3801 | 12.9225 | 0.2 | 0 | 0.9035 | 16.2061 | 6.3 | 6.8064 | 1.0637 | 0.014135
2016-09-18 07:00 | 29.1133 | 28.1267 | 0.98667 | 6.2982 | 2.1575 | -57.8318 | 80.987 | 9.013 | -58.9218 | 58.6773 | 3.2742 | 21.095 | 0.2 | 0 | 1.4557 | 25.8248 | 6.7 | 7.507 | 1.0612 | 0.022473
2016-09-18 08:00 | 40.1567 | 39.0233 | 1.1333 | 5.6194 | 2.1414 | -42.8279 | 78.3646 | 11.6354 | -43.9139 | 44.611 | 4.0004 | 29.2675 | 0.2 | 0 | 2.0078 | 35.2757 | 7.2 | 8.3024 | 1.0584 | 0.030617
2016-09-18 09:00 | 51.2 | 49.92 | 1.28 | 5.4367 | 2.1253 | -27.824 | 76.3826 | 13.6174 | -28.6807 | 31.1149 | 4.6545 | 37.44 | 0.2 | 0 | 2.56 | 44.6545 | 7.5 | 8.8955 | 1.0564 | 0.038681
2016-09-18 10:00 | 52.6967 | 50.9033 | 1.7933 | 7.016 | 2.1093 | -12.8201 | 75.1906 | 14.8094 | -13.2594 | 19.4831 | 6.6143 | 38.1775 | 0.2 | 0 | 2.6348 | 47.4266 | 7.4 | 8.8821 | 1.0564 | 0.041084
2016-09-18 11:00 | 54.1933 | 51.8867 | 2.3067 | 8.845 | 2.0932 | 2.1838 | 74.8831 | 15.1169 | 2.2606 | 15.0276 | 8.5425 | 38.915 | 0.2 | 0 | 2.7097 | 50.1671 | 7.6 | 9.1677 | 1.0554 | 0.043417
2016-09-18 12:00 | 55.69 | 52.87 | 2.82 | 11.2522 | 2.0772 | 17.1877 | 75.486 | 14.514 | 17.7608 | 22.5214 | 10.3941 | 39.6525 | 0.2 | 0 | 2.7845 | 52.8311 | 7.7 | 9.351 | 1.0548 | 0.045694
2016-09-18 13:00 | 61.9467 | 46.5133 | 15.4333 | 68.3603 | 2.0611 | 32.1916 | 76.9522 | 13.0478 | 33.1285 | 34.9744 | 56.015 | 34.885 | 0.2 | 0 | 3.0973 | 93.9973 | 7.9 | 10.8374 | 1.0496 | 0.080898
2016-09-18 14:00 | 68.2033 | 40.1567 | 28.0467 | 149.2579 | 2.045 | 47.1955 | 79.1693 | 10.8307 | 48.2887 | 48.706 | 98.4987 | 30.1175 | 0.2 | 0 | 3.4102 | 132.0263 | 8 | 12.1258 | 1.0451 | 0.11314
2016-09-18 15:00 | 74.46 | 33.8 | 40.66 | 291.245 | 2.029 | 62.1994 | 81.9749 | 8.0251 | 63.2227 | 62.8612 | 132.8507 | 25.35 | 0.2 | 0 | 3.723 | 161.9237 | 8.1 | 13.1601 | 1.0414 | 0.13828
2016-09-18 16:00 | 50.29 | 22.9933 | 27.2967 | 324.4215 | 2.0129 | 77.2033 | 85.1735 | 4.8265 | 77.9673 | 77.1752 | 72.012 | 17.245 | 0.2 | 0 | 2.5145 | 91.7715 | 7.7 | 10.5679 | 1.0505 | 0.079054
2016-09-18 17:00 | 26.12 | 12.1867 | 13.9333 | 0 | 1.9969 | 92.2072 | 88.5522 | 1.4478 | 92.6005 | 91.527 | 0 | 9.14 | 0.2 | 0 | 1.306 | 10.446 | 7.1 | 7.4264 | 1.0615 | 0.0090926
2016-09-18 18:00 | 1.95 | 1.38 | 0.57 | 0 | 1.9808 | 107.2111 | 91.892 | -1.892 | 107.2208 | 105.8285 | 0 | 1.035 | 0.2 | 0 | 0.0975 | 1.1325 | 6.1 | 6.1354 | 1.066 | 0.00098997
2016-09-18 19:00 | 1.3 | 0.92 | 0.38 | 0 | 1.9647 | 122.2151 | 94.9768 | -4.9768 | 121.9234 | 119.9729 | 0 | 0.69 | 0.2 | 0 | 0.065 | 0.755 | 5.1 | 5.1236 | 1.0696 | 0.00066217
2016-09-18 20:00 | 0.65 | 0.46 | 0.19 | 0 | 1.9486 | 137.219 | 97.6023 | -7.6023 | 136.7781 | 133.7633 | 0 | 0.345 | 0.2 | 0 | 0.0325 | 0.3775 | 5 | 5.0118 | 1.07 | 0.00033121
2016-09-18 21:00 | 0 | 0 | 0 | 0 | 1.9326 | 152.2229 | 99.588 | -9.588 | 151.8119 | 146.7133 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.6 | 5.6 | 1.0679 | 0
2016-09-18 22:00 | 0 | 0 | 0 | 0 | 1.9165 | 167.2268 | 100.7913 | -10.7913 | 167.0002 | 157.2978 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.2 | 5.2 | 1.0693 | 0
2016-09-18 23:00 | 0 | 0 | 0 | 0 | 1.9004 | 182.2307 | 101.1229 | -11.1229 | -177.7279 | 161.005 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.9 | 4.9 | 1.0703 | 0
2016-09-19 | 0 | 0 | 0 | 0 | 1.8844 | -162.7654 | 100.5586 | -10.5586 | -162.4688 | 154.6139 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.8 | 4.8 | 1.0707 | 0
2016-09-19 01:00 | 0.023333 | 0.023333 | 0 | 0 | 1.8683 | -147.7615 | 99.1423 | -9.1423 | -147.3149 | 143.042 | 0 | 0.0175 | 0.2 | 0 | 0.0011667 | 0.018667 | 4.7 | 4.7006 | 1.071 | 1.6394e-05
2016-09-19 02:00 | 0.046667 | 0.046667 | 0 | 0 | 1.8522 | -132.7576 | 96.9807 | -6.9807 | -132.3257 | 129.7604 | 0 | 0.035 | 0.2 | 0 | 0.0023333 | 0.037333 | 4.3 | 4.3012 | 1.0724 | 3.2831e-05
2016-09-19 03:00 | 0.07 | 0.07 | 0 | 0 | 1.8361 | -117.7537 | 94.2293 | -4.2293 | -117.5115 | 115.8378 | 0 | 0.0525 | 0.2 | 0 | 0.0035 | 0.056 | 4.5 | 4.5018 | 1.0717 | 4.9214e-05
2016-09-19 04:00 | 16.05 | 7.89 | 8.16 | 0 | 1.82 | -102.7498 | 91.0774 | -1.0774 | -102.8325 | 101.6372 | 0 | 5.9175 | 0.2 | 0 | 0.8025 | 6.72 | 4.3 | 4.51 | 1.0717 | 0.0059056
2016-09-19 05:00 | 32.03 | 15.71 | 16.32 | 0 | 1.804 | -87.7459 | 87.7343 | 2.2657 | -88.2107 | 87.3183 | 0 | 11.7825 | 0.2 | 0 | 1.6015 | 13.384 | 4.3 | 4.7182 | 1.071 | 0.011754
2016-09-19 06:00 | 48.01 | 23.53 | 24.48 | 251.6747 | 1.7879 | -72.742 | 84.4181 | 5.5819 | -73.5488 | 72.9786 | 73.6722 | 17.6475 | 0.2 | 0 | 2.4005 | 93.7202 | 4.1 | 7.0288 | 1.0629 | 0.081684
2016-09-19 07:00 | 42.37 | 26.05 | 16.32 | 108.479 | 1.7718 | -57.7381 | 81.3474 | 8.6526 | -58.7535 | 58.7123 | 56.3369 | 19.5375 | 0.2 | 0 | 2.1185 | 77.9929 | 3.7 | 6.1373 | 1.066 | 0.068176
2016-09-19 08:00 | 36.73 | 28.57 | 8.16 | 41.757 | 1.7557 | -42.7342 | 78.731 | 11.269 | -43.758 | 44.6714 | 29.6955 | 21.4275 | 0.2 | 0 | 1.8365 | 52.9595 | 3.9 | 5.555 | 1.0681 | 0.046382
2016-09-19 09:00 | 31.09 | 31.09 | 0 | 0 | 1.7396 | -27.7303 | 76.7559 | 13.2441 | -28.5421 | 31.2303 | 0 | 23.3175 | 0.2 | 0 | 1.5545 | 24.872 | 3.9 | 4.6772 | 1.0711 | 0.021846
2016-09-19 10:00 | 30.8033 | 30.8033 | 0 | 0 | 1.7235 | -12.7264 | 75.571 | 14.429 | -13.1422 | 19.7236 | 0 | 23.1025 | 0.2 | 0 | 1.5402 | 24.6427 | 3.9 | 4.6701 | 1.0712 | 0.021645
2016-09-19 11:00 | 30.5167 | 30.5167 | 0 | 0 | 1.7074 | 2.2775 | 75.2698 | 14.7302 | 2.3539 | 15.4228 | 0 | 22.8875 | 0.2 | 0 | 1.5258 | 24.4133 | 3.9 | 4.6629 | 1.0712 | 0.021444
2016-09-19 12:00 | 30.23 | 30.23 | 0 | 0 | 1.6914 | 17.2814 | 75.8773 | 14.1227 | 17.8297 | 22.8518 | 0 | 22.6725 | 0.2 | 0 | 1.5115 | 24.184 | 3.9 | 4.6557 | 1.0712 | 0.021243
2016-09-19 13:00 | 25.5967 | 25.5967 | 0 | 0 | 1.6753 | 32.2853 | 77.3466 | 12.6534 | 33.1749 | 35.2354 | 0 | 19.1975 | 0.2 | 0 | 1.2798 | 20.4773 | 4.1 | 4.7399 | 1.0709 | 0.017982
2016-09-19 14:00 | 20.9633 | 20.9633 | 0 | 0 | 1.6592 | 47.2892 | 79.5654 | 10.4346 | 48.3164 | 48.9321 | 0 | 15.7225 | 0.2 | 0 | 1.0482 | 16.7707 | 3.8 | 4.3241 | 1.0724 | 0.014747
2016-09-19 15:00 | 16.33 | 16.33 | 0 | 0 | 1.6431 | 62.2931 | 82.3717 | 7.6283 | 63.2368 | 63.0703 | 0 | 12.2475 | 0.2 | 0 | 0.8165 | 13.064 | 3.8 | 4.2082 | 1.0728 | 0.011492
2016-09-19 16:00 | 11.2067 | 11.12 | 0.086667 | 1.1222 | 1.627 | 77.297 | 85.5705 | 4.4295 | 77.9734 | 77.3774 | 0.24522 | 8.34 | 0.2 | 0 | 0.56033 | 9.1456 | 3.7 | 3.9858 | 1.0735 | 0.0080509
2016-09-19 17:00 | 6.0833 | 5.91 | 0.17333 | 0 | 1.6109 | 92.3009 | 88.9493 | 1.0507 | 92.6047 | 91.7295 | 0 | 4.4325 | 0.2 | 0 | 0.30417 | 4.7367 | 3.6 | 3.748 | 1.0744 | 0.004173
2016-09-19 18:00 | 0.96 | 0.7 | 0.26 | 0 | 1.5948 | 107.3048 | 92.2891 | -2.2891 | 107.229 | 106.038 | 0 | 0.525 | 0.2 | 0 | 0.048 | 0.573 | 3.6 | 3.6179 | 1.0748 | 0.00050502
2016-09-19 19:00 | 0.64 | 0.46667 | 0.17333 | 0 | 1.5787 | 122.3087 | 95.3735 | -5.3735 | 121.9414 | 120.1975 | 0 | 0.35 | 0.2 | 0 | 0.032 | 0.382 | 3.3 | 3.3119 | 1.0759 | 0.00033702
2016-09-19 20:00 | 0.32 | 0.23333 | 0.086667 | 0 | 1.5626 | 137.3125 | 97.9982 | -7.9982 | 136.8112 | 134.0153 | 0 | 0.175 | 0.2 | 0 | 0.016 | 0.191 | 3.1 | 3.106 | 1.0766 | 0.00016862
2016-09-19 21:00 | 0 | 0 | 0 | 0 | 1.5465 | 152.3164 | 99.9819 | -9.9819 | 151.8646 | 147.0136 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-09-19 22:00 | 0 | 0 | 0 | 0 | 1.5304 | 167.3203 | 101.1816 | -11.1816 | 167.0755 | 157.6717 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-09-19 23:00 | 0 | 0 | 0 | 0 | 1.5143 | 182.3242 | 101.5082 | -11.5082 | -177.6289 | 161.3774 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0833 | 0
2016-09-20 | 0 | 0 | 0 | 0 | 1.4982 | -162.6719 | 100.9374 | -10.9374 | -162.3471 | 154.8399 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0819 | 0
2016-09-20 01:00 | 0 | 0 | 0 | 0 | 1.4821 | -147.668 | 99.5142 | -9.5142 | -147.1731 | 143.1652 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-09-20 02:00 | 0 | 0 | 0 | 0 | 1.466 | -132.6641 | 97.3459 | -7.3459 | -132.1678 | 129.8309 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0784 | 0
2016-09-20 03:00 | 0 | 0 | 0 | 0 | 1.4499 | -117.6602 | 94.589 | -4.589 | -117.3421 | 115.8805 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-09-20 04:00 | 8.0733 | 7.2867 | 0.78667 | 0 | 1.4338 | -102.6563 | 91.4336 | -1.4336 | -102.6563 | 101.6656 | 0 | 5.465 | 0.2 | 0 | 0.40367 | 5.8687 | 2.4 | 2.5834 | 1.0785 | 0.0051899
2016-09-20 05:00 | 16.1467 | 14.5733 | 1.5733 | 0 | 1.4177 | -87.6524 | 88.0895 | 1.9105 | -88.0324 | 87.3413 | 0 | 10.93 | 0.2 | 0 | 0.80733 | 11.7373 | 2.5 | 2.8668 | 1.0775 | 0.01037
2016-09-20 06:00 | 24.22 | 21.86 | 2.36 | 25.9153 | 1.4016 | -72.6485 | 84.7751 | 5.2249 | -73.3733 | 73.0041 | 7.5751 | 16.395 | 0.2 | 0 | 1.211 | 25.1811 | 3.6 | 4.3869 | 1.0721 | 0.022138
2016-09-20 07:00 | 43.5833 | 41.18 | 2.4033 | 16.6655 | 1.3855 | -57.6447 | 81.7084 | 8.2916 | -58.5855 | 58.7495 | 8.6457 | 30.885 | 0.2 | 0 | 2.1792 | 41.7099 | 3 | 4.3034 | 1.0724 | 0.03668
2016-09-20 08:00 | 62.9467 | 60.5 | 2.4467 | 12.9365 | 1.3693 | -42.6408 | 79.0981 | 10.9019 | -43.6026 | 44.735 | 9.1897 | 45.375 | 0.2 | 0 | 3.1473 | 57.712 | 2.4 | 4.2035 | 1.0728 | 0.050768
2016-09-20 09:00 | 82.31 | 79.82 | 2.49 | 11.179 | 1.3532 | -27.6369 | 77.13 | 12.87 | -28.4041 | 31.3504 | 9.5469 | 59.865 | 0.2 | 0 | 4.1155 | 73.5274 | 2.8 | 5.0977 | 1.0697 | 0.064492
2016-09-20 10:00 | 103.55 | 88.9033 | 14.6467 | 60.3408 | 1.3371 | -12.633 | 75.9521 | 14.0479 | -13.0256 | 19.9695 | 56.7128 | 66.6775 | 0.2 | 0 | 5.1775 | 128.5678 | 2.7 | 6.7177 | 1.064 | 0.11217
2016-09-20 11:00 | 124.79 | 97.9867 | 26.8033 | 108.1979 | 1.321 | 2.3709 | 75.6571 | 14.3429 | 2.4466 | 15.8186 | 104.1004 | 73.49 | 0.2 | 0 | 6.2395 | 183.8299 | 2.8 | 8.5447 | 1.0576 | 0.15942
2016-09-20 12:00 | 146.03 | 107.07 | 38.96 | 164.1401 | 1.3049 | 17.3748 | 76.2693 | 13.7307 | 17.8981 | 23.1846 | 150.8843 | 80.3025 | 0.2 | 0 | 7.3015 | 238.4883 | 3.3 | 10.7528 | 1.0499 | 0.20531
2016-09-20 13:00 | 115.0867 | 86.5433 | 28.5433 | 134.4354 | 1.2888 | 32.3787 | 77.7417 | 12.2583 | 33.2209 | 35.4987 | 109.4477 | 64.9075 | 0.2 | 0 | 5.7543 | 180.1095 | 3.6 | 9.2284 | 1.0552 | 0.15584
2016-09-20 14:00 | 84.1433 | 66.0167 | 18.1267 | 103.9977 | 1.2727 | 47.3825 | 79.9621 | 10.0379 | 48.3438 | 49.1599 | 68.0094 | 49.5125 | 0.2 | 0 | 4.2072 | 121.729 | 4.1 | 7.904 | 1.0598 | 0.10579
2016-09-20 15:00 | 53.2 | 45.49 | 7.71 | 61.2547 | 1.2565 | 62.3864 | 82.7691 | 7.2309 | 63.2505 | 63.2804 | 27.5416 | 34.1175 | 0.2 | 0 | 2.66 | 64.3191 | 5.3 | 7.31 | 1.0619 | 0.056007
2016-09-20 16:00 | 35.7733 | 30.58 | 5.1933 | 73.8622 | 1.2404 | 77.3903 | 85.9681 | 4.0319 | 77.9791 | 77.5801 | 15.8859 | 22.935 | 0.2 | 0 | 1.7887 | 40.6096 | 5 | 6.269 | 1.0656 | 0.035483
2016-09-20 17:00 | 18.3467 | 15.67 | 2.6767 | 0 | 1.2243 | 92.3942 | 89.347 | 0.65304 | 92.6085 | 91.9319 | 0 | 11.7525 | 0.2 | 0 | 0.91733 | 12.6698 | 5.5 | 5.8959 | 1.0669 | 0.011084
2016-09-20 18:00 | 0.92 | 0.76 | 0.16 | 0 | 1.2082 | 107.3981 | 92.6867 | -2.6867 | 107.2368 | 106.2469 | 0 | 0.57 | 0.2 | 0 | 0.046 | 0.616 | 4.7 | 4.7193 | 1.071 | 0.00054097
2016-09-20 19:00 | 0.61333 | 0.50667 | 0.10667 | 0 | 1.1921 | 122.4019 | 95.7709 | -5.7709 | 121.959 | 120.421 | 0 | 0.38 | 0.2 | 0 | 0.030667 | 0.41067 | 5.5 | 5.5128 | 1.0682 | 0.00035971
2016-09-20 20:00 | 0.30667 | 0.25333 | 0.053333 | 0 | 1.1759 | 137.4058 | 98.3946 | -8.3946 | 136.844 | 134.2657 | 0 | 0.19 | 0.2 | 0 | 0.015333 | 0.20533 | 6 | 6.0064 | 1.0665 | 0.00017957
2016-09-20 21:00 | 0 | 0 | 0 | 0 | 1.1598 | 152.4097 | 100.3763 | -10.3763 | 151.917 | 147.3122 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.5 | 5.5 | 1.0682 | 0
2016-09-20 22:00 | 0 | 0 | 0 | 0 | 1.1437 | 167.4136 | 101.5726 | -11.5726 | 167.1506 | 158.0451 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.5 | 5.5 | 1.0682 | 0
2016-09-20 23:00 | 0 | 0 | 0 | 0 | 1.1276 | 182.4175 | 101.894 | -11.894 | -177.5299 | 161.7494 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.6 | 5.6 | 1.0679 | 0
2016-09-21 | 0 | 0 | 0 | 0 | 1.1114 | -162.5787 | 101.3169 | -11.3169 | -162.2253 | 155.0625 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6 | 6 | 1.0665 | 0
2016-09-21 01:00 | 0 | 0 | 0 | 0 | 1.0953 | -147.5748 | 99.8867 | -9.8867 | -147.0312 | 143.2857 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6.2 | 6.2 | 1.0658 | 0
2016-09-21 02:00 | 0 | 0 | 0 | 0 | 1.0792 | -132.5709 | 97.7116 | -7.7116 | -132.0098 | 129.8998 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6.9 | 6.9 | 1.0634 | 0
2016-09-21 03:00 | 0 | 0 | 0 | 0 | 1.0631 | -117.567 | 94.9493 | -4.9493 | -117.1727 | 115.9224 | 0 | 0 | 0.2 | 0 | 0 | 0 | 7.4 | 7.4 | 1.0616 | 0
2016-09-21 04:00 | 3.5167 | 3.49 | 0.026667 | 0 | 1.0469 | -102.5632 | 91.7905 | -1.7905 | -102.4802 | 101.6938 | 0 | 2.6175 | 0.2 | 0 | 0.17583 | 2.7933 | 5.9 | 5.9873 | 1.0665 | 0.002443
2016-09-21 05:00 | 7.0333 | 6.98 | 0.053333 | 0 | 1.0308 | -87.5593 | 88.4454 | 1.5546 | -87.8544 | 87.3649 | 0 | 5.235 | 0.2 | 0 | 0.35167 | 5.5867 | 6 | 6.1746 | 1.0659 | 0.0048829
2016-09-21 06:00 | 10.55 | 10.47 | 0.08 | 0.94286 | 1.0147 | -72.5554 | 85.1327 | 4.8673 | -73.1981 | 73.0308 | 0.27518 | 7.8525 | 0.2 | 0 | 0.5275 | 8.6552 | 6.8 | 7.0705 | 1.0628 | 0.0075426
2016-09-21 07:00 | 15.7033 | 15.65 | 0.053333 | 0.38659 | 0.99854 | -57.5516 | 82.0702 | 7.9298 | -58.4181 | 58.7887 | 0.20033 | 11.7375 | 0.2 | 0 | 0.78517 | 12.723 | 5.2 | 5.5976 | 1.0679 | 0.011141
2016-09-21 08:00 | 20.8567 | 20.83 | 0.026667 | 0.14586 | 0.98241 | -42.5477 | 79.4658 | 10.5342 | -43.4479 | 44.8018 | 0.1035 | 15.6225 | 0.2 | 0 | 1.0428 | 16.7688 | 4.3 | 4.824 | 1.0706 | 0.014721
2016-09-21 09:00 | 26.01 | 26.01 | 0 | 0 | 0.96627 | -27.5438 | 77.5048 | 12.4952 | -28.2668 | 31.4752 | 0 | 19.5075 | 0.2 | 0 | 1.3005 | 20.808 | 4.7 | 5.3502 | 1.0688 | 0.018236
2016-09-21 10:00 | 31.75 | 31.25 | 0.5 | 2.1163 | 0.95014 | -12.5399 | 76.3339 | 13.6661 | -12.9097 | 20.2207 | 1.9859 | 23.4375 | 0.2 | 0 | 1.5875 | 27.0109 | 5.2 | 6.0441 | 1.0663 | 0.023618
2016-09-21 11:00 | 37.49 | 36.49 | 1 | 4.1466 | 0.934 | 2.4639 | 76.045 | 13.955 | 2.5386 | 16.2151 | 3.9817 | 27.3675 | 0.2 | 0 | 1.8745 | 33.2237 | 4.7 | 5.7382 | 1.0674 | 0.02908
2016-09-21 12:00 | 43.23 | 41.73 | 1.5 | 6.502 | 0.91787 | 17.4678 | 76.6619 | 13.3381 | 17.9659 | 23.5194 | 5.9619 | 31.2975 | 0.2 | 0 | 2.1615 | 39.4209 | 4.7 | 5.9319 | 1.0667 | 0.034482
2016-09-21 13:00 | 35.83 | 34.6667 | 1.1633 | 5.6591 | 0.90173 | 32.4717 | 78.1372 | 11.8628 | 33.2663 | 35.7642 | 4.592 | 26 | 0.2 | 0 | 1.7915 | 32.3835 | 5 | 6.012 | 1.0665 | 0.028319
2016-09-21 14:00 | 28.43 | 27.6033 | 0.82667 | 4.9363 | 0.88559 | 47.4755 | 80.3594 | 9.6406 | 48.3705 | 49.3891 | 3.2131 | 20.7025 | 0.2 | 0 | 1.4215 | 25.3371 | 5.4 | 6.1918 | 1.0658 | 0.022144
2016-09-21 15:00 | 21.03 | 20.54 | 0.49 | 4.1185 | 0.86945 | 62.4794 | 83.167 | 6.833 | 63.2636 | 63.4913 | 1.8382 | 15.405 | 0.2 | 0 | 1.0515 | 18.2947 | 5.2 | 5.7717 | 1.0673 | 0.016011
2016-09-21 16:00 | 14.1233 | 13.7967 | 0.32667 | 5.1542 | 0.85331 | 77.4833 | 86.3662 | 3.6338 | 77.9844 | 77.783 | 1.0907 | 10.3475 | 0.2 | 0 | 0.70617 | 12.1444 | 5 | 5.3795 | 1.0687 | 0.010642
2016-09-21 17:00 | 7.2167 | 7.0533 | 0.16333 | 0 | 0.83717 | 92.4871 | 89.7451 | 0.25493 | 92.6117 | 92.1341 | 0 | 5.29 | 0.2 | 0 | 0.36083 | 5.6508 | 4.6 | 4.7766 | 1.0708 | 0.0049617
2016-09-21 18:00 | 0.31 | 0.31 | 0 | 0 | 0.82103 | 107.491 | 93.0848 | -3.0848 | 107.2441 | 106.455 | 0 | 0.2325 | 0.2 | 0 | 0.0155 | 0.248 | 4.3 | 4.3078 | 1.0724 | 0.00021809
2016-09-21 19:00 | 0.20667 | 0.20667 | 0 | 0 | 0.80489 | 122.4948 | 96.1687 | -6.1687 | 121.9762 | 120.6432 | 0 | 0.155 | 0.2 | 0 | 0.010333 | 0.16533 | 4.5 | 4.5052 | 1.0717 | 0.0001453
2016-09-21 20:00 | 0.10333 | 0.10333 | 0 | 0 | 0.78875 | 137.4987 | 98.7915 | -8.7915 | 136.8764 | 134.5144 | 0 | 0.0775 | 0.2 | 0 | 0.0051667 | 0.082667 | 3.8 | 3.8026 | 1.0742 | 7.2816e-05
2016-09-21 21:00 | 0 | 0 | 0 | 0 | 0.7726 | 152.5026 | 100.7711 | -10.7711 | 151.9692 | 147.6089 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0738 | 0
2016-09-21 22:00 | 0 | 0 | 0 | 0 | 0.75646 | 167.5064 | 101.964 | -11.964 | 167.2255 | 158.4179 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-09-21 23:00 | 0 | 0 | 0 | 0 | 0.74031 | 182.5103 | 102.2803 | -12.2803 | -177.4311 | 162.1209 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0763 | 0
2016-09-22 | 0 | 0 | 0 | 0 | 0.72417 | -162.4859 | 101.6968 | -11.6968 | -162.1035 | 155.2816 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-09-22 01:00 | 0 | 0 | 0 | 0 | 0.70802 | -147.482 | 100.2596 | -10.2596 | -146.8894 | 143.4035 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-09-22 02:00 | 0 | 0 | 0 | 0 | 0.69187 | -132.4782 | 98.0779 | -8.0779 | -131.8519 | 129.9669 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0774 | 0
2016-09-22 03:00 | 0 | 0 | 0 | 0 | 0.67573 | -117.4743 | 95.3101 | -5.3101 | -117.0034 | 115.9635 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.078 | 0
2016-09-22 04:00 | 8.83 | 8.13 | 0.7 | 0 | 0.65958 | -102.4705 | 92.1479 | -2.1479 | -102.3044 | 101.7221 | 0 | 6.0975 | 0.2 | 0 | 0.4415 | 6.539 | 2.8 | 3.0043 | 1.077 | 0.0057748
2016-09-22 05:00 | 17.66 | 16.26 | 1.4 | 0 | 0.64343 | -87.4666 | 88.802 | 1.198 | -87.6768 | 87.3892 | 0 | 12.195 | 0.2 | 0 | 0.883 | 13.078 | 2.4 | 2.8087 | 1.0777 | 0.011557
2016-09-22 06:00 | 26.49 | 24.39 | 2.1 | 26.7121 | 0.62728 | -72.4628 | 85.491 | 4.509 | -73.0234 | 73.0589 | 7.7836 | 18.2925 | 0.2 | 0 | 1.3245 | 27.4006 | 3.3 | 4.1563 | 1.073 | 0.024108
2016-09-22 07:00 | 67.5667 | 34.7767 | 32.79 | 248.9912 | 0.61113 | -57.4589 | 82.4327 | 7.5673 | -58.2513 | 58.8303 | 128.8717 | 26.0825 | 0.2 | 0 | 3.3783 | 158.3325 | 3.5 | 8.4479 | 1.0579 | 0.13735
2016-09-22 08:00 | 108.6433 | 45.1633 | 63.48 | 359.6675 | 0.59498 | -42.4551 | 79.8343 | 10.1657 | -43.2939 | 44.8719 | 254.8914 | 33.8725 | 0.2 | 0 | 5.4322 | 294.196 | 5.3 | 14.4936 | 1.0368 | 0.25011
2016-09-22 09:00 | 149.72 | 55.55 | 94.17 | 448.52 | 0.57882 | -27.4512 | 77.8802 | 12.1198 | -28.1303 | 31.6047 | 381.9973 | 41.6625 | 0.2 | 0 | 7.486 | 431.1458 | 4.9 | 18.3733 | 1.0232 | 0.36174
2016-09-22 10:00 | 154.99 | 55.0367 | 99.9533 | 435.0078 | 0.56267 | -12.4474 | 76.7163 | 13.2837 | -12.7946 | 20.477 | 407.5209 | 41.2775 | 0.2 | 0 | 7.7495 | 456.5479 | 3.9 | 18.1671 | 1.0239 | 0.38332
2016-09-22 11:00 | 160.26 | 54.5233 | 105.7367 | 450.7568 | 0.54652 | 2.5565 | 76.4334 | 13.5666 | 2.6298 | 16.612 | 431.9435 | 40.8925 | 0.2 | 0 | 8.013 | 480.849 | 3.8 | 18.8265 | 1.0216 | 0.40282
2016-09-22 12:00 | 165.53 | 54.01 | 111.52 | 497.8183 | 0.53036 | 17.5603 | 77.0549 | 12.9451 | 18.033 | 23.856 | 455.2871 | 40.5075 | 0.2 | 0 | 8.2765 | 504.0711 | 3.6 | 19.3522 | 1.0198 | 0.42151
2016-09-22 13:00 | 130.3067 | 46.8367 | 83.47 | 419.8699 | 0.51421 | 32.5642 | 78.5332 | 11.4668 | 33.311 | 36.0316 | 339.5458 | 35.1275 | 0.2 | 0 | 6.5153 | 381.1886 | 3.6 | 15.5121 | 1.0332 | 0.32295
2016-09-22 14:00 | 95.0833 | 39.6633 | 55.42 | 345.0314 | 0.49805 | 47.568 | 80.7569 | 9.2431 | 48.3967 | 49.6196 | 223.5319 | 29.7475 | 0.2 | 0 | 4.7542 | 258.0336 | 3.3 | 11.3635 | 1.0477 | 0.22169
2016-09-22 15:00 | 59.86 | 32.49 | 27.37 | 244.2184 | 0.4819 | 62.5719 | 83.5652 | 6.4348 | 63.2762 | 63.7029 | 108.1949 | 24.3675 | 0.2 | 0 | 2.993 | 135.5554 | 3.2 | 7.4361 | 1.0615 | 0.11799
2016-09-22 16:00 | 40.0067 | 21.75 | 18.2567 | 323.4838 | 0.46574 | 77.5757 | 86.7646 | 3.2354 | 77.989 | 77.986 | 67.3332 | 16.3125 | 0.2 | 0 | 2.0003 | 85.6461 | 2.6 | 5.2764 | 1.069 | 0.075078
2016-09-22 17:00 | 20.1533 | 11.01 | 9.1433 | 0 | 0.44958 | 92.5795 | 90.1435 | -0.14352 | 92.6145 | 92.3358 | 0 | 8.2575 | 0.2 | 0 | 1.0077 | 9.2652 | 1.4 | 1.6895 | 1.0816 | 0.0082173
2016-09-22 18:00 | 0.3 | 0.27 | 0.03 | 0 | 0.43342 | 107.5834 | 93.4832 | -3.4832 | 107.2509 | 106.6622 | 0 | 0.2025 | 0.2 | 0 | 0.015 | 0.2175 | 1 | 1.0068 | 1.084 | 0.00019333
2016-09-22 19:00 | 0.2 | 0.18 | 0.02 | 0 | 0.41726 | 122.5872 | 96.5668 | -6.5668 | 121.9928 | 120.864 | 0 | 0.135 | 0.2 | 0 | 0.01 | 0.145 | 1 | 1.0045 | 1.084 | 0.00012889
2016-09-22 20:00 | 0.1 | 0.09 | 0.01 | 0 | 0.40111 | 137.5911 | 99.1887 | -9.1887 | 136.9083 | 134.7612 | 0 | 0.0675 | 0.2 | 0 | 0.005 | 0.0725 | 0.5 | 0.50227 | 1.0857 | 6.4547e-05
2016-09-22 21:00 | 0 | 0 | 0 | 0 | 0.38495 | 152.5949 | 101.1664 | -11.1664 | 152.0209 | 147.9035 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0861 | 0
2016-09-22 22:00 | 0 | 0 | 0 | 0 | 0.36878 | 167.5987 | 102.3557 | -12.3557 | 167.3001 | 158.7899 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-09-22 23:00 | 0 | 0 | 0 | 0 | 0.35262 | 182.6026 | 102.667 | -12.667 | -177.3325 | 162.4918 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-09-23 | 0 | 0 | 0 | 0 | 0.33646 | -162.3936 | 102.0772 | -12.0772 | -161.9819 | 155.4972 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-09-23 01:00 | 0 | 0 | 0 | 0 | 0.3203 | -147.3898 | 100.633 | -10.633 | -146.7476 | 143.5185 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-09-23 02:00 | 0 | 0 | 0 | 0 | 0.30414 | -132.3859 | 98.4446 | -8.4446 | -131.6942 | 130.0325 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.083 | 0
2016-09-23 03:00 | 0 | 0 | 0 | 0 | 0.28797 | -117.3821 | 95.6714 | -5.6714 | -116.8343 | 116.0039 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0826 | 0
2016-09-23 04:00 | 2.79 | 2.7267 | 0.063333 | 0 | 0.27181 | -102.3783 | 92.5058 | -2.5058 | -102.1289 | 101.7504 | 0 | 2.045 | 0.2 | 0 | 0.1395 | 2.1845 | 1.9 | 1.9683 | 1.0806 | 0.0019357
2016-09-23 05:00 | 5.58 | 5.4533 | 0.12667 | 0 | 0.25564 | -87.3745 | 89.159 | 0.84098 | -87.4996 | 87.4142 | 0 | 4.09 | 0.2 | 0 | 0.279 | 4.369 | 1.6 | 1.7365 | 1.0814 | 0.0038743
2016-09-23 06:00 | 8.37 | 8.18 | 0.19 | 2.6253 | 0.23948 | -72.3706 | 85.8498 | 4.1502 | -72.8494 | 73.0885 | 0.7637 | 6.135 | 0.2 | 0 | 0.4185 | 7.3172 | 2.2 | 2.4287 | 1.079 | 0.0064741
2016-09-23 07:00 | 15.2433 | 15.1133 | 0.13 | 1.0366 | 0.22331 | -57.3668 | 82.7956 | 7.2044 | -58.0852 | 58.8741 | 0.53585 | 11.335 | 0.2 | 0 | 0.76217 | 12.633 | 2.4 | 2.7948 | 1.0777 | 0.011164
2016-09-23 08:00 | 22.1167 | 22.0467 | 0.07 | 0.41139 | 0.20715 | -42.363 | 80.2032 | 9.7968 | -43.1407 | 44.9454 | 0.29117 | 16.535 | 0.2 | 0 | 1.1058 | 17.932 | 1.5 | 2.0604 | 1.0803 | 0.015885
2016-09-23 09:00 | 28.99 | 28.98 | 0.01 | 0.049131 | 0.19098 | -27.3592 | 78.256 | 11.744 | -27.9947 | 31.7389 | 0.041783 | 21.735 | 0.2 | 0 | 1.4495 | 23.2263 | 1.8 | 2.5258 | 1.0787 | 0.020544
2016-09-23 10:00 | 29.86 | 29.83 | 0.03 | 0.13437 | 0.17481 | -12.3553 | 77.0991 | 12.9009 | -12.6805 | 20.7382 | 0.12566 | 22.3725 | 0.2 | 0 | 1.493 | 23.9912 | 2.5 | 3.2497 | 1.0761 | 0.02117
2016-09-23 11:00 | 30.73 | 30.68 | 0.05 | 0.21932 | 0.15864 | 2.6485 | 76.8222 | 13.1778 | 2.7201 | 17.0093 | 0.20973 | 23.01 | 0.2 | 0 | 1.5365 | 24.7562 | 2.4 | 3.1736 | 1.0764 | 0.021851
2016-09-23 12:00 | 31.6 | 31.53 | 0.07 | 0.3221 | 0.14248 | 17.6523 | 77.4483 | 12.5517 | 18.0992 | 24.1943 | 0.29381 | 23.6475 | 0.2 | 0 | 1.58 | 25.5213 | 2.1 | 2.8975 | 1.0774 | 0.022546
2016-09-23 13:00 | 24.83 | 24.76 | 0.07 | 0.36455 | 0.12631 | 32.6561 | 78.9295 | 11.0705 | 33.355 | 36.3007 | 0.2938 | 18.57 | 0.2 | 0 | 1.2415 | 20.1053 | 2.8 | 3.4283 | 1.0755 | 0.017731
2016-09-23 14:00 | 18.06 | 17.99 | 0.07 | 0.45524 | 0.11014 | 47.6599 | 81.1548 | 8.8452 | 48.4222 | 49.8513 | 0.29353 | 13.4925 | 0.2 | 0 | 0.903 | 14.689 | 5.4 | 5.859 | 1.067 | 0.012852
2016-09-23 15:00 | 11.29 | 11.22 | 0.07 | 0.66566 | 0.093968 | 62.6637 | 83.9637 | 6.0363 | 63.2881 | 63.9151 | 0.29269 | 8.415 | 0.2 | 0 | 0.5645 | 9.2722 | 4.7 | 4.9898 | 1.07 | 0.0081357
2016-09-23 16:00 | 7.5267 | 7.48 | 0.046667 | 0 | 0.077798 | 77.6676 | 87.1633 | 2.8367 | 77.9931 | 78.189 | 0 | 5.61 | 0.2 | 0 | 0.37633 | 5.9863 | 7 | 7.1871 | 1.0623 | 0.0052148
2016-09-23 17:00 | 3.7633 | 3.74 | 0.023333 | 0 | 0.061627 | 92.6714 | 90.5422 | -0.54219 | 92.6165 | 92.537 | 0 | 2.805 | 0.2 | 0 | 0.18817 | 2.9932 | 7.3 | 7.3935 | 1.0616 | 0.0026056
2016-09-23 18:00 | 0 | 0 | 0 | 0 | 0.045455 | 107.6752 | 93.8818 | -3.8818 | 107.257 | 106.8684 | 0 | 0 | 0.2 | 0 | 0 | 0 | 7.2 | 7.2 | 1.0623 | 0
2016-09-23 19:00 | 0 | 0 | 0 | 0 | 0.029283 | 122.679 | 96.9652 | -6.9652 | 122.0088 | 121.0832 | 0 | 0 | 0.2 | 0 | 0 | 0 | 7.3 | 7.3 | 1.0619 | 0
2016-09-23 20:00 | 0 | 0 | 0 | 0 | 0.013111 | 137.6828 | 99.5862 | -9.5862 | 136.9396 | 135.0058 | 0 | 0 | 0.2 | 0 | 0 | 0 | 7 | 7 | 1.063 | 0
2016-09-23 21:00 | 0 | 0 | 0 | 0 | -0.0030617 | 152.6866 | 101.5619 | -11.5619 | 152.072 | 148.1957 | 0 | 0 | 0.2 | 0 | 0 | 0 | 7.5 | 7.5 | 1.0613 | 0
2016-09-23 22:00 | 0 | 0 | 0 | 0 | -0.019235 | 167.6904 | 102.7478 | -12.7478 | 167.3743 | 159.1609 | 0 | 0 | 0.2 | 0 | 0 | 0 | 7.2 | 7.2 | 1.0623 | 0
2016-09-23 23:00 | 0 | 0 | 0 | 0 | -0.035409 | 182.6942 | 103.0541 | -13.0541 | -177.2343 | 162.862 | 0 | 0 | 0.2 | 0 | 0 | 0 | 7.4 | 7.4 | 1.0616 | 0
2016-09-24 | 0 | 0 | 0 | 0 | -0.051583 | -162.302 | 102.4579 | -12.4579 | -161.8606 | 155.7091 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6.1 | 6.1 | 1.0661 | 0
2016-09-24 01:00 | 0 | 0 | 0 | 0 | -0.067757 | -147.2982 | 101.0067 | -11.0067 | -146.6061 | 143.6307 | 0 | 0 | 0.2 | 0 | 0 | 0 | 7 | 7 | 1.063 | 0
2016-09-24 02:00 | 0 | 0 | 0 | 0 | -0.083932 | -132.2944 | 98.8117 | -8.8117 | -131.5367 | 130.0965 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.7 | 5.7 | 1.0675 | 0
2016-09-24 03:00 | 0 | 0 | 0 | 0 | -0.10011 | -117.2906 | 96.0331 | -6.0331 | -116.6656 | 116.0437 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0745 | 0
2016-09-24 04:00 | 2.8533 | 2.4733 | 0.38 | 0 | -0.11628 | -102.2868 | 92.8642 | -2.8642 | -101.9538 | 101.7788 | 0 | 1.855 | 0.2 | 0 | 0.14267 | 1.9977 | 4.6 | 4.6624 | 1.0712 | 0.0017547
2016-09-24 05:00 | 5.7067 | 4.9467 | 0.76 | 0 | -0.13246 | -87.283 | 89.5165 | 0.48347 | -87.323 | 87.44 | 0 | 3.71 | 0.2 | 0 | 0.28533 | 3.9953 | 3.1 | 3.2249 | 1.0762 | 0.0035259
2016-09-24 06:00 | 8.56 | 7.42 | 1.14 | 17.2426 | -0.14864 | -72.2792 | 86.2091 | 3.7909 | -72.6761 | 73.1197 | 5.0068 | 5.565 | 0.2 | 0 | 0.428 | 10.9998 | 3.8 | 4.1437 | 1.073 | 0.0096782
2016-09-24 07:00 | 16.56 | 14.89 | 1.67 | 14.0204 | -0.16481 | -57.2754 | 83.1591 | 6.8409 | -57.92 | 58.9203 | 7.2377 | 11.1675 | 0.2 | 0 | 0.828 | 19.2332 | 3.2 | 3.801 | 1.0742 | 0.016941
2016-09-24 08:00 | 24.56 | 22.36 | 2.2 | 13.4313 | -0.18099 | -42.2716 | 80.5726 | 9.4274 | -42.9885 | 45.0222 | 9.4936 | 16.77 | 0.2 | 0 | 1.228 | 27.4916 | 3.8 | 4.6591 | 1.0712 | 0.024148
2016-09-24 09:00 | 32.56 | 29.83 | 2.73 | 13.8506 | -0.19717 | -27.2678 | 78.6324 | 11.3676 | -27.8601 | 31.8777 | 11.7616 | 22.3725 | 0.2 | 0 | 1.628 | 35.7621 | 5.1 | 6.2176 | 1.0657 | 0.031253
2016-09-24 10:00 | 37.6 | 35.77 | 1.83 | 8.4432 | -0.21335 | -12.264 | 77.4822 | 12.5178 | -12.5674 | 21.0042 | 7.8822 | 26.8275 | 0.2 | 0 | 1.88 | 36.5897 | 3.8 | 4.9434 | 1.0702 | 0.03211
2016-09-24 11:00 | 42.64 | 41.71 | 0.93 | 4.2014 | -0.22952 | 2.7398 | 77.2113 | 12.7887 | 2.8095 | 17.4068 | 4.009 | 31.2825 | 0.2 | 0 | 2.132 | 37.4235 | 5.5 | 6.6695 | 1.0642 | 0.032656
2016-09-24 12:00 | 47.68 | 47.65 | 0.03 | 0.14244 | -0.2457 | 17.7436 | 77.8419 | 12.1581 | 18.1646 | 24.5339 | 0.12958 | 35.7375 | 0.2 | 0 | 2.384 | 38.2511 | 5.5 | 6.6953 | 1.0641 | 0.033375
2016-09-24 13:00 | 41.3633 | 37.76 | 3.6033 | 19.4543 | -0.26188 | 32.7474 | 79.326 | 10.674 | 33.3982 | 36.5715 | 15.6241 | 28.32 | 0.2 | 0 | 2.0682 | 46.0122 | 5.1 | 6.5379 | 1.0646 | 0.040168
2016-09-24 14:00 | 35.0467 | 27.87 | 7.1767 | 48.8549 | -0.27806 | 47.7511 | 81.5528 | 8.4472 | 48.4469 | 50.084 | 31.3484 | 20.9025 | 0.2 | 0 | 1.7523 | 54.0033 | 5.5 | 7.1876 | 1.0623 | 0.047043
2016-09-24 15:00 | 28.73 | 17.98 | 10.75 | 109.4293 | -0.29424 | 62.7549 | 84.3623 | 5.6377 | 63.2993 | 64.1277 | 47.7513 | 13.485 | 0.2 | 0 | 1.4365 | 62.6728 | 4.3 | 6.2585 | 1.0656 | 0.054763
2016-09-24 16:00 | 19.1633 | 11.9967 | 7.1667 | 0 | -0.31042 | 77.7587 | 87.5621 | 2.4379 | 77.9963 | 78.3919 | 0 | 8.9975 | 0.2 | 0 | 0.95817 | 9.9557 | 4.2 | 4.5111 | 1.0717 | 0.0087491
2016-09-24 17:00 | 9.5967 | 6.0133 | 3.5833 | 0 | -0.3266 | 92.7625 | 90.941 | -0.94097 | 92.6179 | 92.7375 | 0 | 4.51 | 0.2 | 0 | 0.47983 | 4.9898 | 4.2 | 4.3559 | 1.0723 | 0.0043873
2016-09-24 18:00 | 0.03 | 0.03 | 0 | 0 | -0.34278 | 107.7663 | 94.2806 | -4.2806 | 107.2624 | 107.0733 | 0 | 0.0225 | 0.2 | 0 | 0.0015 | 0.024 | 3.4 | 3.4007 | 1.0756 | 2.1168e-05
2016-09-24 19:00 | 0.02 | 0.02 | 0 | 0 | -0.35896 | 122.7701 | 97.3637 | -7.3637 | 122.0241 | 121.3006 | 0 | 0.015 | 0.2 | 0 | 0.001 | 0.016 | 3.9 | 3.9005 | 1.0738 | 1.4089e-05
2016-09-24 20:00 | 0.01 | 0.01 | 0 | 0 | -0.37515 | 137.7738 | 99.9839 | -9.9839 | 136.9703 | 135.2482 | 0 | 0.0075 | 0.2 | 0 | 0.0005 | 0.008 | 3.2 | 3.2003 | 1.0763 | 7.0605e-06
2016-09-24 21:00 | 0 | 0 | 0 | 0 | -0.39133 | 152.7776 | 101.9576 | -11.9576 | 152.1226 | 148.4854 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0763 | 0
2016-09-24 22:00 | 0 | 0 | 0 | 0 | -0.40751 | 167.7814 | 103.1401 | -13.1401 | 167.4479 | 159.5307 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-09-24 23:00 | 0 | 0 | 0 | 0 | -0.42369 | 182.7852 | 103.4413 | -13.4413 | -177.1364 | 163.2312 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0774 | 0
2016-09-25 | 0 | 0 | 0 | 0 | -0.43987 | -162.2111 | 102.8388 | -12.8388 | -161.7396 | 155.9173 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0774 | 0
2016-09-25 01:00 | 0 | 0 | 0 | 0 | -0.45606 | -147.2073 | 101.3807 | -11.3807 | -146.465 | 143.7403 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-09-25 02:00 | 0 | 0 | 0 | 0 | -0.47224 | -132.2035 | 99.179 | -9.179 | -131.3796 | 130.159 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-09-25 03:00 | 0 | 0 | 0 | 0 | -0.48842 | -117.1998 | 96.3951 | -6.3951 | -116.4974 | 116.0829 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0826 | 0
2016-09-25 04:00 | 10.87 | 6.4367 | 4.4333 | 0 | -0.50461 | -102.196 | 93.2229 | -3.2229 | -101.7793 | 101.8075 | 0 | 4.8275 | 0.2 | 0 | 0.5435 | 5.371 | 1.8 | 1.9678 | 1.0806 | 0.0047593
2016-09-25 05:00 | 21.74 | 12.8733 | 8.8667 | 0 | -0.52079 | -87.1922 | 89.8744 | 0.12555 | -87.1471 | 87.4668 | 0 | 9.655 | 0.2 | 0 | 1.087 | 10.742 | 1.6 | 1.9357 | 1.0807 | 0.0095195
2016-09-25 06:00 | 32.61 | 19.31 | 13.3 | 222.2241 | -0.53698 | -72.1885 | 86.5688 | 3.4312 | -72.5036 | 73.1525 | 64.4062 | 14.4825 | 0.2 | 0 | 1.6305 | 80.5192 | 2.6 | 5.1162 | 1.0696 | 0.070621
2016-09-25 07:00 | 55.94 | 43.0067 | 12.9333 | 114.653 | -0.55316 | -57.1847 | 83.523 | 6.477 | -57.7557 | 58.9689 | 59.104 | 32.255 | 0.2 | 0 | 2.797 | 94.156 | 2.5 | 5.4424 | 1.0685 | 0.082493
2016-09-25 08:00 | 79.27 | 66.7033 | 12.5667 | 79.8259 | -0.56934 | -42.181 | 80.9425 | 9.0575 | -42.8373 | 45.1026 | 56.3443 | 50.0275 | 0.2 | 0 | 3.9635 | 110.3353 | 2.6 | 6.048 | 1.0663 | 0.096476
2016-09-25 09:00 | 102.6 | 90.4 | 12.2 | 63.9903 | -0.58553 | -27.1772 | 79.0091 | 10.9909 | -27.7267 | 32.0212 | 54.2543 | 67.8 | 0.2 | 0 | 5.13 | 127.1843 | 2.7 | 6.6745 | 1.0641 | 0.11098
2016-09-25 10:00 | 101.6367 | 90.41 | 11.2267 | 53.4086 | -0.60171 | -12.1734 | 77.8657 | 12.1343 | -12.4554 | 21.2748 | 49.7688 | 67.8075 | 0.2 | 0 | 5.0818 | 122.6582 | 3.5 | 7.3331 | 1.0618 | 0.1068
2016-09-25 11:00 | 100.6733 | 90.42 | 10.2533 | 47.7514 | -0.6179 | 2.8303 | 77.6007 | 12.3993 | 2.8978 | 17.8045 | 45.4643 | 67.815 | 0.2 | 0 | 5.0337 | 118.313 | 3.4 | 7.0973 | 1.0627 | 0.1031
2016-09-25 12:00 | 99.71 | 90.43 | 9.28 | 45.5155 | -0.63408 | 17.8341 | 78.2357 | 11.7643 | 18.2289 | 24.8749 | 41.293 | 67.8225 | 0.2 | 0 | 4.9855 | 114.101 | 3 | 6.5657 | 1.0645 | 0.099599
2016-09-25 13:00 | 78.86 | 69.93 | 8.93 | 50.0524 | -0.65027 | 32.8378 | 79.7227 | 10.2773 | 33.4404 | 36.8436 | 40.0556 | 52.4475 | 0.2 | 0 | 3.943 | 96.4461 | 2.8 | 5.8139 | 1.0672 | 0.084397
2016-09-25 14:00 | 58.01 | 49.43 | 8.58 | 61.2763 | -0.66646 | 47.8416 | 81.9509 | 8.0491 | 48.4707 | 50.3176 | 39.1268 | 37.0725 | 0.2 | 0 | 2.9005 | 79.0998 | 3.4 | 5.8719 | 1.0669 | 0.069204
2016-09-25 15:00 | 37.16 | 28.93 | 8.23 | 90.1319 | -0.68264 | 62.8453 | 84.761 | 5.239 | 63.3096 | 64.3405 | 39.0291 | 21.6975 | 0.2 | 0 | 1.858 | 62.5846 | 2.9 | 4.8558 | 1.0705 | 0.054938
2016-09-25 16:00 | 24.7833 | 19.2867 | 5.4967 | 0 | -0.69883 | 77.8491 | 87.9608 | 2.0392 | 77.9988 | 78.5945 | 0 | 14.465 | 0.2 | 0 | 1.2392 | 15.7042 | 2.8 | 3.2908 | 1.076 | 0.013856
2016-09-25 17:00 | 12.4067 | 9.6433 | 2.7633 | 0 | -0.71501 | 92.8528 | 91.3397 | -1.3397 | 92.6183 | 92.9372 | 0 | 7.2325 | 0.2 | 0 | 0.62033 | 7.8528 | 3.3 | 3.5454 | 1.0751 | 0.0069229
2016-09-25 18:00 | 0.03 | 0 | 0.03 | 0 | -0.7312 | 107.8566 | 94.6793 | -4.6793 | 107.2669 | 107.2768 | 0 | 0 | 0.2 | 0 | 0.0015 | 0.0015 | 2.9 | 2.9 | 1.0773 | 1.3251e-06
2016-09-25 19:00 | 0.02 | 0 | 0.02 | 0 | -0.74739 | 122.8603 | 97.7622 | -7.7622 | 122.0385 | 121.5161 | 0 | 0 | 0.2 | 0 | 0.001 | 0.001 | 2.9 | 2.9 | 1.0773 | 8.8343e-07
2016-09-25 20:00 | 0.01 | 0 | 0.01 | 0 | -0.76357 | 137.864 | 100.3815 | -10.3815 | 137.0001 | 135.4881 | 0 | 0 | 0.2 | 0 | 0.0005 | 0.0005 | 3.8 | 3.8 | 1.0742 | 4.4042e-07
2016-09-25 21:00 | 0 | 0 | 0 | 0 | -0.77976 | 152.8678 | 102.3534 | -12.3534 | 152.1725 | 148.7723 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.4 | 3.4 | 1.0756 | 0
2016-09-25 22:00 | 0 | 0 | 0 | 0 | -0.79595 | 167.8715 | 103.5325 | -13.5325 | 167.5209 | 159.8991 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.4 | 4.4 | 1.0721 | 0
2016-09-25 23:00 | 0 | 0 | 0 | 0 | -0.81213 | 182.8753 | 103.8287 | -13.8287 | -177.0391 | 163.5994 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.0735 | 0
2016-09-26 | 0 | 0 | 0 | 0 | -0.82832 | -162.121 | 103.2199 | -13.2199 | -161.6191 | 156.1217 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0763 | 0
2016-09-26 01:00 | 0 | 0 | 0 | 0 | -0.84451 | -147.1173 | 101.7549 | -11.7549 | -146.3243 | 143.8471 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0763 | 0
2016-09-26 02:00 | 0 | 0 | 0 | 0 | -0.8607 | -132.1135 | 99.5466 | -9.5466 | -131.223 | 130.2201 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0763 | 0
2016-09-26 03:00 | 0 | 0 | 0 | 0 | -0.87688 | -117.1098 | 96.7574 | -6.7574 | -116.3297 | 116.1216 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-09-26 04:00 | 6 | 5.22 | 0.78 | 0 | -0.89307 | -102.1061 | 93.5819 | -3.5819 | -101.6056 | 101.8364 | 0 | 3.915 | 0.2 | 0 | 0.3 | 4.215 | 3.8 | 3.9317 | 1.0737 | 0.0037112
2016-09-26 05:00 | 12 | 10.44 | 1.56 | 0 | -0.90926 | -87.1024 | 90.2327 | -0.23269 | -86.9721 | 87.4945 | 0 | 7.83 | 0.2 | 0 | 0.6 | 8.43 | 4.3 | 4.5634 | 1.0715 | 0.007407
2016-09-26 06:00 | 18 | 15.66 | 2.34 | 43.677 | -0.92545 | -72.0986 | 86.9289 | 3.0711 | -72.3321 | 73.187 | 12.6335 | 11.745 | 0.2 | 0 | 0.9 | 25.2785 | 4.2 | 4.99 | 1.07 | 0.02218
2016-09-26 07:00 | 39.35 | 27.3467 | 12.0033 | 112.7229 | -0.94163 | -57.0949 | 83.8873 | 6.1127 | -57.5926 | 59.0201 | 58.0228 | 20.51 | 0.2 | 0 | 1.9675 | 80.5003 | 5.7 | 8.2156 | 1.0587 | 0.069888
2016-09-26 08:00 | 60.7 | 39.0333 | 21.6667 | 143.4471 | -0.95782 | -42.0912 | 81.3126 | 8.6874 | -42.6874 | 45.1864 | 101.1018 | 29.275 | 0.2 | 0 | 3.035 | 133.4118 | 5.3 | 9.4691 | 1.0544 | 0.11534
2016-09-26 09:00 | 82.05 | 50.72 | 31.33 | 170.0948 | -0.97401 | -27.0875 | 79.386 | 10.614 | -27.5944 | 32.1694 | 143.9815 | 38.04 | 0.2 | 0 | 4.1025 | 186.124 | 4.7 | 10.5164 | 1.0507 | 0.16036
2016-09-26 10:00 | 76.9933 | 55.7533 | 21.24 | 104.2956 | -0.9902 | -12.0838 | 78.2494 | 11.7506 | -12.3446 | 21.5497 | 97.0053 | 41.815 | 0.2 | 0 | 3.8497 | 142.6699 | 5.4 | 9.8584 | 1.053 | 0.12319
2016-09-26 11:00 | 71.9367 | 60.7867 | 11.15 | 53.5854 | -1.0064 | 2.92 | 77.9902 | 12.0098 | 2.9849 | 18.2022 | 50.904 | 45.59 | 0.2 | 0 | 3.5968 | 100.0909 | 5.4 | 8.5278 | 1.0577 | 0.086806
2016-09-26 12:00 | 66.88 | 65.82 | 1.06 | 5.3766 | -1.0226 | 17.9237 | 78.6295 | 11.3705 | 18.2921 | 25.2169 | 4.8642 | 49.365 | 0.2 | 0 | 3.344 | 57.5732 | 5.2 | 6.9992 | 1.063 | 0.050184
2016-09-26 13:00 | 51.8767 | 50.8633 | 1.0133 | 5.9053 | -1.0388 | 32.9274 | 80.1193 | 9.8807 | 33.4816 | 37.117 | 4.7089 | 38.1475 | 0.2 | 0 | 2.5938 | 45.4502 | 5.2 | 6.6203 | 1.0643 | 0.039667
2016-09-26 14:00 | 36.8733 | 35.9067 | 0.96667 | 7.2605 | -1.055 | 47.9311 | 82.3489 | 7.6511 | 48.4935 | 50.5519 | 4.6132 | 26.93 | 0.2 | 0 | 1.8437 | 33.3869 | 5.2 | 6.2433 | 1.0656 | 0.029174
2016-09-26 15:00 | 21.87 | 20.95 | 0.92 | 10.9029 | -1.0711 | 62.9348 | 85.1595 | 4.8405 | 63.319 | 64.5535 | 4.6846 | 15.7125 | 0.2 | 0 | 1.0935 | 21.4906 | 5.5 | 6.1716 | 1.0659 | 0.018784
2016-09-26 16:00 | 14.58 | 13.9667 | 0.61333 | 0 | -1.0873 | 77.9385 | 88.3595 | 1.6405 | 78.0003 | 78.7966 | 0 | 10.475 | 0.2 | 0 | 0.729 | 11.204 | 5.5 | 5.8501 | 1.067 | 0.0098031
2016-09-26 17:00 | 7.29 | 6.9833 | 0.30667 | 0 | -1.1035 | 92.9422 | 91.7384 | -1.7384 | 92.6179 | 93.136 | 0 | 5.2375 | 0.2 | 0 | 0.3645 | 5.602 | 5.8 | 5.9751 | 1.0666 | 0.0048995
2016-09-26 18:00 | 0 | 0 | 0 | 0 | -1.1197 | 107.9459 | 95.078 | -5.078 | 107.2705 | 107.4789 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6.6 | 6.6 | 1.0644 | 0
2016-09-26 19:00 | 0 | 0 | 0 | 0 | -1.1359 | 122.9496 | 98.1606 | -8.1606 | 122.052 | 121.7296 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6.7 | 6.7 | 1.064 | 0
2016-09-26 20:00 | 0 | 0 | 0 | 0 | -1.1521 | 137.9533 | 100.7792 | -10.7792 | 137.0291 | 135.7253 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6.7 | 6.7 | 1.064 | 0
2016-09-26 21:00 | 0 | 0 | 0 | 0 | -1.1683 | 152.957 | 102.7491 | -12.7491 | 152.2215 | 149.0562 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6.8 | 6.8 | 1.0637 | 0
2016-09-26 22:00 | 0 | 0 | 0 | 0 | -1.1845 | 167.9607 | 103.9249 | -13.9249 | 167.5932 | 160.2658 | 0 | 0 | 0.2 | 0 | 0 | 0 | 7.5 | 7.5 | 1.0613 | 0
2016-09-26 23:00 | 0 | 0 | 0 | 0 | -1.2006 | 182.9644 | 104.2161 | -14.2161 | -176.9425 | 163.9664 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.7 | 5.7 | 1.0675 | 0
2016-09-27 | 0 | 0 | 0 | 0 | -1.2168 | -162.0319 | 103.601 | -13.601 | -161.4993 | 156.3221 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6.6 | 6.6 | 1.0644 | 0
2016-09-27 01:00 | 0 | 0 | 0 | 0 | -1.233 | -147.0282 | 102.1292 | -12.1292 | -146.1843 | 143.9513 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5 | 5 | 1.07 | 0
2016-09-27 02:00 | 0 | 0 | 0 | 0 | -1.2492 | -132.0245 | 99.9144 | -9.9144 | -131.0671 | 130.2797 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.2 | 5.2 | 1.0693 | 0
2016-09-27 03:00 | 0 | 0 | 0 | 0 | -1.2654 | -117.0208 | 97.1199 | -7.1199 | -116.1627 | 116.1599 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.0735 | 0
2016-09-27 04:00 | 8.0933 | 4.8233 | 3.27 | 0 | -1.2816 | -102.0171 | 93.9412 | -3.9412 | -101.4326 | 101.8657 | 0 | 3.6175 | 0.2 | 0 | 0.40467 | 4.0222 | 4.1 | 4.2257 | 1.0727 | 0.003538
2016-09-27 05:00 | 16.1867 | 9.6467 | 6.54 | 0 | -1.2978 | -87.0134 | 90.5912 | -0.5912 | -86.798 | 87.5234 | 0 | 7.235 | 0.2 | 0 | 0.80933 | 8.0443 | 5.8 | 6.0514 | 1.0663 | 0.0070338
2016-09-27 06:00 | 24.28 | 14.47 | 9.81 | 0 | -1.314 | -72.0098 | 87.2893 | 2.7107 | -72.1616 | 73.2233 | 0 | 10.8525 | 0.2 | 0 | 1.214 | 12.0665 | 6.6 | 6.9771 | 1.0631 | 0.010519
2016-09-27 07:00 | 57.16 | 22.62 | 34.54 | 344.8574 | -1.3301 | -57.0061 | 84.2518 | 5.7482 | -57.4306 | 59.0738 | 177.2339 | 16.965 | 0.2 | 0 | 2.858 | 197.0569 | 6.4 | 12.558 | 1.0435 | 0.16862
2016-09-27 08:00 | 90.04 | 30.77 | 59.27 | 409.7495 | -1.3463 | -42.0024 | 81.683 | 8.317 | -42.5387 | 45.2738 | 288.3488 | 23.0775 | 0.2 | 0 | 4.502 | 315.9283 | 6.4 | 16.2728 | 1.0305 | 0.26697
2016-09-27 09:00 | 122.92 | 38.92 | 84 | 472.6598 | -1.3625 | -26.9987 | 79.7632 | 10.2368 | -27.4635 | 32.3222 | 399.4235 | 29.19 | 0.2 | 0 | 6.146 | 434.7595 | 5.9 | 19.4862 | 1.0193 | 0.36338
2016-09-27 10:00 | 121.76 | 44.86 | 76.9 | 390.1788 | -1.3787 | -11.9951 | 78.6332 | 11.3668 | -12.2351 | 21.8289 | 362.2024 | 33.645 | 0.2 | 0 | 6.088 | 401.9354 | 6 | 18.5605 | 1.0225 | 0.33702
2016-09-27 11:00 | 120.6 | 50.8 | 69.8 | 346.5322 | -1.3949 | 3.0086 | 78.3797 | 11.6203 | 3.0707 | 18.5998 | 328.4326 | 38.1 | 0.2 | 0 | 6.03 | 372.5626 | 6.1 | 17.7426 | 1.0254 | 0.31326
2016-09-27 12:00 | 119.44 | 56.74 | 62.7 | 329.291 | -1.4111 | 18.0123 | 79.0233 | 10.9767 | 18.3541 | 25.5597 | 297.0653 | 42.555 | 0.2 | 0 | 5.972 | 345.5923 | 5.9 | 16.6998 | 1.0291 | 0.29162
2016-09-27 13:00 | 88.91 | 45.2633 | 43.6467 | 264.8848 | -1.4273 | 33.016 | 80.5158 | 9.4842 | 33.5217 | 37.3915 | 210.4522 | 33.9475 | 0.2 | 0 | 4.4455 | 248.8452 | 6 | 13.7764 | 1.0393 | 0.21207
2016-09-27 14:00 | 58.38 | 33.7867 | 24.5933 | 194.7922 | -1.4435 | 48.0196 | 82.7468 | 7.2532 | 48.5153 | 50.7867 | 123.1494 | 25.34 | 0.2 | 0 | 2.919 | 151.4084 | 6.1 | 10.8315 | 1.0496 | 0.13031
2016-09-27 15:00 | 27.85 | 22.31 | 5.54 | 71.5287 | -1.4596 | 63.0233 | 85.5579 | 4.4421 | 63.3274 | 64.7664 | 30.4934 | 16.7325 | 0.2 | 0 | 1.3925 | 48.6184 | 6.5 | 8.0193 | 1.0594 | 0.042236
2016-09-27 16:00 | 18.5667 | 14.8733 | 3.6933 | 0 | -1.4758 | 78.027 | 88.7579 | 1.2421 | 78.0008 | 78.9982 | 0 | 11.155 | 0.2 | 0 | 0.92833 | 12.0833 | 6.1 | 6.4776 | 1.0648 | 0.010551
2016-09-27 17:00 | 9.2833 | 7.4367 | 1.8467 | 0 | -1.492 | 93.0306 | 92.1368 | -2.1368 | 92.6165 | 93.3336 | 0 | 5.5775 | 0.2 | 0 | 0.46417 | 6.0417 | 5.9 | 6.0888 | 1.0662 | 0.0052821
2016-09-27 18:00 | 0 | 0 | 0 | 0 | -1.5082 | 108.0343 | 95.4764 | -5.4764 | 107.2731 | 107.6793 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.7 | 5.7 | 1.0675 | 0
2016-09-27 19:00 | 0 | 0 | 0 | 0 | -1.5244 | 123.0379 | 98.5588 | -8.5588 | 122.0645 | 121.9408 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6.7 | 6.7 | 1.064 | 0
2016-09-27 20:00 | 0 | 0 | 0 | 0 | -1.5406 | 138.0416 | 101.1766 | -11.1766 | 137.057 | 135.9598 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6.7 | 6.7 | 1.064 | 0
2016-09-27 21:00 | 0 | 0 | 0 | 0 | -1.5568 | 153.0453 | 103.1447 | -13.1447 | 152.2696 | 149.3369 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6.4 | 6.4 | 1.0651 | 0
2016-09-27 22:00 | 0 | 0 | 0 | 0 | -1.5729 | 168.0489 | 104.3171 | -14.3171 | 167.6646 | 160.6307 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6.3 | 6.3 | 1.0655 | 0
2016-09-27 23:00 | 0 | 0 | 0 | 0 | -1.5891 | 183.0526 | 104.6035 | -14.6035 | -176.8467 | 164.332 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6 | 6 | 1.0665 | 0
2016-09-28 | 0 | 0 | 0 | 0 | -1.6053 | -161.9438 | 103.9822 | -13.9822 | -161.3801 | 156.5186 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.8 | 5.8 | 1.0672 | 0
2016-09-28 01:00 | 0 | 0 | 0 | 0 | -1.6215 | -146.9402 | 102.5035 | -12.5035 | -146.0449 | 144.0529 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.9 | 5.9 | 1.0669 | 0
2016-09-28 02:00 | 0 | 0 | 0 | 0 | -1.6377 | -131.9365 | 100.2822 | -10.2822 | -130.9118 | 130.3381 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.8 | 5.8 | 1.0672 | 0
2016-09-28 03:00 | 0 | 0 | 0 | 0 | -1.6539 | -116.9329 | 97.4825 | -7.4825 | -115.9966 | 116.1979 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6.5 | 6.5 | 1.0648 | 0
2016-09-28 04:00 | 4.5533 | 3.7033 | 0.85 | 0 | -1.6701 | -101.9292 | 94.3006 | -4.3006 | -101.2605 | 101.8955 | 0 | 2.7775 | 0.2 | 0 | 0.22767 | 3.0052 | 4.1 | 4.1939 | 1.0728 | 0.0026437
2016-09-28 05:00 | 9.1067 | 7.4067 | 1.7 | 0 | -1.6862 | -86.9256 | 90.9499 | -0.9499 | -86.6249 | 87.5533 | 0 | 5.555 | 0.2 | 0 | 0.45533 | 6.0103 | 3.1 | 3.2878 | 1.076 | 0.005303
2016-09-28 06:00 | 13.66 | 11.11 | 2.55 | 0 | -1.7024 | -71.922 | 87.6498 | 2.3502 | -71.9923 | 73.2614 | 0 | 8.3325 | 0.2 | 0 | 0.683 | 9.0155 | 3.2 | 3.4817 | 1.0753 | 0.0079495
2016-09-28 07:00 | 35.94 | 24.5733 | 11.3667 | 121.1516 | -1.7186 | -56.9183 | 84.6165 | 5.3835 | -57.2699 | 59.1301 | 62.1617 | 18.43 | 0.2 | 0 | 1.797 | 82.3887 | 3.4 | 5.9746 | 1.0666 | 0.072057
2016-09-28 08:00 | 58.22 | 38.0367 | 20.1833 | 145.9949 | -1.7348 | -41.9147 | 82.0536 | 7.9464 | -42.3913 | 45.3647 | 102.5747 | 28.5275 | 0.2 | 0 | 2.911 | 134.0132 | 3.4 | 7.5879 | 1.0609 | 0.11659
2016-09-28 09:00 | 80.5 | 51.5 | 29 | 169.3584 | -1.751 | -26.9111 | 80.1404 | 9.8596 | -27.334 | 32.4795 | 142.868 | 38.625 | 0.2 | 0 | 4.025 | 185.518 | 3.5 | 9.2974 | 1.055 | 0.16049
2016-09-28 10:00 | 81.9167 | 52.4933 | 29.4233 | 154.4394 | -1.7671 | -11.9074 | 79.017 | 10.983 | -12.1271 | 22.112 | 143.0803 | 39.37 | 0.2 | 0 | 4.0958 | 186.5461 | 4.5 | 10.3296 | 1.0513 | 0.16082
2016-09-28 11:00 | 83.3333 | 53.4867 | 29.8467 | 153.2474 | -1.7833 | 3.0962 | 78.7692 | 11.2308 | 3.1552 | 18.9972 | 144.9007 | 40.115 | 0.2 | 0 | 4.1667 | 189.1824 | 5.2 | 11.1119 | 1.0486 | 0.16267
2016-09-28 12:00 | 84.75 | 54.48 | 30.27 | 164.8159 | -1.7995 | 18.0998 | 79.417 | 10.583 | 18.4148 | 25.9032 | 148.2573 | 40.86 | 0.2 | 0 | 4.2375 | 193.3548 | 3.9 | 9.9423 | 1.0527 | 0.16691
2016-09-28 13:00 | 64.82 | 42.2533 | 22.5667 | 142.8722 | -1.8157 | 33.1034 | 80.9121 | 9.0879 | 33.5605 | 37.6669 | 113.0944 | 31.69 | 0.2 | 0 | 3.241 | 148.0254 | 4.1 | 8.7258 | 1.057 | 0.12829
2016-09-28 14:00 | 44.89 | 30.0267 | 14.8633 | 124.5177 | -1.8319 | 48.1071 | 83.1444 | 6.8556 | 48.536 | 51.022 | 78.3244 | 22.52 | 0.2 | 0 | 2.2445 | 103.0889 | 3.9 | 7.1215 | 1.0626 | 0.089823
2016-09-28 15:00 | 24.96 | 17.8 | 7.16 | 101.5268 | -1.8481 | 63.1107 | 85.956 | 4.044 | 63.3347 | 64.9792 | 42.9405 | 13.35 | 0.2 | 0 | 1.248 | 57.5385 | 4.2 | 5.9981 | 1.0665 | 0.050319
2016-09-28 16:00 | 16.64 | 11.8667 | 4.7733 | 0 | -1.8642 | 78.1143 | 89.156 | 0.84398 | 78.0003 | 79.199 | 0 | 8.9 | 0.2 | 0 | 0.832 | 9.732 | 4.7 | 5.0041 | 1.07 | 0.0085387
2016-09-28 17:00 | 8.32 | 5.9333 | 2.3867 | 0 | -1.8804 | 93.1179 | 92.5349 | -2.5349 | 92.6139 | 93.53 | 0 | 4.45 | 0.2 | 0 | 0.416 | 4.866 | 4.4 | 4.5521 | 1.0716 | 0.0042757
2016-09-28 18:00 | 0 | 0 | 0 | 0 | -1.8966 | 108.1215 | 95.8744 | -5.8744 | 107.2745 | 107.878 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.0735 | 0
2016-09-28 19:00 | 0 | 0 | 0 | 0 | -1.9128 | 123.1251 | 98.9567 | -8.9567 | 122.076 | 122.1497 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-09-28 20:00 | 0 | 0 | 0 | 0 | -1.929 | 138.1287 | 101.5737 | -11.5737 | 137.084 | 136.1912 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0738 | 0
2016-09-28 21:00 | 0 | 0 | 0 | 0 | -1.9451 | 153.1323 | 103.5401 | -13.5401 | 152.3167 | 149.6142 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6.2 | 6.2 | 1.0658 | 0
2016-09-28 22:00 | 0 | 0 | 0 | 0 | -1.9613 | 168.136 | 104.7093 | -14.7093 | 167.7351 | 160.9935 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.1 | 5.1 | 1.0696 | 0
2016-09-28 23:00 | 0 | 0 | 0 | 0 | -1.9775 | 183.1396 | 104.9908 | -14.9908 | -176.7517 | 164.6962 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.2 | 4.2 | 1.0728 | 0
2016-09-29 | 0 | 0 | 0 | 0 | -1.9937 | -161.8569 | 104.3633 | -14.3633 | -161.2618 | 156.711 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.2 | 5.2 | 1.0693 | 0
2016-09-29 01:00 | 0 | 0 | 0 | 0 | -2.0098 | -146.8533 | 102.8778 | -12.8778 | -145.9063 | 144.1519 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.0735 | 0
2016-09-29 02:00 | 0 | 0 | 0 | 0 | -2.026 | -131.8497 | 100.65 | -10.65 | -130.7574 | 130.3953 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5 | 5 | 1.07 | 0
2016-09-29 03:00 | 0 | 0 | 0 | 0 | -2.0422 | -116.8461 | 97.8451 | -7.8451 | -115.8314 | 116.2356 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.5 | 5.5 | 1.0682 | 0
2016-09-29 04:00 | 3.4067 | 3.05 | 0.35667 | 0 | -2.0584 | -101.8425 | 94.6601 | -4.6601 | -101.0895 | 101.9258 | 0 | 2.2875 | 0.2 | 0 | 0.17033 | 2.4578 | 6.9 | 6.9768 | 1.0631 | 0.0021426
2016-09-29 05:00 | 6.8133 | 6.1 | 0.71333 | 0 | -2.0746 | -86.8389 | 91.3087 | -1.3087 | -86.453 | 87.5845 | 0 | 4.575 | 0.2 | 0 | 0.34067 | 4.9157 | 7.2 | 7.3536 | 1.0618 | 0.0042798
2016-09-29 06:00 | 10.22 | 9.15 | 1.07 | 0 | -2.0907 | -71.8353 | 88.0105 | 1.9895 | -71.8243 | 73.3015 | 0 | 6.8625 | 0.2 | 0 | 0.511 | 7.3735 | 6.9 | 7.1304 | 1.0625 | 0.0064244
2016-09-29 07:00 | 21.0067 | 20.19 | 0.81667 | 9.3354 | -2.1069 | -56.8317 | 84.9813 | 5.0187 | -57.1106 | 59.1892 | 4.7817 | 15.1425 | 0.2 | 0 | 1.0503 | 20.9745 | 7.2 | 7.8555 | 1.06 | 0.018231
2016-09-29 08:00 | 31.7933 | 31.23 | 0.56333 | 4.273 | -2.1231 | -41.8281 | 82.4242 | 7.5758 | -42.2455 | 45.4593 | 2.9971 | 23.4225 | 0.2 | 0 | 1.5897 | 28.0093 | 6.5 | 7.3753 | 1.0617 | 0.024384
2016-09-29 09:00 | 42.58 | 42.27 | 0.31 | 1.8817 | -2.1393 | -26.8246 | 80.5177 | 9.4823 | -27.2061 | 32.6414 | 1.5845 | 31.7025 | 0.2 | 0 | 2.129 | 35.416 | 6.2 | 7.3068 | 1.0619 | 0.03084
2016-09-29 10:00 | 43.7667 | 43.55 | 0.21667 | 1.1779 | -2.1554 | -11.821 | 79.4008 | 10.5992 | -12.0206 | 22.399 | 1.0891 | 32.6625 | 0.2 | 0 | 2.1883 | 35.9399 | 5.6 | 6.7231 | 1.064 | 0.031356
2016-09-29 11:00 | 44.9533 | 44.83 | 0.12333 | 0.65571 | -2.1716 | 3.1826 | 79.1585 | 10.8415 | 3.2382 | 19.3942 | 0.6185 | 33.6225 | 0.2 | 0 | 2.2477 | 36.4887 | 5.3 | 6.4403 | 1.065 | 0.031864
2016-09-29 12:00 | 46.14 | 46.11 | 0.03 | 0.16958 | -2.1878 | 18.1862 | 79.8104 | 10.1896 | 18.4741 | 26.2472 | 0.1521 | 34.5825 | 0.2 | 0 | 2.307 | 37.0416 | 5.3 | 6.4575 | 1.0649 | 0.032345
2016-09-29 13:00 | 34.8733 | 34.8533 | 0.02 | 0.13234 | -2.2039 | 33.1897 | 81.3081 | 8.6919 | 33.5981 | 37.943 | 0.10437 | 26.14 | 0.2 | 0 | 1.7437 | 27.988 | 4.7 | 5.5746 | 1.068 | 0.024511
2016-09-29 14:00 | 23.6067 | 23.5967 | 0.01 | 0.088904 | -2.2201 | 48.1933 | 83.5416 | 6.4584 | 48.5554 | 51.2575 | 0.055638 | 17.6975 | 0.2 | 0 | 1.1803 | 18.9335 | 4 | 4.5917 | 1.0714 | 0.016634
2016-09-29 15:00 | 12.34 | 12.34 | 0 | 0 | -2.2363 | 63.1969 | 86.3536 | 3.6464 | 63.3407 | 65.1917 | 0 | 9.255 | 0.2 | 0 | 0.617 | 9.872 | 3.7 | 4.0085 | 1.0735 | 0.0086898
2016-09-29 16:00 | 8.2267 | 8.2267 | 0 | 0 | -2.2525 | 78.2004 | 89.5537 | 0.44634 | 77.9985 | 79.399 | 0 | 6.17 | 0.2 | 0 | 0.41133 | 6.5813 | 3.9 | 4.1057 | 1.0731 | 0.0057914
2016-09-29 17:00 | 4.1133 | 4.1133 | 0 | 0 | -2.2686 | 93.204 | 92.9325 | -2.9325 | 92.6102 | 93.725 | 0 | 3.085 | 0.2 | 0 | 0.20567 | 3.2907 | 4 | 4.1028 | 1.0731 | 0.0028957
2016-09-29 18:00 | 0 | 0 | 0 | 0 | -2.2848 | 108.2076 | 96.272 | -6.272 | 107.2748 | 108.0747 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.6 | 3.6 | 1.0749 | 0
2016-09-29 19:00 | 0 | 0 | 0 | 0 | -2.301 | 123.2111 | 99.3542 | -9.3542 | 122.0862 | 122.3561 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-09-29 20:00 | 0 | 0 | 0 | 0 | -2.3171 | 138.2147 | 101.9705 | -11.9705 | 137.1097 | 136.4196 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.8 | 3.8 | 1.0742 | 0
2016-09-29 21:00 | 0 | 0 | 0 | 0 | -2.3333 | 153.2182 | 103.9351 | -13.9351 | 152.3627 | 149.8879 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.4 | 3.4 | 1.0756 | 0
2016-09-29 22:00 | 0 | 0 | 0 | 0 | -2.3495 | 168.2218 | 105.1011 | -15.1011 | 167.8045 | 161.354 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0763 | 0
2016-09-29 23:00 | 0 | 0 | 0 | 0 | -2.3656 | 183.2253 | 105.3778 | -15.3778 | -176.6576 | 165.0588 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0774 | 0
2016-09-30 | 0 | 0 | 0 | 0 | -2.3818 | -161.7711 | 104.7441 | -14.7441 | -161.1443 | 156.8992 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-09-30 01:00 | 0 | 0 | 0 | 0 | -2.398 | -146.7676 | 103.2519 | -13.2519 | -145.7686 | 144.2483 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-09-30 02:00 | 0 | 0 | 0 | 0 | -2.4141 | -131.7641 | 101.0178 | -11.0178 | -130.604 | 130.4512 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.078 | 0
2016-09-30 03:00 | 0 | 0 | 0 | 0 | -2.4303 | -116.7605 | 98.2077 | -8.2077 | -115.6671 | 116.2732 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-09-30 04:00 | 2.62 | 2.4667 | 0.15333 | 0 | -2.4465 | -101.757 | 95.0196 | -5.0196 | -100.9196 | 101.9566 | 0 | 1.85 | 0.2 | 0 | 0.131 | 1.981 | 3.1 | 3.1619 | 1.0764 | 0.0017486
2016-09-30 05:00 | 5.24 | 4.9333 | 0.30667 | 0 | -2.4626 | -86.7534 | 91.6676 | -1.6676 | -86.2823 | 87.617 | 0 | 3.7 | 0.2 | 0 | 0.262 | 3.962 | 3.7 | 3.8238 | 1.0741 | 0.0034896
2016-09-30 06:00 | 7.86 | 7.4 | 0.46 | 0 | -2.4788 | -71.7499 | 88.3713 | 1.6287 | -71.6577 | 73.3435 | 0 | 5.55 | 0.2 | 0 | 0.393 | 5.943 | 3.9 | 4.0857 | 1.0732 | 0.00523
2016-09-30 07:00 | 22.4767 | 19.1667 | 3.31 | 40.7965 | -2.495 | -56.7464 | 85.3462 | 4.6538 | -56.9529 | 59.251 | 20.8584 | 14.375 | 0.2 | 0 | 1.1238 | 36.3572 | 3.4 | 4.5362 | 1.0716 | 0.031948
2016-09-30 08:00 | 37.0933 | 30.9333 | 6.16 | 49.1143 | -2.5111 | -41.7429 | 82.7949 | 7.2051 | -42.1013 | 45.5575 | 34.3895 | 23.2 | 0.2 | 0 | 1.8547 | 59.4442 | 3.8 | 5.6576 | 1.0677 | 0.052044
2016-09-30 09:00 | 51.71 | 42.7 | 9.01 | 56.9365 | -2.5273 | -26.7393 | 80.8949 | 9.1051 | -27.0798 | 32.8077 | 47.8547 | 32.025 | 0.2 | 0 | 2.5855 | 82.4652 | 2.7 | 5.277 | 1.069 | 0.072289
2016-09-30 10:00 | 56.2867 | 44.38 | 11.9067 | 67.1357 | -2.5434 | -11.7358 | 79.7844 | 10.2156 | -11.9157 | 22.6896 | 61.9399 | 33.285 | 0.2 | 0 | 2.8143 | 98.0392 | 2.3 | 5.3637 | 1.0687 | 0.085917
2016-09-30 11:00 | 60.8633 | 46.06 | 14.8033 | 81.5978 | -2.5596 | 3.2677 | 79.5476 | 10.4524 | 3.3196 | 19.7909 | 76.7782 | 34.545 | 0.2 | 0 | 3.0432 | 114.3664 | 2.7 | 6.2739 | 1.0655 | 0.099927
2016-09-30 12:00 | 65.44 | 47.74 | 17.7 | 104.0266 | -2.5758 | 18.2712 | 80.2035 | 9.7965 | 18.5319 | 26.5916 | 93.0227 | 35.805 | 0.2 | 0 | 3.272 | 132.0997 | 2.6 | 6.7281 | 1.064 | 0.11525
2016-09-30 13:00 | 47.5233 | 35.6133 | 11.91 | 82.5399 | -2.5919 | 33.2747 | 81.7036 | 8.2964 | 33.6343 | 38.2196 | 64.8471 | 26.71 | 0.2 | 0 | 2.3762 | 93.9332 | 2.7 | 5.6354 | 1.0678 | 0.082246
2016-09-30 14:00 | 29.6067 | 23.4867 | 6.12 | 57.9556 | -2.6081 | 48.2782 | 83.9384 | 6.0616 | 48.5735 | 51.4931 | 36.0837 | 17.615 | 0.2 | 0 | 1.4803 | 55.179 | 2.8 | 4.5243 | 1.0717 | 0.048489
2016-09-30 15:00 | 11.69 | 11.36 | 0.33 | 5.822 | -2.6242 | 63.2818 | 86.7507 | 3.2493 | 63.3456 | 65.4037 | 2.4233 | 8.52 | 0.2 | 0 | 0.5845 | 11.5278 | 3.1 | 3.4602 | 1.0754 | 0.010165
2016-09-30 16:00 | 7.7933 | 7.5733 | 0.22 | 0 | -2.6404 | 78.2853 | 89.9507 | 0.049256 | 77.9955 | 79.5981 | 0 | 5.68 | 0.2 | 0 | 0.38967 | 6.0697 | 3.8 | 3.9897 | 1.0735 | 0.0053431
2016-09-30 17:00 | 3.8967 | 3.7867 | 0.11 | 0 | -2.6566 | 93.2888 | 93.3295 | -3.3295 | 92.6053 | 93.9185 | 0 | 2.84 | 0.2 | 0 | 0.19483 | 3.0348 | 3.3 | 3.3948 | 1.0756 | 0.0026767
2016-09-30 18:00 | 0 | 0 | 0 | 0 | -2.6727 | 108.2923 | 96.6691 | -6.6691 | 107.2739 | 108.2693 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0745 | 0
2016-09-30 19:00 | 0 | 0 | 0 | 0 | -2.6889 | 123.2958 | 99.7511 | -9.7511 | 122.0952 | 122.5598 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-09-30 20:00 | 0 | 0 | 0 | 0 | -2.705 | 138.2993 | 102.3668 | -12.3668 | 137.1342 | 136.6445 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.2 | 4.2 | 1.0728 | 0
2016-09-30 21:00 | 0 | 0 | 0 | 0 | -2.7212 | 153.3028 | 104.3297 | -14.3297 | 152.4075 | 150.1577 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0774 | 0
2016-09-30 22:00 | 0 | 0 | 0 | 0 | -2.7373 | 168.3063 | 105.4925 | -15.4925 | 167.8728 | 161.7119 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0745 | 0
2016-09-30 23:00 | 0 | 0 | 0 | 0 | -2.7535 | 183.3098 | 105.7644 | -15.7644 | -176.5647 | 165.4196 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.0735 | 0
2016-10-01 | 0 | 0 | 0 | 0 | -2.7696 | -161.6868 | 105.1248 | -15.1248 | -161.028 | 157.0833 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.5 | 5.5 | 1.0682 | 0
2016-10-01 01:00 | 0 | 0 | 0 | 0 | -2.7858 | -146.6833 | 103.6259 | -13.6259 | -145.632 | 144.3422 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5 | 4.5 | 1.0717 | 0
2016-10-01 02:00 | 0 | 0 | 0 | 0 | -2.8019 | -131.6798 | 101.3854 | -11.3854 | -130.4516 | 130.5061 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0714 | 0
2016-10-01 03:00 | 0 | 0 | 0 | 0 | -2.8181 | -116.6763 | 98.5703 | -8.5703 | -115.5041 | 116.3106 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0714 | 0
2016-10-01 04:00 | 2.0767 | 2.0767 | 0 | 0 | -2.8342 | -101.6728 | 95.3791 | -5.3791 | -100.7509 | 101.9882 | 0 | 1.5575 | 0.2 | 0 | 0.10383 | 1.6613 | 5.1 | 5.1519 | 1.0695 | 0.0014569
2016-10-01 05:00 | 4.1533 | 4.1533 | 0 | 0 | -2.8504 | -86.6694 | 92.0265 | -2.0265 | -86.113 | 87.6508 | 0 | 3.115 | 0.2 | 0 | 0.20767 | 3.3227 | 5.8 | 5.9038 | 1.0668 | 0.0029067
2016-10-01 06:00 | 6.23 | 6.23 | 0 | 0 | -2.8665 | -71.6659 | 88.732 | 1.268 | -71.4926 | 73.3876 | 0 | 4.6725 | 0.2 | 0 | 0.3115 | 4.984 | 5.4 | 5.5558 | 1.0681 | 0.004365
2016-10-01 07:00 | 16.74 | 16.68 | 0.06 | 0.80229 | -2.8827 | -56.6624 | 85.7111 | 4.2889 | -56.7967 | 59.3155 | 0.40942 | 12.51 | 0.2 | 0 | 0.837 | 13.7564 | 5.4 | 5.8299 | 1.0671 | 0.012037
2016-10-01 08:00 | 27.25 | 27.13 | 0.12 | 1.0084 | -2.8988 | -41.659 | 83.1655 | 6.8345 | -41.9588 | 45.6593 | 0.70478 | 20.3475 | 0.2 | 0 | 1.3625 | 22.4148 | 5.1 | 5.8005 | 1.0672 | 0.019615
2016-10-01 09:00 | 37.76 | 37.58 | 0.18 | 1.1862 | -2.915 | -26.6555 | 81.2719 | 8.7281 | -26.9552 | 32.9785 | 0.99507 | 28.185 | 0.2 | 0 | 1.888 | 31.0681 | 4.5 | 5.4709 | 1.0684 | 0.027217
2016-10-01 10:00 | 38.7033 | 38.5133 | 0.19 | 1.1126 | -2.9311 | -11.652 | 80.1678 | 9.8322 | -11.8125 | 22.9836 | 1.0243 | 28.885 | 0.2 | 0 | 1.9352 | 31.8445 | 5.8 | 6.7951 | 1.0637 | 0.027776
2016-10-01 11:00 | 39.6467 | 39.4467 | 0.2 | 1.1445 | -2.9473 | 3.3514 | 79.9363 | 10.0637 | 3.3994 | 20.1869 | 1.0742 | 29.585 | 0.2 | 0 | 1.9823 | 32.6416 | 5.7 | 6.72 | 1.064 | 0.028479
2016-10-01 12:00 | 40.59 | 40.38 | 0.21 | 1.2853 | -2.9634 | 18.3549 | 80.5962 | 9.4038 | 18.5882 | 26.936 | 1.1458 | 30.285 | 0.2 | 0 | 2.0295 | 33.4603 | 4.5 | 5.5456 | 1.0681 | 0.029306
2016-10-01 13:00 | 30.16 | 30.02 | 0.14 | 1.0184 | -2.9795 | 33.3583 | 82.0986 | 7.9014 | 33.669 | 38.4966 | 0.79706 | 22.515 | 0.2 | 0 | 1.508 | 24.8201 | 5 | 5.7756 | 1.0673 | 0.021722
2016-10-01 14:00 | 19.73 | 19.66 | 0.07 | 0.70907 | -2.9957 | 48.3618 | 84.3345 | 5.6655 | 48.5902 | 51.7287 | 0.43919 | 14.745 | 0.2 | 0 | 0.9865 | 16.1707 | 4.8 | 5.3053 | 1.0689 | 0.014174
2016-10-01 15:00 | 9.3 | 9.3 | 0 | 0 | -3.0118 | 63.3653 | 87.1471 | 2.8529 | 63.349 | 65.6151 | 0 | 6.975 | 0.2 | 0 | 0.465 | 7.44 | 4.8 | 5.0325 | 1.0699 | 0.0065272
2016-10-01 16:00 | 6.2 | 6.2 | 0 | 0 | -3.028 | 78.3687 | 90.3471 | -0.34714 | 77.9912 | 79.796 | 0 | 4.65 | 0.2 | 0 | 0.31 | 4.96 | 5.9 | 6.055 | 1.0663 | 0.0043369
2016-10-01 17:00 | 3.1 | 3.1 | 0 | 0 | -3.0441 | 93.3721 | 93.7259 | -3.7259 | 92.5989 | 94.1104 | 0 | 2.325 | 0.2 | 0 | 0.155 | 2.48 | 6.1 | 6.1775 | 1.0659 | 0.0021676
2016-10-01 18:00 | 0 | 0 | 0 | 0 | -3.0602 | 108.3756 | 97.0654 | -7.0654 | 107.2716 | 108.4618 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.3 | 4.3 | 1.0724 | 0
2016-10-01 19:00 | 0 | 0 | 0 | 0 | -3.0764 | 123.379 | 100.1473 | -10.1473 | 122.1028 | 122.7607 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-10-01 20:00 | 0 | 0 | 0 | 0 | -3.0925 | 138.3825 | 102.7624 | -12.7624 | 137.1573 | 136.866 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.3 | 4.3 | 1.0724 | 0
2016-10-01 21:00 | 0 | 0 | 0 | 0 | -3.1087 | 153.3859 | 104.7237 | -14.7237 | 152.451 | 150.4235 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.4 | 4.4 | 1.0721 | 0
2016-10-01 22:00 | 0 | 0 | 0 | 0 | -3.1248 | 168.3893 | 105.8834 | -15.8834 | 167.9399 | 162.067 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.0735 | 0
2016-10-01 23:00 | 0 | 0 | 0 | 0 | -3.1409 | 183.3928 | 106.1507 | -16.1507 | -176.473 | 165.7785 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0714 | 0
2016-10-02 | 0 | 0 | 0 | 0 | -3.1571 | -161.6038 | 105.505 | -15.505 | -160.9127 | 157.2632 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-10-02 01:00 | 0 | 0 | 0 | 0 | -3.1732 | -146.6004 | 103.9995 | -13.9995 | -145.4965 | 144.4337 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.0735 | 0
2016-10-02 02:00 | 0 | 0 | 0 | 0 | -3.1893 | -131.597 | 101.7527 | -11.7527 | -130.3004 | 130.5599 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.6 | 3.6 | 1.0749 | 0
2016-10-02 03:00 | 0 | 0 | 0 | 0 | -3.2054 | -116.5936 | 98.9326 | -8.9326 | -115.3423 | 116.348 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0763 | 0
2016-10-02 04:00 | 3.54 | 2.47 | 1.07 | 0 | -3.2216 | -101.5901 | 95.7384 | -5.7384 | -100.5837 | 102.0204 | 0 | 1.8525 | 0.2 | 0 | 0.177 | 2.0295 | 3.3 | 3.3634 | 1.0757 | 0.0017902
2016-10-02 05:00 | 7.08 | 4.94 | 2.14 | 0 | -3.2377 | -86.5867 | 92.3852 | -2.3852 | -85.9453 | 87.6861 | 0 | 3.705 | 0.2 | 0 | 0.354 | 4.059 | 2.7 | 2.8268 | 1.0776 | 0.0035867
2016-10-02 06:00 | 10.62 | 7.41 | 3.21 | 0 | -3.2538 | -71.5833 | 89.0927 | 0.90729 | -71.3292 | 73.4337 | 0 | 5.5575 | 0.2 | 0 | 0.531 | 6.0885 | 3.4 | 3.5903 | 1.0749 | 0.0053667
2016-10-02 07:00 | 29.7733 | 18.4133 | 11.36 | 165.9949 | -3.27 | -56.5799 | 86.0758 | 3.9242 | -56.6423 | 59.3829 | 84.5408 | 13.81 | 0.2 | 0 | 1.4887 | 99.8395 | 3.5 | 6.62 | 1.0643 | 0.087135
2016-10-02 08:00 | 48.9267 | 29.4167 | 19.51 | 173.2976 | -3.2861 | -41.5765 | 83.5359 | 6.4641 | -41.8181 | 45.7647 | 120.8935 | 22.0625 | 0.2 | 0 | 2.4463 | 145.4024 | 2.9 | 7.4438 | 1.0614 | 0.12656
2016-10-02 09:00 | 68.08 | 40.42 | 27.66 | 190.4413 | -3.3022 | -26.5731 | 81.6487 | 8.3513 | -26.8324 | 33.1536 | 159.4388 | 30.315 | 0.2 | 0 | 3.404 | 193.1578 | 3 | 9.0362 | 1.0559 | 0.16724
2016-10-02 10:00 | 66.3667 | 41.0633 | 25.3033 | 154.1261 | -3.3183 | -11.5697 | 80.5508 | 9.4492 | -11.7111 | 23.2809 | 141.5769 | 30.7975 | 0.2 | 0 | 3.3183 | 175.6927 | 3.1 | 8.5904 | 1.0574 | 0.15234
2016-10-02 11:00 | 64.6533 | 41.7067 | 22.9467 | 136.5338 | -3.3345 | 3.4337 | 80.3246 | 9.6754 | 3.4774 | 20.5823 | 127.8185 | 31.28 | 0.2 | 0 | 3.2327 | 162.3312 | 3.1 | 8.1729 | 1.0589 | 0.14095
2016-10-02 12:00 | 62.94 | 42.35 | 20.59 | 131.4505 | -3.3506 | 18.4371 | 80.9883 | 9.0117 | 18.6429 | 27.2804 | 116.8297 | 31.7625 | 0.2 | 0 | 3.147 | 151.7392 | 3.9 | 8.6419 | 1.0573 | 0.13155
2016-10-02 13:00 | 47.0433 | 31.6967 | 15.3467 | 117.4665 | -3.3667 | 33.4405 | 82.493 | 7.507 | 33.7021 | 38.7738 | 91.5797 | 23.7725 | 0.2 | 0 | 2.3522 | 117.7043 | 3.3 | 6.9783 | 1.0631 | 0.10261
2016-10-02 14:00 | 31.1467 | 21.0433 | 10.1033 | 109.9977 | -3.3828 | 48.4439 | 84.7299 | 5.2701 | 48.6054 | 51.964 | 67.7757 | 15.7825 | 0.2 | 0 | 1.5573 | 85.1156 | 3.1 | 5.7599 | 1.0673 | 0.074495
2016-10-02 15:00 | 15.25 | 10.39 | 4.86 | 0 | -3.3989 | 63.4473 | 87.5428 | 2.4572 | 63.3511 | 65.8258 | 0 | 7.7925 | 0.2 | 0 | 0.7625 | 8.555 | 2.4 | 2.6673 | 1.0782 | 0.0075634
2016-10-02 16:00 | 10.1667 | 6.9267 | 3.24 | 0 | -3.4151 | 78.4506 | 90.7427 | -0.74274 | 77.9855 | 79.9926 | 0 | 5.195 | 0.2 | 0 | 0.50833 | 5.7033 | 1.7 | 1.8782 | 1.0809 | 0.0050552
2016-10-02 17:00 | 5.0833 | 3.4633 | 1.62 | 0 | -3.4312 | 93.454 | 94.1214 | -4.1214 | 92.5912 | 94.3005 | 0 | 2.5975 | 0.2 | 0 | 0.25417 | 2.8517 | 1.3 | 1.3891 | 1.0826 | 0.0025316
2016-10-02 18:00 | 0 | 0 | 0 | 0 | -3.4473 | 108.4574 | 97.461 | -7.461 | 107.2678 | 108.6519 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.084 | 0
2016-10-02 19:00 | 0 | 0 | 0 | 0 | -3.4634 | 123.4608 | 100.5428 | -10.5428 | 122.1089 | 122.9586 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0843 | 0
2016-10-02 20:00 | 0 | 0 | 0 | 0 | -3.4795 | 138.4641 | 103.1574 | -13.1574 | 137.179 | 137.0839 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0847 | 0
2016-10-02 21:00 | 0 | 0 | 0 | 0 | -3.4956 | 153.4675 | 105.1171 | -15.1171 | 152.493 | 150.6849 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-10-02 22:00 | 0 | 0 | 0 | 0 | -3.5117 | 168.4709 | 106.2738 | -16.2738 | 168.0055 | 162.419 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0847 | 0
2016-10-02 23:00 | 0 | 0 | 0 | 0 | -3.5279 | 183.4742 | 106.5365 | -16.5365 | -176.3825 | 166.1353 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-10-03 | 0 | 0 | 0 | 0 | -3.544 | -161.5224 | 105.8849 | -15.8849 | -160.7988 | 157.4387 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-10-03 01:00 | 0 | 0 | 0 | 0 | -3.5601 | -146.519 | 104.3728 | -14.3728 | -145.3623 | 144.5228 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-10-03 02:00 | 0 | 0 | 0 | 0 | -3.5762 | -131.5157 | 102.1198 | -12.1198 | -130.1505 | 130.6127 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0861 | 0
2016-10-03 03:00 | 0 | 0 | 0 | 0 | -3.5923 | -116.5123 | 99.2948 | -9.2948 | -115.1819 | 116.3854 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-10-03 04:00 | 2.7167 | 2.05 | 0.66667 | 0 | -3.6084 | -101.509 | 96.0976 | -6.0976 | -100.4179 | 102.0535 | 0 | 1.5375 | 0.2 | 0 | 0.13583 | 1.6733 | 0 | 0.052292 | 1.0873 | 0.0014919
2016-10-03 05:00 | 5.4333 | 4.1 | 1.3333 | 0 | -3.6245 | -86.5056 | 92.7438 | -2.7438 | -85.7791 | 87.7229 | 0 | 3.075 | 0.2 | 0 | 0.27167 | 3.3467 | -0.3 | -0.19542 | 1.0882 | 0.0029863
2016-10-03 06:00 | 8.15 | 6.15 | 2 | 0 | -3.6406 | -71.5023 | 89.4532 | 0.54677 | -71.1674 | 73.4821 | 0 | 4.6125 | 0.2 | 0 | 0.4075 | 5.02 | -0.4 | -0.24313 | 1.0884 | 0.0044801
2016-10-03 07:00 | 20.8033 | 15.84 | 4.9633 | 79.9424 | -3.6567 | -56.499 | 86.4404 | 3.5596 | -56.4897 | 59.4532 | 40.6301 | 11.88 | 0.2 | 0 | 1.0402 | 53.5503 | 0 | 1.6734 | 1.0816 | 0.047496
2016-10-03 08:00 | 33.4567 | 25.53 | 7.9267 | 74.668 | -3.6728 | -41.4956 | 83.9061 | 6.0939 | -41.6792 | 45.8738 | 51.9869 | 19.1475 | 0.2 | 0 | 1.6728 | 72.8072 | 0.3 | 2.5752 | 1.0785 | 0.064388
2016-10-03 09:00 | 46.11 | 35.22 | 10.89 | 78.4936 | -3.6889 | -26.4923 | 82.0252 | 7.9748 | -26.7116 | 33.333 | 65.5807 | 26.415 | 0.2 | 0 | 2.3055 | 94.3012 | 0.3 | 3.2469 | 1.0761 | 0.083214
2016-10-03 10:00 | 49.7633 | 37.17 | 12.5933 | 79.9158 | -3.705 | -11.489 | 80.9334 | 9.0666 | -11.6117 | 23.5812 | 73.2424 | 27.8775 | 0.2 | 0 | 2.4882 | 103.6081 | 0.6 | 3.8378 | 1.0741 | 0.091251
2016-10-03 11:00 | 53.4167 | 39.12 | 14.2967 | 88.5839 | -3.7211 | 3.5144 | 80.7123 | 9.2877 | 3.5536 | 20.9769 | 82.713 | 29.34 | 0.2 | 0 | 2.6708 | 114.7238 | 1.3 | 4.8851 | 1.0704 | 0.1007
2016-10-03 12:00 | 57.07 | 41.07 | 16 | 106.7479 | -3.7372 | 18.5177 | 81.3797 | 8.6203 | 18.6958 | 27.6246 | 94.5791 | 30.8025 | 0.2 | 0 | 2.8535 | 128.2351 | 1.6 | 5.6073 | 1.0679 | 0.11229
2016-10-03 13:00 | 42.05 | 30.4567 | 11.5933 | 93.6207 | -3.7533 | 33.521 | 82.8866 | 7.1134 | 33.7336 | 39.0511 | 72.7044 | 22.8425 | 0.2 | 0 | 2.1025 | 97.6494 | 1.2 | 4.2515 | 1.0726 | 0.085887
2016-10-03 14:00 | 27.03 | 19.8433 | 7.1867 | 84.5585 | -3.7694 | 48.5243 | 85.1245 | 4.8755 | 48.6191 | 52.199 | 51.8276 | 14.8825 | 0.2 | 0 | 1.3515 | 68.0616 | 0.8 | 2.9269 | 1.0773 | 0.060122
2016-10-03 15:00 | 12.01 | 9.23 | 2.78 | 0 | -3.7855 | 63.5277 | 87.9376 | 2.0624 | 63.3516 | 66.0357 | 0 | 6.9225 | 0.2 | 0 | 0.6005 | 7.523 | -1 | -0.76491 | 1.0902 | 0.0067252
2016-10-03 16:00 | 8.0067 | 6.1533 | 1.8533 | 0 | -3.8016 | 78.531 | 91.1374 | -1.1374 | 77.9783 | 80.1879 | 0 | 4.615 | 0.2 | 0 | 0.40033 | 5.0153 | -0.6 | -0.44327 | 1.0891 | 0.0044788
2016-10-03 17:00 | 4.0033 | 3.0767 | 0.92667 | 0 | -3.8177 | 93.5343 | 94.516 | -4.516 | 92.582 | 94.4886 | 0 | 2.3075 | 0.2 | 0 | 0.20017 | 2.5077 | -0.7 | -0.62164 | 1.0897 | 0.0022407
2016-10-03 18:00 | 0 | 0 | 0 | 0 | -3.8338 | 108.5376 | 97.8556 | -7.8556 | 107.2625 | 108.8396 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-10-03 19:00 | 0 | 0 | 0 | 0 | -3.8499 | 123.5409 | 100.9374 | -10.9374 | 122.1135 | 123.1535 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-10-03 20:00 | 0 | 0 | 0 | 0 | -3.8659 | 138.5442 | 103.5515 | -13.5515 | 137.1992 | 137.2979 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-10-03 21:00 | 0 | 0 | 0 | 0 | -3.882 | 153.5475 | 105.5097 | -15.5097 | 152.5335 | 150.9419 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-10-03 22:00 | 0 | 0 | 0 | 0 | -3.8981 | 168.5508 | 106.6635 | -16.6635 | 168.0697 | 162.7677 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-10-03 23:00 | 0 | 0 | 0 | 0 | -3.9142 | 183.5541 | 106.9216 | -16.9216 | -176.2935 | 166.4898 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-10-04 | 0 | 0 | 0 | 0 | -3.9303 | -161.4426 | 106.2642 | -16.2642 | -160.6862 | 157.61 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-10-04 01:00 | 0 | 0 | 0 | 0 | -3.9464 | -146.4393 | 104.7456 | -14.7456 | -145.2295 | 144.6096 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-10-04 02:00 | 0 | 0 | 0 | 0 | -3.9624 | -131.436 | 102.4865 | -12.4865 | -130.002 | 130.6647 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-10-04 03:00 | 0 | 0 | 0 | 0 | -3.9785 | -116.4328 | 99.6566 | -9.6566 | -115.0229 | 116.4229 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-10-04 04:00 | 1.35 | 1.34 | 0.01 | 0 | -3.9946 | -101.4295 | 96.4565 | -6.4565 | -100.2537 | 102.0875 | 0 | 1.005 | 0.2 | 0 | 0.0675 | 1.0725 | 0 | 0.033516 | 1.0874 | 0.0009563
2016-10-04 05:00 | 2.7 | 2.68 | 0.02 | 0 | -4.0107 | -86.4262 | 93.1022 | -3.1022 | -85.6146 | 87.7612 | 0 | 2.01 | 0.2 | 0 | 0.135 | 2.145 | 0.8 | 0.86703 | 1.0845 | 0.0019075
2016-10-04 06:00 | 4.05 | 4.02 | 0.03 | 0 | -4.0268 | -71.4229 | 89.8135 | 0.18649 | -71.0075 | 73.5326 | 0 | 3.015 | 0.2 | 0 | 0.2025 | 3.2175 | 0.5 | 0.60055 | 1.0854 | 0.0028637
2016-10-04 07:00 | 23.0033 | 15.73 | 7.2733 | 130.4892 | -4.0428 | -56.4197 | 86.8047 | 3.1953 | -56.339 | 59.5264 | 66.1765 | 11.7975 | 0.2 | 0 | 1.1502 | 79.1242 | 1 | 3.4726 | 1.0753 | 0.06977
2016-10-04 08:00 | 41.9567 | 27.44 | 14.5167 | 145.5478 | -4.0589 | -41.4164 | 84.2759 | 5.7241 | -41.5424 | 45.9866 | 101.1306 | 20.58 | 0.2 | 0 | 2.0978 | 123.8084 | 2 | 5.869 | 1.067 | 0.10832
2016-10-04 09:00 | 60.91 | 39.15 | 21.76 | 164.5563 | -4.075 | -26.4131 | 82.4013 | 7.5987 | -26.5928 | 33.5166 | 137.1948 | 29.3625 | 0.2 | 0 | 3.0455 | 169.6028 | 1.5 | 6.8001 | 1.0637 | 0.14793
2016-10-04 10:00 | 56.2167 | 38.1767 | 18.04 | 119.4749 | -4.091 | -11.4099 | 81.3155 | 8.6845 | -11.5142 | 23.8844 | 109.2436 | 28.6325 | 0.2 | 0 | 2.8108 | 140.6869 | 4.2 | 8.5965 | 1.0574 | 0.12199
2016-10-04 11:00 | 51.5233 | 37.2033 | 14.32 | 92.5541 | -4.1071 | 3.5934 | 81.0994 | 8.9006 | 3.6279 | 21.3707 | 86.1903 | 27.9025 | 0.2 | 0 | 2.5762 | 116.669 | 4.5 | 8.1459 | 1.059 | 0.10131
2016-10-04 12:00 | 46.83 | 36.23 | 10.6 | 74.0528 | -4.1232 | 18.5966 | 81.7704 | 8.2296 | 18.7469 | 27.9684 | 65.4039 | 27.1725 | 0.2 | 0 | 2.3415 | 94.9179 | 4.4 | 7.3662 | 1.0617 | 0.082636
2016-10-04 13:00 | 33.58 | 26.3767 | 7.2033 | 61.5524 | -4.1392 | 33.5999 | 83.2794 | 6.7206 | 33.7635 | 39.3283 | 47.6125 | 19.7825 | 0.2 | 0 | 1.679 | 69.074 | 4.3 | 6.4586 | 1.0649 | 0.060316
2016-10-04 14:00 | 20.33 | 16.5233 | 3.8067 | 48.7143 | -4.1553 | 48.6031 | 85.5182 | 4.4818 | 48.6311 | 52.4336 | 29.7002 | 12.3925 | 0.2 | 0 | 1.0165 | 43.1092 | 4.2 | 5.5472 | 1.0681 | 0.037756
2016-10-04 15:00 | 7.08 | 6.67 | 0.41 | 0 | -4.1714 | 63.6064 | 88.3314 | 1.6686 | 63.3505 | 66.2445 | 0 | 5.0025 | 0.2 | 0 | 0.354 | 5.3565 | 4.6 | 4.7674 | 1.0708 | 0.0047034
2016-10-04 16:00 | 4.72 | 4.4467 | 0.27333 | 0 | -4.1874 | 78.6096 | 91.5311 | -1.5311 | 77.9695 | 80.3817 | 0 | 3.335 | 0.2 | 0 | 0.236 | 3.571 | 4.3 | 4.4116 | 1.0721 | 0.0031392
2016-10-04 17:00 | 2.36 | 2.2233 | 0.13667 | 0 | -4.2035 | 93.6129 | 94.9096 | -4.9096 | 92.5712 | 94.6748 | 0 | 1.6675 | 0.2 | 0 | 0.118 | 1.7855 | 4.8 | 4.8558 | 1.0705 | 0.0015673
2016-10-04 18:00 | 0 | 0 | 0 | 0 | -4.2196 | 108.6161 | 98.2492 | -8.2492 | 107.2556 | 109.0247 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0714 | 0
2016-10-04 19:00 | 0 | 0 | 0 | 0 | -4.2356 | 123.6193 | 101.3311 | -11.3311 | 122.1165 | 123.3451 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.8 | 4.8 | 1.0707 | 0
2016-10-04 20:00 | 0 | 0 | 0 | 0 | -4.2517 | 138.6226 | 103.9446 | -13.9446 | 137.2177 | 137.5079 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.7 | 4.7 | 1.0711 | 0
2016-10-04 21:00 | 0 | 0 | 0 | 0 | -4.2677 | 153.6258 | 105.9015 | -15.9015 | 152.5725 | 151.1941 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.3 | 5.3 | 1.069 | 0
2016-10-04 22:00 | 0 | 0 | 0 | 0 | -4.2838 | 168.629 | 107.0524 | -17.0524 | 168.1324 | 163.1127 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.8 | 5.8 | 1.0672 | 0
2016-10-04 23:00 | 0 | 0 | 0 | 0 | -4.2998 | 183.6322 | 107.3061 | -17.3061 | -176.206 | 166.8419 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.8 | 5.8 | 1.0672 | 0
2016-10-05 | 0 | 0 | 0 | 0 | -4.3159 | -161.3645 | 106.6428 | -16.6428 | -160.5751 | 157.7769 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.8 | 5.8 | 1.0672 | 0
2016-10-05 01:00 | 0 | 0 | 0 | 0 | -4.3319 | -146.3613 | 105.1179 | -15.1179 | -145.0981 | 144.6941 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6 | 6 | 1.0665 | 0
2016-10-05 02:00 | 0 | 0 | 0 | 0 | -4.348 | -131.3581 | 102.8527 | -12.8527 | -129.8551 | 130.7158 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6.5 | 6.5 | 1.0648 | 0
2016-10-05 03:00 | 0 | 0 | 0 | 0 | -4.364 | -116.3549 | 100.018 | -10.018 | -114.8656 | 116.4606 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6.2 | 6.2 | 1.0658 | 0
2016-10-05 04:00 | 1.1467 | 1.1467 | 0 | 0 | -4.3801 | -101.3517 | 96.815 | -6.815 | -100.0912 | 102.1224 | 0 | 0.86 | 0.2 | 0 | 0.057333 | 0.91733 | 6.3 | 6.3287 | 1.0653 | 0.00080137
2016-10-05 05:00 | 2.2933 | 2.2933 | 0 | 0 | -4.3961 | -86.3485 | 93.4603 | -3.4603 | -85.4519 | 87.8011 | 0 | 1.72 | 0.2 | 0 | 0.11467 | 1.8347 | 5.5 | 5.5573 | 1.068 | 0.0016068
2016-10-05 06:00 | 3.44 | 3.44 | 0 | 0 | -4.4122 | -71.3453 | 90.1735 | -0.17348 | -70.8495 | 73.5854 | 0 | 2.58 | 0.2 | 0 | 0.172 | 2.752 | 6 | 6.086 | 1.0662 | 0.002406
2016-10-05 07:00 | 15.2067 | 13.4167 | 1.79 | 0 | -4.4282 | -56.3421 | 87.1687 | 2.8313 | -56.1904 | 59.6025 | 0 | 10.0625 | 0.2 | 0 | 0.76033 | 10.8228 | 5.8 | 6.1382 | 1.066 | 0.0094606
2016-10-05 08:00 | 26.9733 | 23.3933 | 3.58 | 38.3625 | -4.4443 | -41.3389 | 84.6453 | 5.3547 | -41.4076 | 46.103 | 26.5992 | 17.545 | 0.2 | 0 | 1.3487 | 45.4928 | 5.4 | 6.8217 | 1.0636 | 0.039678
2016-10-05 09:00 | 38.74 | 33.37 | 5.37 | 42.709 | -4.4603 | -26.3357 | 82.7768 | 7.2232 | -26.4761 | 33.7043 | 35.5302 | 25.0275 | 0.2 | 0 | 1.937 | 62.4947 | 5.7 | 7.653 | 1.0607 | 0.054357
2016-10-05 10:00 | 42.8967 | 33.7233 | 9.1733 | 63.5229 | -4.4763 | -11.3325 | 81.6969 | 8.3031 | -11.4188 | 24.1902 | 57.945 | 25.2925 | 0.2 | 0 | 2.1448 | 85.3823 | 5.1 | 7.7682 | 1.0603 | 0.074236
2016-10-05 11:00 | 47.0533 | 34.0767 | 12.9767 | 87.6474 | -4.4924 | 3.6706 | 81.4858 | 8.5142 | 3.7002 | 21.7633 | 81.4002 | 25.5575 | 0.2 | 0 | 2.3527 | 109.3104 | 5 | 8.4159 | 1.058 | 0.094837
2016-10-05 12:00 | 51.21 | 34.43 | 16.78 | 123.0165 | -4.5084 | 18.6738 | 82.1602 | 7.8398 | 18.7961 | 28.3117 | 108.3013 | 25.8225 | 0.2 | 0 | 2.5605 | 136.6843 | 4.7 | 8.9714 | 1.0561 | 0.11837
2016-10-05 13:00 | 37.7667 | 25.5933 | 12.1733 | 110.4319 | -4.5244 | 33.677 | 83.6712 | 6.3288 | 33.7915 | 39.6051 | 85.0829 | 19.195 | 0.2 | 0 | 1.8883 | 106.1663 | 4.4 | 7.7177 | 1.0605 | 0.092322
2016-10-05 14:00 | 24.3233 | 16.7567 | 7.5667 | 106.11 | -4.5405 | 48.6802 | 85.9108 | 4.0892 | 48.6415 | 52.6674 | 64.3494 | 12.5675 | 0.2 | 0 | 1.2162 | 78.1331 | 3.9 | 6.3417 | 1.0653 | 0.068253
2016-10-05 15:00 | 10.88 | 7.92 | 2.96 | 0 | -4.5565 | 63.6833 | 88.724 | 1.276 | 63.3478 | 66.4523 | 0 | 5.94 | 0.2 | 0 | 0.544 | 6.484 | 3.7 | 3.9026 | 1.0738 | 0.0057095
2016-10-05 16:00 | 7.2533 | 5.28 | 1.9733 | 0 | -4.5725 | 78.6865 | 91.9236 | -1.9236 | 77.959 | 80.5738 | 0 | 3.96 | 0.2 | 0 | 0.36267 | 4.3227 | 4.3 | 4.4351 | 1.072 | 0.0037997
2016-10-05 17:00 | 3.6267 | 2.64 | 0.98667 | 0 | -4.5886 | 93.6897 | 95.302 | -5.302 | 92.5587 | 94.8587 | 0 | 1.98 | 0.2 | 0 | 0.18133 | 2.1613 | 4.8 | 4.8675 | 1.0705 | 0.0018972
2016-10-05 18:00 | 0 | 0 | 0 | 0 | -4.6046 | 108.6928 | 98.6417 | -8.6417 | 107.247 | 109.207 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.8 | 3.8 | 1.0742 | 0
2016-10-05 19:00 | 0 | 0 | 0 | 0 | -4.6206 | 123.696 | 101.7235 | -11.7235 | 122.1178 | 123.5334 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-10-05 20:00 | 0 | 0 | 0 | 0 | -4.6366 | 138.6991 | 104.3368 | -14.3368 | 137.2345 | 137.7138 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-10-05 21:00 | 0 | 0 | 0 | 0 | -4.6526 | 153.7023 | 106.2922 | -16.2922 | 152.6097 | 151.4414 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.6 | 3.6 | 1.0749 | 0
2016-10-05 22:00 | 0 | 0 | 0 | 0 | -4.6687 | 168.7054 | 107.4404 | -17.4404 | 168.1934 | 163.4539 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-10-05 23:00 | 0 | 0 | 0 | 0 | -4.6847 | 183.7086 | 107.6897 | -17.6897 | -176.1201 | 167.1915 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0784 | 0
2016-10-06 | 0 | 0 | 0 | 0 | -4.7007 | -161.2883 | 107.0208 | -17.0208 | -160.4655 | 157.9394 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-10-06 01:00 | 0 | 0 | 0 | 0 | -4.7167 | -146.2851 | 105.4896 | -15.4896 | -144.9683 | 144.7763 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0801 | 0
2016-10-06 02:00 | 0 | 0 | 0 | 0 | -4.7327 | -131.282 | 103.2184 | -13.2184 | -129.7097 | 130.7662 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0816 | 0
2016-10-06 03:00 | 0 | 0 | 0 | 0 | -4.7487 | -116.2789 | 100.3789 | -10.3789 | -114.7099 | 116.4985 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.083 | 0
2016-10-06 04:00 | 1.5967 | 1.2867 | 0.31 | 0 | -4.7648 | -101.2757 | 97.1731 | -7.1731 | -99.9305 | 102.1583 | 0 | 0.965 | 0.2 | 0 | 0.079833 | 1.0448 | 0.9 | 0.93265 | 1.0842 | 0.00092893
2016-10-06 05:00 | 3.1933 | 2.5733 | 0.62 | 0 | -4.7808 | -86.2726 | 93.8179 | -3.8179 | -85.2912 | 87.8427 | 0 | 1.93 | 0.2 | 0 | 0.15967 | 2.0897 | 0.9 | 0.9653 | 1.0841 | 0.0018577
2016-10-06 06:00 | 4.79 | 3.86 | 0.93 | 0 | -4.7968 | -71.2695 | 90.5331 | -0.53305 | -70.6935 | 73.6405 | 0 | 2.895 | 0.2 | 0 | 0.2395 | 3.1345 | 0.1 | 0.19795 | 1.0868 | 0.0027934
2016-10-06 07:00 | 18.63 | 13.4267 | 5.2033 | 0 | -4.8128 | -56.2664 | 87.5322 | 2.4678 | -56.0439 | 59.6816 | 0 | 10.07 | 0.2 | 0 | 0.9315 | 11.0015 | 0 | 0.3438 | 1.0863 | 0.0097997
2016-10-06 08:00 | 32.47 | 22.9933 | 9.4767 | 109.0432 | -4.8288 | -41.2633 | 85.0143 | 4.9857 | -41.2751 | 46.223 | 75.4419 | 17.245 | 0.2 | 0 | 1.6235 | 94.3104 | 1 | 3.9472 | 1.0737 | 0.083033
2016-10-06 09:00 | 46.31 | 32.56 | 13.75 | 115.314 | -4.8448 | -26.2602 | 83.1518 | 6.8482 | -26.3616 | 33.8961 | 95.7164 | 24.42 | 0.2 | 0 | 2.3155 | 122.4519 | 1.6 | 5.4266 | 1.0685 | 0.10729
2016-10-06 10:00 | 46.9233 | 33.2833 | 13.64 | 98.9612 | -4.8608 | -11.257 | 82.0776 | 7.9224 | -11.3255 | 24.4984 | 90.052 | 24.9625 | 0.2 | 0 | 2.3462 | 117.3607 | 1.3 | 4.9675 | 1.0701 | 0.10298
2016-10-06 11:00 | 47.5367 | 34.0067 | 13.53 | 95.6871 | -4.8768 | 3.7461 | 81.8712 | 8.1288 | 3.7704 | 22.1549 | 88.6223 | 25.505 | 0.2 | 0 | 2.3768 | 116.5042 | 2.2 | 5.8408 | 1.0671 | 0.10194
2016-10-06 12:00 | 48.15 | 34.73 | 13.42 | 103.4867 | -4.8928 | 18.7492 | 82.549 | 7.451 | 18.8433 | 28.6542 | 90.8126 | 26.0475 | 0.2 | 0 | 2.4075 | 119.2676 | 1.7 | 5.4271 | 1.0685 | 0.1045
2016-10-06 13:00 | 33.6333 | 24.6867 | 8.9467 | 86.4801 | -4.9088 | 33.7523 | 84.0619 | 5.9381 | 33.8176 | 39.8816 | 66.3623 | 18.515 | 0.2 | 0 | 1.6817 | 86.559 | 1.7 | 4.405 | 1.0721 | 0.076095
2016-10-06 14:00 | 19.1167 | 14.6433 | 4.4733 | 69.361 | -4.9248 | 48.7553 | 86.3022 | 3.6978 | 48.65 | 52.9005 | 41.8386 | 10.9825 | 0.2 | 0 | 0.95583 | 53.7769 | 2.7 | 4.3805 | 1.0722 | 0.047279
2016-10-06 15:00 | 4.6 | 4.6 | 0 | 0 | -4.9408 | 63.7584 | 89.1155 | 0.8845 | 63.3434 | 66.6587 | 0 | 3.45 | 0.2 | 0 | 0.23 | 3.68 | 2.7 | 2.815 | 1.0776 | 0.0032519
2016-10-06 16:00 | 3.0667 | 3.0667 | 0 | 0 | -4.9567 | 78.7615 | 92.3148 | -2.3148 | 77.9469 | 80.7641 | 0 | 2.3 | 0.2 | 0 | 0.15333 | 2.4533 | 2 | 2.0767 | 1.0802 | 0.0021731
2016-10-06 17:00 | 1.5333 | 1.5333 | 0 | 0 | -4.9727 | 93.7646 | 95.6931 | -5.6931 | 92.5445 | 95.0404 | 0 | 1.15 | 0.2 | 0 | 0.076667 | 1.2267 | 2.4 | 2.4383 | 1.079 | 0.0010853
2016-10-06 18:00 | 0 | 0 | 0 | 0 | -4.9887 | 108.7677 | 99.0329 | -9.0329 | 107.2367 | 109.3865 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-10-06 19:00 | 0 | 0 | 0 | 0 | -5.0047 | 123.7708 | 102.1148 | -12.1148 | 122.1173 | 123.7181 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-10-06 20:00 | 0 | 0 | 0 | 0 | -5.0207 | 138.7738 | 104.7277 | -14.7277 | 137.2495 | 137.9154 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.0735 | 0
2016-10-06 21:00 | 0 | 0 | 0 | 0 | -5.0367 | 153.7769 | 106.6819 | -16.6819 | 152.6451 | 151.6835 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.5 | 5.5 | 1.0682 | 0
2016-10-06 22:00 | 0 | 0 | 0 | 0 | -5.0527 | 168.78 | 107.8274 | -17.8274 | 168.2526 | 163.7908 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.3 | 5.3 | 1.069 | 0
2016-10-06 23:00 | 0 | 0 | 0 | 0 | -5.0686 | 183.783 | 108.0725 | -18.0725 | -176.0359 | 167.5382 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.3 | 5.3 | 1.069 | 0
2016-10-07 | 0 | 0 | 0 | 0 | -5.0846 | -161.2139 | 107.398 | -17.398 | -160.3577 | 158.0975 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.5 | 5.5 | 1.0682 | 0
2016-10-07 01:00 | 0 | 0 | 0 | 0 | -5.1006 | -146.2108 | 105.8606 | -15.8606 | -144.8402 | 144.8564 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.6 | 5.6 | 1.0679 | 0
2016-10-07 02:00 | 0 | 0 | 0 | 0 | -5.1166 | -131.2078 | 103.5835 | -13.5835 | -129.5661 | 130.816 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.5 | 5.5 | 1.0682 | 0
2016-10-07 03:00 | 0 | 0 | 0 | 0 | -5.1325 | -116.2047 | 100.7393 | -10.7393 | -114.5561 | 116.5368 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.9 | 5.9 | 1.0669 | 0
2016-10-07 04:00 | 1.1033 | 0.95 | 0.15333 | 0 | -5.1485 | -101.2017 | 97.5308 | -7.5308 | -99.7717 | 102.1953 | 0 | 0.7125 | 0.2 | 0 | 0.055167 | 0.76767 | 5.1 | 5.124 | 1.0696 | 0.00067328
2016-10-07 05:00 | 2.2067 | 1.9 | 0.30667 | 0 | -5.1645 | -86.1987 | 94.1751 | -4.1751 | -85.1325 | 87.8861 | 0 | 1.425 | 0.2 | 0 | 0.11033 | 1.5353 | 4.9 | 4.948 | 1.0702 | 0.0013473
2016-10-07 06:00 | 3.31 | 2.85 | 0.46 | 0 | -5.1804 | -71.1956 | 90.8922 | -0.89216 | -70.5396 | 73.698 | 0 | 2.1375 | 0.2 | 0 | 0.1655 | 2.303 | 5.2 | 5.272 | 1.069 | 0.0020189
2016-10-07 07:00 | 24.6967 | 13.6967 | 11 | 0 | -5.1964 | -56.1926 | 87.8953 | 2.1047 | -55.8996 | 59.7636 | 0 | 10.2725 | 0.2 | 0 | 1.2348 | 11.5073 | 4.8 | 5.1596 | 1.0694 | 0.010091
2016-10-07 08:00 | 46.0833 | 24.5433 | 21.54 | 267.5738 | -5.2124 | -41.1895 | 85.3826 | 4.6174 | -41.1448 | 46.3466 | 184.7045 | 18.4075 | 0.2 | 0 | 2.3042 | 205.4162 | 5.4 | 11.8193 | 1.0461 | 0.17621
2016-10-07 09:00 | 67.47 | 35.39 | 32.08 | 284.5187 | -5.2283 | -26.1865 | 83.526 | 6.474 | -26.2494 | 34.0917 | 235.6218 | 26.5425 | 0.2 | 0 | 3.3735 | 265.5378 | 5 | 13.2981 | 1.041 | 0.22666
2016-10-07 10:00 | 72.8533 | 35.5 | 37.3533 | 284.5713 | -5.2443 | -11.1835 | 82.4575 | 7.5425 | -11.2345 | 24.809 | 258.3088 | 26.625 | 0.2 | 0 | 3.6427 | 288.5764 | 4.7 | 13.718 | 1.0395 | 0.24598
2016-10-07 11:00 | 78.2367 | 35.61 | 42.6267 | 316.3355 | -5.2602 | 3.8195 | 82.2558 | 7.7442 | 3.8385 | 22.5452 | 292.1604 | 26.7075 | 0.2 | 0 | 3.9118 | 322.7797 | 4.4 | 14.4869 | 1.0368 | 0.27442
2016-10-07 12:00 | 83.62 | 35.72 | 47.9 | 389.541 | -5.2762 | 18.8225 | 82.9367 | 7.0633 | 18.8885 | 28.9959 | 340.7137 | 26.79 | 0.2 | 0 | 4.181 | 371.6847 | 4.4 | 16.0151 | 1.0314 | 0.31437
2016-10-07 13:00 | 58.9067 | 25.9067 | 33 | 341.3001 | -5.2922 | 33.8256 | 84.4515 | 5.5485 | 33.8419 | 40.1574 | 260.8474 | 19.43 | 0.2 | 0 | 2.9453 | 283.2227 | 4.4 | 13.2507 | 1.0411 | 0.24179
2016-10-07 14:00 | 34.1933 | 16.0933 | 18.1 | 313.7094 | -5.3081 | 48.8286 | 86.6924 | 3.3076 | 48.6568 | 53.1327 | 188.2145 | 12.07 | 0.2 | 0 | 1.7097 | 201.9942 | 4.5 | 10.8123 | 1.0497 | 0.17386
2016-10-07 15:00 | 9.48 | 6.28 | 3.2 | 0 | -5.3241 | 63.8316 | 89.5056 | 0.49439 | 63.3372 | 66.8637 | 0 | 4.71 | 0.2 | 0 | 0.474 | 5.184 | 4.8 | 4.962 | 1.0701 | 0.004549
2016-10-07 16:00 | 6.32 | 4.1867 | 2.1333 | 0 | -5.34 | 78.8346 | 92.7047 | -2.7047 | 77.933 | 80.9526 | 0 | 3.14 | 0.2 | 0 | 0.316 | 3.456 | 4.7 | 4.808 | 1.0707 | 0.0030342
2016-10-07 17:00 | 3.16 | 2.0933 | 1.0667 | 0 | -5.356 | 93.8376 | 96.0828 | -6.0828 | 92.5286 | 95.2197 | 0 | 1.57 | 0.2 | 0 | 0.158 | 1.728 | 5 | 5.054 | 1.0698 | 0.0015159
2016-10-07 18:00 | 0 | 0 | 0 | 0 | -5.3719 | 108.8406 | 99.4227 | -9.4227 | 107.2246 | 109.563 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.9 | 4.9 | 1.0703 | 0
2016-10-07 19:00 | 0 | 0 | 0 | 0 | -5.3878 | 123.8436 | 102.5047 | -12.5047 | 122.1149 | 123.8992 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.3 | 5.3 | 1.069 | 0
2016-10-07 20:00 | 0 | 0 | 0 | 0 | -5.4038 | 138.8466 | 105.1174 | -15.1174 | 137.2627 | 138.1126 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.4 | 5.4 | 1.0686 | 0
2016-10-07 21:00 | 0 | 0 | 0 | 0 | -5.4197 | 153.8495 | 107.0704 | -17.0704 | 152.6787 | 151.9203 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.2 | 5.2 | 1.0693 | 0
2016-10-07 22:00 | 0 | 0 | 0 | 0 | -5.4357 | 168.8525 | 108.2133 | -18.2133 | 168.31 | 164.1231 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.9 | 4.9 | 1.0703 | 0
2016-10-07 23:00 | 0 | 0 | 0 | 0 | -5.4516 | 183.8555 | 108.4542 | -18.4542 | -175.9536 | 167.882 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.4 | 4.4 | 1.0721 | 0
2016-10-08 | 0 | 0 | 0 | 0 | -5.4675 | -161.1415 | 107.7743 | -17.7743 | -160.2516 | 158.2512 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-10-08 01:00 | 0 | 0 | 0 | 0 | -5.4835 | -146.1385 | 106.2308 | -16.2308 | -144.7139 | 144.9344 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0745 | 0
2016-10-08 02:00 | 0 | 0 | 0 | 0 | -5.4994 | -131.1356 | 103.9479 | -13.9479 | -129.4243 | 130.8651 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0738 | 0
2016-10-08 03:00 | 0 | 0 | 0 | 0 | -5.5153 | -116.1326 | 101.099 | -11.099 | -114.4041 | 116.5755 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.6 | 3.6 | 1.0749 | 0
2016-10-08 04:00 | 1.1533 | 0.9 | 0.25333 | 0 | -5.5312 | -101.1297 | 97.8878 | -7.8878 | -99.6149 | 102.2335 | 0 | 0.675 | 0.2 | 0 | 0.057667 | 0.73267 | 3.7 | 3.7229 | 1.0745 | 0.00064553
2016-10-08 05:00 | 2.3067 | 1.8 | 0.50667 | 0 | -5.5472 | -86.1267 | 94.5318 | -4.5318 | -84.9759 | 87.9312 | 0 | 1.35 | 0.2 | 0 | 0.11533 | 1.4653 | 3.5 | 3.5458 | 1.0751 | 0.0012918
2016-10-08 06:00 | 3.46 | 2.7 | 0.76 | 0 | -5.5631 | -71.1237 | 91.2507 | -1.2507 | -70.388 | 73.7579 | 0 | 2.025 | 0.2 | 0 | 0.173 | 2.198 | 3.4 | 3.4687 | 1.0754 | 0.0019382
2016-10-08 07:00 | 20.5333 | 12.6267 | 7.9067 | 0 | -5.579 | -56.1208 | 88.2577 | 1.7423 | -55.7576 | 59.8487 | 0 | 9.47 | 0.2 | 0 | 1.0267 | 10.4967 | 3.5 | 3.828 | 1.0741 | 0.0092451
2016-10-08 08:00 | 37.6067 | 22.5533 | 15.0533 | 203.1398 | -5.5949 | -41.1178 | 85.7503 | 4.2497 | -41.0169 | 46.4739 | 139.8994 | 16.915 | 0.2 | 0 | 1.8803 | 158.6947 | 4.1 | 9.0592 | 1.0558 | 0.13739
2016-10-08 09:00 | 54.68 | 32.48 | 22.2 | 208.8963 | -5.6108 | -26.1149 | 83.8995 | 6.1005 | -26.1395 | 34.2912 | 172.5871 | 24.36 | 0.2 | 0 | 2.734 | 199.6811 | 4 | 10.24 | 1.0517 | 0.1722
2016-10-08 10:00 | 59.8067 | 33.3567 | 26.45 | 212.1057 | -5.6268 | -11.112 | 82.8365 | 7.1635 | -11.1459 | 25.1215 | 192.0424 | 25.0175 | 0.2 | 0 | 2.9903 | 220.0503 | 4.4 | 11.2766 | 1.048 | 0.18911
2016-10-08 11:00 | 64.9333 | 34.2333 | 30.7 | 239.6251 | -5.6427 | 3.891 | 82.6392 | 7.3608 | 3.9043 | 22.9341 | 220.6836 | 25.675 | 0.2 | 0 | 3.2467 | 249.6052 | 4.4 | 12.2002 | 1.0448 | 0.21385
2016-10-08 12:00 | 70.06 | 35.11 | 34.95 | 300.6012 | -5.6586 | 18.8939 | 83.3233 | 6.6767 | 18.9316 | 29.3365 | 262.0512 | 26.3325 | 0.2 | 0 | 3.503 | 291.8867 | 4.2 | 13.3215 | 1.0409 | 0.24913
2016-10-08 13:00 | 48.9133 | 24.9933 | 23.92 | 265.9465 | -5.6745 | 33.8968 | 84.8397 | 5.1603 | 33.8641 | 40.4324 | 202.4308 | 18.745 | 0.2 | 0 | 2.4457 | 223.6215 | 4.3 | 11.2882 | 1.048 | 0.19217
2016-10-08 14:00 | 27.7667 | 14.8767 | 12.89 | 0 | -5.6904 | 48.8998 | 87.0811 | 2.9189 | 48.6616 | 53.3637 | 0 | 11.1575 | 0.2 | 0 | 1.3883 | 12.5458 | 4.1 | 4.4921 | 1.0718 | 0.011026
2016-10-08 15:00 | 6.62 | 4.76 | 1.86 | 0 | -5.7063 | 63.9027 | 89.8943 | 0.10574 | 63.3291 | 67.0672 | 0 | 3.57 | 0.2 | 0 | 0.331 | 3.901 | 4.2 | 4.3219 | 1.0724 | 0.0034303
2016-10-08 16:00 | 4.4133 | 3.1733 | 1.24 | 0 | -5.7222 | 78.9056 | 93.093 | -3.093 | 77.9172 | 81.139 | 0 | 2.38 | 0.2 | 0 | 0.22067 | 2.6007 | 4 | 4.0813 | 1.0732 | 0.0022887
2016-10-08 17:00 | 2.2067 | 1.5867 | 0.62 | 0 | -5.7381 | 93.9085 | 96.471 | -6.471 | 92.5107 | 95.3964 | 0 | 1.19 | 0.2 | 0 | 0.11033 | 1.3003 | 4.1 | 4.1406 | 1.073 | 0.0011441
2016-10-08 18:00 | 0 | 0 | 0 | 0 | -5.754 | 108.9114 | 99.811 | -9.811 | 107.2105 | 109.7364 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.3 | 4.3 | 1.0724 | 0
2016-10-08 19:00 | 0 | 0 | 0 | 0 | -5.7699 | 123.9143 | 102.8932 | -12.8932 | 122.1106 | 124.0766 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-10-08 20:00 | 0 | 0 | 0 | 0 | -5.7858 | 138.9172 | 105.5056 | -15.5056 | 137.2738 | 138.3052 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0738 | 0
2016-10-08 21:00 | 0 | 0 | 0 | 0 | -5.8017 | 153.9201 | 107.4576 | -17.4576 | 152.7103 | 152.1515 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.8 | 3.8 | 1.0742 | 0
2016-10-08 22:00 | 0 | 0 | 0 | 0 | -5.8176 | 168.923 | 108.598 | -18.598 | 168.3654 | 164.4506 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0745 | 0
2016-10-08 23:00 | 0 | 0 | 0 | 0 | -5.8334 | 183.9259 | 108.8349 | -18.8349 | -175.8731 | 168.2226 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0745 | 0
2016-10-09 | 0 | 0 | 0 | 0 | -5.8493 | -161.0712 | 108.1496 | -18.1496 | -160.1475 | 158.4005 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0738 | 0
2016-10-09 01:00 | 0 | 0 | 0 | 0 | -5.8652 | -146.0683 | 106.6001 | -16.6001 | -144.5895 | 145.0104 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-10-09 02:00 | 0 | 0 | 0 | 0 | -5.8811 | -131.0654 | 104.3114 | -14.3114 | -129.2845 | 130.9137 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-10-09 03:00 | 0 | 0 | 0 | 0 | -5.897 | -116.0626 | 101.4581 | -11.4581 | -114.2542 | 116.6146 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0763 | 0
2016-10-09 04:00 | 0.91 | 0.70667 | 0.20333 | 0 | -5.9129 | -101.0597 | 98.2442 | -8.2442 | -99.4602 | 102.2729 | 0 | 0.53 | 0.2 | 0 | 0.0455 | 0.5755 | 3.5 | 3.518 | 1.0752 | 0.00050739
2016-10-09 05:00 | 1.82 | 1.4133 | 0.40667 | 0 | -5.9287 | -86.0568 | 94.8878 | -4.8878 | -84.8215 | 87.9782 | 0 | 1.06 | 0.2 | 0 | 0.091 | 1.151 | 3.5 | 3.536 | 1.0751 | 0.0010147
2016-10-09 06:00 | 2.73 | 2.12 | 0.61 | 0 | -5.9446 | -71.054 | 91.6086 | -1.6086 | -70.2387 | 73.8201 | 0 | 1.59 | 0.2 | 0 | 0.1365 | 1.7265 | 3.5 | 3.554 | 1.0751 | 0.001522
2016-10-09 07:00 | 21.2067 | 11.5133 | 9.6933 | 0 | -5.9605 | -56.0511 | 88.6194 | 1.3806 | -55.618 | 59.9367 | 0 | 8.635 | 0.2 | 0 | 1.0603 | 9.6953 | 3.6 | 3.903 | 1.0738 | 0.0085372
2016-10-09 08:00 | 39.6833 | 20.9067 | 18.7767 | 277.2861 | -5.9763 | -41.0482 | 86.1172 | 3.8828 | -40.8914 | 46.6047 | 190.5034 | 15.68 | 0.2 | 0 | 1.9842 | 208.1676 | 3.6 | 10.1052 | 1.0521 | 0.1796
2016-10-09 09:00 | 58.16 | 30.3 | 27.86 | 279.1451 | -5.9922 | -26.0454 | 84.2721 | 5.7279 | -26.0321 | 34.4943 | 230.0665 | 22.725 | 0.2 | 0 | 2.908 | 255.6995 | 3.9 | 11.8906 | 1.0459 | 0.21929
2016-10-09 10:00 | 59.8533 | 31.3233 | 28.53 | 241.4636 | -6.0081 | -11.0425 | 83.2144 | 6.7856 | -11.0596 | 25.436 | 218.0574 | 23.4925 | 0.2 | 0 | 2.9927 | 244.5426 | 3.6 | 11.242 | 1.0482 | 0.21018
2016-10-09 11:00 | 61.5467 | 32.3467 | 29.2 | 240.3359 | -6.0239 | 3.9603 | 83.0215 | 6.9785 | 3.9678 | 23.3215 | 220.6999 | 24.26 | 0.2 | 0 | 3.0773 | 248.0372 | 3.7 | 11.4512 | 1.0474 | 0.21304
2016-10-09 12:00 | 63.24 | 33.37 | 29.87 | 272.5713 | -6.0398 | 18.9631 | 83.7085 | 6.2915 | 18.9725 | 29.676 | 236.8206 | 25.0275 | 0.2 | 0 | 3.162 | 265.0101 | 3.6 | 11.8816 | 1.0459 | 0.22729
2016-10-09 13:00 | 43.9933 | 23.5933 | 20.4 | 245.1417 | -6.0557 | 33.966 | 85.2265 | 4.7735 | 33.8842 | 40.7066 | 185.832 | 17.695 | 0.2 | 0 | 2.1997 | 205.7267 | 4.2 | 10.629 | 1.0503 | 0.17718
2016-10-09 14:00 | 24.7467 | 13.8167 | 10.93 | 0 | -6.0715 | 48.9688 | 87.4684 | 2.5316 | 48.6644 | 53.5936 | 0 | 10.3625 | 0.2 | 0 | 1.2373 | 11.5998 | 4.4 | 4.7625 | 1.0708 | 0.010186
2016-10-09 15:00 | 5.5 | 4.04 | 1.46 | 0 | -6.0874 | 63.9716 | 90.2813 | -0.28133 | 63.3191 | 67.2691 | 0 | 3.03 | 0.2 | 0 | 0.275 | 3.305 | 4.6 | 4.7033 | 1.071 | 0.0029026
2016-10-09 16:00 | 3.6667 | 2.6933 | 0.97333 | 0 | -6.1032 | 78.9745 | 93.4798 | -3.4798 | 77.8995 | 81.3232 | 0 | 2.02 | 0.2 | 0 | 0.18333 | 2.2033 | 4.6 | 4.6689 | 1.0712 | 0.0019353
2016-10-09 17:00 | 1.8333 | 1.3467 | 0.48667 | 0 | -6.1191 | 93.9773 | 96.8576 | -6.8576 | 92.4909 | 95.5705 | 0 | 1.01 | 0.2 | 0 | 0.091667 | 1.1017 | 4.1 | 4.1344 | 1.073 | 0.00096934
2016-10-09 18:00 | 0 | 0 | 0 | 0 | -6.1349 | 108.9801 | 100.1976 | -10.1976 | 107.1945 | 109.9066 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.4 | 4.4 | 1.0721 | 0
2016-10-09 19:00 | 0 | 0 | 0 | 0 | -6.1508 | 123.9829 | 103.2801 | -13.2801 | 122.1042 | 124.2501 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0738 | 0
2016-10-09 20:00 | 0 | 0 | 0 | 0 | -6.1666 | 138.9857 | 105.8924 | -15.8924 | 137.2829 | 138.493 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0714 | 0
2016-10-09 21:00 | 0 | 0 | 0 | 0 | -6.1824 | 153.9885 | 107.8434 | -17.8434 | 152.7398 | 152.377 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0714 | 0
2016-10-09 22:00 | 0 | 0 | 0 | 0 | -6.1983 | 168.9914 | 108.9814 | -18.9814 | 168.4188 | 164.773 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0738 | 0
2016-10-09 23:00 | 0 | 0 | 0 | 0 | -6.2141 | 183.9942 | 109.2144 | -19.2144 | -175.7947 | 168.5599 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-10-10 | 0 | 0 | 0 | 0 | -6.2299 | -161.0031 | 108.5238 | -18.5238 | -160.0453 | 158.5454 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0738 | 0
2016-10-10 01:00 | 0 | 0 | 0 | 0 | -6.2458 | -146.0003 | 106.9684 | -16.9684 | -144.4671 | 145.0845 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.8 | 3.8 | 1.0742 | 0
2016-10-10 02:00 | 0 | 0 | 0 | 0 | -6.2616 | -130.9975 | 104.6741 | -14.6741 | -129.1467 | 130.9619 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0714 | 0
2016-10-10 03:00 | 0 | 0 | 0 | 0 | -6.2774 | -115.9947 | 101.8163 | -11.8163 | -114.1065 | 116.6543 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.1 | 5.1 | 1.0696 | 0
2016-10-10 04:00 | 0.48333 | 0.40667 | 0.076667 | 0 | -6.2933 | -100.9919 | 98.5999 | -8.5999 | -99.3077 | 102.3135 | 0 | 0.305 | 0.2 | 0 | 0.024167 | 0.32917 | 5.3 | 5.3103 | 1.0689 | 0.00028852
2016-10-10 05:00 | 0.96667 | 0.81333 | 0.15333 | 0 | -6.3091 | -85.9891 | 95.2431 | -5.2431 | -84.6694 | 88.027 | 0 | 0.61 | 0.2 | 0 | 0.048333 | 0.65833 | 5.6 | 5.6206 | 1.0678 | 0.00057645
2016-10-10 06:00 | 1.45 | 1.22 | 0.23 | 0 | -6.3249 | -70.9864 | 91.9658 | -1.9658 | -70.0918 | 73.8849 | 0 | 0.915 | 0.2 | 0 | 0.0725 | 0.9875 | 5.9 | 5.9309 | 1.0667 | 0.00086379
2016-10-10 07:00 | 18.78 | 10.3167 | 8.4633 | 0 | -6.3407 | -55.9836 | 88.9804 | 1.0196 | -55.4809 | 60.0278 | 0 | 7.7375 | 0.2 | 0 | 0.939 | 8.6765 | 5.8 | 6.0711 | 1.0663 | 0.0075861
2016-10-10 08:00 | 36.11 | 19.4133 | 16.6967 | 272.196 | -6.3565 | -40.9808 | 86.4832 | 3.5168 | -40.7685 | 46.739 | 186.5422 | 14.56 | 0.2 | 0 | 1.8055 | 202.9077 | 5.7 | 12.0409 | 1.0454 | 0.17393
2016-10-10 09:00 | 53.44 | 28.51 | 24.93 | 267.061 | -6.3723 | -25.9781 | 84.6437 | 5.3563 | -25.9273 | 34.7011 | 219.5598 | 21.3825 | 0.2 | 0 | 2.672 | 243.6143 | 6 | 13.6129 | 1.0399 | 0.20773
2016-10-10 10:00 | 54.8867 | 29.24 | 25.6467 | 229.7651 | -6.3881 | -10.9753 | 83.5912 | 6.4088 | -10.9758 | 25.7522 | 206.9452 | 21.93 | 0.2 | 0 | 2.7443 | 231.6195 | 5.8 | 13.0381 | 1.0419 | 0.19788
2016-10-10 11:00 | 56.3333 | 29.97 | 26.3633 | 229.4598 | -6.404 | 4.0274 | 83.4025 | 6.5975 | 4.029 | 23.7074 | 210.0959 | 22.4775 | 0.2 | 0 | 2.8167 | 235.3901 | 5.8 | 13.1559 | 1.0415 | 0.20102
2016-10-10 12:00 | 57.78 | 30.7 | 27.08 | 263.1055 | -6.4198 | 19.0302 | 84.0924 | 5.9076 | 19.0111 | 30.0141 | 227.8236 | 23.025 | 0.2 | 0 | 2.889 | 253.7376 | 5.9 | 13.8293 | 1.0391 | 0.2162
2016-10-10 13:00 | 40.2067 | 21.61 | 18.5967 | 243.0484 | -6.4356 | 34.0329 | 85.6118 | 4.3882 | 33.9023 | 40.9796 | 183.4876 | 16.2075 | 0.2 | 0 | 2.0103 | 201.7054 | 6 | 12.3033 | 1.0444 | 0.17275
2016-10-10 14:00 | 22.6333 | 12.52 | 10.1133 | 0 | -6.4514 | 49.0357 | 87.854 | 2.146 | 48.6652 | 53.822 | 0 | 9.39 | 0.2 | 0 | 1.1317 | 10.5217 | 6.3 | 6.6288 | 1.0643 | 0.0091825
2016-10-10 15:00 | 5.06 | 3.43 | 1.63 | 0 | -6.4672 | 64.0384 | 90.6667 | -0.6667 | 63.3071 | 67.4691 | 0 | 2.5725 | 0.2 | 0 | 0.253 | 2.8255 | 6.3 | 6.3883 | 1.0651 | 0.0024678
2016-10-10 16:00 | 3.3733 | 2.2867 | 1.0867 | 0 | -6.483 | 79.0411 | 93.8647 | -3.8647 | 77.8798 | 81.5052 | 0 | 1.715 | 0.2 | 0 | 0.16867 | 1.8837 | 6.1 | 6.1589 | 1.0659 | 0.0016465
2016-10-10 17:00 | 1.6867 | 1.1433 | 0.54333 | 0 | -6.4988 | 94.0439 | 97.2424 | -7.2424 | 92.4691 | 95.7418 | 0 | 0.8575 | 0.2 | 0 | 0.084333 | 0.94183 | 6.2 | 6.2294 | 1.0657 | 0.00082304
2016-10-10 18:00 | 0 | 0 | 0 | 0 | -6.5145 | 109.0466 | 100.5826 | -10.5826 | 107.1764 | 110.0735 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.7 | 5.7 | 1.0675 | 0
2016-10-10 19:00 | 0 | 0 | 0 | 0 | -6.5303 | 124.0493 | 103.6653 | -13.6653 | 122.0958 | 124.4196 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.6 | 5.6 | 1.0679 | 0
2016-10-10 20:00 | 0 | 0 | 0 | 0 | -6.5461 | 139.052 | 106.2775 | -16.2775 | 137.2899 | 138.676 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.1 | 5.1 | 1.0696 | 0
2016-10-10 21:00 | 0 | 0 | 0 | 0 | -6.5619 | 154.0547 | 108.2276 | -18.2276 | 152.7671 | 152.5965 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.7 | 4.7 | 1.0711 | 0
2016-10-10 22:00 | 0 | 0 | 0 | 0 | -6.5777 | 169.0575 | 109.3635 | -19.3635 | 168.47 | 165.0897 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.2 | 5.2 | 1.0693 | 0
2016-10-10 23:00 | 0 | 0 | 0 | 0 | -6.5935 | 184.0602 | 109.5926 | -19.5926 | -175.7184 | 168.8936 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-10-11 | 0 | 0 | 0 | 0 | -6.6092 | -160.9371 | 108.8969 | -18.8969 | -159.9453 | 158.6859 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0714 | 0
2016-10-11 01:00 | 0 | 0 | 0 | 0 | -6.625 | -145.9344 | 107.3357 | -17.3357 | -144.3468 | 145.1566 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.4 | 4.4 | 1.0721 | 0
2016-10-11 02:00 | 0 | 0 | 0 | 0 | -6.6408 | -130.9317 | 105.0359 | -15.0359 | -129.0111 | 131.0096 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5 | 4.5 | 1.0717 | 0
2016-10-11 03:00 | 0 | 0 | 0 | 0 | -6.6566 | -115.9291 | 102.1737 | -12.1737 | -113.9609 | 116.6945 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.4 | 4.4 | 1.0721 | 0
2016-10-11 04:00 | 0.25 | 0.25 | 0 | 0 | -6.6723 | -100.9264 | 98.9548 | -8.9548 | -99.1576 | 102.3554 | 0 | 0.1875 | 0.2 | 0 | 0.0125 | 0.2 | 4.5 | 4.5062 | 1.0717 | 0.00017576
2016-10-11 05:00 | 0.5 | 0.5 | 0 | 0 | -6.6881 | -85.9237 | 95.5977 | -5.5977 | -84.5198 | 88.0778 | 0 | 0.375 | 0.2 | 0 | 0.025 | 0.4 | 4.3 | 4.3125 | 1.0724 | 0.00035175
2016-10-11 06:00 | 0.75 | 0.75 | 0 | 0 | -6.7039 | -70.921 | 92.3222 | -2.3222 | -69.9475 | 73.9521 | 0 | 0.5625 | 0.2 | 0 | 0.0375 | 0.6 | 4.4 | 4.4188 | 1.072 | 0.00052744
2016-10-11 07:00 | 6.7333 | 6.3067 | 0.42667 | 0 | -6.7196 | -55.9183 | 89.3405 | 0.65948 | -55.3464 | 60.1219 | 0 | 4.73 | 0.2 | 0 | 0.33667 | 5.0667 | 4.8 | 4.9583 | 1.0701 | 0.0044461
2016-10-11 08:00 | 12.7167 | 11.8633 | 0.85333 | 15.5209 | -6.7354 | -40.9157 | 86.8483 | 3.1517 | -40.6482 | 46.8768 | 10.6096 | 8.8975 | 0.2 | 0 | 0.63583 | 20.143 | 5.1 | 5.7295 | 1.0674 | 0.017631
2016-10-11 09:00 | 18.7 | 17.42 | 1.28 | 14.728 | -6.7511 | -25.913 | 85.0142 | 4.9858 | -25.825 | 34.9113 | 12.0776 | 13.065 | 0.2 | 0 | 0.935 | 26.0776 | 4.9 | 5.7149 | 1.0675 | 0.022827
2016-10-11 10:00 | 21.94 | 19.12 | 2.82 | 26.8304 | -6.7669 | -10.9104 | 83.9668 | 6.0332 | -10.8945 | 26.0699 | 24.1007 | 14.34 | 0.2 | 0 | 1.097 | 39.5377 | 4.9 | 6.1356 | 1.066 | 0.034562
2016-10-11 11:00 | 25.18 | 20.82 | 4.36 | 40.2555 | -6.7826 | 4.0923 | 83.7822 | 6.2178 | 4.0877 | 24.0915 | 36.749 | 15.615 | 0.2 | 0 | 1.259 | 53.623 | 4.8 | 6.4757 | 1.0648 | 0.046822
2016-10-11 12:00 | 28.42 | 22.52 | 5.9 | 61.2766 | -6.7984 | 19.095 | 84.4747 | 5.5253 | 19.0474 | 30.3507 | 52.8785 | 16.89 | 0.2 | 0 | 1.421 | 71.1895 | 4.6 | 6.8247 | 1.0636 | 0.062089
2016-10-11 13:00 | 20.0233 | 15.83 | 4.1933 | 60.045 | -6.8141 | 34.0976 | 85.9954 | 4.0046 | 33.9181 | 41.2515 | 45.1432 | 11.8725 | 0.2 | 0 | 1.0012 | 58.0169 | 5.6 | 7.413 | 1.0616 | 0.050502
2016-10-11 14:00 | 11.6267 | 9.14 | 2.4867 | 0 | -6.8299 | 49.1002 | 88.2379 | 1.7621 | 48.6638 | 54.049 | 0 | 6.855 | 0.2 | 0 | 0.58133 | 7.4363 | 5 | 5.2324 | 1.0692 | 0.0065197
2016-10-11 15:00 | 3.23 | 2.45 | 0.78 | 0 | -6.8456 | 64.1029 | 91.0503 | -1.0503 | 63.293 | 67.6672 | 0 | 1.8375 | 0.2 | 0 | 0.1615 | 1.999 | 5.5 | 5.5625 | 1.068 | 0.0017507
2016-10-11 16:00 | 2.1533 | 1.6333 | 0.52 | 0 | -6.8613 | 79.1055 | 94.2479 | -4.2479 | 77.8581 | 81.6849 | 0 | 1.225 | 0.2 | 0 | 0.10767 | 1.3327 | 4.3 | 4.3416 | 1.0723 | 0.0011718
2016-10-11 17:00 | 1.0767 | 0.81667 | 0.26 | 0 | -6.8771 | 94.1082 | 97.6253 | -7.6253 | 92.4453 | 95.9102 | 0 | 0.6125 | 0.2 | 0 | 0.053833 | 0.66633 | 4.3 | 4.3208 | 1.0724 | 0.00058594
2016-10-11 18:00 | 0 | 0 | 0 | 0 | -6.8928 | 109.1108 | 100.9656 | -10.9656 | 107.1562 | 110.237 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0738 | 0
2016-10-11 19:00 | 0 | 0 | 0 | 0 | -6.9085 | 124.1134 | 104.0486 | -14.0486 | 122.0852 | 124.585 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0774 | 0
2016-10-11 20:00 | 0 | 0 | 0 | 0 | -6.9243 | 139.116 | 106.6609 | -16.6609 | 137.2946 | 138.8541 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.4 | 3.4 | 1.0756 | 0
2016-10-11 21:00 | 0 | 0 | 0 | 0 | -6.94 | 154.1186 | 108.6102 | -18.6102 | 152.7922 | 152.8099 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.4 | 4.4 | 1.0721 | 0
2016-10-11 22:00 | 0 | 0 | 0 | 0 | -6.9557 | 169.1212 | 109.7439 | -19.7439 | 168.519 | 165.4006 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.8 | 4.8 | 1.0707 | 0
2016-10-11 23:00 | 0 | 0 | 0 | 0 | -6.9714 | 184.1239 | 109.9694 | -19.9694 | -175.6443 | 169.2235 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.2 | 5.2 | 1.0693 | 0
2016-10-12 | 0 | 0 | 0 | 0 | -6.9871 | -160.8735 | 109.2687 | -19.2687 | -159.8475 | 158.8219 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-10-12 01:00 | 0 | 0 | 0 | 0 | -7.0028 | -145.8709 | 107.7018 | -17.7018 | -144.2287 | 145.227 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.2 | 4.2 | 1.0728 | 0
2016-10-12 02:00 | 0 | 0 | 0 | 0 | -7.0186 | -130.8684 | 105.3966 | -15.3966 | -128.8777 | 131.0571 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.0735 | 0
2016-10-12 03:00 | 0 | 0 | 0 | 0 | -7.0343 | -115.8658 | 102.5301 | -12.5301 | -113.8177 | 116.7354 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.6 | 3.6 | 1.0749 | 0
2016-10-12 04:00 | 0.31 | 0.25333 | 0.056667 | 0 | -7.05 | -100.8632 | 99.3087 | -9.3087 | -99.0099 | 102.3988 | 0 | 0.19 | 0.2 | 0 | 0.0155 | 0.2055 | 2.8 | 2.8064 | 1.0777 | 0.0001816
2016-10-12 05:00 | 0.62 | 0.50667 | 0.11333 | 0 | -7.0657 | -85.8606 | 95.9513 | -5.9513 | -84.3726 | 88.1306 | 0 | 0.38 | 0.2 | 0 | 0.031 | 0.411 | 2.6 | 2.6128 | 1.0784 | 0.00036343
2016-10-12 06:00 | 0.93 | 0.76 | 0.17 | 0 | -7.0814 | -70.858 | 92.6777 | -2.6777 | -69.8057 | 74.0218 | 0 | 0.57 | 0.2 | 0 | 0.0465 | 0.6165 | 2.6 | 2.6193 | 1.0783 | 0.00054513
2016-10-12 07:00 | 12.3067 | 8.18 | 4.1267 | 0 | -7.0971 | -55.8554 | 89.6997 | 0.30032 | -55.2146 | 60.219 | 0 | 6.135 | 0.2 | 0 | 0.61533 | 6.7503 | 2 | 2.2109 | 1.0798 | 0.0059768
2016-10-12 08:00 | 23.6833 | 15.6 | 8.0833 | 0 | -7.1128 | -40.8529 | 87.2124 | 2.7876 | -40.5306 | 47.018 | 0 | 11.7 | 0.2 | 0 | 1.1842 | 12.8842 | 2.5 | 2.9026 | 1.0773 | 0.011382
2016-10-12 09:00 | 35.06 | 23.02 | 12.04 | 149.5922 | -7.1285 | -25.8503 | 85.3835 | 4.6165 | -25.7255 | 35.1248 | 122.3515 | 17.265 | 0.2 | 0 | 1.753 | 141.3695 | 3.3 | 7.7178 | 1.0605 | 0.12293
2016-10-12 10:00 | 36.8267 | 23.82 | 13.0067 | 131.905 | -7.1441 | -10.8477 | 84.3411 | 5.6589 | -10.8159 | 26.3888 | 118.1603 | 17.865 | 0.2 | 0 | 1.8413 | 137.8666 | 3.1 | 7.4083 | 1.0616 | 0.12001
2016-10-12 11:00 | 38.5933 | 24.62 | 13.9733 | 137.3375 | -7.1598 | 4.1548 | 84.1604 | 5.8396 | 4.1439 | 24.4738 | 124.9979 | 18.465 | 0.2 | 0 | 1.9297 | 145.3926 | 2.9 | 7.4435 | 1.0614 | 0.12655
2016-10-12 12:00 | 40.36 | 25.42 | 14.94 | 166.6127 | -7.1755 | 19.1574 | 84.8554 | 5.1446 | 19.0814 | 30.6857 | 143.2835 | 19.065 | 0.2 | 0 | 2.018 | 164.3665 | 2.9 | 8.0365 | 1.0594 | 0.14278
2016-10-12 13:00 | 27.6033 | 17.4967 | 10.1067 | 159.9505 | -7.1912 | 34.1599 | 86.3773 | 3.6227 | 33.9316 | 41.5219 | 119.7553 | 13.1225 | 0.2 | 0 | 1.3802 | 134.258 | 2.6 | 6.7956 | 1.0637 | 0.11711
2016-10-12 14:00 | 14.8467 | 9.5733 | 5.2733 | 0 | -7.2069 | 49.1625 | 88.6199 | 1.3801 | 48.6604 | 54.2744 | 0 | 7.18 | 0.2 | 0 | 0.74233 | 7.9223 | 2.3 | 2.5476 | 1.0786 | 0.0070068
2016-10-12 15:00 | 2.09 | 1.65 | 0.44 | 0 | -7.2226 | 64.165 | 91.4319 | -1.4319 | 63.2769 | 67.8633 | 0 | 1.2375 | 0.2 | 0 | 0.1045 | 1.342 | 2.3 | 2.3419 | 1.0793 | 0.0011877
2016-10-12 16:00 | 1.3933 | 1.1 | 0.29333 | 0 | -7.2382 | 79.1675 | 94.629 | -4.629 | 77.8343 | 81.862 | 0 | 0.825 | 0.2 | 0 | 0.069667 | 0.89467 | 2.2 | 2.228 | 1.0797 | 0.0007921
2016-10-12 17:00 | 0.69667 | 0.55 | 0.14667 | 0 | -7.2539 | 94.1701 | 98.0063 | -8.0063 | 92.4193 | 96.0757 | 0 | 0.4125 | 0.2 | 0 | 0.034833 | 0.44733 | 2.1 | 2.114 | 1.0801 | 0.0003962
2016-10-12 18:00 | 0 | 0 | 0 | 0 | -7.2696 | 109.1726 | 101.3467 | -11.3467 | 107.1338 | 110.3969 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2 | 2 | 1.0805 | 0
2016-10-12 19:00 | 0 | 0 | 0 | 0 | -7.2852 | 124.1751 | 104.4301 | -14.4301 | 122.0723 | 124.7462 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0819 | 0
2016-10-12 20:00 | 0 | 0 | 0 | 0 | -7.3009 | 139.1776 | 107.0425 | -17.0425 | 137.2971 | 139.027 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0847 | 0
2016-10-12 21:00 | 0 | 0 | 0 | 0 | -7.3165 | 154.1801 | 108.9911 | -18.9911 | 152.815 | 153.0169 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0861 | 0
2016-10-12 22:00 | 0 | 0 | 0 | 0 | -7.3322 | 169.1826 | 110.1228 | -20.1228 | 168.5656 | 165.7053 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0833 | 0
2016-10-12 23:00 | 0 | 0 | 0 | 0 | -7.3479 | 184.1852 | 110.3447 | -20.3447 | -175.5726 | 169.5494 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-10-13 | 0 | 0 | 0 | 0 | -7.3635 | -160.8123 | 109.6392 | -19.6392 | -159.7519 | 158.9536 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-10-13 01:00 | 0 | 0 | 0 | 0 | -7.3792 | -145.8098 | 108.0667 | -18.0667 | -144.113 | 145.2956 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0847 | 0
2016-10-13 02:00 | 0 | 0 | 0 | 0 | -7.3948 | -130.8074 | 105.7562 | -15.7562 | -128.7467 | 131.1044 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-10-13 03:00 | 0 | 0 | 0 | 0 | -7.4104 | -115.8049 | 102.8855 | -12.8855 | -113.6768 | 116.7771 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-10-13 04:00 | 0.25667 | 0.18333 | 0.073333 | 0 | -7.4261 | -100.8024 | 99.6617 | -9.6617 | -98.8646 | 102.4435 | 0 | 0.1375 | 0.2 | 0 | 0.012833 | 0.15033 | 1.1 | 1.1047 | 1.0836 | 0.00013358
2016-10-13 05:00 | 0.51333 | 0.36667 | 0.14667 | 0 | -7.4417 | -85.7999 | 96.304 | -6.304 | -84.2281 | 88.1853 | 0 | 0.275 | 0.2 | 0 | 0.025667 | 0.30067 | 1.4 | 1.4094 | 1.0826 | 0.0002669
2016-10-13 06:00 | 0.77 | 0.55 | 0.22 | 0 | -7.4574 | -70.7974 | 93.0322 | -3.0322 | -69.6666 | 74.0941 | 0 | 0.4125 | 0.2 | 0 | 0.0385 | 0.451 | 1.2 | 1.2141 | 1.0833 | 0.00040061
2016-10-13 07:00 | 13.2833 | 7.8067 | 5.4767 | 0 | -7.473 | -55.795 | 90.0578 | -0.057796 | -55.0855 | 60.3192 | 0 | 5.855 | 0.2 | 0 | 0.66417 | 6.5192 | 1.2 | 1.4037 | 1.0826 | 0.0057872
2016-10-13 08:00 | 25.7967 | 15.0633 | 10.7333 | 0 | -7.4886 | -40.7925 | 87.5752 | 2.4248 | -40.4158 | 47.1626 | 0 | 11.2975 | 0.2 | 0 | 1.2898 | 12.5873 | 1.2 | 1.5934 | 1.0819 | 0.011167
2016-10-13 09:00 | 38.31 | 22.32 | 15.99 | 215.8452 | -7.5042 | -25.79 | 85.7516 | 4.2484 | -25.6286 | 35.3416 | 176.0688 | 16.74 | 0.2 | 0 | 1.9155 | 194.7243 | 0.9 | 6.9851 | 1.0631 | 0.16974
2016-10-13 10:00 | 37.5733 | 22.7567 | 14.8167 | 160.8256 | -7.5199 | -10.7876 | 84.7139 | 5.2861 | -10.7399 | 26.7089 | 143.6657 | 17.0675 | 0.2 | 0 | 1.8787 | 162.6119 | 0.8 | 5.8816 | 1.0669 | 0.14226
2016-10-13 11:00 | 36.8367 | 23.1933 | 13.6433 | 143.3065 | -7.5355 | 4.2149 | 84.5369 | 5.4631 | 4.1975 | 24.8541 | 130.0336 | 17.395 | 0.2 | 0 | 1.8418 | 149.2704 | 1.1 | 5.7647 | 1.0673 | 0.13064
2016-10-13 12:00 | 36.1 | 23.63 | 12.47 | 150.0969 | -7.5511 | 19.2173 | 85.2344 | 4.7656 | 19.1129 | 31.0189 | 128.6326 | 17.7225 | 0.2 | 0 | 1.805 | 148.1601 | 1 | 5.63 | 1.0678 | 0.12973
2016-10-13 13:00 | 24.5633 | 16.1567 | 8.4067 | 148.6176 | -7.5667 | 34.2198 | 86.7573 | 3.2427 | 33.9429 | 41.7908 | 110.8067 | 12.1175 | 0.2 | 0 | 1.2282 | 124.1524 | 1 | 4.8798 | 1.0704 | 0.10897
2016-10-13 14:00 | 13.0267 | 8.6833 | 4.3433 | 0 | -7.5823 | 49.2222 | 89 | 1 | 48.6547 | 54.4979 | 0 | 6.5125 | 0.2 | 0 | 0.65133 | 7.1638 | 0.8 | 1.0239 | 1.0839 | 0.0063673
2016-10-13 15:00 | 1.49 | 1.21 | 0.28 | 0 | -7.5979 | 64.2247 | 91.8114 | -1.8114 | 63.2585 | 68.0572 | 0 | 0.9075 | 0.2 | 0 | 0.0745 | 0.982 | 0.6 | 0.63069 | 1.0853 | 0.00087392
2016-10-13 16:00 | 0.99333 | 0.80667 | 0.18667 | 0 | -7.6135 | 79.2271 | 95.0081 | -5.0081 | 77.8084 | 82.0365 | 0 | 0.605 | 0.2 | 0 | 0.049667 | 0.65467 | 0.5 | 0.52046 | 1.0857 | 0.00058282
2016-10-13 17:00 | 0.49667 | 0.40333 | 0.093333 | 0 | -7.6291 | 94.2295 | 98.3851 | -8.3851 | 92.3912 | 96.238 | 0 | 0.3025 | 0.2 | 0 | 0.024833 | 0.32733 | 0.5 | 0.51023 | 1.0857 | 0.00029142
2016-10-13 18:00 | 0 | 0 | 0 | 0 | -7.6447 | 109.2319 | 101.7257 | -11.7257 | 107.1092 | 110.5531 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-10-13 19:00 | 0 | 0 | 0 | 0 | -7.6603 | 124.2344 | 104.8095 | -14.8095 | 122.0572 | 124.9031 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0847 | 0
2016-10-13 20:00 | 0 | 0 | 0 | 0 | -7.6759 | 139.2368 | 107.4221 | -17.4221 | 137.2971 | 139.1946 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-10-13 21:00 | 0 | 0 | 0 | 0 | -7.6915 | 154.2392 | 109.3701 | -19.3701 | 152.8354 | 153.2174 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0847 | 0
2016-10-13 22:00 | 0 | 0 | 0 | 0 | -7.7071 | 169.2416 | 110.5 | -20.5 | 168.6099 | 166.0032 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0816 | 0
2016-10-13 23:00 | 0 | 0 | 0 | 0 | -7.7227 | 184.244 | 110.7185 | -20.7185 | -175.5032 | 169.871 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.078 | 0
2016-10-14 | 0 | 0 | 0 | 0 | -7.7383 | -160.7536 | 110.0082 | -20.0082 | -159.6588 | 159.081 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0774 | 0
2016-10-14 01:00 | 0 | 0 | 0 | 0 | -7.7538 | -145.7512 | 108.4303 | -18.4303 | -143.9997 | 145.3626 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0784 | 0
2016-10-14 02:00 | 0 | 0 | 0 | 0 | -7.7694 | -130.7488 | 106.1145 | -16.1145 | -128.6181 | 131.1515 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0816 | 0
2016-10-14 03:00 | 0 | 0 | 0 | 0 | -7.785 | -115.7465 | 103.2397 | -13.2397 | -113.5386 | 116.8195 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0763 | 0
2016-10-14 04:00 | 0.073333 | 0.073333 | 0 | 0 | -7.8006 | -100.7441 | 100.0136 | -10.0136 | -98.722 | 102.4898 | 0 | 0.055 | 0.2 | 0 | 0.0036667 | 0.058667 | 3.6 | 3.6018 | 1.0749 | 5.171e-05
2016-10-14 05:00 | 0.14667 | 0.14667 | 0 | 0 | -7.8161 | -85.7417 | 96.6556 | -6.6556 | -84.0862 | 88.2421 | 0 | 0.11 | 0.2 | 0 | 0.0073333 | 0.11733 | 5 | 5.0037 | 1.07 | 0.00010295
2016-10-14 06:00 | 0.22 | 0.22 | 0 | 0 | -7.8317 | -70.7393 | 93.3856 | -3.3856 | -69.5303 | 74.1689 | 0 | 0.165 | 0.2 | 0 | 0.011 | 0.176 | 4.9 | 4.9055 | 1.0703 | 0.00015447
2016-10-14 07:00 | 4.8333 | 4.82 | 0.013333 | 0 | -7.8472 | -55.737 | 90.4148 | -0.41478 | -54.9592 | 60.4223 | 0 | 3.615 | 0.2 | 0 | 0.24167 | 3.8567 | 4.6 | 4.7205 | 1.071 | 0.0033869
2016-10-14 08:00 | 9.4467 | 9.42 | 0.026667 | 0 | -7.8628 | -40.7346 | 87.9369 | 2.0631 | -40.3038 | 47.3105 | 0 | 7.065 | 0.2 | 0 | 0.47233 | 7.5373 | 5.2 | 5.4355 | 1.0685 | 0.0066038
2016-10-14 09:00 | 14.06 | 14.02 | 0.04 | 0.59087 | -7.8784 | -25.7323 | 86.1183 | 3.8817 | -25.5347 | 35.5615 | 0.48067 | 10.515 | 0.2 | 0 | 0.703 | 11.6987 | 4.5 | 4.8656 | 1.0705 | 0.010269
2016-10-14 10:00 | 14.7033 | 14.5833 | 0.12 | 1.4007 | -7.8939 | -10.7299 | 85.0852 | 4.9148 | -10.6667 | 27.03 | 1.2477 | 10.9375 | 0.2 | 0 | 0.73517 | 12.9203 | 5 | 5.4038 | 1.0686 | 0.011321
2016-10-14 11:00 | 15.3467 | 15.1467 | 0.2 | 2.2551 | -7.9094 | 4.2724 | 84.9118 | 5.0882 | 4.2485 | 25.2323 | 2.0399 | 11.36 | 0.2 | 0 | 0.76733 | 14.1672 | 5.1 | 5.5427 | 1.0681 | 0.012408
2016-10-14 12:00 | 15.99 | 15.71 | 0.28 | 3.6592 | -7.925 | 19.2748 | 85.6115 | 4.3885 | 19.1418 | 31.3502 | 3.125 | 11.7825 | 0.2 | 0 | 0.7995 | 15.707 | 5.8 | 6.2908 | 1.0655 | 0.013723
2016-10-14 13:00 | 10.8433 | 10.6567 | 0.18667 | 0 | -7.9405 | 34.2771 | 87.1353 | 2.8647 | 33.9517 | 42.0581 | 0 | 7.9925 | 0.2 | 0 | 0.54217 | 8.5347 | 5.7 | 5.9667 | 1.0666 | 0.0074646
2016-10-14 14:00 | 5.6967 | 5.6033 | 0.093333 | 0 | -7.9561 | 49.2795 | 89.3779 | 0.62206 | 48.6467 | 54.7196 | 0 | 4.2025 | 0.2 | 0 | 0.28483 | 4.4873 | 4.8 | 4.9402 | 1.0702 | 0.003938
2016-10-14 15:00 | 0.55 | 0.55 | 0 | 0 | -7.9716 | 64.2818 | 92.1888 | -2.1888 | 63.238 | 68.2488 | 0 | 0.4125 | 0.2 | 0 | 0.0275 | 0.44 | 4.7 | 4.7138 | 1.071 | 0.00038642
2016-10-14 16:00 | 0.36667 | 0.36667 | 0 | 0 | -7.9871 | 79.2841 | 95.3849 | -5.3849 | 77.7802 | 82.2083 | 0 | 0.275 | 0.2 | 0 | 0.018333 | 0.29333 | 4.7 | 4.7092 | 1.071 | 0.00025762
2016-10-14 17:00 | 0.18333 | 0.18333 | 0 | 0 | -8.0027 | 94.2864 | 98.7617 | -8.7617 | 92.3608 | 96.3972 | 0 | 0.1375 | 0.2 | 0 | 0.0091667 | 0.14667 | 5 | 5.0046 | 1.07 | 0.00012868
2016-10-14 18:00 | 0 | 0 | 0 | 0 | -8.0182 | 109.2888 | 102.1025 | -12.1025 | 107.0823 | 110.7057 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.1 | 5.1 | 1.0696 | 0
2016-10-14 19:00 | 0 | 0 | 0 | 0 | -8.0337 | 124.2911 | 105.1867 | -15.1867 | 122.0397 | 125.0555 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.3 | 5.3 | 1.069 | 0
2016-10-14 20:00 | 0 | 0 | 0 | 0 | -8.0492 | 139.2934 | 107.7996 | -17.7996 | 137.2948 | 139.3569 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.1 | 5.1 | 1.0696 | 0
2016-10-14 21:00 | 0 | 0 | 0 | 0 | -8.0648 | 154.2957 | 109.7472 | -19.7472 | 152.8534 | 153.4113 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.1 | 5.1 | 1.0696 | 0
2016-10-14 22:00 | 0 | 0 | 0 | 0 | -8.0803 | 169.298 | 110.8753 | -20.8753 | 168.6516 | 166.2942 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5 | 5 | 1.07 | 0
2016-10-14 23:00 | 0 | 0 | 0 | 0 | -8.0958 | 184.3003 | 111.0905 | -21.0905 | -175.4364 | 170.1881 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.2 | 5.2 | 1.0693 | 0
2016-10-15 | 0 | 0 | 0 | 0 | -8.1113 | -160.6974 | 110.3756 | -20.3756 | -159.5682 | 159.2041 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5 | 5 | 1.07 | 0
2016-10-15 01:00 | 0 | 0 | 0 | 0 | -8.1268 | -145.6952 | 108.7924 | -18.7924 | -143.8889 | 145.4281 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.8 | 4.8 | 1.0707 | 0
2016-10-15 02:00 | 0 | 0 | 0 | 0 | -8.1423 | -130.6929 | 106.4716 | -16.4716 | -128.4921 | 131.1985 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.7 | 4.7 | 1.0711 | 0
2016-10-15 03:00 | 0 | 0 | 0 | 0 | -8.1578 | -115.6906 | 103.5928 | -13.5928 | -113.4029 | 116.8628 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.7 | 4.7 | 1.0711 | 0
2016-10-15 04:00 | 0.03 | 0.03 | 0 | 0 | -8.1733 | -100.6883 | 100.3643 | -10.3643 | -98.5821 | 102.5375 | 0 | 0.0225 | 0.2 | 0 | 0.0015 | 0.024 | 5 | 5.0008 | 1.07 | 2.1058e-05
2016-10-15 05:00 | 0.06 | 0.06 | 0 | 0 | -8.1888 | -85.6861 | 97.0061 | -7.0061 | -83.9472 | 88.301 | 0 | 0.045 | 0.2 | 0 | 0.003 | 0.048 | 5 | 5.0015 | 1.07 | 4.2115e-05
2016-10-15 06:00 | 0.09 | 0.09 | 0 | 0 | -8.2043 | -70.6838 | 93.7379 | -3.7379 | -69.3969 | 74.2463 | 0 | 0.0675 | 0.2 | 0 | 0.0045 | 0.072 | 4.7 | 4.7023 | 1.071 | 6.3234e-05
2016-10-15 07:00 | 9.2367 | 6.0333 | 3.2033 | 0 | -8.2197 | -55.6815 | 90.7705 | -0.77053 | -54.8359 | 60.5284 | 0 | 4.525 | 0.2 | 0 | 0.46183 | 4.9868 | 5.3 | 5.4558 | 1.0684 | 0.0043689
2016-10-15 08:00 | 18.3833 | 11.9767 | 6.4067 | 0 | -8.2352 | -40.6793 | 88.2972 | 1.7028 | -40.1948 | 47.4617 | 0 | 8.9825 | 0.2 | 0 | 0.91917 | 9.9017 | 4.8 | 5.1094 | 1.0696 | 0.0086846
2016-10-15 09:00 | 27.53 | 17.92 | 9.61 | 156.6765 | -8.2507 | -25.677 | 86.4835 | 3.5165 | -25.4436 | 35.7843 | 127.0998 | 13.44 | 0.2 | 0 | 1.3765 | 141.9163 | 3.4 | 7.8349 | 1.0601 | 0.12336
2016-10-15 10:00 | 28.6733 | 18.5933 | 10.08 | 127.2013 | -8.2662 | -10.6748 | 85.4549 | 4.5451 | -10.5963 | 27.3518 | 112.9805 | 13.945 | 0.2 | 0 | 1.4337 | 128.3591 | 2.6 | 6.6112 | 1.0644 | 0.11203
2016-10-15 11:00 | 29.8167 | 19.2667 | 10.55 | 128.3434 | -8.2816 | 4.3274 | 85.2849 | 4.7151 | 4.2968 | 25.6084 | 115.7361 | 14.45 | 0.2 | 0 | 1.4908 | 131.677 | 1.5 | 5.6149 | 1.0678 | 0.1153
2016-10-15 12:00 | 30.96 | 19.94 | 11.02 | 157.4531 | -8.2971 | 19.3297 | 85.9866 | 4.0134 | 19.1683 | 31.6794 | 133.9926 | 14.955 | 0.2 | 0 | 1.548 | 150.4956 | 0.7 | 5.403 | 1.0686 | 0.13187
2016-10-15 13:00 | 20.8 | 13.4233 | 7.3767 | 0 | -8.3126 | 34.3319 | 87.5112 | 2.4888 | 33.9582 | 42.3235 | 0 | 10.0675 | 0.2 | 0 | 1.04 | 11.1075 | 0 | 0.34711 | 1.0863 | 0.009894
2016-10-15 14:00 | 10.64 | 6.9067 | 3.7333 | 0 | -8.328 | 49.3341 | 89.7537 | 0.24632 | 48.6364 | 54.9393 | 0 | 5.18 | 0.2 | 0 | 0.532 | 5.712 | -0.8 | -0.6215 | 1.0897 | 0.0051039
2016-10-15 15:00 | 0.48 | 0.39 | 0.09 | 0 | -8.3435 | 64.3363 | 92.5639 | -2.5639 | 63.2152 | 68.438 | 0 | 0.2925 | 0.2 | 0 | 0.024 | 0.3165 | -1.2 | -1.1901 | 1.0917 | 0.00028332
2016-10-15 16:00 | 0.32 | 0.26 | 0.06 | 0 | -8.359 | 79.3386 | 95.7594 | -5.7594 | 77.7499 | 82.3772 | 0 | 0.195 | 0.2 | 0 | 0.016 | 0.211 | -2.4 | -2.3934 | 1.0959 | 0.00018961
2016-10-15 17:00 | 0.16 | 0.13 | 0.03 | 0 | -8.3744 | 94.3408 | 99.1359 | -9.1359 | 92.3282 | 96.553 | 0 | 0.0975 | 0.2 | 0 | 0.008 | 0.1055 | -2.7 | -2.6967 | 1.0969 | 9.4896e-05
2016-10-15 18:00 | 0 | 0 | 0 | 0 | -8.3899 | 109.343 | 102.4769 | -12.4769 | 107.0531 | 110.8543 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-10-15 19:00 | 0 | 0 | 0 | 0 | -8.4053 | 124.3452 | 105.5616 | -15.5616 | 122.0197 | 125.2034 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-10-15 20:00 | 0 | 0 | 0 | 0 | -8.4207 | 139.3474 | 108.1749 | -18.1749 | 137.2899 | 139.5138 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-10-15 21:00 | 0 | 0 | 0 | 0 | -8.4362 | 154.3496 | 110.1221 | -20.1221 | 152.8687 | 153.5983 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-10-15 22:00 | 0 | 0 | 0 | 0 | -8.4516 | 169.3518 | 111.2486 | -21.2486 | 168.6908 | 166.5777 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-10-15 23:00 | 0 | 0 | 0 | 0 | -8.467 | 184.3539 | 111.4607 | -21.4607 | -175.3721 | 170.5004 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-10-16 | 0 | 0 | 0 | 0 | -8.4825 | -160.6439 | 110.7414 | -20.7414 | -159.4802 | 159.3229 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-10-16 01:00 | 0 | 0 | 0 | 0 | -8.4979 | -145.6417 | 109.1531 | -19.1531 | -143.7807 | 145.492 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-10-16 02:00 | 0 | 0 | 0 | 0 | -8.5133 | -130.6395 | 106.8272 | -16.8272 | -128.3688 | 131.2455 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-10-16 03:00 | 0 | 0 | 0 | 0 | -8.5287 | -115.6374 | 103.9445 | -13.9445 | -113.2699 | 116.907 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-10-16 04:00 | 0.0033333 | 0.0033333 | 0 | 0 | -8.5442 | -100.6352 | 100.7138 | -10.7138 | -98.445 | 102.5868 | 0 | 0.0025 | 0.2 | 0 | 0.00016667 | 0.0026667 | -1.3 | -1.2999 | 1.092 | 2.3879e-06
2016-10-16 05:00 | 0.0066667 | 0.0066667 | 0 | 0 | -8.5596 | -85.6331 | 97.3553 | -7.3553 | -83.811 | 88.362 | 0 | 0.005 | 0.2 | 0 | 0.00033333 | 0.0053333 | -1.2 | -1.1998 | 1.0917 | 4.7744e-06
2016-10-16 06:00 | 0.01 | 0.01 | 0 | 0 | -8.575 | -70.6309 | 94.0889 | -4.0889 | -69.2664 | 74.3262 | 0 | 0.0075 | 0.2 | 0 | 0.0005 | 0.008 | -1.2 | -1.1998 | 1.0917 | 7.1615e-06
2016-10-16 07:00 | 4.9833 | 4.1233 | 0.86 | 0 | -8.5904 | -55.6288 | 91.125 | -1.125 | -54.7156 | 60.6374 | 0 | 3.0925 | 0.2 | 0 | 0.24917 | 3.3417 | -1.2 | -1.0956 | 1.0913 | 0.0029904
2016-10-16 08:00 | 9.9567 | 8.2367 | 1.72 | 0 | -8.6058 | -40.6266 | 88.6561 | 1.3439 | -40.0887 | 47.616 | 0 | 6.1775 | 0.2 | 0 | 0.49783 | 6.6753 | -1.2 | -0.9914 | 1.091 | 0.0059717
2016-10-16 09:00 | 14.93 | 12.35 | 2.58 | 46.9081 | -8.6212 | -25.6245 | 86.8471 | 3.1529 | -25.3555 | 36.0099 | 37.9447 | 9.2625 | 0.2 | 0 | 0.7465 | 47.9537 | -1.2 | 0.29855 | 1.0865 | 0.042722
2016-10-16 10:00 | 16.1433 | 13.0867 | 3.0567 | 41.963 | -8.6366 | -10.6223 | 85.8228 | 4.1772 | -10.5288 | 27.6741 | 37.1625 | 9.815 | 0.2 | 0 | 0.80717 | 47.7847 | -1 | 0.49327 | 1.0858 | 0.042544
2016-10-16 11:00 | 17.3567 | 13.8233 | 3.5333 | 46.6484 | -8.652 | 4.3798 | 85.656 | 4.344 | 4.3423 | 25.9821 | 41.9337 | 10.3675 | 0.2 | 0 | 0.86783 | 53.169 | -0.9 | 0.76153 | 1.0848 | 0.047297
2016-10-16 12:00 | 18.57 | 14.56 | 4.01 | 63.1571 | -8.6673 | 19.3819 | 86.3597 | 3.6403 | 19.1921 | 32.0064 | 53.5565 | 10.92 | 0.2 | 0 | 0.9285 | 65.405 | -0.7 | 1.3439 | 1.0828 | 0.058073
2016-10-16 13:00 | 12.5233 | 9.7933 | 2.73 | 0 | -8.6827 | 34.384 | 87.8849 | 2.1151 | 33.9622 | 42.587 | 0 | 7.345 | 0.2 | 0 | 0.62617 | 7.9712 | -0.6 | -0.3509 | 1.0887 | 0.0071163
2016-10-16 14:00 | 6.4767 | 5.0267 | 1.45 | 0 | -8.6981 | 49.3861 | 90.1271 | -0.12709 | 48.6237 | 55.1568 | 0 | 3.77 | 0.2 | 0 | 0.32383 | 4.0938 | -0.4 | -0.27207 | 1.0885 | 0.0036539
2016-10-16 15:00 | 0.43 | 0.26 | 0.17 | 0 | -8.7135 | 64.3882 | 92.9366 | -2.9366 | 63.1901 | 68.6247 | 0 | 0.195 | 0.2 | 0 | 0.0215 | 0.2165 | 0.1 | 0.10677 | 1.0871 | 0.000193
2016-10-16 16:00 | 0.28667 | 0.17333 | 0.11333 | 0 | -8.7289 | 79.3903 | 96.1314 | -6.1314 | 77.7172 | 82.5432 | 0 | 0.13 | 0.2 | 0 | 0.014333 | 0.14433 | 0.7 | 0.70451 | 1.085 | 0.00012842
2016-10-16 17:00 | 0.14333 | 0.086667 | 0.056667 | 0 | -8.7442 | 94.3924 | 99.5076 | -9.5076 | 92.2932 | 96.7055 | 0 | 0.065 | 0.2 | 0 | 0.0071667 | 0.072167 | 0.6 | 0.60226 | 1.0854 | 6.423e-05
2016-10-16 18:00 | 0 | 0 | 0 | 0 | -8.7596 | 109.3945 | 102.8489 | -12.8489 | 107.0214 | 110.9991 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0837 | 0
2016-10-16 19:00 | 0 | 0 | 0 | 0 | -8.775 | 124.3966 | 105.9341 | -15.9341 | 121.9973 | 125.3467 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-10-16 20:00 | 0 | 0 | 0 | 0 | -8.7903 | 139.3987 | 108.5479 | -18.5479 | 137.2825 | 139.6651 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.0788 | 0
2016-10-16 21:00 | 0 | 0 | 0 | 0 | -8.8057 | 154.4008 | 110.4949 | -20.4949 | 152.8814 | 153.7783 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-10-16 22:00 | 0 | 0 | 0 | 0 | -8.821 | 169.4029 | 111.6199 | -21.6199 | 168.7273 | 166.8533 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-10-16 23:00 | 0 | 0 | 0 | 0 | -8.8364 | 184.4049 | 111.8291 | -21.8291 | -175.3105 | 170.8075 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-10-17 | 0 | 0 | 0 | 0 | -8.8517 | -160.593 | 111.1054 | -21.1054 | -159.3948 | 159.4374 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.4 | 3.4 | 1.0756 | 0
2016-10-17 01:00 | 0 | 0 | 0 | 0 | -8.8671 | -145.5909 | 109.5121 | -19.5121 | -143.6752 | 145.5545 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.6 | 3.6 | 1.0749 | 0
2016-10-17 02:00 | 0 | 0 | 0 | 0 | -8.8824 | -130.5889 | 107.1814 | -17.1814 | -128.2482 | 131.2925 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-10-17 03:00 | 0 | 0 | 0 | 0 | -8.8977 | -115.5868 | 104.2948 | -14.2948 | -113.1398 | 116.9521 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-10-17 04:00 | 0 | 0 | 0 | 0 | -8.9131 | -100.5848 | 101.0619 | -11.0619 | -98.3108 | 102.6377 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.078 | 0
2016-10-17 05:00 | 0 | 0 | 0 | 0 | -8.9284 | -85.5827 | 97.7033 | -7.7033 | -83.6778 | 88.425 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-10-17 06:00 | 0 | 0 | 0 | 0 | -8.9437 | -70.5807 | 94.4386 | -4.4386 | -69.1389 | 74.4087 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.6 | 3.6 | 1.0749 | 0
2016-10-17 07:00 | 6.5967 | 4.5033 | 2.0933 | 0 | -8.959 | -55.5787 | 91.478 | -1.478 | -54.5983 | 60.7494 | 0 | 3.3775 | 0.2 | 0 | 0.32983 | 3.7073 | 3.6 | 3.7159 | 1.0745 | 0.0032665
2016-10-17 08:00 | 13.1933 | 9.0067 | 4.1867 | 0 | -8.9743 | -40.5766 | 89.0134 | 0.98659 | -39.9858 | 47.7735 | 0 | 6.755 | 0.2 | 0 | 0.65967 | 7.4147 | 4.3 | 4.5317 | 1.0716 | 0.0065156
2016-10-17 09:00 | 19.79 | 13.51 | 6.28 | 0 | -8.9897 | -25.5746 | 87.209 | 2.791 | -25.2704 | 36.2381 | 0 | 10.1325 | 0.2 | 0 | 0.9895 | 11.122 | 3.8 | 4.1476 | 1.073 | 0.0097857
2016-10-17 10:00 | 21.3467 | 14.2933 | 7.0533 | 106.1147 | -9.005 | -10.5726 | 86.1888 | 3.8112 | -10.4642 | 27.9969 | 93.6965 | 10.72 | 0.2 | 0 | 1.0673 | 105.4838 | 3.3 | 6.5964 | 1.0644 | 0.092068
2016-10-17 11:00 | 22.9033 | 15.0767 | 7.8267 | 112.9086 | -9.0203 | 4.4294 | 86.0251 | 3.9749 | 4.3851 | 26.3535 | 101.1743 | 11.3075 | 0.2 | 0 | 1.1452 | 113.6269 | 3.5 | 7.0508 | 1.0628 | 0.099027
2016-10-17 12:00 | 24.46 | 15.86 | 8.6 | 150.794 | -9.0356 | 19.4314 | 86.7306 | 3.2694 | 19.2133 | 32.331 | 127.4168 | 11.895 | 0.2 | 0 | 1.223 | 140.5348 | 2.9 | 7.2917 | 1.062 | 0.12238
2016-10-17 13:00 | 16.34 | 10.5967 | 5.7433 | 0 | -9.0509 | 34.4334 | 88.2563 | 1.7437 | 33.9636 | 42.8483 | 0 | 7.9475 | 0.2 | 0 | 0.817 | 8.7645 | 2.6 | 2.8739 | 1.0774 | 0.0077435
2016-10-17 14:00 | 8.22 | 5.3333 | 2.8867 | 0 | -9.0662 | 49.4354 | 90.4981 | -0.49805 | 48.6087 | 55.372 | 0 | 4 | 0.2 | 0 | 0.411 | 4.411 | 3.8 | 3.9378 | 1.0737 | 0.0038837
2016-10-17 15:00 | 0.1 | 0.07 | 0.03 | 0 | -9.0815 | 64.4374 | 93.3068 | -3.3068 | 63.1627 | 68.8087 | 0 | 0.0525 | 0.2 | 0 | 0.005 | 0.0575 | 3.6 | 3.6018 | 1.0749 | 5.0681e-05
2016-10-17 16:00 | 0.066667 | 0.046667 | 0.02 | 0 | -9.0967 | 79.4394 | 96.5008 | -6.5008 | 77.6821 | 82.7062 | 0 | 0.035 | 0.2 | 0 | 0.0033333 | 0.038333 | 3.5 | 3.5012 | 1.0752 | 3.3799e-05
2016-10-17 17:00 | 0.033333 | 0.023333 | 0.01 | 0 | -9.112 | 94.4414 | 99.8767 | -9.8767 | 92.2558 | 96.8544 | 0 | 0.0175 | 0.2 | 0 | 0.0016667 | 0.019167 | 3.5 | 3.5006 | 1.0752 | 1.6899e-05
2016-10-17 18:00 | 0 | 0 | 0 | 0 | -9.1273 | 109.4434 | 103.2183 | -13.2183 | 106.9873 | 111.1398 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.8 | 3.8 | 1.0742 | 0
2016-10-17 19:00 | 0 | 0 | 0 | 0 | -9.1426 | 124.4453 | 106.3041 | -16.3041 | 121.9723 | 125.4854 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-10-17 20:00 | 0 | 0 | 0 | 0 | -9.1579 | 139.4473 | 108.9184 | -18.9184 | 137.2725 | 139.8108 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-10-17 21:00 | 0 | 0 | 0 | 0 | -9.1731 | 154.4493 | 110.8653 | -20.8653 | 152.8915 | 153.9511 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-10-17 22:00 | 0 | 0 | 0 | 0 | -9.1884 | 169.4512 | 111.989 | -21.989 | 168.761 | 167.1207 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0763 | 0
2016-10-17 23:00 | 0 | 0 | 0 | 0 | -9.2037 | 184.4532 | 112.1954 | -22.1954 | -175.2517 | 171.1093 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-10-18 | 0 | 0 | 0 | 0 | -9.2189 | -160.5449 | 111.4676 | -21.4676 | -159.3122 | 159.5479 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.0788 | 0
2016-10-18 01:00 | 0 | 0 | 0 | 0 | -9.2342 | -145.5429 | 109.8694 | -19.8694 | -143.5725 | 145.6157 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-10-18 02:00 | 0 | 0 | 0 | 0 | -9.2494 | -130.541 | 107.5339 | -17.5339 | -128.1304 | 131.3397 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-10-18 03:00 | 0 | 0 | 0 | 0 | -9.2647 | -115.539 | 104.6436 | -14.6436 | -113.0125 | 116.9982 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-10-18 04:00 | 0 | 0 | 0 | 0 | -9.2799 | -100.5371 | 101.4086 | -11.4086 | -98.1795 | 102.6903 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-10-18 05:00 | 0 | 0 | 0 | 0 | -9.2951 | -85.5352 | 98.0498 | -8.0498 | -83.5476 | 88.4903 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-10-18 06:00 | 0 | 0 | 0 | 0 | -9.3104 | -70.5333 | 94.7868 | -4.7868 | -69.0145 | 74.4937 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0784 | 0
2016-10-18 07:00 | 3.2733 | 2.8367 | 0.43667 | 0 | -9.3256 | -55.5314 | 91.8294 | -1.8294 | -54.4841 | 60.8643 | 0 | 2.1275 | 0.2 | 0 | 0.16367 | 2.2912 | 3.1 | 3.1716 | 1.0764 | 0.0020223
2016-10-18 08:00 | 6.5467 | 5.6733 | 0.87333 | 0 | -9.3408 | -40.5294 | 89.3691 | 0.63091 | -39.8859 | 47.934 | 0 | 4.255 | 0.2 | 0 | 0.32733 | 4.5823 | 3.6 | 3.7432 | 1.0744 | 0.0040371
2016-10-18 09:00 | 9.82 | 8.51 | 1.31 | 0 | -9.3561 | -25.5275 | 87.5691 | 2.4309 | -25.1883 | 36.4689 | 0 | 6.3825 | 0.2 | 0 | 0.491 | 6.8735 | 3.4 | 3.6148 | 1.0748 | 0.0060581
2016-10-18 10:00 | 9.68 | 8.58 | 1.1 | 18.2945 | -9.3713 | -10.5256 | 86.5529 | 3.4471 | -10.4026 | 28.3198 | 16.1049 | 6.435 | 0.2 | 0 | 0.484 | 23.0239 | 3.9 | 4.6195 | 1.0713 | 0.020226
2016-10-18 11:00 | 9.54 | 8.65 | 0.89 | 14.1432 | -9.3865 | 4.4763 | 86.3921 | 3.6079 | 4.425 | 26.7223 | 12.6326 | 6.4875 | 0.2 | 0 | 0.477 | 19.5971 | 4.2 | 4.8124 | 1.0707 | 0.017205
2016-10-18 12:00 | 9.4 | 8.72 | 0.68 | 0 | -9.4017 | 19.4781 | 87.0991 | 2.9009 | 19.2318 | 32.6532 | 0 | 6.54 | 0.2 | 0 | 0.47 | 7.01 | 4.4 | 4.6191 | 1.0713 | 0.0061582
2016-10-18 13:00 | 6.2767 | 5.8233 | 0.45333 | 0 | -9.4169 | 34.48 | 88.6252 | 1.3748 | 33.9625 | 43.1074 | 0 | 4.3675 | 0.2 | 0 | 0.31383 | 4.6813 | 4.4 | 4.5463 | 1.0716 | 0.0041135
2016-10-18 14:00 | 3.1533 | 2.9267 | 0.22667 | 0 | -9.4321 | 49.4819 | 90.8664 | -0.86645 | 48.5912 | 55.5847 | 0 | 2.195 | 0.2 | 0 | 0.15767 | 2.3527 | 3.9 | 3.9735 | 1.0736 | 0.0020712
2016-10-18 15:00 | 0.03 | 0.03 | 0 | 0 | -9.4473 | 64.4838 | 93.6743 | -3.6743 | 63.1329 | 68.99 | 0 | 0.0225 | 0.2 | 0 | 0.0015 | 0.024 | 3.8 | 3.8007 | 1.0742 | 2.114e-05
2016-10-18 16:00 | 0.02 | 0.02 | 0 | 0 | -9.4625 | 79.4857 | 96.8675 | -6.8675 | 77.6447 | 82.8661 | 0 | 0.015 | 0.2 | 0 | 0.001 | 0.016 | 4.3 | 4.3005 | 1.0724 | 1.4071e-05
2016-10-18 17:00 | 0.01 | 0.01 | 0 | 0 | -9.4777 | 94.4875 | 100.2432 | -10.2432 | 92.216 | 96.9998 | 0 | 0.0075 | 0.2 | 0 | 0.0005 | 0.008 | 3.7 | 3.7003 | 1.0745 | 7.049e-06
2016-10-18 18:00 | 0 | 0 | 0 | 0 | -9.4929 | 109.4894 | 103.5849 | -13.5849 | 106.9508 | 111.2765 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0745 | 0
2016-10-18 19:00 | 0 | 0 | 0 | 0 | -9.5081 | 124.4912 | 106.6714 | -16.6714 | 121.9448 | 125.6192 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.0735 | 0
2016-10-18 20:00 | 0 | 0 | 0 | 0 | -9.5233 | 139.4931 | 109.2864 | -19.2864 | 137.2598 | 139.9508 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-10-18 21:00 | 0 | 0 | 0 | 0 | -9.5384 | 154.4949 | 111.2333 | -21.2333 | 152.8987 | 154.1167 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-10-18 22:00 | 0 | 0 | 0 | 0 | -9.5536 | 169.4968 | 112.3559 | -22.3559 | 168.792 | 167.3793 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-10-18 23:00 | 0 | 0 | 0 | 0 | -9.5688 | 184.4986 | 112.5596 | -22.5596 | -175.1957 | 171.4053 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.8 | 3.8 | 1.0742 | 0
2016-10-19 | 0 | 0 | 0 | 0 | -9.5839 | -160.4996 | 111.8278 | -21.8278 | -159.2325 | 159.6542 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-10-19 01:00 | 0 | 0 | 0 | 0 | -9.5991 | -145.4977 | 110.2249 | -20.2249 | -143.4726 | 145.6757 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.8 | 3.8 | 1.0742 | 0
2016-10-19 02:00 | 0 | 0 | 0 | 0 | -9.6143 | -130.4959 | 107.8848 | -17.8848 | -128.0156 | 131.387 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.8 | 3.8 | 1.0742 | 0
2016-10-19 03:00 | 0 | 0 | 0 | 0 | -9.6294 | -115.4941 | 104.9909 | -14.9909 | -112.8882 | 117.0454 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.6 | 3.6 | 1.0749 | 0
2016-10-19 04:00 | 0 | 0 | 0 | 0 | -9.6446 | -100.4923 | 101.7538 | -11.7538 | -98.0512 | 102.7445 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0745 | 0
2016-10-19 05:00 | 0 | 0 | 0 | 0 | -9.6597 | -85.4905 | 98.3948 | -8.3948 | -83.4205 | 88.5577 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-10-19 06:00 | 0 | 0 | 0 | 0 | -9.6748 | -70.4887 | 95.1335 | -5.1335 | -68.8933 | 74.5813 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.8 | 3.8 | 1.0742 | 0
2016-10-19 07:00 | 3 | 2.56 | 0.44 | 0 | -9.69 | -55.4869 | 92.1793 | -2.1793 | -54.3732 | 60.982 | 0 | 1.92 | 0.2 | 0 | 0.15 | 2.07 | 4 | 4.0647 | 1.0733 | 0.0018218
2016-10-19 08:00 | 6 | 5.12 | 0.88 | 0 | -9.7051 | -40.4851 | 89.723 | 0.27696 | -39.7893 | 48.0974 | 0 | 3.84 | 0.2 | 0 | 0.3 | 4.14 | 3.9 | 4.0294 | 1.0734 | 0.003644
2016-10-19 09:00 | 9 | 7.68 | 1.32 | 0 | -9.7202 | -25.4833 | 87.9274 | 2.0726 | -25.1095 | 36.702 | 0 | 5.76 | 0.2 | 0 | 0.45 | 6.21 | 3.7 | 3.8941 | 1.0739 | 0.0054684
2016-10-19 10:00 | 10.2367 | 8.3567 | 1.88 | 34.9315 | -9.7354 | -10.4815 | 86.9149 | 3.0851 | -10.3441 | 28.6428 | 30.6567 | 6.2675 | 0.2 | 0 | 0.51183 | 37.4361 | 4.2 | 5.3699 | 1.0687 | 0.032807
2016-10-19 11:00 | 11.4733 | 9.0333 | 2.44 | 43.1295 | -9.7505 | 4.5203 | 86.7568 | 3.2432 | 4.462 | 27.0884 | 38.3984 | 6.775 | 0.2 | 0 | 0.57367 | 45.7471 | 3.8 | 5.2296 | 1.0692 | 0.040108
2016-10-19 12:00 | 12.71 | 9.71 | 3 | 0 | -9.7656 | 19.522 | 87.4653 | 2.5347 | 19.2475 | 32.9727 | 0 | 7.2825 | 0.2 | 0 | 0.6355 | 7.918 | 4 | 4.2474 | 1.0726 | 0.0069644
2016-10-19 13:00 | 8.4733 | 6.4733 | 2 | 0 | -9.7807 | 34.5238 | 88.9916 | 1.0084 | 33.9589 | 43.3642 | 0 | 4.855 | 0.2 | 0 | 0.42367 | 5.2787 | 4.1 | 4.265 | 1.0726 | 0.0046426
2016-10-19 14:00 | 4.2367 | 3.2367 | 1 | 0 | -9.7958 | 49.5256 | 91.2322 | -1.2322 | 48.5712 | 55.795 | 0 | 2.4275 | 0.2 | 0 | 0.21183 | 2.6393 | 3.9 | 3.9825 | 1.0736 | 0.0023235
2016-10-19 15:00 | 0 | 0 | 0 | 0 | -9.8109 | 64.5273 | 94.039 | -4.039 | 63.1006 | 69.1685 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.6 | 3.6 | 1.0749 | 0
2016-10-19 16:00 | 0 | 0 | 0 | 0 | -9.826 | 79.5291 | 97.2314 | -7.2314 | 77.6049 | 83.0227 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-10-19 17:00 | 0 | 0 | 0 | 0 | -9.8411 | 94.5308 | 100.6067 | -10.6067 | 92.1738 | 97.1416 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.2 | 4.2 | 1.0728 | 0
2016-10-19 18:00 | 0 | 0 | 0 | 0 | -9.8562 | 109.5326 | 103.9488 | -13.9488 | 106.9116 | 111.4089 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.0735 | 0
2016-10-19 19:00 | 0 | 0 | 0 | 0 | -9.8713 | 124.5343 | 107.036 | -17.036 | 121.9146 | 125.7483 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-10-19 20:00 | 0 | 0 | 0 | 0 | -9.8864 | 139.536 | 109.6517 | -19.6517 | 137.2443 | 140.0849 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.2 | 4.2 | 1.0728 | 0
2016-10-19 21:00 | 0 | 0 | 0 | 0 | -9.9015 | 154.5377 | 111.5988 | -21.5988 | 152.9032 | 154.2749 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-10-19 22:00 | 0 | 0 | 0 | 0 | -9.9166 | 169.5395 | 112.7204 | -22.7204 | 168.82 | 167.6288 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0763 | 0
2016-10-19 23:00 | 0 | 0 | 0 | 0 | -9.9316 | 184.5412 | 112.9216 | -22.9216 | -175.1427 | 171.6952 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-10-20 | 0 | 0 | 0 | 0 | -9.9467 | -160.4571 | 112.186 | -22.186 | -159.1558 | 159.7565 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0738 | 0
2016-10-20 01:00 | 0 | 0 | 0 | 0 | -9.9618 | -145.4554 | 110.5785 | -20.5785 | -143.3758 | 145.7345 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-10-20 02:00 | 0 | 0 | 0 | 0 | -9.9768 | -130.4537 | 108.2339 | -18.2339 | -127.9037 | 131.4346 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.6 | 3.6 | 1.0749 | 0
2016-10-20 03:00 | 0 | 0 | 0 | 0 | -9.9919 | -115.452 | 105.3364 | -15.3364 | -112.767 | 117.0937 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.4 | 4.4 | 1.0721 | 0
2016-10-20 04:00 | 0 | 0 | 0 | 0 | -10.0069 | -100.4503 | 102.0974 | -12.0974 | -97.9261 | 102.8005 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.8 | 4.8 | 1.0707 | 0
2016-10-20 05:00 | 0 | 0 | 0 | 0 | -10.022 | -85.4486 | 98.7382 | -8.7382 | -83.2966 | 88.6272 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.7 | 4.7 | 1.0711 | 0
2016-10-20 06:00 | 0 | 0 | 0 | 0 | -10.037 | -70.447 | 95.4786 | -5.4786 | -68.7754 | 74.6714 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.8 | 4.8 | 1.0707 | 0
2016-10-20 07:00 | 2.17 | 1.9133 | 0.25667 | 0 | -10.0521 | -55.4453 | 92.5274 | -2.5274 | -54.2655 | 61.1025 | 0 | 1.435 | 0.2 | 0 | 0.1085 | 1.5435 | 4.6 | 4.6482 | 1.0712 | 0.0013558
2016-10-20 08:00 | 4.34 | 3.8267 | 0.51333 | 0 | -10.0671 | -40.4436 | 90.0751 | -0.075135 | -39.6959 | 48.2637 | 0 | 2.87 | 0.2 | 0 | 0.217 | 3.087 | 4.4 | 4.4965 | 1.0718 | 0.002713
2016-10-20 09:00 | 6.51 | 5.74 | 0.77 | 0 | -10.0821 | -25.4419 | 88.2836 | 1.7164 | -25.0338 | 36.9373 | 0 | 4.305 | 0.2 | 0 | 0.3255 | 4.6305 | 4.7 | 4.8447 | 1.0705 | 0.0040649
2016-10-20 10:00 | 7.8133 | 6.49 | 1.3233 | 0 | -10.0971 | -10.4403 | 87.2747 | 2.7253 | -10.2886 | 28.9656 | 0 | 4.8675 | 0.2 | 0 | 0.39067 | 5.2582 | 4.7 | 4.8643 | 1.0705 | 0.0046156
2016-10-20 11:00 | 9.1167 | 7.24 | 1.8767 | 0 | -10.1122 | 4.5614 | 87.1192 | 2.8808 | 4.4961 | 27.4518 | 0 | 5.43 | 0.2 | 0 | 0.45583 | 5.8858 | 4.4 | 4.5839 | 1.0715 | 0.0051713
2016-10-20 12:00 | 10.42 | 7.99 | 2.43 | 0 | -10.1272 | 19.563 | 87.8289 | 2.1711 | 19.2605 | 33.2895 | 0 | 5.9925 | 0.2 | 0 | 0.521 | 6.5135 | 4.2 | 4.4035 | 1.0721 | 0.0057261
2016-10-20 13:00 | 6.9467 | 5.3267 | 1.62 | 0 | -10.1422 | 34.5647 | 89.3552 | 0.64479 | 33.9525 | 43.6185 | 0 | 3.995 | 0.2 | 0 | 0.34733 | 4.3423 | 4.6 | 4.7357 | 1.0709 | 0.0038133
2016-10-20 14:00 | 3.4733 | 2.6633 | 0.81 | 0 | -10.1572 | 49.5663 | 91.5951 | -1.5951 | 48.5487 | 56.0026 | 0 | 1.9975 | 0.2 | 0 | 0.17367 | 2.1712 | 4.7 | 4.7678 | 1.0708 | 0.0019064
2016-10-20 15:00 | 0 | 0 | 0 | 0 | -10.1722 | 64.5679 | 94.4008 | -4.4008 | 63.0659 | 69.344 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.9 | 4.9 | 1.0703 | 0
2016-10-20 16:00 | 0 | 0 | 0 | 0 | -10.1872 | 79.5696 | 97.5924 | -7.5924 | 77.5627 | 83.176 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.7 | 4.7 | 1.0711 | 0
2016-10-20 17:00 | 0 | 0 | 0 | 0 | -10.2022 | 94.5712 | 100.9673 | -10.9673 | 92.1291 | 97.2796 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0714 | 0
2016-10-20 18:00 | 0 | 0 | 0 | 0 | -10.2172 | 109.5728 | 104.3096 | -14.3096 | 106.8699 | 111.5371 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-10-20 19:00 | 0 | 0 | 0 | 0 | -10.2322 | 124.5744 | 107.3977 | -17.3977 | 121.8817 | 125.8724 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.9 | 4.9 | 1.0703 | 0
2016-10-20 20:00 | 0 | 0 | 0 | 0 | -10.2472 | 139.576 | 110.0142 | -20.0142 | 137.226 | 140.2132 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.3 | 4.3 | 1.0724 | 0
2016-10-20 21:00 | 0 | 0 | 0 | 0 | -10.2622 | 154.5776 | 111.9616 | -21.9616 | 152.9047 | 154.4256 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.3 | 4.3 | 1.0724 | 0
2016-10-20 22:00 | 0 | 0 | 0 | 0 | -10.2771 | 169.5792 | 113.0823 | -23.0823 | 168.8451 | 167.8688 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.8 | 4.8 | 1.0707 | 0
2016-10-20 23:00 | 0 | 0 | 0 | 0 | -10.2921 | 184.5808 | 113.2812 | -23.2812 | -175.0926 | 171.9787 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0714 | 0
2016-10-21 | 0 | 0 | 0 | 0 | -10.3071 | -160.4176 | 112.5419 | -22.5419 | -159.082 | 159.8549 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5333 | 4.5333 | 1.0716 | 0
2016-10-21 01:00 | 0 | 0 | 0 | 0 | -10.322 | -145.416 | 110.93 | -20.93 | -143.282 | 145.7922 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.4667 | 4.4667 | 1.0719 | 0
2016-10-21 02:00 | 0 | 0 | 0 | 0 | -10.337 | -130.4144 | 108.5812 | -18.5812 | -127.795 | 131.4825 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.4 | 4.4 | 1.0721 | 0
2016-10-21 03:00 | 0 | 0 | 0 | 0 | -10.3519 | -115.4129 | 105.6802 | -15.6802 | -112.649 | 117.1432 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.8 | 4.8 | 1.0707 | 0
2016-10-21 04:00 | 0 | 0 | 0 | 0 | -10.3669 | -100.4113 | 102.4392 | -12.4392 | -97.8043 | 102.8582 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.8 | 4.8 | 1.0707 | 0
2016-10-21 05:00 | 0 | 0 | 0 | 0 | -10.3818 | -85.4097 | 99.0799 | -9.0799 | -83.176 | 88.6989 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.9 | 4.9 | 1.0703 | 0
2016-10-21 06:00 | 0 | 0 | 0 | 0 | -10.3968 | -70.4082 | 95.8219 | -5.8219 | -68.6607 | 74.7641 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.8 | 4.8 | 1.0707 | 0
2016-10-21 07:00 | 2.7467 | 2.0267 | 0.72 | 0 | -10.4117 | -55.4066 | 92.8737 | -2.8737 | -54.1612 | 61.2258 | 0 | 1.52 | 0.2 | 0 | 0.13733 | 1.6573 | 4.8 | 4.8518 | 1.0705 | 0.0014548
2016-10-21 08:00 | 5.4933 | 4.0533 | 1.44 | 0 | -10.4266 | -40.4051 | 90.4253 | -0.42528 | -39.6058 | 48.4327 | 0 | 3.04 | 0.2 | 0 | 0.27467 | 3.3147 | 4.8 | 4.9036 | 1.0703 | 0.0029092
2016-10-21 09:00 | 8.24 | 6.08 | 2.16 | 0 | -10.4416 | -25.4035 | 88.6377 | 1.3623 | -24.9613 | 37.1746 | 0 | 4.56 | 0.2 | 0 | 0.412 | 4.972 | 4.8 | 4.9554 | 1.0702 | 0.0043631
2016-10-21 10:00 | 8.41 | 6.3033 | 2.1067 | 0 | -10.4565 | -10.402 | 87.6322 | 2.3678 | -10.2362 | 29.2881 | 0 | 4.7275 | 0.2 | 0 | 0.4205 | 5.148 | 4.7 | 4.8609 | 1.0705 | 0.0045189
2016-10-21 11:00 | 8.58 | 6.5267 | 2.0533 | 0 | -10.4714 | 4.5995 | 87.479 | 2.521 | 4.5272 | 27.8124 | 0 | 4.895 | 0.2 | 0 | 0.429 | 5.324 | 4.9 | 5.0664 | 1.0698 | 0.0046703
2016-10-21 12:00 | 8.75 | 6.75 | 2 | 0 | -10.4863 | 19.6011 | 88.1898 | 1.8102 | 19.2706 | 33.6034 | 0 | 5.0625 | 0.2 | 0 | 0.4375 | 5.5 | 5.2 | 5.3719 | 1.0687 | 0.0048198
2016-10-21 13:00 | 5.8333 | 4.5 | 1.3333 | 0 | -10.5012 | 34.6026 | 89.7161 | 0.28394 | 33.9436 | 43.8701 | 0 | 3.375 | 0.2 | 0 | 0.29167 | 3.6667 | 5.2 | 5.3146 | 1.0689 | 0.0032138
2016-10-21 14:00 | 2.9167 | 2.25 | 0.66667 | 0 | -10.5161 | 49.6041 | 91.955 | -1.955 | 48.5236 | 56.2075 | 0 | 1.6875 | 0.2 | 0 | 0.14583 | 1.8333 | 5.8 | 5.8573 | 1.067 | 0.0016041
2016-10-21 15:00 | 0 | 0 | 0 | 0 | -10.531 | 64.6056 | 94.7597 | -4.7597 | 63.0287 | 69.5165 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.8 | 5.8 | 1.0672 | 0
2016-10-21 16:00 | 0 | 0 | 0 | 0 | -10.5459 | 79.6071 | 97.9503 | -7.9503 | 77.5179 | 83.3259 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6 | 6 | 1.0665 | 0
2016-10-21 17:00 | 0 | 0 | 0 | 0 | -10.5608 | 94.6086 | 101.3248 | -11.3248 | 92.0819 | 97.4137 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5 | 5 | 1.07 | 0
2016-10-21 18:00 | 0 | 0 | 0 | 0 | -10.5757 | 109.6101 | 104.6675 | -14.6675 | 106.8256 | 111.661 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.7 | 5.7 | 1.0675 | 0
2016-10-21 19:00 | 0 | 0 | 0 | 0 | -10.5906 | 124.6116 | 107.7563 | -17.7563 | 121.8461 | 125.9915 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.4 | 5.4 | 1.0686 | 0
2016-10-21 20:00 | 0 | 0 | 0 | 0 | -10.6055 | 139.6131 | 110.3738 | -20.3738 | 137.2049 | 140.3355 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.2 | 5.2 | 1.0693 | 0
2016-10-21 21:00 | 0 | 0 | 0 | 0 | -10.6203 | 154.6145 | 112.3216 | -22.3216 | 152.9033 | 154.5687 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.6 | 5.6 | 1.0679 | 0
2016-10-21 22:00 | 0 | 0 | 0 | 0 | -10.6352 | 169.616 | 113.4417 | -23.4417 | 168.8672 | 168.0987 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.6 | 5.6 | 1.0679 | 0
2016-10-21 23:00 | 0 | 0 | 0 | 0 | -10.6501 | 184.6175 | 113.6384 | -23.6384 | -175.0456 | 172.2553 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.9 | 5.9 | 1.0669 | 0
2016-10-22 | 0 | 0 | 0 | 0 | -10.6649 | -160.3811 | 112.8957 | -22.8957 | -159.0114 | 159.9494 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.9 | 5.9 | 1.0669 | 0
2016-10-22 01:00 | 0 | 0 | 0 | 0 | -10.6798 | -145.3796 | 111.2795 | -21.2795 | -143.1913 | 145.849 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.6 | 5.6 | 1.0679 | 0
2016-10-22 02:00 | 0 | 0 | 0 | 0 | -10.6946 | -130.3781 | 108.9264 | -18.9264 | -127.6894 | 131.5308 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.6 | 5.6 | 1.0679 | 0
2016-10-22 03:00 | 0 | 0 | 0 | 0 | -10.7095 | -115.3767 | 106.0221 | -16.0221 | -112.5341 | 117.1938 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5 | 5 | 1.07 | 0
2016-10-22 04:00 | 0 | 0 | 0 | 0 | -10.7243 | -100.3753 | 102.7793 | -12.7793 | -97.6856 | 102.9176 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.3 | 5.3 | 1.069 | 0
2016-10-22 05:00 | 0 | 0 | 0 | 0 | -10.7392 | -85.3738 | 99.4198 | -9.4198 | -83.0587 | 88.7728 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.4 | 5.4 | 1.0686 | 0
2016-10-22 06:00 | 0 | 0 | 0 | 0 | -10.754 | -70.3724 | 96.1634 | -6.1634 | -68.5494 | 74.8592 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.3 | 5.3 | 1.069 | 0
2016-10-22 07:00 | 2.81 | 1.8967 | 0.91333 | 0 | -10.7688 | -55.371 | 93.2181 | -3.2181 | -54.0602 | 61.3518 | 0 | 1.4225 | 0.2 | 0 | 0.1405 | 1.563 | 5.3 | 5.3488 | 1.0688 | 0.0013698
2016-10-22 08:00 | 5.62 | 3.7933 | 1.8267 | 0 | -10.7837 | -40.3695 | 90.7734 | -0.77336 | -39.5191 | 48.6044 | 0 | 2.845 | 0.2 | 0 | 0.281 | 3.126 | 5.6 | 5.6977 | 1.0676 | 0.0027365
2016-10-22 09:00 | 8.43 | 5.69 | 2.74 | 0 | -10.7985 | -25.3681 | 88.9895 | 1.0105 | -24.8921 | 37.4138 | 0 | 4.2675 | 0.2 | 0 | 0.4215 | 4.689 | 5.1 | 5.2465 | 1.0691 | 0.0041108
2016-10-22 10:00 | 8.93 | 6.0233 | 2.9067 | 0 | -10.8133 | -10.3667 | 87.9873 | 2.0127 | -10.187 | 29.6101 | 0 | 4.5175 | 0.2 | 0 | 0.4465 | 4.964 | 5.4 | 5.5551 | 1.0681 | 0.0043475
2016-10-22 11:00 | 9.43 | 6.3567 | 3.0733 | 0 | -10.8281 | 4.6347 | 87.8363 | 2.1637 | 4.5552 | 28.1699 | 0 | 4.7675 | 0.2 | 0 | 0.4715 | 5.239 | 6 | 6.1637 | 1.0659 | 0.0045792
2016-10-22 12:00 | 9.93 | 6.69 | 3.24 | 0 | -10.8429 | 19.6361 | 88.548 | 1.452 | 19.278 | 33.9143 | 0 | 5.0175 | 0.2 | 0 | 0.4965 | 5.514 | 5.2 | 5.3723 | 1.0687 | 0.0048321
2016-10-22 13:00 | 6.62 | 4.46 | 2.16 | 0 | -10.8577 | 34.6375 | 90.074 | -0.073995 | 33.9319 | 44.1189 | 0 | 3.345 | 0.2 | 0 | 0.331 | 3.676 | 4.9 | 5.0149 | 1.0699 | 0.0032252
2016-10-22 14:00 | 3.31 | 2.23 | 1.08 | 0 | -10.8725 | 49.6389 | 92.312 | -2.312 | 48.496 | 56.4095 | 0 | 1.6725 | 0.2 | 0 | 0.1655 | 1.838 | 4.7 | 4.7574 | 1.0708 | 0.0016139
2016-10-22 15:00 | 0 | 0 | 0 | 0 | -10.8873 | 64.6402 | 95.1154 | -5.1154 | 62.9891 | 69.6858 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0714 | 0
2016-10-22 16:00 | 0 | 0 | 0 | 0 | -10.9021 | 79.6416 | 98.3049 | -8.3049 | 77.4707 | 83.4723 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5 | 5 | 1.07 | 0
2016-10-22 17:00 | 0 | 0 | 0 | 0 | -10.9169 | 94.643 | 101.6791 | -11.6791 | 92.0321 | 97.544 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.9 | 5.9 | 1.0669 | 0
2016-10-22 18:00 | 0 | 0 | 0 | 0 | -10.9316 | 109.6444 | 105.0221 | -15.0221 | 106.7787 | 111.7806 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.3 | 5.3 | 1.069 | 0
2016-10-22 19:00 | 0 | 0 | 0 | 0 | -10.9464 | 124.6457 | 108.1119 | -18.1119 | 121.8077 | 126.1056 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.6 | 5.6 | 1.0679 | 0
2016-10-22 20:00 | 0 | 0 | 0 | 0 | -10.9612 | 139.6471 | 110.7304 | -20.7304 | 137.1808 | 140.4519 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.6 | 5.6 | 1.0679 | 0
2016-10-22 21:00 | 0 | 0 | 0 | 0 | -10.9759 | 154.6484 | 112.6788 | -22.6788 | 152.8989 | 154.7041 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.8 | 5.8 | 1.0672 | 0
2016-10-22 22:00 | 0 | 0 | 0 | 0 | -10.9907 | 169.6498 | 113.7983 | -23.7983 | 168.8861 | 168.3182 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5 | 5 | 1.07 | 0
2016-10-22 23:00 | 0 | 0 | 0 | 0 | -11.0055 | 184.6511 | 113.9931 | -23.9931 | -175.0018 | 172.5245 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.4 | 4.4 | 1.0721 | 0
2016-10-23 | 0 | 0 | 0 | 0 | -11.0202 | -160.3476 | 113.247 | -23.247 | -158.9439 | 160.0401 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.9 | 4.9 | 1.0703 | 0
2016-10-23 01:00 | 0 | 0 | 0 | 0 | -11.035 | -145.3462 | 111.6268 | -21.6268 | -143.1039 | 145.9048 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0714 | 0
2016-10-23 02:00 | 0 | 0 | 0 | 0 | -11.0497 | -130.3449 | 109.2696 | -19.2696 | -127.5871 | 131.5796 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.7 | 5.7 | 1.0675 | 0
2016-10-23 03:00 | 0 | 0 | 0 | 0 | -11.0644 | -115.3436 | 106.3621 | -16.3621 | -112.4226 | 117.2457 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.3 | 5.3 | 1.069 | 0
2016-10-23 04:00 | 0 | 0 | 0 | 0 | -11.0792 | -100.3423 | 103.1174 | -13.1174 | -97.5704 | 102.9788 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6.1 | 6.1 | 1.0661 | 0
2016-10-23 05:00 | 0 | 0 | 0 | 0 | -11.0939 | -85.341 | 99.7579 | -9.7579 | -82.9448 | 88.8489 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6.2 | 6.2 | 1.0658 | 0
2016-10-23 06:00 | 0 | 0 | 0 | 0 | -11.1086 | -70.3397 | 96.5029 | -6.5029 | -68.4416 | 74.9568 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6.1 | 6.1 | 1.0661 | 0
2016-10-23 07:00 | 1.1033 | 0.98 | 0.12333 | 0 | -11.1233 | -55.3384 | 93.5605 | -3.5605 | -53.9627 | 61.4805 | 0 | 0.735 | 0.2 | 0 | 0.055167 | 0.79017 | 5.9 | 5.9247 | 1.0668 | 0.0006912
2016-10-23 08:00 | 2.2067 | 1.96 | 0.24667 | 0 | -11.138 | -40.3371 | 91.1193 | -1.1193 | -39.4357 | 48.7787 | 0 | 1.47 | 0.2 | 0 | 0.11033 | 1.5803 | 5.6 | 5.6494 | 1.0677 | 0.0013836
2016-10-23 09:00 | 3.31 | 2.94 | 0.37 | 0 | -11.1527 | -25.3358 | 89.3391 | 0.66092 | -24.8263 | 37.6547 | 0 | 2.205 | 0.2 | 0 | 0.1655 | 2.3705 | 5.6 | 5.6741 | 1.0676 | 0.0020753
2016-10-23 10:00 | 3.34 | 3.0367 | 0.30333 | 0 | -11.1674 | -10.3345 | 88.3399 | 1.6601 | -10.141 | 29.9314 | 0 | 2.2775 | 0.2 | 0 | 0.167 | 2.4445 | 5.5 | 5.5764 | 1.068 | 0.0021408
2016-10-23 11:00 | 3.37 | 3.1333 | 0.23667 | 0 | -11.1821 | 4.6668 | 88.1908 | 1.8092 | 4.5803 | 28.5243 | 0 | 2.35 | 0.2 | 0 | 0.1685 | 2.5185 | 5.3 | 5.3787 | 1.0687 | 0.002207
2016-10-23 12:00 | 3.4 | 3.23 | 0.17 | 0 | -11.1968 | 19.668 | 88.9032 | 1.0968 | 19.2824 | 34.222 | 0 | 2.4225 | 0.2 | 0 | 0.17 | 2.5925 | 5.2 | 5.281 | 1.069 | 0.0022726
2016-10-23 13:00 | 2.2667 | 2.1533 | 0.11333 | 0 | -11.2115 | 34.6693 | 90.4289 | -0.42889 | 33.9175 | 44.3649 | 0 | 1.615 | 0.2 | 0 | 0.11333 | 1.7283 | 5.1 | 5.154 | 1.0695 | 0.0015157
2016-10-23 14:00 | 1.1333 | 1.0767 | 0.056667 | 0 | -11.2262 | 49.6706 | 92.6657 | -2.6657 | 48.4658 | 56.6085 | 0 | 0.8075 | 0.2 | 0 | 0.056667 | 0.86417 | 5.3 | 5.327 | 1.0689 | 0.00075741
2016-10-23 15:00 | 0 | 0 | 0 | 0 | -11.2409 | 64.6718 | 95.4678 | -5.4678 | 62.9468 | 69.8519 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.6 | 5.6 | 1.0679 | 0
2016-10-23 16:00 | 0 | 0 | 0 | 0 | -11.2555 | 79.6731 | 98.6563 | -8.6563 | 77.421 | 83.6151 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.1 | 5.1 | 1.0696 | 0
2016-10-23 17:00 | 0 | 0 | 0 | 0 | -11.2702 | 94.6743 | 102.0301 | -12.0301 | 91.9797 | 97.6703 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-10-23 18:00 | 0 | 0 | 0 | 0 | -11.2849 | 109.6756 | 105.3734 | -15.3734 | 106.7291 | 111.8956 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.3 | 4.3 | 1.0724 | 0
2016-10-23 19:00 | 0 | 0 | 0 | 0 | -11.2995 | 124.6768 | 108.4641 | -18.4641 | 121.7665 | 126.2147 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5 | 4.5 | 1.0717 | 0
2016-10-23 20:00 | 0 | 0 | 0 | 0 | -11.3142 | 139.678 | 111.0838 | -21.0838 | 137.1539 | 140.5622 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0714 | 0
2016-10-23 21:00 | 0 | 0 | 0 | 0 | -11.3288 | 154.6792 | 113.0329 | -23.0329 | 152.8914 | 154.8317 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.4 | 4.4 | 1.0721 | 0
2016-10-23 22:00 | 0 | 0 | 0 | 0 | -11.3435 | 169.6805 | 114.152 | -24.152 | 168.902 | 168.5269 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.8 | 4.8 | 1.0707 | 0
2016-10-23 23:00 | 0 | 0 | 0 | 0 | -11.3581 | 184.6817 | 114.3451 | -24.3451 | -174.9612 | 172.786 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.4 | 4.4 | 1.0721 | 0
2016-10-24 | 0 | 0 | 0 | 0 | -11.3728 | -160.3171 | 113.5959 | -23.5959 | -158.8797 | 160.1272 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5 | 4.5 | 1.0717 | 0
2016-10-24 01:00 | 0 | 0 | 0 | 0 | -11.3874 | -145.3159 | 111.9717 | -21.9717 | -143.0198 | 145.9598 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5 | 4.5 | 1.0717 | 0
2016-10-24 02:00 | 0 | 0 | 0 | 0 | -11.402 | -130.3147 | 109.6106 | -19.6106 | -127.4882 | 131.6288 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0745 | 0
2016-10-24 03:00 | 0 | 0 | 0 | 0 | -11.4166 | -115.3135 | 106.7 | -16.7 | -112.3145 | 117.2989 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.3 | 4.3 | 1.0724 | 0
2016-10-24 04:00 | 0 | 0 | 0 | 0 | -11.4312 | -100.3124 | 103.4535 | -13.4535 | -97.4586 | 103.0418 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.6 | 3.6 | 1.0749 | 0
2016-10-24 05:00 | 0 | 0 | 0 | 0 | -11.4458 | -85.3112 | 100.0939 | -10.0939 | -82.8344 | 88.9272 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.0735 | 0
2016-10-24 06:00 | 0 | 0 | 0 | 0 | -11.4604 | -70.31 | 96.8404 | -6.8404 | -68.3373 | 75.0569 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.2 | 4.2 | 1.0728 | 0
2016-10-24 07:00 | 0.78 | 0.69667 | 0.083333 | 0 | -11.475 | -55.3088 | 93.9007 | -3.9007 | -53.8687 | 61.6117 | 0 | 0.5225 | 0.2 | 0 | 0.039 | 0.5615 | 4.4 | 4.4175 | 1.072 | 0.0004936
2016-10-24 08:00 | 1.56 | 1.3933 | 0.16667 | 0 | -11.4896 | -40.3077 | 91.4629 | -1.4629 | -39.3559 | 48.9554 | 0 | 1.045 | 0.2 | 0 | 0.078 | 1.123 | 3.5 | 3.5351 | 1.0751 | 0.00099004
2016-10-24 09:00 | 2.34 | 2.09 | 0.25 | 0 | -11.5042 | -25.3065 | 89.6862 | 0.31384 | -24.7639 | 37.8972 | 0 | 1.5675 | 0.2 | 0 | 0.117 | 1.6845 | 2.4 | 2.4526 | 1.0789 | 0.0014903
2016-10-24 10:00 | 2.5333 | 2.2633 | 0.27 | 0 | -11.5188 | -10.3054 | 88.6898 | 1.3102 | -10.0983 | 30.2519 | 0 | 1.6975 | 0.2 | 0 | 0.12667 | 1.8242 | 3.3 | 3.357 | 1.0758 | 0.0016091
2016-10-24 11:00 | 2.7267 | 2.4367 | 0.29 | 0 | -11.5334 | 4.6958 | 88.5426 | 1.4574 | 4.6022 | 28.8755 | 0 | 1.8275 | 0.2 | 0 | 0.13633 | 1.9638 | 3 | 3.0614 | 1.0768 | 0.001734
2016-10-24 12:00 | 2.92 | 2.61 | 0.31 | 0 | -11.548 | 19.6969 | 89.2555 | 0.74449 | 19.2839 | 34.5266 | 0 | 1.9575 | 0.2 | 0 | 0.146 | 2.1035 | 3.6 | 3.6657 | 1.0747 | 0.0018537
2016-10-24 13:00 | 1.9467 | 1.74 | 0.20667 | 0 | -11.5625 | 34.698 | 90.7806 | -0.78062 | 33.9004 | 44.6079 | 0 | 1.305 | 0.2 | 0 | 0.097333 | 1.4023 | 3 | 3.0438 | 1.0768 | 0.0012383
2016-10-24 14:00 | 0.97333 | 0.87 | 0.10333 | 0 | -11.5771 | 49.6992 | 93.0162 | -3.0162 | 48.4329 | 56.8044 | 0 | 0.6525 | 0.2 | 0 | 0.048667 | 0.70117 | 3.1 | 3.1219 | 1.0766 | 0.00061898
2016-10-24 15:00 | 0 | 0 | 0 | 0 | -11.5917 | 64.7003 | 95.8168 | -5.8168 | 62.9021 | 70.0147 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.0788 | 0
2016-10-24 16:00 | 0 | 0 | 0 | 0 | -11.6062 | 79.7014 | 99.0043 | -9.0043 | 77.3687 | 83.7543 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-10-24 17:00 | 0 | 0 | 0 | 0 | -11.6208 | 94.7025 | 102.3776 | -12.3776 | 91.9248 | 97.7926 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-10-24 18:00 | 0 | 0 | 0 | 0 | -11.6353 | 109.7036 | 105.7213 | -15.7213 | 106.6768 | 112.0062 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-10-24 19:00 | 0 | 0 | 0 | 0 | -11.6498 | 124.7047 | 108.813 | -18.813 | 121.7225 | 126.3186 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0763 | 0
2016-10-24 20:00 | 0 | 0 | 0 | 0 | -11.6644 | 139.7058 | 111.4339 | -21.4339 | 137.124 | 140.6664 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0763 | 0
2016-10-24 21:00 | 0 | 0 | 0 | 0 | -11.6789 | 154.7069 | 113.3839 | -23.3839 | 152.8808 | 154.9515 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-10-24 22:00 | 0 | 0 | 0 | 0 | -11.6934 | 169.708 | 114.5028 | -24.5028 | 168.9146 | 168.7242 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-10-24 23:00 | 0 | 0 | 0 | 0 | -11.7079 | 184.7091 | 114.6943 | -24.6943 | -174.9238 | 173.0393 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-10-25 | 0 | 0 | 0 | 0 | -11.7225 | -160.2898 | 113.9422 | -23.9422 | -158.8189 | 160.2107 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-10-25 01:00 | 0 | 0 | 0 | 0 | -11.737 | -145.2888 | 112.3142 | -22.3142 | -142.939 | 146.0141 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-10-25 02:00 | 0 | 0 | 0 | 0 | -11.7515 | -130.2877 | 109.9494 | -19.9494 | -127.3926 | 131.6786 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-10-25 03:00 | 0 | 0 | 0 | 0 | -11.766 | -115.2866 | 107.0357 | -17.0357 | -112.2098 | 117.3533 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0745 | 0
2016-10-25 04:00 | 0 | 0 | 0 | 0 | -11.7805 | -100.2856 | 103.7875 | -13.7875 | -97.3503 | 103.1066 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.8 | 3.8 | 1.0742 | 0
2016-10-25 05:00 | 0 | 0 | 0 | 0 | -11.7949 | -85.2845 | 100.4278 | -10.4278 | -82.7276 | 89.0076 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0763 | 0
2016-10-25 06:00 | 0 | 0 | 0 | 0 | -11.8094 | -70.2835 | 97.1757 | -7.1757 | -68.2365 | 75.1594 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.3 | 4.3 | 1.0724 | 0
2016-10-25 07:00 | 0.88667 | 0.68 | 0.20667 | 0 | -11.8239 | -55.2825 | 94.2387 | -4.2387 | -53.7782 | 61.7455 | 0 | 0.51 | 0.2 | 0 | 0.044333 | 0.55433 | 4.5 | 4.5173 | 1.0717 | 0.00048714
2016-10-25 08:00 | 1.7733 | 1.36 | 0.41333 | 0 | -11.8384 | -40.2814 | 91.8042 | -1.8042 | -39.2796 | 49.1344 | 0 | 1.02 | 0.2 | 0 | 0.088667 | 1.1087 | 3 | 3.0346 | 1.0769 | 0.000979
2016-10-25 09:00 | 2.66 | 2.04 | 0.62 | 0 | -11.8528 | -25.2804 | 90.0307 | -0.030694 | -24.7048 | 38.141 | 0 | 1.53 | 0.2 | 0 | 0.133 | 1.663 | 3 | 3.052 | 1.0768 | 0.0014684
2016-10-25 10:00 | 2.8467 | 2.16 | 0.68667 | 0 | -11.8673 | -10.2794 | 89.037 | 0.96303 | -10.0588 | 30.5713 | 0 | 1.62 | 0.2 | 0 | 0.14233 | 1.7623 | 2.6 | 2.6551 | 1.0782 | 0.0015581
2016-10-25 11:00 | 3.0333 | 2.28 | 0.75333 | 0 | -11.8818 | 4.7216 | 88.8913 | 1.1087 | 4.6211 | 29.2234 | 0 | 1.71 | 0.2 | 0 | 0.15167 | 1.8617 | 2.2 | 2.2582 | 1.0796 | 0.0016481
2016-10-25 12:00 | 3.22 | 2.4 | 0.82 | 0 | -11.8962 | 19.7226 | 89.6047 | 0.39533 | 19.2826 | 34.8277 | 0 | 1.8 | 0.2 | 0 | 0.161 | 1.961 | 2 | 2.0613 | 1.0803 | 0.0017371
2016-10-25 13:00 | 2.1467 | 1.6 | 0.54667 | 0 | -11.9107 | 34.7236 | 91.1291 | -1.1291 | 33.8805 | 44.8477 | 0 | 1.2 | 0.2 | 0 | 0.10733 | 1.3073 | 1.8 | 1.8409 | 1.0811 | 0.0011589
2016-10-25 14:00 | 1.0733 | 0.8 | 0.27333 | 0 | -11.9251 | 49.7246 | 93.3633 | -3.3633 | 48.3975 | 56.9971 | 0 | 0.6 | 0.2 | 0 | 0.053667 | 0.65367 | 1.5 | 1.5204 | 1.0822 | 0.00058005
2016-10-25 15:00 | 0 | 0 | 0 | 0 | -11.9395 | 64.7256 | 96.1624 | -6.1624 | 62.8548 | 70.174 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0816 | 0
2016-10-25 16:00 | 0 | 0 | 0 | 0 | -11.954 | 79.7266 | 99.3487 | -9.3487 | 77.3138 | 83.8898 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0819 | 0
2016-10-25 17:00 | 0 | 0 | 0 | 0 | -11.9684 | 94.7276 | 102.7215 | -12.7215 | 91.8672 | 97.9108 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0819 | 0
2016-10-25 18:00 | 0 | 0 | 0 | 0 | -11.9828 | 109.7286 | 106.0656 | -16.0656 | 106.6218 | 112.1123 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0819 | 0
2016-10-25 19:00 | 0 | 0 | 0 | 0 | -11.9972 | 124.7295 | 109.1584 | -19.1584 | 121.6757 | 126.4174 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0816 | 0
2016-10-25 20:00 | 0 | 0 | 0 | 0 | -12.0116 | 139.7305 | 111.7807 | -21.7807 | 137.091 | 140.7645 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0819 | 0
2016-10-25 21:00 | 0 | 0 | 0 | 0 | -12.026 | 154.7315 | 113.7316 | -23.7316 | 152.867 | 155.0634 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-10-25 22:00 | 0 | 0 | 0 | 0 | -12.0404 | 169.7324 | 114.8505 | -24.8505 | 168.9239 | 168.9099 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0816 | 0
2016-10-25 23:00 | 0 | 0 | 0 | 0 | -12.0548 | 184.7334 | 115.0406 | -25.0406 | -174.8898 | 173.2838 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0826 | 0
2016-10-26 | 0 | 0 | 0 | 0 | -12.0692 | -160.2657 | 114.2857 | -24.2857 | -158.7614 | 160.2907 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-10-26 01:00 | 0 | 0 | 0 | 0 | -12.0836 | -145.2648 | 112.6542 | -22.6542 | -142.8617 | 146.0677 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0816 | 0
2016-10-26 02:00 | 0 | 0 | 0 | 0 | -12.098 | -130.2638 | 110.2857 | -20.2857 | -127.3006 | 131.729 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-10-26 03:00 | 0 | 0 | 0 | 0 | -12.1123 | -115.2629 | 107.3691 | -17.3691 | -112.1086 | 117.4091 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-10-26 04:00 | 0 | 0 | 0 | 0 | -12.1267 | -100.262 | 104.1193 | -14.1193 | -97.2455 | 103.1732 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0774 | 0
2016-10-26 05:00 | 0 | 0 | 0 | 0 | -12.1411 | -85.2611 | 100.7595 | -10.7595 | -82.6243 | 89.0902 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0745 | 0
2016-10-26 06:00 | 0 | 0 | 0 | 0 | -12.1554 | -70.2602 | 97.5088 | -7.5088 | -68.1393 | 75.2643 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.6 | 3.6 | 1.0749 | 0
2016-10-26 07:00 | 0.25667 | 0.25667 | 0 | 0 | -12.1698 | -55.2593 | 94.5743 | -4.5743 | -53.6914 | 61.8817 | 0 | 0.1925 | 0.2 | 0 | 0.012833 | 0.20533 | 4.2 | 4.2064 | 1.0728 | 0.00018063
2016-10-26 08:00 | 0.51333 | 0.51333 | 0 | 0 | -12.1841 | -40.2584 | 92.1429 | -2.1429 | -39.2068 | 49.3156 | 0 | 0.385 | 0.2 | 0 | 0.025667 | 0.41067 | 4.2 | 4.2128 | 1.0728 | 0.00036125
2016-10-26 09:00 | 0.77 | 0.77 | 0 | 0 | -12.1985 | -25.2575 | 90.3726 | -0.37255 | -24.6492 | 38.3861 | 0 | 0.5775 | 0.2 | 0 | 0.0385 | 0.616 | 3.8 | 3.8192 | 1.0741 | 0.00054257
2016-10-26 10:00 | 0.84333 | 0.84333 | 0 | 0 | -12.2128 | -10.2566 | 89.3813 | 0.61871 | -10.0226 | 30.8896 | 0 | 0.6325 | 0.2 | 0 | 0.042167 | 0.67467 | 4.1 | 4.1211 | 1.0731 | 0.00059365
2016-10-26 11:00 | 0.91667 | 0.91667 | 0 | 0 | -12.2271 | 4.7443 | 89.2371 | 0.76293 | 4.6368 | 29.5678 | 0 | 0.6875 | 0.2 | 0 | 0.045833 | 0.73333 | 4 | 4.0229 | 1.0734 | 0.00064548
2016-10-26 12:00 | 0.99 | 0.99 | 0 | 0 | -12.2415 | 19.7452 | 89.9506 | 0.04942 | 19.2782 | 35.1253 | 0 | 0.7425 | 0.2 | 0 | 0.0495 | 0.792 | 4.4 | 4.4248 | 1.072 | 0.00069621
2016-10-26 13:00 | 0.66 | 0.66 | 0 | 0 | -12.2558 | 34.746 | 91.4741 | -1.4741 | 33.8579 | 45.0843 | 0 | 0.495 | 0.2 | 0 | 0.033 | 0.528 | 5.8 | 5.8165 | 1.0671 | 0.00046203
2016-10-26 14:00 | 0.33 | 0.33 | 0 | 0 | -12.2701 | 49.7469 | 93.7069 | -3.7069 | 48.3594 | 57.1865 | 0 | 0.2475 | 0.2 | 0 | 0.0165 | 0.264 | 5.7 | 5.7082 | 1.0675 | 0.0002311
2016-10-26 15:00 | 0 | 0 | 0 | 0 | -12.2844 | 64.7478 | 96.5044 | -6.5044 | 62.8049 | 70.3298 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.9 | 5.9 | 1.0669 | 0
2016-10-26 16:00 | 0 | 0 | 0 | 0 | -12.2987 | 79.7486 | 99.6894 | -9.6894 | 77.2564 | 84.0215 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.8 | 5.8 | 1.0672 | 0
2016-10-26 17:00 | 0 | 0 | 0 | 0 | -12.313 | 94.7495 | 103.0618 | -13.0618 | 91.8071 | 98.0249 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.7 | 5.7 | 1.0675 | 0
2016-10-26 18:00 | 0 | 0 | 0 | 0 | -12.3273 | 109.7503 | 106.4062 | -16.4062 | 106.564 | 112.2137 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.6 | 5.6 | 1.0679 | 0
2016-10-26 19:00 | 0 | 0 | 0 | 0 | -12.3416 | 124.7511 | 109.5002 | -19.5002 | 121.6259 | 126.5109 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.6 | 5.6 | 1.0679 | 0
2016-10-26 20:00 | 0 | 0 | 0 | 0 | -12.3558 | 139.752 | 112.1239 | -22.1239 | 137.0551 | 140.8565 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.9 | 4.9 | 1.0703 | 0
2016-10-26 21:00 | 0 | 0 | 0 | 0 | -12.3701 | 154.7528 | 114.076 | -24.076 | 152.8501 | 155.1674 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5 | 4.5 | 1.0717 | 0
2016-10-26 22:00 | 0 | 0 | 0 | 0 | -12.3844 | 169.7536 | 115.1951 | -25.1951 | 168.9299 | 169.0836 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.4 | 5.4 | 1.0686 | 0
2016-10-26 23:00 | 0 | 0 | 0 | 0 | -12.3987 | 184.7544 | 115.3839 | -25.3839 | -174.8593 | 173.5189 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.4 | 4.4 | 1.0721 | 0
2016-10-27 | 0 | 0 | 0 | 0 | -12.4129 | -160.2448 | 114.6265 | -24.6265 | -158.7074 | 160.3673 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5 | 4.5 | 1.0717 | 0
2016-10-27 01:00 | 0 | 0 | 0 | 0 | -12.4272 | -145.244 | 112.9916 | -22.9916 | -142.7879 | 146.1207 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5 | 4.5 | 1.0717 | 0
2016-10-27 02:00 | 0 | 0 | 0 | 0 | -12.4414 | -130.2432 | 110.6196 | -20.6196 | -127.2121 | 131.78 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.8 | 4.8 | 1.0707 | 0
2016-10-27 03:00 | 0 | 0 | 0 | 0 | -12.4556 | -115.2424 | 107.7002 | -17.7002 | -112.0111 | 117.4663 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.3 | 4.3 | 1.0724 | 0
2016-10-27 04:00 | 0 | 0 | 0 | 0 | -12.4699 | -100.2416 | 104.4488 | -14.4488 | -97.1444 | 103.2417 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.7 | 4.7 | 1.0711 | 0
2016-10-27 05:00 | 0 | 0 | 0 | 0 | -12.4841 | -85.2408 | 101.0889 | -11.0889 | -82.5247 | 89.175 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0714 | 0
2016-10-27 06:00 | 0 | 0 | 0 | 0 | -12.4983 | -70.2401 | 97.8396 | -7.8396 | -68.0459 | 75.3715 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5 | 4.5 | 1.0717 | 0
2016-10-27 07:00 | 0.16667 | 0.14 | 0.026667 | 0 | -12.5126 | -55.2393 | 94.9075 | -4.9075 | -53.6082 | 62.0203 | 0 | 0.105 | 0.2 | 0 | 0.0083333 | 0.11333 | 4.2 | 4.2035 | 1.0728 | 9.9698e-05
2016-10-27 08:00 | 0.33333 | 0.28 | 0.053333 | 0 | -12.5268 | -40.2385 | 92.4791 | -2.4791 | -39.1376 | 49.499 | 0 | 0.21 | 0.2 | 0 | 0.016667 | 0.22667 | 4.3 | 4.3071 | 1.0724 | 0.00019933
2016-10-27 09:00 | 0.5 | 0.42 | 0.08 | 0 | -12.541 | -25.2378 | 90.7116 | -0.71162 | -24.5971 | 38.6323 | 0 | 0.315 | 0.2 | 0 | 0.025 | 0.34 | 4.5 | 4.5106 | 1.0717 | 0.00029879
2016-10-27 10:00 | 0.55667 | 0.47333 | 0.083333 | 0 | -12.5552 | -10.237 | 89.7226 | 0.27737 | -9.9898 | 31.2065 | 0 | 0.355 | 0.2 | 0 | 0.027833 | 0.38283 | 4 | 4.012 | 1.0735 | 0.00033698
2016-10-27 11:00 | 0.61333 | 0.52667 | 0.086667 | 0 | -12.5694 | 4.7637 | 89.5796 | 0.42039 | 4.6494 | 29.9087 | 0 | 0.395 | 0.2 | 0 | 0.030667 | 0.42567 | 3.8 | 3.8133 | 1.0742 | 0.00037493
2016-10-27 12:00 | 0.67 | 0.58 | 0.09 | 0 | -12.5836 | 19.7645 | 90.2931 | -0.29314 | 19.271 | 35.4194 | 0 | 0.435 | 0.2 | 0 | 0.0335 | 0.4685 | 3.6 | 3.6146 | 1.0748 | 0.00041292
2016-10-27 13:00 | 0.44667 | 0.38667 | 0.06 | 0 | -12.5978 | 34.7652 | 91.8157 | -1.8157 | 33.8325 | 45.3175 | 0 | 0.29 | 0.2 | 0 | 0.022333 | 0.31233 | 3.3 | 3.3098 | 1.0759 | 0.00027556
2016-10-27 14:00 | 0.22333 | 0.19333 | 0.03 | 0 | -12.6119 | 49.7659 | 94.0468 | -4.0468 | 48.3186 | 57.3725 | 0 | 0.145 | 0.2 | 0 | 0.011167 | 0.15617 | 3.3 | 3.3049 | 1.0759 | 0.00013778
2016-10-27 15:00 | 0 | 0 | 0 | 0 | -12.6261 | 64.7667 | 96.8426 | -6.8426 | 62.7524 | 70.482 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0774 | 0
2016-10-27 16:00 | 0 | 0 | 0 | 0 | -12.6403 | 79.7674 | 100.0263 | -10.0263 | 77.1965 | 84.1493 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-10-27 17:00 | 0 | 0 | 0 | 0 | -12.6544 | 94.7681 | 103.3982 | -13.3982 | 91.7443 | 98.1348 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-10-27 18:00 | 0 | 0 | 0 | 0 | -12.6686 | 109.7688 | 106.7431 | -16.7431 | 106.5035 | 112.3106 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-10-27 19:00 | 0 | 0 | 0 | 0 | -12.6827 | 124.7695 | 109.8383 | -19.8383 | 121.5733 | 126.5993 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-10-27 20:00 | 0 | 0 | 0 | 0 | -12.6969 | 139.7702 | 112.4635 | -22.4635 | 137.016 | 140.9424 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0819 | 0
2016-10-27 21:00 | 0 | 0 | 0 | 0 | -12.711 | 154.7709 | 114.4168 | -24.4168 | 152.8299 | 155.2634 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-10-27 22:00 | 0 | 0 | 0 | 0 | -12.7252 | 169.7716 | 115.5363 | -25.5363 | 168.9326 | 169.2449 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-10-27 23:00 | 0 | 0 | 0 | 0 | -12.7393 | 184.7722 | 115.7241 | -25.7241 | -174.8321 | 173.7441 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0774 | 0
2016-10-28 | 0 | 0 | 0 | 0 | -12.7534 | -160.2271 | 114.9644 | -24.9644 | -158.657 | 160.4408 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-10-28 01:00 | 0 | 0 | 0 | 0 | -12.7675 | -145.2264 | 113.3262 | -23.3262 | -142.7176 | 146.1732 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0763 | 0
2016-10-28 02:00 | 0 | 0 | 0 | 0 | -12.7816 | -130.2258 | 110.9509 | -20.9509 | -127.1272 | 131.8318 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-10-28 03:00 | 0 | 0 | 0 | 0 | -12.7958 | -115.2251 | 108.0288 | -18.0288 | -111.9172 | 117.5249 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-10-28 04:00 | 0 | 0 | 0 | 0 | -12.8099 | -100.2245 | 104.7759 | -14.7759 | -97.047 | 103.312 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0763 | 0
2016-10-28 05:00 | 0 | 0 | 0 | 0 | -12.824 | -85.2238 | 101.4159 | -11.4159 | -82.4289 | 89.2618 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-10-28 06:00 | 0 | 0 | 0 | 0 | -12.838 | -70.2232 | 98.1679 | -8.1679 | -67.9561 | 75.4811 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0763 | 0
2016-10-28 07:00 | 0.043333 | 0.04 | 0.0033333 | 0 | -12.8521 | -55.2225 | 95.2381 | -5.2381 | -53.5287 | 62.1612 | 0 | 0.03 | 0.2 | 0 | 0.0021667 | 0.032167 | 2.6 | 2.601 | 1.0784 | 2.8445e-05
2016-10-28 08:00 | 0.086667 | 0.08 | 0.0066667 | 0 | -12.8662 | -40.2219 | 92.8125 | -2.8125 | -39.072 | 49.6843 | 0 | 0.06 | 0.2 | 0 | 0.0043333 | 0.064333 | 3.2 | 3.202 | 1.0763 | 5.6778e-05
2016-10-28 09:00 | 0.13 | 0.12 | 0.01 | 0 | -12.8803 | -25.2213 | 91.0478 | -1.0478 | -24.5485 | 38.8793 | 0 | 0.09 | 0.2 | 0 | 0.0065 | 0.0965 | 3.4 | 3.403 | 1.0756 | 8.5111e-05
2016-10-28 10:00 | 0.16 | 0.13667 | 0.023333 | 0 | -12.8943 | -10.2207 | 90.0609 | -0.06087 | -9.9603 | 31.5218 | 0 | 0.1025 | 0.2 | 0 | 0.008 | 0.1105 | 3.7 | 3.7035 | 1.0745 | 9.7364e-05
2016-10-28 11:00 | 0.19 | 0.15333 | 0.036667 | 0 | -12.9084 | 4.7799 | 89.9189 | 0.081136 | 4.6589 | 30.2459 | 0 | 0.115 | 0.2 | 0 | 0.0095 | 0.1245 | 3.6 | 3.6039 | 1.0749 | 0.00010974
2016-10-28 12:00 | 0.22 | 0.17 | 0.05 | 0 | -12.9224 | 19.7805 | 90.6322 | -0.63222 | 19.2607 | 35.7097 | 0 | 0.1275 | 0.2 | 0 | 0.011 | 0.1385 | 2.8 | 2.8043 | 1.0777 | 0.00012239
2016-10-28 13:00 | 0.14667 | 0.11333 | 0.033333 | 0 | -12.9365 | 34.7811 | 92.1536 | -2.1536 | 33.8043 | 45.5473 | 0 | 0.085 | 0.2 | 0 | 0.0073333 | 0.092333 | 3.3 | 3.3029 | 1.0759 | 8.1463e-05
2016-10-28 14:00 | 0.073333 | 0.056667 | 0.016667 | 0 | -12.9505 | 49.7817 | 94.383 | -4.383 | 48.2752 | 57.555 | 0 | 0.0425 | 0.2 | 0 | 0.0036667 | 0.046167 | 2.7 | 2.7014 | 1.078 | 4.0811e-05
2016-10-28 15:00 | 0 | 0 | 0 | 0 | -12.9646 | 64.7823 | 97.177 | -7.177 | 62.6974 | 70.6306 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.4 | 3.4 | 1.0756 | 0
2016-10-28 16:00 | 0 | 0 | 0 | 0 | -12.9786 | 79.7829 | 100.3594 | -10.3594 | 77.1339 | 84.2731 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.6 | 3.6 | 1.0749 | 0
2016-10-28 17:00 | 0 | 0 | 0 | 0 | -12.9926 | 94.7835 | 103.7307 | -13.7307 | 91.6788 | 98.2404 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0745 | 0
2016-10-28 18:00 | 0 | 0 | 0 | 0 | -13.0066 | 109.784 | 107.076 | -17.076 | 106.4403 | 112.4027 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.4 | 3.4 | 1.0756 | 0
2016-10-28 19:00 | 0 | 0 | 0 | 0 | -13.0207 | 124.7846 | 110.1724 | -20.1724 | 121.5178 | 126.6824 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-10-28 20:00 | 0 | 0 | 0 | 0 | -13.0347 | 139.7852 | 112.7993 | -22.7993 | 136.9739 | 141.0221 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-10-28 21:00 | 0 | 0 | 0 | 0 | -13.0487 | 154.7857 | 114.7541 | -24.7541 | 152.8065 | 155.3516 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-10-28 22:00 | 0 | 0 | 0 | 0 | -13.0627 | 169.7863 | 115.8741 | -25.8741 | 168.9318 | 169.3935 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2 | 2 | 1.0805 | 0
2016-10-28 23:00 | 0 | 0 | 0 | 0 | -13.0767 | 184.7868 | 116.0611 | -26.0611 | -174.8085 | 173.9588 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0801 | 0
2016-10-29 | 0 | 0 | 0 | 0 | -13.0906 | -160.2127 | 115.2992 | -25.2992 | -158.6101 | 160.511 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-10-29 01:00 | 0 | 0 | 0 | 0 | -13.1046 | -145.2121 | 113.658 | -23.658 | -142.6511 | 146.2253 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2 | 2 | 1.0805 | 0
2016-10-29 02:00 | 0 | 0 | 0 | 0 | -13.1186 | -130.2116 | 111.2795 | -21.2795 | -127.046 | 131.8843 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-10-29 03:00 | 0 | 0 | 0 | 0 | -13.1326 | -115.2111 | 108.3548 | -18.3548 | -111.827 | 117.5848 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-10-29 04:00 | 0 | 0 | 0 | 0 | -13.1465 | -100.2106 | 105.1004 | -15.1004 | -96.9534 | 103.3841 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-10-29 05:00 | 0 | 0 | 0 | 0 | -13.1605 | -85.2101 | 101.7404 | -11.7404 | -82.3368 | 89.3508 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-10-29 06:00 | 0 | 0 | 0 | 0 | -13.1744 | -70.2096 | 98.4936 | -8.4936 | -67.8701 | 75.5928 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-10-29 07:00 | 0.01 | 0.01 | 0 | 0 | -13.1884 | -55.2091 | 95.566 | -5.566 | -53.4529 | 62.3043 | 0 | 0.0075 | 0.2 | 0 | 0.0005 | 0.008 | 2.8 | 2.8003 | 1.0777 | 7.0697e-06
2016-10-29 08:00 | 0.02 | 0.02 | 0 | 0 | -13.2023 | -40.2086 | 93.1431 | -3.1431 | -39.01 | 49.8714 | 0 | 0.015 | 0.2 | 0 | 0.001 | 0.016 | 2.9 | 2.9005 | 1.0773 | 1.4135e-05
2016-10-29 09:00 | 0.03 | 0.03 | 0 | 0 | -13.2162 | -25.2081 | 91.381 | -1.381 | -24.5034 | 39.127 | 0 | 0.0225 | 0.2 | 0 | 0.0015 | 0.024 | 2.6 | 2.6008 | 1.0784 | 2.1223e-05
2016-10-29 10:00 | 0.036667 | 0.033333 | 0.0033333 | 0 | -13.2301 | -10.2076 | 90.3959 | -0.3959 | -9.9342 | 31.8356 | 0 | 0.025 | 0.2 | 0 | 0.0018333 | 0.026833 | 2.5 | 2.5008 | 1.0787 | 2.3736e-05
2016-10-29 11:00 | 0.043333 | 0.036667 | 0.0066667 | 0 | -13.2441 | 4.7928 | 90.2547 | -0.25471 | 4.6651 | 30.5794 | 0 | 0.0275 | 0.2 | 0 | 0.0021667 | 0.029667 | 1.7 | 1.7009 | 1.0815 | 2.631e-05
2016-10-29 12:00 | 0.05 | 0.04 | 0.01 | 0 | -13.258 | 19.7933 | 90.9677 | -0.96772 | 19.2475 | 35.9962 | 0 | 0.03 | 0.2 | 0 | 0.0025 | 0.0325 | 2.4 | 2.401 | 1.0791 | 2.8758e-05
2016-10-29 13:00 | 0.033333 | 0.026667 | 0.0066667 | 0 | -13.2719 | 34.7938 | 92.4878 | -2.4878 | 33.7733 | 45.7735 | 0 | 0.02 | 0.2 | 0 | 0.0016667 | 0.021667 | 2.4 | 2.4007 | 1.0791 | 1.9172e-05
2016-10-29 14:00 | 0.016667 | 0.013333 | 0.0033333 | 0 | -13.2858 | 49.7942 | 94.7153 | -4.7153 | 48.2291 | 57.734 | 0 | 0.01 | 0.2 | 0 | 0.00083333 | 0.010833 | 2.1 | 2.1003 | 1.0801 | 9.5953e-06
2016-10-29 15:00 | 0 | 0 | 0 | 0 | -13.2997 | 64.7947 | 97.5074 | -7.5074 | 62.6397 | 70.7754 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-10-29 16:00 | 0 | 0 | 0 | 0 | -13.3136 | 79.7951 | 100.6884 | -10.6884 | 77.0688 | 84.393 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-10-29 17:00 | 0 | 0 | 0 | 0 | -13.3274 | 94.7955 | 104.0591 | -14.0591 | 91.6108 | 98.3417 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-10-29 18:00 | 0 | 0 | 0 | 0 | -13.3413 | 109.796 | 107.4049 | -17.4049 | 106.3743 | 112.4902 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0816 | 0
2016-10-29 19:00 | 0 | 0 | 0 | 0 | -13.3552 | 124.7964 | 110.5027 | -20.5027 | 121.4593 | 126.7603 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0801 | 0
2016-10-29 20:00 | 0 | 0 | 0 | 0 | -13.369 | 139.7968 | 113.1313 | -23.1313 | 136.9286 | 141.0956 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0801 | 0
2016-10-29 21:00 | 0 | 0 | 0 | 0 | -13.3829 | 154.7972 | 115.0876 | -25.0876 | 152.7798 | 155.4318 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-10-29 22:00 | 0 | 0 | 0 | 0 | -13.3968 | 169.7976 | 116.2084 | -26.2084 | 168.9276 | 169.5292 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-10-29 23:00 | 0 | 0 | 0 | 0 | -13.4106 | 184.798 | 116.3948 | -26.3948 | -174.7885 | 174.1624 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-10-30 | 0 | 0 | 0 | 0 | -13.4244 | -160.2016 | 115.6309 | -25.6309 | -158.5669 | 160.5783 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-10-30 01:00 | 0 | 0 | 0 | 0 | -13.4383 | -145.2012 | 113.9869 | -23.9869 | -142.5882 | 146.2771 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0816 | 0
2016-10-30 02:00 | 0 | 0 | 0 | 0 | -13.4521 | -130.2008 | 111.6053 | -21.6053 | -126.9685 | 131.9377 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.0822 | 0
2016-10-30 03:00 | 0 | 0 | 0 | 0 | -13.4659 | -115.2004 | 108.6781 | -18.6781 | -111.7406 | 117.6463 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.0822 | 0
2016-10-30 04:00 | 0 | 0 | 0 | 0 | -13.4797 | -100.2 | 105.4224 | -15.4224 | -96.8636 | 103.4581 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0819 | 0
2016-10-30 05:00 | 0 | 0 | 0 | 0 | -13.4935 | -85.1997 | 102.0622 | -12.0622 | -82.2485 | 89.4419 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0826 | 0
2016-10-30 06:00 | 0 | 0 | 0 | 0 | -13.5073 | -70.1993 | 98.8166 | -8.8166 | -67.7879 | 75.7068 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0826 | 0
2016-10-30 07:00 | 0.0066667 | 0.0033333 | 0.0033333 | 0 | -13.5211 | -55.1989 | 95.8912 | -5.8912 | -53.3809 | 62.4495 | 0 | 0.0025 | 0.2 | 0 | 0.00033333 | 0.0028333 | 1.3 | 1.3001 | 1.0829 | 2.5161e-06
2016-10-30 08:00 | 0.013333 | 0.0066667 | 0.0066667 | 0 | -13.5349 | -40.1986 | 93.4708 | -3.4708 | -38.9518 | 50.0603 | 0 | 0.005 | 0.2 | 0 | 0.00066667 | 0.0056667 | 1.3 | 1.3002 | 1.0829 | 5.0321e-06
2016-10-30 09:00 | 0.02 | 0.01 | 0.01 | 0 | -13.5487 | -25.1982 | 91.711 | -1.711 | -24.4619 | 39.3752 | 0 | 0.0075 | 0.2 | 0 | 0.001 | 0.0085 | 1.5 | 1.5003 | 1.0822 | 7.5433e-06
2016-10-30 10:00 | 0.023333 | 0.013333 | 0.01 | 0 | -13.5625 | -10.1979 | 90.7276 | -0.72761 | -9.9114 | 32.1474 | 0 | 0.01 | 0.2 | 0 | 0.0011667 | 0.011167 | 1 | 1.0003 | 1.084 | 9.9258e-06
2016-10-30 11:00 | 0.026667 | 0.016667 | 0.01 | 0 | -13.5763 | 4.8024 | 90.587 | -0.58703 | 4.6682 | 30.909 | 0 | 0.0125 | 0.2 | 0 | 0.0013333 | 0.013833 | 0.7 | 0.70043 | 1.085 | 1.2308e-05
2016-10-30 12:00 | 0.03 | 0.02 | 0.01 | 0 | -13.59 | 19.8028 | 91.2995 | -1.2995 | 19.2313 | 36.2787 | 0 | 0.015 | 0.2 | 0 | 0.0015 | 0.0165 | 0.7 | 0.70052 | 1.085 | 1.4681e-05
2016-10-30 13:00 | 0.02 | 0.013333 | 0.0066667 | 0 | -13.6038 | 34.8031 | 92.8181 | -2.8181 | 33.7394 | 45.996 | 0 | 0.01 | 0.2 | 0 | 0.001 | 0.011 | 0.5 | 0.50034 | 1.0857 | 9.7935e-06
2016-10-30 14:00 | 0.01 | 0.0066667 | 0.0033333 | 0 | -13.6175 | 49.8034 | 95.0436 | -5.0436 | 48.1804 | 57.9092 | 0 | 0.005 | 0.2 | 0 | 0.0005 | 0.0055 | 0.7 | 0.70017 | 1.085 | 4.8936e-06
2016-10-30 15:00 | 0 | 0 | 0 | 0 | -13.6313 | 64.8037 | 97.8337 | -7.8337 | 62.5795 | 70.9163 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-10-30 16:00 | 0 | 0 | 0 | 0 | -13.645 | 79.804 | 101.0132 | -11.0132 | 77.0011 | 84.5089 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-10-30 17:00 | 0 | 0 | 0 | 0 | -13.6588 | 94.8043 | 104.3834 | -14.3834 | 91.5401 | 98.4387 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-10-30 18:00 | 0 | 0 | 0 | 0 | -13.6725 | 109.8046 | 107.7296 | -17.7296 | 106.3056 | 112.573 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0872 | 0
2016-10-30 19:00 | 0 | 0 | 0 | 0 | -13.6862 | 124.8049 | 110.8288 | -20.8288 | 121.398 | 126.8329 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-10-30 20:00 | 0 | 0 | 0 | 0 | -13.6999 | 139.8052 | 113.4593 | -23.4593 | 136.8803 | 141.1631 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-10-30 21:00 | 0 | 0 | 0 | 0 | -13.7136 | 154.8055 | 115.4173 | -25.4173 | 152.7497 | 155.5041 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-10-30 22:00 | 0 | 0 | 0 | 0 | -13.7273 | 169.8057 | 116.539 | -26.539 | 168.9199 | 169.6517 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0861 | 0
2016-10-30 23:00 | 0 | 0 | 0 | 0 | -13.741 | 184.806 | 116.7249 | -26.7249 | -174.7721 | 174.3542 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-10-31 | 0 | 0 | 0 | 0 | -13.7547 | -160.1938 | 115.9593 | -25.9593 | -158.5274 | 160.6428 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0872 | 0
2016-10-31 01:00 | 0 | 0 | 0 | 0 | -13.7684 | -145.1935 | 114.3126 | -24.3126 | -142.5291 | 146.3287 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-10-31 02:00 | 0 | 0 | 0 | 0 | -13.7821 | -130.1933 | 111.9282 | -21.9282 | -126.8949 | 131.9918 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-10-31 03:00 | 0 | 0 | 0 | 0 | -13.7957 | -115.193 | 108.9986 | -18.9986 | -111.6581 | 117.7091 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0872 | 0
2016-10-31 04:00 | 0 | 0 | 0 | 0 | -13.8094 | -100.1928 | 105.7415 | -15.7415 | -96.7776 | 103.5339 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0872 | 0
2016-10-31 05:00 | 0 | 0 | 0 | 0 | -13.8231 | -85.1926 | 102.3813 | -12.3813 | -82.1641 | 89.535 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-10-31 06:00 | 0 | 0 | 0 | 0 | -13.8367 | -70.1923 | 99.1368 | -9.1368 | -67.7096 | 75.8229 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-10-31 07:00 | 0 | 0 | 0 | 0 | -13.8504 | -55.1921 | 96.2134 | -6.2134 | -53.3127 | 62.5968 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-10-31 08:00 | 0 | 0 | 0 | 0 | -13.864 | -40.1919 | 93.7954 | -3.7954 | -38.8973 | 50.2507 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0872 | 0
2016-10-31 09:00 | 0 | 0 | 0 | 0 | -13.8776 | -25.1917 | 92.0378 | -2.0378 | -24.4239 | 39.6239 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-10-31 10:00 | 0 | 0 | 0 | 0 | -13.8913 | -10.1915 | 91.0559 | -1.0559 | -9.8921 | 32.4573 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-10-31 11:00 | 0 | 0 | 0 | 0 | -13.9049 | 4.8087 | 90.9157 | -0.9157 | 4.6681 | 31.2345 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-10-31 12:00 | 0 | 0 | 0 | 0 | -13.9185 | 19.8089 | 91.6275 | -1.6275 | 19.2121 | 36.5571 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-10-31 13:00 | 0 | 0 | 0 | 0 | -13.9321 | 34.8091 | 93.1444 | -3.1444 | 33.7028 | 46.2147 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-10-31 14:00 | 0 | 0 | 0 | 0 | -13.9457 | 49.8093 | 95.3678 | -5.3678 | 48.129 | 58.0807 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-10-31 15:00 | 0 | 0 | 0 | 0 | -13.9593 | 64.8094 | 98.1558 | -8.1558 | 62.5167 | 71.0534 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-10-31 16:00 | 0 | 0 | 0 | 0 | -13.9729 | 79.8096 | 101.3338 | -11.3338 | 76.9309 | 84.6206 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-10-31 17:00 | 0 | 0 | 0 | 0 | -13.9865 | 94.8097 | 104.7034 | -14.7034 | 91.4668 | 98.5313 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-10-31 18:00 | 0 | 0 | 0 | 0 | -14 | 109.8099 | 108.0501 | -18.0501 | 106.2341 | 112.6511 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-10-31 19:00 | 0 | 0 | 0 | 0 | -14.0136 | 124.81 | 111.1506 | -21.1506 | 121.3337 | 126.9003 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-10-31 20:00 | 0 | 0 | 0 | 0 | -14.0272 | 139.8102 | 113.7832 | -23.7832 | 136.8288 | 141.2244 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-10-31 21:00 | 0 | 0 | 0 | 0 | -14.0407 | 154.8103 | 115.7431 | -25.7431 | 152.7164 | 155.5685 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-10-31 22:00 | 0 | 0 | 0 | 0 | -14.0543 | 169.8105 | 116.8658 | -26.8658 | 168.9087 | 169.7608 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-10-31 23:00 | 0 | 0 | 0 | 0 | -14.0678 | 184.8106 | 117.0516 | -27.0516 | -174.7593 | 174.5335 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-11-01 | 0 | 0 | 0 | 0 | -14.0813 | -160.1893 | 116.2844 | -26.2844 | -158.4916 | 160.7045 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-11-01 01:00 | 0 | 0 | 0 | 0 | -14.0949 | -145.1892 | 114.6352 | -24.6352 | -142.4738 | 146.38 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-11-01 02:00 | 0 | 0 | 0 | 0 | -14.1084 | -130.1891 | 112.2481 | -22.2481 | -126.8251 | 132.0469 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-11-01 03:00 | 0 | 0 | 0 | 0 | -14.1219 | -115.189 | 109.3162 | -19.3162 | -111.5794 | 117.7735 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-11-01 04:00 | 0 | 0 | 0 | 0 | -14.1354 | -100.1889 | 106.0579 | -16.0579 | -96.6955 | 103.6115 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-11-01 05:00 | 0 | 0 | 0 | 0 | -14.1489 | -85.1888 | 102.6976 | -12.6976 | -82.0836 | 89.6301 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-11-01 06:00 | 0 | 0 | 0 | 0 | -14.1624 | -70.1887 | 99.4542 | -9.4542 | -67.6352 | 75.9411 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-11-01 07:00 | 0 | 0 | 0 | 0 | -14.1759 | -55.1886 | 96.5326 | -6.5326 | -53.2483 | 62.746 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-11-01 08:00 | 0 | 0 | 0 | 0 | -14.1894 | -40.1886 | 94.1168 | -4.1168 | -38.8465 | 50.4426 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-11-01 09:00 | 0 | 0 | 0 | 0 | -14.2029 | -25.1885 | 92.3612 | -2.3612 | -24.3896 | 39.8727 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-11-01 10:00 | 0 | 0 | 0 | 0 | -14.2163 | -10.1884 | 91.3806 | -1.3806 | -9.8761 | 32.765 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-11-01 11:00 | 0 | 0 | 0 | 0 | -14.2298 | 4.8116 | 91.2406 | -1.2406 | 4.6648 | 31.556 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-11-01 12:00 | 0 | 0 | 0 | 0 | -14.2433 | 19.8117 | 91.9515 | -1.9515 | 19.19 | 36.8314 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-11-01 13:00 | 0 | 0 | 0 | 0 | -14.2567 | 34.8117 | 93.4667 | -3.4667 | 33.6635 | 46.4295 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-11-01 14:00 | 0 | 0 | 0 | 0 | -14.2702 | 49.8117 | 95.6878 | -5.6878 | 48.075 | 58.2483 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.098 | 0
2016-11-01 15:00 | 0 | 0 | 0 | 0 | -14.2836 | 64.8118 | 98.4736 | -8.4736 | 62.4514 | 71.1865 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-11-01 16:00 | 0 | 0 | 0 | 0 | -14.297 | 79.8118 | 101.65 | -11.65 | 76.8581 | 84.7282 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-11-01 17:00 | 0 | 0 | 0 | 0 | -14.3104 | 94.8118 | 105.0189 | -15.0189 | 91.3909 | 98.6195 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-11-01 18:00 | 0 | 0 | 0 | 0 | -14.3239 | 109.8118 | 108.3661 | -18.3661 | 106.1599 | 112.7244 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-11-01 19:00 | 0 | 0 | 0 | 0 | -14.3373 | 124.8118 | 111.4682 | -21.4682 | 121.2665 | 126.9624 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-11-01 20:00 | 0 | 0 | 0 | 0 | -14.3507 | 139.8118 | 114.1028 | -24.1028 | 136.7742 | 141.2796 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-11-01 21:00 | 0 | 0 | 0 | 0 | -14.3641 | 154.8118 | 116.0647 | -26.0647 | 152.6796 | 155.6252 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-11-01 22:00 | 0 | 0 | 0 | 0 | -14.3775 | 169.8118 | 117.1887 | -27.1887 | 168.894 | 169.8565 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-11-01 23:00 | 0 | 0 | 0 | 0 | -14.3908 | 184.8118 | 117.3745 | -27.3745 | -174.7503 | 174.6998 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-11-02 | 0 | 0 | 0 | 0 | -14.4042 | -160.1882 | 116.606 | -26.606 | -158.4596 | 160.7635 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-11-02 01:00 | 0 | 0 | 0 | 0 | -14.4176 | -145.1882 | 114.9546 | -24.9546 | -142.4224 | 146.4313 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.098 | 0
2016-11-02 02:00 | 0 | 0 | 0 | 0 | -14.431 | -130.1883 | 112.5648 | -22.5648 | -126.7593 | 132.1029 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-11-02 03:00 | 0 | 0 | 0 | 0 | -14.4443 | -115.1883 | 109.6308 | -19.6308 | -111.5047 | 117.8393 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-11-02 04:00 | 0 | 0 | 0 | 0 | -14.4577 | -100.1883 | 106.3713 | -16.3713 | -96.6174 | 103.6909 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.8 | -2.8 | 1.0973 | 0
2016-11-02 05:00 | 0 | 0 | 0 | 0 | -14.471 | -85.1884 | 103.0109 | -13.0109 | -82.0071 | 89.7272 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-11-02 06:00 | 0 | 0 | 0 | 0 | -14.4843 | -70.1885 | 99.7685 | -9.7685 | -67.5647 | 76.0613 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-11-02 07:00 | 0 | 0 | 0 | 0 | -14.4977 | -55.1885 | 96.8487 | -6.8487 | -53.1878 | 62.8971 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.098 | 0
2016-11-02 08:00 | 0 | 0 | 0 | 0 | -14.511 | -40.1886 | 94.435 | -4.435 | -38.7994 | 50.6359 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-11-02 09:00 | 0 | 0 | 0 | 0 | -14.5243 | -25.1887 | 92.6812 | -2.6812 | -24.3588 | 40.1215 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.8 | -3.8 | 1.1008 | 0
2016-11-02 10:00 | 0 | 0 | 0 | 0 | -14.5376 | -10.1887 | 91.7016 | -1.7016 | -9.8636 | 33.0704 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.0994 | 0
2016-11-02 11:00 | 0 | 0 | 0 | 0 | -14.5509 | 4.8112 | 91.5617 | -1.5617 | 4.6582 | 31.8733 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-11-02 12:00 | 0 | 0 | 0 | 0 | -14.5642 | 19.8111 | 92.2715 | -2.2715 | 19.1648 | 37.1014 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-11-02 13:00 | 0 | 0 | 0 | 0 | -14.5775 | 34.811 | 93.7847 | -3.7847 | 33.6213 | 46.6403 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.8 | -2.8 | 1.0973 | 0
2016-11-02 14:00 | 0 | 0 | 0 | 0 | -14.5908 | 49.8109 | 96.0034 | -6.0034 | 48.0183 | 58.412 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-11-02 15:00 | 0 | 0 | 0 | 0 | -14.6041 | 64.8108 | 98.787 | -8.787 | 62.3835 | 71.3156 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.2 | -2.2 | 1.0952 | 0
2016-11-02 16:00 | 0 | 0 | 0 | 0 | -14.6173 | 79.8107 | 101.9617 | -11.9617 | 76.7828 | 84.8317 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.2 | -2.2 | 1.0952 | 0
2016-11-02 17:00 | 0 | 0 | 0 | 0 | -14.6306 | 94.8105 | 105.33 | -15.33 | 91.3124 | 98.7033 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.2 | -2.2 | 1.0952 | 0
2016-11-02 18:00 | 0 | 0 | 0 | 0 | -14.6438 | 109.8104 | 108.6777 | -18.6777 | 106.083 | 112.7929 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-11-02 19:00 | 0 | 0 | 0 | 0 | -14.6571 | 124.8103 | 111.7813 | -21.7813 | 121.1963 | 127.0193 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-11-02 20:00 | 0 | 0 | 0 | 0 | -14.6703 | 139.8101 | 114.4181 | -24.4181 | 136.7164 | 141.3288 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.2 | -2.2 | 1.0952 | 0
2016-11-02 21:00 | 0 | 0 | 0 | 0 | -14.6836 | 154.81 | 116.3822 | -26.3822 | 152.6395 | 155.6741 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.0945 | 0
2016-11-02 22:00 | 0 | 0 | 0 | 0 | -14.6968 | 169.8098 | 117.5076 | -27.5076 | 168.8756 | 169.9387 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-11-02 23:00 | 0 | 0 | 0 | 0 | -14.71 | 184.8097 | 117.6936 | -27.6936 | -174.7449 | 174.8524 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-11-03 | 0 | 0 | 0 | 0 | -14.7232 | -160.1905 | 116.924 | -26.924 | -158.4315 | 160.8202 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-11-03 01:00 | 0 | 0 | 0 | 0 | -14.7364 | -145.1907 | 115.2705 | -25.2705 | -142.3749 | 146.4825 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-11-03 02:00 | 0 | 0 | 0 | 0 | -14.7496 | -130.1908 | 112.8784 | -22.8784 | -126.6974 | 132.1599 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-11-03 03:00 | 0 | 0 | 0 | 0 | -14.7628 | -115.191 | 109.9423 | -19.9423 | -111.4341 | 117.9066 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.3 | -3.3 | 1.0991 | 0
2016-11-03 04:00 | 0 | 0 | 0 | 0 | -14.776 | -100.1912 | 106.6816 | -16.6816 | -96.5433 | 103.7721 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.7 | -3.7 | 1.1004 | 0
2016-11-03 05:00 | 0 | 0 | 0 | 0 | -14.7892 | -85.1914 | 103.3211 | -13.3211 | -81.9346 | 89.8262 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.9 | -3.9 | 1.1012 | 0
2016-11-03 06:00 | 0 | 0 | 0 | 0 | -14.8023 | -70.1916 | 100.0797 | -10.0797 | -67.4981 | 76.1834 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.9 | -3.9 | 1.1012 | 0
2016-11-03 07:00 | 0 | 0 | 0 | 0 | -14.8155 | -55.1918 | 97.1615 | -7.1615 | -53.1312 | 63.0499 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4 | -4 | 1.1015 | 0
2016-11-03 08:00 | 0 | 0 | 0 | 0 | -14.8287 | -40.192 | 94.7497 | -4.7497 | -38.7562 | 50.8302 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-11-03 09:00 | 0 | 0 | 0 | 0 | -14.8418 | -25.1922 | 92.9975 | -2.9975 | -24.3317 | 40.3702 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-11-03 10:00 | 0 | 0 | 0 | 0 | -14.855 | -10.1924 | 92.0188 | -2.0188 | -9.8545 | 33.3733 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-11-03 11:00 | 0 | 0 | 0 | 0 | -14.8681 | 4.8073 | 91.8787 | -1.8787 | 4.6485 | 32.1863 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-11-03 12:00 | 0 | 0 | 0 | 0 | -14.8812 | 19.8071 | 92.5872 | -2.5872 | 19.1367 | 37.3671 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4 | -4 | 1.1015 | 0
2016-11-03 13:00 | 0 | 0 | 0 | 0 | -14.8943 | 34.8069 | 94.0984 | -4.0984 | 33.5764 | 46.847 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4 | -4 | 1.1015 | 0
2016-11-03 14:00 | 0 | 0 | 0 | 0 | -14.9075 | 49.8066 | 96.3146 | -6.3146 | 47.9591 | 58.5717 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-11-03 15:00 | 0 | 0 | 0 | 0 | -14.9206 | 64.8064 | 99.0958 | -9.0958 | 62.3131 | 71.4407 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4 | -4 | 1.1015 | 0
2016-11-03 16:00 | 0 | 0 | 0 | 0 | -14.9337 | 79.8061 | 102.2688 | -12.2688 | 76.705 | 84.9308 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.7 | -3.7 | 1.1004 | 0
2016-11-03 17:00 | 0 | 0 | 0 | 0 | -14.9468 | 94.8059 | 105.6364 | -15.6364 | 91.2313 | 98.7827 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.3 | -3.3 | 1.0991 | 0
2016-11-03 18:00 | 0 | 0 | 0 | 0 | -14.9598 | 109.8056 | 108.9846 | -18.9846 | 106.0033 | 112.8567 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.8 | -3.8 | 1.1008 | 0
2016-11-03 19:00 | 0 | 0 | 0 | 0 | -14.9729 | 124.8053 | 112.0898 | -22.0898 | 121.1233 | 127.071 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.8 | -3.8 | 1.1008 | 0
2016-11-03 20:00 | 0 | 0 | 0 | 0 | -14.986 | 139.805 | 114.7289 | -24.7289 | 136.6555 | 141.372 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-11-03 21:00 | 0 | 0 | 0 | 0 | -14.9991 | 154.8047 | 116.6953 | -26.6953 | 152.5961 | 155.7154 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.0994 | 0
2016-11-03 22:00 | 0 | 0 | 0 | 0 | -15.0121 | 169.8045 | 117.8224 | -27.8224 | 168.8537 | 170.0075 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-11-03 23:00 | 0 | 0 | 0 | 0 | -15.0252 | 184.8042 | 118.0088 | -28.0088 | -174.7433 | 174.9907 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-11-04 | 0 | 0 | 0 | 0 | -15.0382 | -160.1961 | 117.2383 | -27.2383 | -158.4073 | 160.8745 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-11-04 01:00 | 0 | 0 | 0 | 0 | -15.0513 | -145.1965 | 115.5829 | -25.5829 | -142.3313 | 146.5338 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-11-04 02:00 | 0 | 0 | 0 | 0 | -15.0643 | -130.1968 | 113.1885 | -23.1885 | -126.6395 | 132.2179 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-11-04 03:00 | 0 | 0 | 0 | 0 | -15.0773 | -115.1971 | 110.2506 | -20.2506 | -111.3674 | 117.9754 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-11-04 04:00 | 0 | 0 | 0 | 0 | -15.0903 | -100.1974 | 106.9887 | -16.9887 | -96.4733 | 103.8551 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-11-04 05:00 | 0 | 0 | 0 | 0 | -15.1033 | -85.1978 | 103.6282 | -13.6282 | -81.8661 | 89.9271 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-11-04 06:00 | 0 | 0 | 0 | 0 | -15.1163 | -70.1981 | 100.3876 | -10.3876 | -67.4356 | 76.3074 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-11-04 07:00 | 0 | 0 | 0 | 0 | -15.1293 | -55.1984 | 97.471 | -7.471 | -53.0785 | 63.2043 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-11-04 08:00 | 0 | 0 | 0 | 0 | -15.1423 | -40.1988 | 95.061 | -5.061 | -38.7167 | 51.0257 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-11-04 09:00 | 0 | 0 | 0 | 0 | -15.1553 | -25.1991 | 93.3102 | -3.3102 | -24.3082 | 40.6186 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-11-04 10:00 | 0 | 0 | 0 | 0 | -15.1683 | -10.1995 | 92.3322 | -2.3322 | -9.8488 | 33.6736 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-11-04 11:00 | 0 | 0 | 0 | 0 | -15.1812 | 4.8001 | 92.1917 | -2.1917 | 4.6356 | 32.4948 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0843 | 0
2016-11-04 12:00 | 0 | 0 | 0 | 0 | -15.1942 | 19.7998 | 92.8987 | -2.8987 | 19.1057 | 37.6282 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0861 | 0
2016-11-04 13:00 | 0 | 0 | 0 | 0 | -15.2071 | 34.7994 | 94.4076 | -4.4076 | 33.5287 | 47.0495 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-11-04 14:00 | 0 | 0 | 0 | 0 | -15.2201 | 49.799 | 96.6212 | -6.6212 | 47.8972 | 58.7273 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0847 | 0
2016-11-04 15:00 | 0 | 0 | 0 | 0 | -15.233 | 64.7986 | 99.3999 | -9.3999 | 62.2402 | 71.5615 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-11-04 16:00 | 0 | 0 | 0 | 0 | -15.2459 | 79.7982 | 102.5711 | -12.5711 | 76.6247 | 85.0258 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-11-04 17:00 | 0 | 0 | 0 | 0 | -15.2589 | 94.7978 | 105.9381 | -15.9381 | 91.1477 | 98.8576 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0847 | 0
2016-11-04 18:00 | 0 | 0 | 0 | 0 | -15.2718 | 109.7974 | 109.2868 | -19.2868 | 105.921 | 112.9157 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0826 | 0
2016-11-04 19:00 | 0 | 0 | 0 | 0 | -15.2847 | 124.797 | 112.3937 | -22.3937 | 121.0474 | 127.1175 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-11-04 20:00 | 0 | 0 | 0 | 0 | -15.2976 | 139.7965 | 115.0351 | -25.0351 | 136.5915 | 141.4093 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-11-04 21:00 | 0 | 0 | 0 | 0 | -15.3105 | 154.7961 | 117.0041 | -27.0041 | 152.5492 | 155.7491 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-11-04 22:00 | 0 | 0 | 0 | 0 | -15.3234 | 169.7957 | 118.1329 | -28.1329 | 168.8282 | 170.0627 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-11-04 23:00 | 0 | 0 | 0 | 0 | -15.3362 | 184.7952 | 118.32 | -28.32 | -174.7455 | 175.1142 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-11-05 | 0 | 0 | 0 | 0 | -15.3491 | -160.2052 | 117.5488 | -27.5488 | -158.387 | 160.9266 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-11-05 01:00 | 0 | 0 | 0 | 0 | -15.362 | -145.2056 | 115.8917 | -25.8917 | -142.2918 | 146.5852 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0861 | 0
2016-11-05 02:00 | 0 | 0 | 0 | 0 | -15.3748 | -130.2061 | 113.4952 | -23.4952 | -126.5857 | 132.2769 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-11-05 03:00 | 0 | 0 | 0 | 0 | -15.3877 | -115.2066 | 110.5555 | -20.5555 | -111.3048 | 118.0458 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-11-05 04:00 | 0 | 0 | 0 | 0 | -15.4005 | -100.207 | 107.2926 | -17.2926 | -96.4073 | 103.9398 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-11-05 05:00 | 0 | 0 | 0 | 0 | -15.4133 | -85.2075 | 103.932 | -13.932 | -81.8016 | 90.0299 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-11-05 06:00 | 0 | 0 | 0 | 0 | -15.4262 | -70.208 | 100.6922 | -10.6922 | -67.3771 | 76.4332 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-11-05 07:00 | 0 | 0 | 0 | 0 | -15.439 | -55.2085 | 97.7771 | -7.7771 | -53.0297 | 63.3603 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-11-05 08:00 | 0 | 0 | 0 | 0 | -15.4518 | -40.209 | 95.3686 | -5.3686 | -38.681 | 51.222 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-11-05 09:00 | 0 | 0 | 0 | 0 | -15.4646 | -25.2095 | 93.6191 | -3.6191 | -24.2883 | 40.8665 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-11-05 10:00 | 0 | 0 | 0 | 0 | -15.4774 | -10.21 | 92.6415 | -2.6415 | -9.8465 | 33.9712 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-11-05 11:00 | 0 | 0 | 0 | 0 | -15.4902 | 4.7895 | 92.5004 | -2.5004 | 4.6196 | 32.7989 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-11-05 12:00 | 0 | 0 | 0 | 0 | -15.503 | 19.789 | 93.2058 | -3.2058 | 19.0717 | 37.8848 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.8 | -3.8 | 1.1008 | 0
2016-11-05 13:00 | 0 | 0 | 0 | 0 | -15.5158 | 34.7885 | 94.7123 | -4.7123 | 33.4783 | 47.2477 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.8 | -3.8 | 1.1008 | 0
2016-11-05 14:00 | 0 | 0 | 0 | 0 | -15.5285 | 49.788 | 96.9231 | -6.9231 | 47.8328 | 58.8787 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-11-05 15:00 | 0 | 0 | 0 | 0 | -15.5413 | 64.7874 | 99.6993 | -9.6993 | 62.1649 | 71.6782 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.8 | -2.8 | 1.0973 | 0
2016-11-05 16:00 | 0 | 0 | 0 | 0 | -15.554 | 79.7869 | 102.8687 | -12.8687 | 76.5419 | 85.1164 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-11-05 17:00 | 0 | 0 | 0 | 0 | -15.5668 | 94.7863 | 106.2348 | -16.2348 | 91.0616 | 98.928 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-11-05 18:00 | 0 | 0 | 0 | 0 | -15.5795 | 109.7858 | 109.5841 | -19.5841 | 105.836 | 112.97 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-11-05 19:00 | 0 | 0 | 0 | 0 | -15.5922 | 124.7852 | 112.6927 | -22.6927 | 120.9686 | 127.1588 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-11-05 20:00 | 0 | 0 | 0 | 0 | -15.605 | 139.7847 | 115.3367 | -25.3367 | 136.5243 | 141.4407 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.8 | -2.8 | 1.0973 | 0
2016-11-05 21:00 | 0 | 0 | 0 | 0 | -15.6177 | 154.7841 | 117.3082 | -27.3082 | 152.499 | 155.7754 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-11-05 22:00 | 0 | 0 | 0 | 0 | -15.6304 | 169.7835 | 118.4391 | -28.4391 | 168.7991 | 170.1048 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-11-05 23:00 | 0 | 0 | 0 | 0 | -15.6431 | 184.7829 | 118.627 | -28.627 | -174.7515 | 175.2226 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-11-06 | 0 | 0 | 0 | 0 | -15.6558 | -160.2176 | 117.8554 | -27.8554 | -158.3706 | 160.9767 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-11-06 01:00 | 0 | 0 | 0 | 0 | -15.6685 | -145.2182 | 116.1968 | -26.1968 | -142.2563 | 146.6368 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-11-06 02:00 | 0 | 0 | 0 | 0 | -15.6811 | -130.2188 | 113.7984 | -23.7984 | -126.536 | 132.337 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-11-06 03:00 | 0 | 0 | 0 | 0 | -15.6938 | -115.2194 | 110.857 | -20.857 | -111.2464 | 118.1176 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-11-06 04:00 | 0 | 0 | 0 | 0 | -15.7065 | -100.2201 | 107.5931 | -17.5931 | -96.3455 | 104.0263 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-11-06 05:00 | 0 | 0 | 0 | 0 | -15.7191 | -85.2207 | 104.2324 | -14.2324 | -81.7413 | 90.1345 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0837 | 0
2016-11-06 06:00 | 0 | 0 | 0 | 0 | -15.7318 | -70.2213 | 100.9934 | -10.9934 | -67.3226 | 76.5607 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.084 | 0
2016-11-06 07:00 | 0 | 0 | 0 | 0 | -15.7444 | -55.2219 | 98.0795 | -8.0795 | -52.9849 | 63.5177 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0833 | 0
2016-11-06 08:00 | 0 | 0 | 0 | 0 | -15.757 | -40.2225 | 95.6725 | -5.6725 | -38.6492 | 51.419 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-11-06 09:00 | 0 | 0 | 0 | 0 | -15.7697 | -25.2232 | 93.924 | -3.924 | -24.2721 | 41.1138 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.084 | 0
2016-11-06 10:00 | 0 | 0 | 0 | 0 | -15.7823 | -10.2238 | 92.9466 | -2.9466 | -9.8477 | 34.2658 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-11-06 11:00 | 0 | 0 | 0 | 0 | -15.7949 | 4.7755 | 92.8048 | -2.8048 | 4.6003 | 33.0983 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-11-06 12:00 | 0 | 0 | 0 | 0 | -15.8075 | 19.7749 | 93.5084 | -3.5084 | 19.0348 | 38.1367 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.084 | 0
2016-11-06 13:00 | 0 | 0 | 0 | 0 | -15.8201 | 34.7742 | 95.0123 | -5.0123 | 33.4251 | 47.4416 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0843 | 0
2016-11-06 14:00 | 0 | 0 | 0 | 0 | -15.8327 | 49.7735 | 97.2203 | -7.2203 | 47.7658 | 59.0258 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-11-06 15:00 | 0 | 0 | 0 | 0 | -15.8452 | 64.7729 | 99.9938 | -9.9938 | 62.0871 | 71.7906 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-11-06 16:00 | 0 | 0 | 0 | 0 | -15.8578 | 79.7722 | 103.1612 | -13.1612 | 76.4568 | 85.2026 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.0788 | 0
2016-11-06 17:00 | 0 | 0 | 0 | 0 | -15.8704 | 94.7715 | 106.5266 | -16.5266 | 90.973 | 98.9939 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-11-06 18:00 | 0 | 0 | 0 | 0 | -15.8829 | 109.7708 | 109.8765 | -19.8765 | 105.7484 | 113.0196 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-11-06 19:00 | 0 | 0 | 0 | 0 | -15.8955 | 124.7701 | 112.9868 | -22.9868 | 120.887 | 127.195 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0784 | 0
2016-11-06 20:00 | 0 | 0 | 0 | 0 | -15.908 | 139.7694 | 115.6334 | -25.6334 | 136.4541 | 141.4662 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-11-06 21:00 | 0 | 0 | 0 | 0 | -15.9205 | 154.7687 | 117.6077 | -27.6077 | 152.4454 | 155.7944 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-11-06 22:00 | 0 | 0 | 0 | 0 | -15.9331 | 169.768 | 118.7408 | -28.7408 | 168.7663 | 170.1337 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0745 | 0
2016-11-06 23:00 | 0 | 0 | 0 | 0 | -15.9456 | 184.7672 | 118.9298 | -28.9298 | -174.7614 | 175.3156 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-11-07 | 0 | 0 | 0 | 0 | -15.9581 | -160.2335 | 118.1579 | -28.1579 | -158.3582 | 161.0249 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-11-07 01:00 | 0 | 0 | 0 | 0 | -15.9706 | -145.2342 | 116.498 | -26.498 | -142.2249 | 146.6887 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.8 | 3.8 | 1.0742 | 0
2016-11-07 02:00 | 0 | 0 | 0 | 0 | -15.9831 | -130.235 | 114.0979 | -24.0979 | -126.4904 | 132.3982 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-11-07 03:00 | 0 | 0 | 0 | 0 | -15.9956 | -115.2357 | 111.1549 | -21.1549 | -111.1921 | 118.191 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.2 | 4.2 | 1.0728 | 0
2016-11-07 04:00 | 0 | 0 | 0 | 0 | -16.0081 | -100.2365 | 107.89 | -17.89 | -96.2878 | 104.1144 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0738 | 0
2016-11-07 05:00 | 0 | 0 | 0 | 0 | -16.0205 | -85.2372 | 104.5293 | -14.5293 | -81.6851 | 90.2408 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-11-07 06:00 | 0 | 0 | 0 | 0 | -16.033 | -70.238 | 101.2909 | -11.2909 | -67.2721 | 76.6899 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.2 | 4.2 | 1.0728 | 0
2016-11-07 07:00 | 0 | 0 | 0 | 0 | -16.0454 | -55.2387 | 98.3783 | -8.3783 | -52.944 | 63.6765 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.0735 | 0
2016-11-07 08:00 | 0 | 0 | 0 | 0 | -16.0579 | -40.2395 | 95.9725 | -5.9725 | -38.6211 | 51.6167 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.0735 | 0
2016-11-07 09:00 | 0 | 0 | 0 | 0 | -16.0703 | -25.2403 | 94.2248 | -4.2248 | -24.2594 | 41.3602 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.2 | 4.2 | 1.0728 | 0
2016-11-07 10:00 | 0 | 0 | 0 | 0 | -16.0828 | -10.2411 | 93.2475 | -3.2475 | -9.8522 | 34.5574 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.2 | 4.2 | 1.0728 | 0
2016-11-07 11:00 | 0 | 0 | 0 | 0 | -16.0952 | 4.7581 | 93.1047 | -3.1047 | 4.5779 | 33.393 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.3 | 4.3 | 1.0724 | 0
2016-11-07 12:00 | 0 | 0 | 0 | 0 | -16.1076 | 19.7573 | 93.8064 | -3.8064 | 18.9949 | 38.3838 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.4 | 4.4 | 1.0721 | 0
2016-11-07 13:00 | 0 | 0 | 0 | 0 | -16.12 | 34.7565 | 95.3075 | -5.3075 | 33.3693 | 47.631 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.2 | 4.2 | 1.0728 | 0
2016-11-07 14:00 | 0 | 0 | 0 | 0 | -16.1324 | 49.7557 | 97.5125 | -7.5125 | 47.6963 | 59.1687 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.3 | 4.3 | 1.0724 | 0
2016-11-07 15:00 | 0 | 0 | 0 | 0 | -16.1448 | 64.7549 | 100.2832 | -10.2832 | 62.0068 | 71.8988 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.4 | 4.4 | 1.0721 | 0
2016-11-07 16:00 | 0 | 0 | 0 | 0 | -16.1572 | 79.7541 | 103.4487 | -13.4487 | 76.3692 | 85.2845 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5 | 4.5 | 1.0717 | 0
2016-11-07 17:00 | 0 | 0 | 0 | 0 | -16.1696 | 94.7532 | 106.8134 | -16.8134 | 90.8819 | 99.0553 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.7 | 4.7 | 1.0711 | 0
2016-11-07 18:00 | 0 | 0 | 0 | 0 | -16.1819 | 109.7524 | 110.1638 | -20.1638 | 105.6582 | 113.0644 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.9 | 4.9 | 1.0703 | 0
2016-11-07 19:00 | 0 | 0 | 0 | 0 | -16.1943 | 124.7516 | 113.2759 | -23.2759 | 120.8026 | 127.2261 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.8 | 4.8 | 1.0707 | 0
2016-11-07 20:00 | 0 | 0 | 0 | 0 | -16.2066 | 139.7507 | 115.9252 | -25.9252 | 136.3808 | 141.4861 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5 | 5 | 1.07 | 0
2016-11-07 21:00 | 0 | 0 | 0 | 0 | -16.219 | 154.7499 | 117.9024 | -27.9024 | 152.3885 | 155.8062 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.3 | 5.3 | 1.069 | 0
2016-11-07 22:00 | 0 | 0 | 0 | 0 | -16.2313 | 169.749 | 119.0379 | -29.0379 | 168.73 | 170.1499 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.2 | 5.2 | 1.0693 | 0
2016-11-07 23:00 | 0 | 0 | 0 | 0 | -16.2436 | 184.7481 | 119.2282 | -29.2282 | -174.7751 | 175.3929 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.3 | 5.3 | 1.069 | 0
2016-11-08 | 0 | 0 | 0 | 0 | -16.256 | -160.2527 | 118.4562 | -28.4562 | -158.3498 | 161.0714 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.2 | 5.2 | 1.0693 | 0
2016-11-08 01:00 | 0 | 0 | 0 | 0 | -16.2683 | -145.2536 | 116.7952 | -26.7952 | -142.1976 | 146.7409 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.2 | 5.2 | 1.0693 | 0
2016-11-08 02:00 | 0 | 0 | 0 | 0 | -16.2806 | -130.2545 | 114.3936 | -24.3936 | -126.449 | 132.4605 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5 | 5 | 1.07 | 0
2016-11-08 03:00 | 0 | 0 | 0 | 0 | -16.2929 | -115.2554 | 111.4491 | -21.4491 | -111.142 | 118.2658 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5 | 5 | 1.07 | 0
2016-11-08 04:00 | 0 | 0 | 0 | 0 | -16.3052 | -100.2563 | 108.1834 | -18.1834 | -96.2344 | 104.2043 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0714 | 0
2016-11-08 05:00 | 0 | 0 | 0 | 0 | -16.3175 | -85.2572 | 104.8225 | -14.8225 | -81.633 | 90.3489 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.4 | 4.4 | 1.0721 | 0
2016-11-08 06:00 | 0 | 0 | 0 | 0 | -16.3297 | -70.2581 | 101.5848 | -11.5848 | -67.2258 | 76.8206 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0714 | 0
2016-11-08 07:00 | 0 | 0 | 0 | 0 | -16.342 | -55.259 | 98.6732 | -8.6732 | -52.9071 | 63.8364 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-11-08 08:00 | 0 | 0 | 0 | 0 | -16.3542 | -40.2599 | 96.2685 | -6.2685 | -38.5969 | 51.8148 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.7 | 4.7 | 1.0711 | 0
2016-11-08 09:00 | 0 | 0 | 0 | 0 | -16.3665 | -25.2608 | 94.5215 | -4.5215 | -24.2504 | 41.6057 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.3 | 4.3 | 1.0724 | 0
2016-11-08 10:00 | 0 | 0 | 0 | 0 | -16.3787 | -10.2617 | 93.5441 | -3.5441 | -9.8601 | 34.8457 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.0735 | 0
2016-11-08 11:00 | 0 | 0 | 0 | 0 | -16.391 | 4.7373 | 93.4001 | -3.4001 | 4.5524 | 33.6829 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.6 | 3.6 | 1.0749 | 0
2016-11-08 12:00 | 0 | 0 | 0 | 0 | -16.4032 | 19.7364 | 94.0996 | -4.0996 | 18.9522 | 38.626 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-11-08 13:00 | 0 | 0 | 0 | 0 | -16.4154 | 34.7355 | 95.5978 | -5.5978 | 33.3109 | 47.8158 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-11-08 14:00 | 0 | 0 | 0 | 0 | -16.4276 | 49.7345 | 97.7997 | -7.7997 | 47.6244 | 59.3071 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0784 | 0
2016-11-08 15:00 | 0 | 0 | 0 | 0 | -16.4398 | 64.7335 | 100.5676 | -10.5676 | 61.9243 | 72.0026 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.0788 | 0
2016-11-08 16:00 | 0 | 0 | 0 | 0 | -16.452 | 79.7326 | 103.7311 | -13.7311 | 76.2793 | 85.3621 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-11-08 17:00 | 0 | 0 | 0 | 0 | -16.4642 | 94.7316 | 107.0949 | -17.0949 | 90.7885 | 99.1122 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.078 | 0
2016-11-08 18:00 | 0 | 0 | 0 | 0 | -16.4764 | 109.7306 | 110.4458 | -20.4458 | 105.5655 | 113.1045 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0738 | 0
2016-11-08 19:00 | 0 | 0 | 0 | 0 | -16.4885 | 124.7297 | 113.5599 | -23.5599 | 120.7154 | 127.2522 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.7 | 4.7 | 1.0711 | 0
2016-11-08 20:00 | 0 | 0 | 0 | 0 | -16.5007 | 139.7287 | 116.2119 | -26.2119 | 136.3044 | 141.5002 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.8 | 4.8 | 1.0707 | 0
2016-11-08 21:00 | 0 | 0 | 0 | 0 | -16.5129 | 154.7277 | 118.1922 | -28.1922 | 152.3282 | 155.811 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.8 | 4.8 | 1.0707 | 0
2016-11-08 22:00 | 0 | 0 | 0 | 0 | -16.525 | 169.7267 | 119.3303 | -29.3303 | 168.69 | 170.1536 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0714 | 0
2016-11-08 23:00 | 0 | 0 | 0 | 0 | -16.5371 | 184.7257 | 119.5221 | -29.5221 | -174.7926 | 175.4547 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.7 | 4.7 | 1.0711 | 0
2016-11-09 | 0 | 0 | 0 | 0 | -16.5493 | -160.2753 | 118.7503 | -28.7503 | -158.3454 | 161.1163 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.4 | 4.4 | 1.0721 | 0
2016-11-09 01:00 | 0 | 0 | 0 | 0 | -16.5614 | -145.2763 | 117.0884 | -27.0884 | -142.1744 | 146.7935 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5 | 4.5 | 1.0717 | 0
2016-11-09 02:00 | 0 | 0 | 0 | 0 | -16.5735 | -130.2774 | 114.6853 | -24.6853 | -126.4118 | 132.524 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.4 | 4.4 | 1.0721 | 0
2016-11-09 03:00 | 0 | 0 | 0 | 0 | -16.5856 | -115.2784 | 111.7395 | -21.7395 | -111.0961 | 118.3421 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-11-09 04:00 | 0 | 0 | 0 | 0 | -16.5977 | -100.2794 | 108.473 | -18.473 | -96.1851 | 104.2958 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-11-09 05:00 | 0 | 0 | 0 | 0 | -16.6098 | -85.2805 | 105.112 | -15.112 | -81.5852 | 90.4585 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.0735 | 0
2016-11-09 06:00 | 0 | 0 | 0 | 0 | -16.6219 | -70.2815 | 101.8749 | -11.8749 | -67.1835 | 76.9528 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.0735 | 0
2016-11-09 07:00 | 0 | 0 | 0 | 0 | -16.6339 | -55.2826 | 98.9642 | -8.9642 | -52.8742 | 63.9974 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0738 | 0
2016-11-09 08:00 | 0 | 0 | 0 | 0 | -16.646 | -40.2836 | 96.5604 | -6.5604 | -38.5765 | 52.0132 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0738 | 0
2016-11-09 09:00 | 0 | 0 | 0 | 0 | -16.658 | -25.2847 | 94.8139 | -4.8139 | -24.245 | 41.8499 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.0735 | 0
2016-11-09 10:00 | 0 | 0 | 0 | 0 | -16.6701 | -10.2857 | 93.8361 | -3.8361 | -9.8714 | 35.1308 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5 | 4.5 | 1.0717 | 0
2016-11-09 11:00 | 0 | 0 | 0 | 0 | -16.6821 | 4.7132 | 93.6907 | -3.6907 | 4.5238 | 33.9678 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0738 | 0
2016-11-09 12:00 | 0 | 0 | 0 | 0 | -16.6942 | 19.7121 | 94.3879 | -4.3879 | 18.9067 | 38.8633 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.2 | 4.2 | 1.0728 | 0
2016-11-09 13:00 | 0 | 0 | 0 | 0 | -16.7062 | 34.711 | 95.8831 | -5.8831 | 33.2498 | 47.996 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-11-09 14:00 | 0 | 0 | 0 | 0 | -16.7182 | 49.7099 | 98.0817 | -8.0817 | 47.55 | 59.4412 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0745 | 0
2016-11-09 15:00 | 0 | 0 | 0 | 0 | -16.7302 | 64.7088 | 100.8467 | -10.8467 | 61.8393 | 72.102 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-11-09 16:00 | 0 | 0 | 0 | 0 | -16.7422 | 79.7077 | 104.0081 | -14.0081 | 76.1871 | 85.4352 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0714 | 0
2016-11-09 17:00 | 0 | 0 | 0 | 0 | -16.7542 | 94.7066 | 107.3711 | -17.3711 | 90.6926 | 99.1646 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.7 | 4.7 | 1.0711 | 0
2016-11-09 18:00 | 0 | 0 | 0 | 0 | -16.7662 | 109.7055 | 110.7226 | -20.7226 | 105.4702 | 113.14 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-11-09 19:00 | 0 | 0 | 0 | 0 | -16.7781 | 124.7044 | 113.8386 | -23.8386 | 120.6254 | 127.2732 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.8 | 4.8 | 1.0707 | 0
2016-11-09 20:00 | 0 | 0 | 0 | 0 | -16.7901 | 139.7032 | 116.4935 | -26.4935 | 136.2251 | 141.5089 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.0735 | 0
2016-11-09 21:00 | 0 | 0 | 0 | 0 | -16.8021 | 154.7021 | 118.477 | -28.477 | 152.2646 | 155.809 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.9 | 4.9 | 1.0703 | 0
2016-11-09 22:00 | 0 | 0 | 0 | 0 | -16.814 | 169.701 | 119.6178 | -29.6178 | 168.6464 | 170.1452 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0714 | 0
2016-11-09 23:00 | 0 | 0 | 0 | 0 | -16.8259 | 184.6998 | 119.8113 | -29.8113 | -174.814 | 175.501 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0714 | 0
2016-11-10 | 0 | 0 | 0 | 0 | -16.8379 | -160.3013 | 119.04 | -29.04 | -158.3451 | 161.1598 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.3 | 4.3 | 1.0724 | 0
2016-11-10 01:00 | 0 | 0 | 0 | 0 | -16.8498 | -145.3025 | 117.3774 | -27.3774 | -142.1554 | 146.8466 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.3 | 4.3 | 1.0724 | 0
2016-11-10 02:00 | 0 | 0 | 0 | 0 | -16.8617 | -130.3036 | 114.9731 | -24.9731 | -126.3788 | 132.5887 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-11-10 03:00 | 0 | 0 | 0 | 0 | -16.8736 | -115.3048 | 112.026 | -22.026 | -111.0545 | 118.42 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.2 | 4.2 | 1.0728 | 0
2016-11-10 04:00 | 0 | 0 | 0 | 0 | -16.8855 | -100.306 | 108.7588 | -18.7588 | -96.1401 | 104.3888 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.2 | 4.2 | 1.0728 | 0
2016-11-10 05:00 | 0 | 0 | 0 | 0 | -16.8974 | -85.3072 | 105.3977 | -15.3977 | -81.5415 | 90.5698 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-11-10 06:00 | 0 | 0 | 0 | 0 | -16.9093 | -70.3083 | 102.161 | -12.161 | -67.1454 | 77.0864 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-11-10 07:00 | 0 | 0 | 0 | 0 | -16.9212 | -55.3095 | 99.2512 | -9.2512 | -52.8453 | 64.1594 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-11-10 08:00 | 0 | 0 | 0 | 0 | -16.933 | -40.3107 | 96.8481 | -6.8481 | -38.5599 | 52.2118 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0784 | 0
2016-11-10 09:00 | 0 | 0 | 0 | 0 | -16.9449 | -25.3119 | 95.1019 | -5.1019 | -24.2432 | 42.0929 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0774 | 0
2016-11-10 10:00 | 0 | 0 | 0 | 0 | -16.9567 | -10.3131 | 94.1236 | -4.1236 | -9.886 | 35.4123 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.0788 | 0
2016-11-10 11:00 | 0 | 0 | 0 | 0 | -16.9686 | 4.6857 | 93.9766 | -3.9766 | 4.4921 | 34.2478 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-11-10 12:00 | 0 | 0 | 0 | 0 | -16.9804 | 19.6844 | 94.6713 | -4.6713 | 18.8583 | 39.0955 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-11-10 13:00 | 0 | 0 | 0 | 0 | -16.9922 | 34.6832 | 96.1633 | -6.1633 | 33.1861 | 48.1715 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-11-10 14:00 | 0 | 0 | 0 | 0 | -17.004 | 49.682 | 98.3586 | -8.3586 | 47.4732 | 59.5707 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0816 | 0
2016-11-10 15:00 | 0 | 0 | 0 | 0 | -17.0158 | 64.6807 | 101.1205 | -11.1205 | 61.7521 | 72.197 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-11-10 16:00 | 0 | 0 | 0 | 0 | -17.0276 | 79.6795 | 104.2798 | -14.2798 | 76.0926 | 85.5039 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-11-10 17:00 | 0 | 0 | 0 | 0 | -17.0394 | 94.6782 | 107.6419 | -17.6419 | 90.5945 | 99.2125 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0801 | 0
2016-11-10 18:00 | 0 | 0 | 0 | 0 | -17.0512 | 109.677 | 110.994 | -20.994 | 105.3725 | 113.1707 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.0822 | 0
2016-11-10 19:00 | 0 | 0 | 0 | 0 | -17.063 | 124.6757 | 114.1119 | -24.1119 | 120.5328 | 127.2894 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-11-10 20:00 | 0 | 0 | 0 | 0 | -17.0747 | 139.6745 | 116.7698 | -26.7698 | 136.1427 | 141.512 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-11-10 21:00 | 0 | 0 | 0 | 0 | -17.0865 | 154.6732 | 118.7566 | -28.7566 | 152.1976 | 155.8002 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-11-10 22:00 | 0 | 0 | 0 | 0 | -17.0982 | 169.6719 | 119.9005 | -29.9005 | 168.5991 | 170.1252 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-11-10 23:00 | 0 | 0 | 0 | 0 | -17.11 | 184.6706 | 120.0959 | -30.0959 | -174.8393 | 175.5322 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.0788 | 0
2016-11-11 | 0 | 0 | 0 | 0 | -17.1217 | -160.3307 | 119.3252 | -29.3252 | -158.3489 | 161.2019 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-11-11 01:00 | 0 | 0 | 0 | 0 | -17.1334 | -145.332 | 117.6621 | -27.6621 | -142.1406 | 146.9002 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-11-11 02:00 | 0 | 0 | 0 | 0 | -17.1451 | -130.3333 | 115.2567 | -25.2567 | -126.3501 | 132.6545 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-11-11 03:00 | 0 | 0 | 0 | 0 | -17.1568 | -115.3346 | 112.3086 | -22.3086 | -111.0172 | 118.4993 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-11-11 04:00 | 0 | 0 | 0 | 0 | -17.1685 | -100.3359 | 109.0406 | -19.0406 | -96.0993 | 104.4835 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-11-11 05:00 | 0 | 0 | 0 | 0 | -17.1802 | -85.3372 | 105.6794 | -15.6794 | -81.502 | 90.6825 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-11-11 06:00 | 0 | 0 | 0 | 0 | -17.1919 | -70.3385 | 102.4431 | -12.4431 | -67.1113 | 77.2213 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-11-11 07:00 | 0 | 0 | 0 | 0 | -17.2035 | -55.3398 | 99.534 | -9.534 | -52.8203 | 64.3223 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-11-11 08:00 | 0 | 0 | 0 | 0 | -17.2152 | -40.3412 | 97.1315 | -7.1315 | -38.5471 | 52.4104 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-11-11 09:00 | 0 | 0 | 0 | 0 | -17.2269 | -25.3425 | 95.3854 | -5.3854 | -24.245 | 42.3344 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0801 | 0
2016-11-11 10:00 | 0 | 0 | 0 | 0 | -17.2385 | -10.3439 | 94.4063 | -4.4063 | -9.904 | 35.6902 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-11-11 11:00 | 0 | 0 | 0 | 0 | -17.2501 | 4.6548 | 94.2576 | -4.2576 | 4.4573 | 34.5226 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-11-11 12:00 | 0 | 0 | 0 | 0 | -17.2618 | 19.6534 | 94.9496 | -4.9496 | 18.8071 | 39.3225 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-11-11 13:00 | 0 | 0 | 0 | 0 | -17.2734 | 34.6521 | 96.4383 | -6.4383 | 33.1199 | 48.3422 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-11-11 14:00 | 0 | 0 | 0 | 0 | -17.285 | 49.6507 | 98.63 | -8.63 | 47.3941 | 59.6956 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0801 | 0
2016-11-11 15:00 | 0 | 0 | 0 | 0 | -17.2966 | 64.6493 | 101.3889 | -11.3889 | 61.6627 | 72.2875 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-11-11 16:00 | 0 | 0 | 0 | 0 | -17.3082 | 79.6479 | 104.546 | -14.546 | 75.9959 | 85.5681 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-11-11 17:00 | 0 | 0 | 0 | 0 | -17.3197 | 94.6465 | 107.9071 | -17.9071 | 90.4941 | 99.2559 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0826 | 0
2016-11-11 18:00 | 0 | 0 | 0 | 0 | -17.3313 | 109.6451 | 111.2598 | -21.2598 | 105.2723 | 113.1969 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-11-11 19:00 | 0 | 0 | 0 | 0 | -17.3429 | 124.6437 | 114.3798 | -24.3798 | 120.4375 | 127.3006 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0801 | 0
2016-11-11 20:00 | 0 | 0 | 0 | 0 | -17.3544 | 139.6423 | 117.0407 | -27.0407 | 136.0574 | 141.5098 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-11-11 21:00 | 0 | 0 | 0 | 0 | -17.366 | 154.6409 | 119.0311 | -29.0311 | 152.1275 | 155.7849 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.083 | 0
2016-11-11 22:00 | 0 | 0 | 0 | 0 | -17.3775 | 169.6395 | 120.178 | -30.178 | 168.5483 | 170.094 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.084 | 0
2016-11-11 23:00 | 0 | 0 | 0 | 0 | -17.3891 | 184.6381 | 120.3756 | -30.3756 | -174.8684 | 175.5488 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0843 | 0
2016-11-12 | 0 | 0 | 0 | 0 | -17.4006 | -160.3633 | 119.6057 | -29.6057 | -158.3567 | 161.243 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-11-12 01:00 | 0 | 0 | 0 | 0 | -17.4121 | -145.3648 | 117.9424 | -27.9424 | -142.13 | 146.9544 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-11-12 02:00 | 0 | 0 | 0 | 0 | -17.4236 | -130.3662 | 115.5361 | -25.5361 | -126.3256 | 132.7216 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-11-12 03:00 | 0 | 0 | 0 | 0 | -17.4351 | -115.3677 | 112.587 | -22.587 | -110.9841 | 118.5801 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-11-12 04:00 | 0 | 0 | 0 | 0 | -17.4466 | -100.3691 | 109.3183 | -19.3183 | -96.0628 | 104.5797 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-11-12 05:00 | 0 | 0 | 0 | 0 | -17.4581 | -85.3706 | 105.957 | -15.957 | -81.4667 | 90.7967 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2 | 2 | 1.0805 | 0
2016-11-12 06:00 | 0 | 0 | 0 | 0 | -17.4695 | -70.372 | 102.7211 | -12.7211 | -67.0814 | 77.3574 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-11-12 07:00 | 0 | 0 | 0 | 0 | -17.481 | -55.3735 | 99.8125 | -9.8125 | -52.7993 | 64.4859 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-11-12 08:00 | 0 | 0 | 0 | 0 | -17.4924 | -40.375 | 97.4105 | -7.4105 | -38.5381 | 52.6088 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0774 | 0
2016-11-12 09:00 | 0 | 0 | 0 | 0 | -17.5039 | -25.3764 | 95.6642 | -5.6642 | -24.2504 | 42.5742 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-11-12 10:00 | 0 | 0 | 0 | 0 | -17.5153 | -10.3779 | 94.6842 | -4.6842 | -9.9253 | 35.9643 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-11-12 11:00 | 0 | 0 | 0 | 0 | -17.5267 | 4.6206 | 94.5336 | -4.5336 | 4.4195 | 34.7922 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0763 | 0
2016-11-12 12:00 | 0 | 0 | 0 | 0 | -17.5382 | 19.6191 | 95.2227 | -5.2227 | 18.7532 | 39.5443 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-11-12 13:00 | 0 | 0 | 0 | 0 | -17.5496 | 34.6176 | 96.7079 | -6.7079 | 33.0512 | 48.5081 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-11-12 14:00 | 0 | 0 | 0 | 0 | -17.561 | 49.6161 | 98.8961 | -8.8961 | 47.3126 | 59.816 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-11-12 15:00 | 0 | 0 | 0 | 0 | -17.5723 | 64.6146 | 101.6518 | -11.6518 | 61.5711 | 72.3735 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-11-12 16:00 | 0 | 0 | 0 | 0 | -17.5837 | 79.613 | 104.8066 | -14.8066 | 75.8971 | 85.6279 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-11-12 17:00 | 0 | 0 | 0 | 0 | -17.5951 | 94.6115 | 108.1668 | -18.1668 | 90.3915 | 99.2948 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0801 | 0
2016-11-12 18:00 | 0 | 0 | 0 | 0 | -17.6065 | 109.61 | 111.5201 | -21.5201 | 105.1699 | 113.2185 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.0822 | 0
2016-11-12 19:00 | 0 | 0 | 0 | 0 | -17.6178 | 124.6084 | 114.642 | -24.642 | 120.3397 | 127.3071 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.0822 | 0
2016-11-12 20:00 | 0 | 0 | 0 | 0 | -17.6292 | 139.6069 | 117.3061 | -27.3061 | 135.9692 | 141.5023 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.083 | 0
2016-11-12 21:00 | 0 | 0 | 0 | 0 | -17.6405 | 154.6054 | 119.3001 | -29.3001 | 152.054 | 155.7633 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.083 | 0
2016-11-12 22:00 | 0 | 0 | 0 | 0 | -17.6518 | 169.6038 | 120.4504 | -30.4504 | 168.494 | 170.0523 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-11-12 23:00 | 0 | 0 | 0 | 0 | -17.6631 | 184.6022 | 120.6503 | -30.6503 | -174.9013 | 175.5516 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0861 | 0
2016-11-13 | 0 | 0 | 0 | 0 | -17.6745 | -160.3993 | 119.8816 | -29.8816 | -158.3685 | 161.2831 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-11-13 01:00 | 0 | 0 | 0 | 0 | -17.6858 | -145.4009 | 118.2182 | -28.2182 | -142.1236 | 147.0093 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-11-13 02:00 | 0 | 0 | 0 | 0 | -17.697 | -130.4025 | 115.8111 | -25.8111 | -126.3055 | 132.7899 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-11-13 03:00 | 0 | 0 | 0 | 0 | -17.7083 | -115.4041 | 112.8611 | -22.8611 | -110.9554 | 118.6623 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-11-13 04:00 | 0 | 0 | 0 | 0 | -17.7196 | -100.4056 | 109.5919 | -19.5919 | -96.0306 | 104.6773 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-11-13 05:00 | 0 | 0 | 0 | 0 | -17.7309 | -85.4072 | 106.2304 | -16.2304 | -81.4356 | 90.9123 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-11-13 06:00 | 0 | 0 | 0 | 0 | -17.7421 | -70.4088 | 102.9948 | -12.9948 | -67.0556 | 77.4946 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-11-13 07:00 | 0 | 0 | 0 | 0 | -17.7534 | -55.4104 | 100.0866 | -10.0866 | -52.7824 | 64.65 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-11-13 08:00 | 0 | 0 | 0 | 0 | -17.7646 | -40.4121 | 97.6849 | -7.6849 | -38.5329 | 52.807 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-11-13 09:00 | 0 | 0 | 0 | 0 | -17.7758 | -25.4137 | 95.9384 | -5.9384 | -24.2593 | 42.8122 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-11-13 10:00 | 0 | 0 | 0 | 0 | -17.7871 | -10.4153 | 94.9572 | -4.9572 | -9.9499 | 36.2346 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-11-13 11:00 | 0 | 0 | 0 | 0 | -17.7983 | 4.5831 | 94.8044 | -4.8044 | 4.3787 | 35.0565 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-11-13 12:00 | 0 | 0 | 0 | 0 | -17.8095 | 19.5814 | 95.4905 | -5.4905 | 18.6966 | 39.7608 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-11-13 13:00 | 0 | 0 | 0 | 0 | -17.8207 | 34.5798 | 96.9721 | -6.9721 | 32.9801 | 48.6689 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-11-13 14:00 | 0 | 0 | 0 | 0 | -17.8318 | 49.5782 | 99.1566 | -9.1566 | 47.2289 | 59.9317 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-11-13 15:00 | 0 | 0 | 0 | 0 | -17.843 | 64.5765 | 101.909 | -11.909 | 61.4773 | 72.4551 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-11-13 16:00 | 0 | 0 | 0 | 0 | -17.8542 | 79.5748 | 105.0615 | -15.0615 | 75.7962 | 85.6832 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-11-13 17:00 | 0 | 0 | 0 | 0 | -17.8653 | 94.5732 | 108.4207 | -18.4207 | 90.2867 | 99.3293 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-11-13 18:00 | 0 | 0 | 0 | 0 | -17.8765 | 109.5715 | 111.7746 | -21.7746 | 105.0651 | 113.2355 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0872 | 0
2016-11-13 19:00 | 0 | 0 | 0 | 0 | -17.8876 | 124.5698 | 114.8986 | -24.8986 | 120.2393 | 127.3088 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.0822 | 0
2016-11-13 20:00 | 0 | 0 | 0 | 0 | -17.8988 | 139.5682 | 117.566 | -27.566 | 135.8782 | 141.4897 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.083 | 0
2016-11-13 21:00 | 0 | 0 | 0 | 0 | -17.9099 | 154.5665 | 119.5637 | -29.5637 | 151.9774 | 155.7356 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0843 | 0
2016-11-13 22:00 | 0 | 0 | 0 | 0 | -17.921 | 169.5648 | 120.7175 | -30.7175 | 168.4361 | 170.0004 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-11-13 23:00 | 0 | 0 | 0 | 0 | -17.9321 | 184.5631 | 120.92 | -30.92 | -174.9382 | 175.5413 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-11-14 | 0 | 0 | 0 | 0 | -17.9432 | -160.4386 | 120.1525 | -30.1525 | -158.3845 | 161.3223 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-11-14 01:00 | 0 | 0 | 0 | 0 | -17.9543 | -145.4403 | 118.4893 | -28.4893 | -142.1214 | 147.0649 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-11-14 02:00 | 0 | 0 | 0 | 0 | -17.9653 | -130.442 | 116.0817 | -26.0817 | -126.2896 | 132.8594 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.0788 | 0
2016-11-14 03:00 | 0 | 0 | 0 | 0 | -17.9764 | -115.4438 | 113.1309 | -23.1309 | -110.931 | 118.746 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0774 | 0
2016-11-14 04:00 | 0 | 0 | 0 | 0 | -17.9875 | -100.4455 | 109.8611 | -19.8611 | -96.0027 | 104.7764 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-11-14 05:00 | 0 | 0 | 0 | 0 | -17.9985 | -85.4472 | 106.4995 | -16.4995 | -81.4088 | 91.0292 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0745 | 0
2016-11-14 06:00 | 0 | 0 | 0 | 0 | -18.0096 | -70.4489 | 103.2641 | -13.2641 | -67.0339 | 77.6328 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.2 | 4.2 | 1.0728 | 0
2016-11-14 07:00 | 0 | 0 | 0 | 0 | -18.0206 | -55.4507 | 100.3563 | -10.3563 | -52.7693 | 64.8147 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.4 | 4.4 | 1.0721 | 0
2016-11-14 08:00 | 0 | 0 | 0 | 0 | -18.0316 | -40.4524 | 97.9546 | -7.9546 | -38.5315 | 53.0047 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5 | 4.5 | 1.0717 | 0
2016-11-14 09:00 | 0 | 0 | 0 | 0 | -18.0426 | -25.4542 | 96.2076 | -6.2076 | -24.2718 | 43.0483 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5 | 4.5 | 1.0717 | 0
2016-11-14 10:00 | 0 | 0 | 0 | 0 | -18.0536 | -10.4559 | 95.2251 | -5.2251 | -9.9777 | 36.5008 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.3 | 4.3 | 1.0724 | 0
2016-11-14 11:00 | 0 | 0 | 0 | 0 | -18.0646 | 4.5423 | 95.07 | -5.07 | 4.3349 | 35.3153 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.9 | 4.9 | 1.0703 | 0
2016-11-14 12:00 | 0 | 0 | 0 | 0 | -18.0756 | 19.5405 | 95.7529 | -5.7529 | 18.6373 | 39.9719 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.1 | 5.1 | 1.0696 | 0
2016-11-14 13:00 | 0 | 0 | 0 | 0 | -18.0866 | 34.5387 | 97.2308 | -7.2308 | 32.9065 | 48.8248 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5 | 5 | 1.07 | 0
2016-11-14 14:00 | 0 | 0 | 0 | 0 | -18.0975 | 49.537 | 99.4114 | -9.4114 | 47.143 | 60.0426 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0745 | 0
2016-11-14 15:00 | 0 | 0 | 0 | 0 | -18.1085 | 64.5352 | 102.1604 | -12.1604 | 61.3815 | 72.532 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-11-14 16:00 | 0 | 0 | 0 | 0 | -18.1194 | 79.5334 | 105.3105 | -15.3105 | 75.6933 | 85.7341 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-11-14 17:00 | 0 | 0 | 0 | 0 | -18.1304 | 94.5316 | 108.6688 | -18.6688 | 90.1799 | 99.3593 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.0735 | 0
2016-11-14 18:00 | 0 | 0 | 0 | 0 | -18.1413 | 109.5298 | 112.0233 | -22.0233 | 104.9581 | 113.248 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5 | 4.5 | 1.0717 | 0
2016-11-14 19:00 | 0 | 0 | 0 | 0 | -18.1522 | 124.528 | 115.1495 | -25.1495 | 120.1364 | 127.3059 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0732 | 0
2016-11-14 20:00 | 0 | 0 | 0 | 0 | -18.1631 | 139.5262 | 117.8201 | -27.8201 | 135.7843 | 141.4721 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-11-14 21:00 | 0 | 0 | 0 | 0 | -18.174 | 154.5243 | 119.8217 | -29.8217 | 151.8977 | 155.702 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0774 | 0
2016-11-14 22:00 | 0 | 0 | 0 | 0 | -18.1849 | 169.5225 | 120.9792 | -30.9792 | 168.3746 | 169.9391 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0774 | 0
2016-11-14 23:00 | 0 | 0 | 0 | 0 | -18.1958 | 184.5207 | 121.1845 | -31.1845 | -174.9788 | 175.5188 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.078 | 0
2016-11-15 | 0 | 0 | 0 | 0 | -18.2067 | -160.4812 | 120.4185 | -30.4185 | -158.4045 | 161.3609 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-11-15 01:00 | 0 | 0 | 0 | 0 | -18.2175 | -145.483 | 118.7557 | -28.7557 | -142.1234 | 147.1213 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-11-15 02:00 | 0 | 0 | 0 | 0 | -18.2284 | -130.4848 | 116.3477 | -26.3477 | -126.278 | 132.9302 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.4 | 3.4 | 1.0756 | 0
2016-11-15 03:00 | 0 | 0 | 0 | 0 | -18.2392 | -115.4867 | 113.3962 | -23.3962 | -110.9109 | 118.831 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-11-15 04:00 | 0 | 0 | 0 | 0 | -18.2501 | -100.4886 | 110.126 | -20.126 | -95.9791 | 104.8769 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0801 | 0
2016-11-15 05:00 | 0 | 0 | 0 | 0 | -18.2609 | -85.4904 | 106.7642 | -16.7642 | -81.3862 | 91.1473 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.0822 | 0
2016-11-15 06:00 | 0 | 0 | 0 | 0 | -18.2717 | -70.4923 | 103.5289 | -13.5289 | -67.0164 | 77.7719 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-11-15 07:00 | 0 | 0 | 0 | 0 | -18.2825 | -55.4942 | 100.6213 | -10.6213 | -52.7603 | 64.9797 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.4 | 3.4 | 1.0756 | 0
2016-11-15 08:00 | 0 | 0 | 0 | 0 | -18.2933 | -40.4961 | 98.2196 | -8.2196 | -38.5338 | 53.2019 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.078 | 0
2016-11-15 09:00 | 0 | 0 | 0 | 0 | -18.3041 | -25.4979 | 96.4719 | -6.4719 | -24.2877 | 43.2822 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.078 | 0
2016-11-15 10:00 | 0 | 0 | 0 | 0 | -18.3149 | -10.4998 | 95.4879 | -5.4879 | -10.0087 | 36.7629 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0816 | 0
2016-11-15 11:00 | 0 | 0 | 0 | 0 | -18.3257 | 4.4983 | 95.3303 | -5.3303 | 4.2883 | 35.5687 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0745 | 0
2016-11-15 12:00 | 0 | 0 | 0 | 0 | -18.3364 | 19.4964 | 96.0098 | -6.0098 | 18.5754 | 40.1775 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-11-15 13:00 | 0 | 0 | 0 | 0 | -18.3472 | 34.4944 | 97.4838 | -7.4838 | 32.8306 | 48.9756 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0784 | 0
2016-11-15 14:00 | 0 | 0 | 0 | 0 | -18.3579 | 49.4925 | 99.6604 | -9.6604 | 47.0549 | 60.1488 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0784 | 0
2016-11-15 15:00 | 0 | 0 | 0 | 0 | -18.3686 | 64.4906 | 102.4061 | -12.4061 | 61.2836 | 72.6044 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-11-15 16:00 | 0 | 0 | 0 | 0 | -18.3794 | 79.4887 | 105.5537 | -15.5537 | 75.5884 | 85.7805 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0774 | 0
2016-11-15 17:00 | 0 | 0 | 0 | 0 | -18.3901 | 94.4868 | 108.911 | -18.911 | 90.0711 | 99.3849 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0774 | 0
2016-11-15 18:00 | 0 | 0 | 0 | 0 | -18.4008 | 109.4848 | 112.266 | -22.266 | 104.8489 | 113.2561 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.078 | 0
2016-11-15 19:00 | 0 | 0 | 0 | 0 | -18.4115 | 124.4829 | 115.3944 | -25.3944 | 120.0312 | 127.2983 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-11-15 20:00 | 0 | 0 | 0 | 0 | -18.4222 | 139.4809 | 118.0685 | -28.0685 | 135.6878 | 141.4495 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-11-15 21:00 | 0 | 0 | 0 | 0 | -18.4328 | 154.479 | 120.0741 | -30.0741 | 151.8148 | 155.6626 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.6 | 3.6 | 1.0749 | 0
2016-11-15 22:00 | 0 | 0 | 0 | 0 | -18.4435 | 169.477 | 121.2354 | -31.2354 | 168.3098 | 169.8689 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0738 | 0
2016-11-15 23:00 | 0 | 0 | 0 | 0 | -18.4542 | 184.475 | 121.4437 | -31.4437 | -175.0232 | 175.4852 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0738 | 0
2016-11-16 | 0 | 0 | 0 | 0 | -18.4648 | -160.5269 | 120.6795 | -30.6795 | -158.4285 | 161.399 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.2 | 4.2 | 1.0728 | 0
2016-11-16 01:00 | 0 | 0 | 0 | 0 | -18.4754 | -145.5289 | 119.0172 | -29.0172 | -142.1297 | 147.1785 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-11-16 02:00 | 0 | 0 | 0 | 0 | -18.4861 | -130.5309 | 116.6089 | -26.6089 | -126.2708 | 133.0022 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.8 | 3.8 | 1.0742 | 0
2016-11-16 03:00 | 0 | 0 | 0 | 0 | -18.4967 | -115.5329 | 113.657 | -23.657 | -110.8952 | 118.9175 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0784 | 0
2016-11-16 04:00 | 0 | 0 | 0 | 0 | -18.5073 | -100.5349 | 110.3863 | -20.3863 | -95.9598 | 104.9788 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0784 | 0
2016-11-16 05:00 | 0 | 0 | 0 | 0 | -18.5179 | -85.5369 | 107.0244 | -17.0244 | -81.3679 | 91.2666 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-11-16 06:00 | 0 | 0 | 0 | 0 | -18.5285 | -70.5389 | 103.7891 | -13.7891 | -67.0029 | 77.9119 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0774 | 0
2016-11-16 07:00 | 0 | 0 | 0 | 0 | -18.5391 | -55.5409 | 100.8816 | -10.8816 | -52.7552 | 65.145 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0745 | 0
2016-11-16 08:00 | 0 | 0 | 0 | 0 | -18.5496 | -40.5429 | 98.4797 | -8.4797 | -38.5399 | 53.3983 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5 | 4.5 | 1.0717 | 0
2016-11-16 09:00 | 0 | 0 | 0 | 0 | -18.5602 | -25.5449 | 96.7312 | -6.7312 | -24.3072 | 43.5138 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.2 | 4.2 | 1.0728 | 0
2016-11-16 10:00 | 0 | 0 | 0 | 0 | -18.5708 | -10.5469 | 95.7454 | -5.7454 | -10.0429 | 37.0207 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5 | 4.5 | 1.0717 | 0
2016-11-16 11:00 | 0 | 0 | 0 | 0 | -18.5813 | 4.451 | 95.5851 | -5.5851 | 4.2387 | 35.8166 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.7 | 4.7 | 1.0711 | 0
2016-11-16 12:00 | 0 | 0 | 0 | 0 | -18.5918 | 19.449 | 96.2611 | -6.2611 | 18.5109 | 40.3775 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.8 | 4.8 | 1.0707 | 0
2016-11-16 13:00 | 0 | 0 | 0 | 0 | -18.6024 | 34.4469 | 97.7311 | -7.7311 | 32.7523 | 49.1213 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0714 | 0
2016-11-16 14:00 | 0 | 0 | 0 | 0 | -18.6129 | 49.4449 | 99.9037 | -9.9037 | 46.9648 | 60.2502 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0714 | 0
2016-11-16 15:00 | 0 | 0 | 0 | 0 | -18.6234 | 64.4428 | 102.6458 | -12.6458 | 61.1838 | 72.6722 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0763 | 0
2016-11-16 16:00 | 0 | 0 | 0 | 0 | -18.6339 | 79.4408 | 105.7909 | -15.7909 | 75.4816 | 85.8225 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.0788 | 0
2016-11-16 17:00 | 0 | 0 | 0 | 0 | -18.6444 | 94.4387 | 109.1471 | -19.1471 | 89.9603 | 99.4061 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-11-16 18:00 | 0 | 0 | 0 | 0 | -18.6548 | 109.4366 | 112.5027 | -22.5027 | 104.7377 | 113.2598 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.8 | 3.8 | 1.0742 | 0
2016-11-16 19:00 | 0 | 0 | 0 | 0 | -18.6653 | 124.4346 | 115.6333 | -25.6333 | 119.9235 | 127.2863 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-11-16 20:00 | 0 | 0 | 0 | 0 | -18.6757 | 139.4325 | 118.3109 | -28.3109 | 135.5886 | 141.4222 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-11-16 21:00 | 0 | 0 | 0 | 0 | -18.6862 | 154.4304 | 120.3207 | -30.3207 | 151.7289 | 155.6178 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-11-16 22:00 | 0 | 0 | 0 | 0 | -18.6966 | 169.4283 | 121.486 | -31.486 | 168.2414 | 169.7904 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0774 | 0
2016-11-16 23:00 | 0 | 0 | 0 | 0 | -18.7071 | 184.4262 | 121.6975 | -31.6975 | -175.0715 | 175.4415 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.0788 | 0
2016-11-17 | 0 | 0 | 0 | 0 | -18.7175 | -160.5759 | 120.9352 | -30.9352 | -158.4566 | 161.4367 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2 | 2 | 1.0805 | 0
2016-11-17 01:00 | 0 | 0 | 0 | 0 | -18.7279 | -145.578 | 119.2737 | -29.2737 | -142.1402 | 147.2367 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-11-17 02:00 | 0 | 0 | 0 | 0 | -18.7383 | -130.5801 | 116.8654 | -26.8654 | -126.2679 | 133.0756 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0816 | 0
2016-11-17 03:00 | 0 | 0 | 0 | 0 | -18.7487 | -115.5822 | 113.9131 | -23.9131 | -110.8838 | 119.0053 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-11-17 04:00 | 0 | 0 | 0 | 0 | -18.759 | -100.5844 | 110.642 | -20.642 | -95.9448 | 105.0819 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-11-17 05:00 | 0 | 0 | 0 | 0 | -18.7694 | -85.5865 | 107.2799 | -17.2799 | -81.3538 | 91.3869 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-11-17 06:00 | 0 | 0 | 0 | 0 | -18.7798 | -70.5886 | 104.0446 | -14.0446 | -66.9936 | 78.0525 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.6 | 3.6 | 1.0749 | 0
2016-11-17 07:00 | 0 | 0 | 0 | 0 | -18.7901 | -55.5908 | 101.1371 | -11.1371 | -52.754 | 65.3103 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0738 | 0
2016-11-17 08:00 | 0 | 0 | 0 | 0 | -18.8005 | -40.5929 | 98.7348 | -8.7348 | -38.5496 | 53.5938 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.7 | 4.7 | 1.0711 | 0
2016-11-17 09:00 | 0 | 0 | 0 | 0 | -18.8108 | -25.5951 | 96.9852 | -6.9852 | -24.33 | 43.743 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5 | 4.5 | 1.0717 | 0
2016-11-17 10:00 | 0 | 0 | 0 | 0 | -18.8211 | -10.5972 | 95.9975 | -5.9975 | -10.0803 | 37.2741 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5 | 5 | 1.07 | 0
2016-11-17 11:00 | 0 | 0 | 0 | 0 | -18.8314 | 4.4006 | 95.8343 | -5.8343 | 4.1863 | 36.0587 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.8 | 4.8 | 1.0707 | 0
2016-11-17 12:00 | 0 | 0 | 0 | 0 | -18.8417 | 19.3984 | 96.5066 | -6.5066 | 18.4439 | 40.5719 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.7 | 4.7 | 1.0711 | 0
2016-11-17 13:00 | 0 | 0 | 0 | 0 | -18.852 | 34.3963 | 97.9725 | -7.9725 | 32.6718 | 49.2617 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.7 | 4.7 | 1.0711 | 0
2016-11-17 14:00 | 0 | 0 | 0 | 0 | -18.8623 | 49.3941 | 100.1409 | -10.1409 | 46.8726 | 60.3467 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.3 | 4.3 | 1.0724 | 0
2016-11-17 15:00 | 0 | 0 | 0 | 0 | -18.8726 | 64.3919 | 102.8794 | -12.8794 | 61.0822 | 72.7354 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0745 | 0
2016-11-17 16:00 | 0 | 0 | 0 | 0 | -18.8828 | 79.3897 | 106.0221 | -16.0221 | 75.373 | 85.86 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0763 | 0
2016-11-17 17:00 | 0 | 0 | 0 | 0 | -18.8931 | 94.3875 | 109.3771 | -19.3771 | 89.8477 | 99.4229 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-11-17 18:00 | 0 | 0 | 0 | 0 | -18.9033 | 109.3853 | 112.7334 | -22.7334 | 104.6244 | 113.2591 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-11-17 19:00 | 0 | 0 | 0 | 0 | -18.9136 | 124.3831 | 115.8662 | -25.8662 | 119.8137 | 127.2699 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-11-17 20:00 | 0 | 0 | 0 | 0 | -18.9238 | 139.3809 | 118.5473 | -28.5473 | 135.4867 | 141.3902 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-11-17 21:00 | 0 | 0 | 0 | 0 | -18.934 | 154.3787 | 120.5613 | -30.5613 | 151.64 | 155.5677 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0774 | 0
2016-11-17 22:00 | 0 | 0 | 0 | 0 | -18.9442 | 169.3764 | 121.7309 | -31.7309 | 168.1697 | 169.7042 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.0788 | 0
2016-11-17 23:00 | 0 | 0 | 0 | 0 | -18.9544 | 184.3742 | 121.9458 | -31.9458 | -175.1234 | 175.3889 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.6 | 3.6 | 1.0749 | 0
2016-11-18 | 0 | 0 | 0 | 0 | -18.9646 | -160.628 | 121.1857 | -31.1857 | -158.4888 | 161.4742 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-11-18 01:00 | 0 | 0 | 0 | 0 | -18.9747 | -145.6303 | 119.5251 | -29.5251 | -142.1549 | 147.2957 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.0753 | 0
2016-11-18 02:00 | 0 | 0 | 0 | 0 | -18.9849 | -130.6325 | 117.117 | -27.117 | -126.2693 | 133.1502 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-11-18 03:00 | 0 | 0 | 0 | 0 | -18.9951 | -115.6348 | 114.1643 | -24.1643 | -110.8768 | 119.0945 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-11-18 04:00 | 0 | 0 | 0 | 0 | -19.0052 | -100.637 | 110.893 | -20.893 | -95.9341 | 105.1863 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0763 | 0
2016-11-18 05:00 | 0 | 0 | 0 | 0 | -19.0153 | -85.6393 | 107.5307 | -17.5307 | -81.3439 | 91.5083 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-11-18 06:00 | 0 | 0 | 0 | 0 | -19.0255 | -70.6415 | 104.2953 | -14.2953 | -66.9884 | 78.1938 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.078 | 0
2016-11-18 07:00 | 0 | 0 | 0 | 0 | -19.0356 | -55.6438 | 101.3876 | -11.3876 | -52.7567 | 65.4757 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-11-18 08:00 | 0 | 0 | 0 | 0 | -19.0457 | -40.6461 | 98.9847 | -8.9847 | -38.5631 | 53.7883 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.078 | 0
2016-11-18 09:00 | 0 | 0 | 0 | 0 | -19.0558 | -25.6484 | 97.234 | -7.234 | -24.3563 | 43.9697 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-11-18 10:00 | 0 | 0 | 0 | 0 | -19.0659 | -10.6507 | 96.2441 | -6.2441 | -10.1208 | 37.523 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.0788 | 0
2016-11-18 11:00 | 0 | 0 | 0 | 0 | -19.0759 | 4.3471 | 96.0779 | -6.0779 | 4.1312 | 36.2951 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0784 | 0
2016-11-18 12:00 | 0 | 0 | 0 | 0 | -19.086 | 19.3448 | 96.7464 | -6.7464 | 18.3744 | 40.7606 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0819 | 0
2016-11-18 13:00 | 0 | 0 | 0 | 0 | -19.0961 | 34.3424 | 98.2079 | -8.2079 | 32.5892 | 49.3968 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2 | 2 | 1.0805 | 0
2016-11-18 14:00 | 0 | 0 | 0 | 0 | -19.1061 | 49.3401 | 100.3721 | -10.3721 | 46.7784 | 60.4383 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-11-18 15:00 | 0 | 0 | 0 | 0 | -19.1161 | 64.3378 | 103.1069 | -13.1069 | 60.9787 | 72.794 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0801 | 0
2016-11-18 16:00 | 0 | 0 | 0 | 0 | -19.1262 | 79.3355 | 106.247 | -16.247 | 75.2627 | 85.893 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0816 | 0
2016-11-18 17:00 | 0 | 0 | 0 | 0 | -19.1362 | 94.3332 | 109.601 | -19.601 | 89.7333 | 99.4354 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-11-18 18:00 | 0 | 0 | 0 | 0 | -19.1462 | 109.3308 | 112.9578 | -22.9578 | 104.5092 | 113.2542 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0833 | 0
2016-11-18 19:00 | 0 | 0 | 0 | 0 | -19.1562 | 124.3285 | 116.0928 | -26.0928 | 119.7016 | 127.2491 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0843 | 0
2016-11-18 20:00 | 0 | 0 | 0 | 0 | -19.1662 | 139.3262 | 118.7776 | -28.7776 | 135.3824 | 141.3538 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-11-18 21:00 | 0 | 0 | 0 | 0 | -19.1761 | 154.3238 | 120.796 | -30.796 | 151.5481 | 155.5125 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2 | 2 | 1.0805 | 0
2016-11-18 22:00 | 0 | 0 | 0 | 0 | -19.1861 | 169.3215 | 121.97 | -31.97 | 168.0946 | 169.6109 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0801 | 0
2016-11-18 23:00 | 0 | 0 | 0 | 0 | -19.196 | 184.3191 | 122.1884 | -32.1884 | -175.1791 | 175.3283 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2 | 2 | 1.0805 | 0
2016-11-19 | 0 | 0 | 0 | 0 | -19.206 | -160.6832 | 121.4308 | -31.4308 | -158.5249 | 161.5116 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.0822 | 0
2016-11-19 01:00 | 0 | 0 | 0 | 0 | -19.2159 | -145.6856 | 119.7714 | -29.7714 | -142.1738 | 147.3558 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.083 | 0
2016-11-19 02:00 | 0 | 0 | 0 | 0 | -19.2259 | -130.688 | 117.3635 | -27.3635 | -126.275 | 133.2261 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0837 | 0
2016-11-19 03:00 | 0 | 0 | 0 | 0 | -19.2358 | -115.6904 | 114.4107 | -24.4107 | -110.8741 | 119.185 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0833 | 0
2016-11-19 04:00 | 0 | 0 | 0 | 0 | -19.2457 | -100.6928 | 111.1391 | -21.1391 | -95.9278 | 105.2919 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.084 | 0
2016-11-19 05:00 | 0 | 0 | 0 | 0 | -19.2556 | -85.6951 | 107.7766 | -17.7766 | -81.3383 | 91.6306 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0837 | 0
2016-11-19 06:00 | 0 | 0 | 0 | 0 | -19.2655 | -70.6975 | 104.5411 | -14.5411 | -66.9872 | 78.3356 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0819 | 0
2016-11-19 07:00 | 0 | 0 | 0 | 0 | -19.2753 | -55.6999 | 101.633 | -11.633 | -52.7633 | 65.6409 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0819 | 0
2016-11-19 08:00 | 0 | 0 | 0 | 0 | -19.2852 | -40.7023 | 99.2295 | -9.2295 | -38.5802 | 53.9817 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-11-19 09:00 | 0 | 0 | 0 | 0 | -19.295 | -25.7048 | 97.4773 | -7.4773 | -24.386 | 44.1936 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0826 | 0
2016-11-19 10:00 | 0 | 0 | 0 | 0 | -19.3049 | -10.7072 | 96.4852 | -6.4852 | -10.1644 | 37.7672 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0801 | 0
2016-11-19 11:00 | 0 | 0 | 0 | 0 | -19.3147 | 4.2904 | 96.3158 | -6.3158 | 4.0733 | 36.5256 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0801 | 0
2016-11-19 12:00 | 0 | 0 | 0 | 0 | -19.3245 | 19.288 | 96.9802 | -6.9802 | 18.3025 | 40.9434 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-11-19 13:00 | 0 | 0 | 0 | 0 | -19.3344 | 34.2856 | 98.4374 | -8.4374 | 32.5044 | 49.5267 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-11-19 14:00 | 0 | 0 | 0 | 0 | -19.3442 | 49.2831 | 100.5972 | -10.5972 | 46.6824 | 60.5249 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0816 | 0
2016-11-19 15:00 | 0 | 0 | 0 | 0 | -19.354 | 64.2807 | 103.3283 | -13.3283 | 60.8735 | 72.8479 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-11-19 16:00 | 0 | 0 | 0 | 0 | -19.3637 | 79.2782 | 106.4657 | -16.4657 | 75.1506 | 85.9216 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2 | 2 | 1.0805 | 0
2016-11-19 17:00 | 0 | 0 | 0 | 0 | -19.3735 | 94.2758 | 109.8185 | -19.8185 | 89.6171 | 99.4436 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-11-19 18:00 | 0 | 0 | 0 | 0 | -19.3833 | 109.2733 | 113.1759 | -23.1759 | 104.3921 | 113.245 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-11-19 19:00 | 0 | 0 | 0 | 0 | -19.393 | 124.2708 | 116.3132 | -26.3132 | 119.5875 | 127.2241 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2 | 2 | 1.0805 | 0
2016-11-19 20:00 | 0 | 0 | 0 | 0 | -19.4028 | 139.2684 | 119.0017 | -29.0017 | 135.2756 | 141.3129 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.0788 | 0
2016-11-19 21:00 | 0 | 0 | 0 | 0 | -19.4125 | 154.2659 | 121.0246 | -31.0246 | 151.4534 | 155.4526 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0767 | 0
2016-11-19 22:00 | 0 | 0 | 0 | 0 | -19.4222 | 169.2634 | 122.2031 | -32.2031 | 168.0163 | 169.5112 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0763 | 0
2016-11-19 23:00 | 0 | 0 | 0 | 0 | -19.4319 | 184.2609 | 122.4254 | -32.4254 | -175.2385 | 175.261 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-11-20 | 0 | 0 | 0 | 0 | -19.4416 | -160.7415 | 121.6703 | -31.6703 | -158.5651 | 161.5491 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-11-20 01:00 | 0 | 0 | 0 | 0 | -19.4513 | -145.744 | 120.0123 | -30.0123 | -142.1969 | 147.4169 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.0788 | 0
2016-11-20 02:00 | 0 | 0 | 0 | 0 | -19.461 | -130.7465 | 117.6049 | -27.6049 | -126.2851 | 133.3033 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-11-20 03:00 | 0 | 0 | 0 | 0 | -19.4707 | -115.749 | 114.6521 | -24.6521 | -110.8757 | 119.2767 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-11-20 04:00 | 0 | 0 | 0 | 0 | -19.4803 | -100.7516 | 111.3802 | -21.3802 | -95.9257 | 105.3986 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.0822 | 0
2016-11-20 05:00 | 0 | 0 | 0 | 0 | -19.49 | -85.7541 | 108.0175 | -18.0175 | -81.3368 | 91.7538 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-11-20 06:00 | 0 | 0 | 0 | 0 | -19.4996 | -70.7566 | 104.7818 | -14.7818 | -66.9901 | 78.4778 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-11-20 07:00 | 0 | 0 | 0 | 0 | -19.5093 | -55.7591 | 101.8733 | -11.8733 | -52.7738 | 65.8058 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0801 | 0
2016-11-20 08:00 | 0 | 0 | 0 | 0 | -19.5189 | -40.7617 | 99.4689 | -9.4689 | -38.6009 | 54.1737 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.0788 | 0
2016-11-20 09:00 | 0 | 0 | 0 | 0 | -19.5285 | -25.7642 | 97.7151 | -7.7151 | -24.419 | 44.4146 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.0788 | 0
2016-11-20 10:00 | 0 | 0 | 0 | 0 | -19.5381 | -10.7667 | 96.7206 | -6.7206 | -10.2109 | 38.0067 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.0788 | 0
2016-11-20 11:00 | 0 | 0 | 0 | 0 | -19.5477 | 4.2307 | 96.5477 | -6.5477 | 4.0127 | 36.7502 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.0788 | 0
2016-11-20 12:00 | 0 | 0 | 0 | 0 | -19.5573 | 19.2282 | 97.2081 | -7.2081 | 18.2282 | 41.1204 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0784 | 0
2016-11-20 13:00 | 0 | 0 | 0 | 0 | -19.5668 | 34.2256 | 98.6606 | -8.6606 | 32.4175 | 49.6511 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-11-20 14:00 | 0 | 0 | 0 | 0 | -19.5764 | 49.2231 | 100.816 | -10.816 | 46.5846 | 60.6067 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-11-20 15:00 | 0 | 0 | 0 | 0 | -19.5859 | 64.2205 | 103.5433 | -13.5433 | 60.7666 | 72.8971 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.078 | 0
2016-11-20 16:00 | 0 | 0 | 0 | 0 | -19.5955 | 79.2179 | 106.678 | -16.678 | 75.037 | 85.9458 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0784 | 0
2016-11-20 17:00 | 0 | 0 | 0 | 0 | -19.605 | 94.2153 | 110.0296 | -20.0296 | 89.4994 | 99.4475 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-11-20 18:00 | 0 | 0 | 0 | 0 | -19.6145 | 109.2127 | 113.3876 | -23.3876 | 104.2733 | 113.2316 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-11-20 19:00 | 0 | 0 | 0 | 0 | -19.624 | 124.2102 | 116.5272 | -26.5272 | 119.4713 | 127.195 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-11-20 20:00 | 0 | 0 | 0 | 0 | -19.6335 | 139.2076 | 119.2194 | -29.2194 | 135.1664 | 141.2679 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.083 | 0
2016-11-20 21:00 | 0 | 0 | 0 | 0 | -19.643 | 154.205 | 121.247 | -31.247 | 151.3559 | 155.388 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0816 | 0
2016-11-20 22:00 | 0 | 0 | 0 | 0 | -19.6525 | 169.2024 | 122.4302 | -32.4302 | 167.9347 | 169.4057 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0819 | 0
2016-11-20 23:00 | 0 | 0 | 0 | 0 | -19.6619 | 184.1998 | 122.6565 | -32.6565 | -175.3015 | 175.1879 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0826 | 0
2016-11-21 | 0 | 0 | 0 | 0 | -19.6714 | -160.8029 | 121.9042 | -31.9042 | -158.6092 | 161.5868 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0826 | 0
2016-11-21 01:00 | 0 | 0 | 0 | 0 | -19.6808 | -145.8055 | 120.2478 | -30.2478 | -142.2242 | 147.4791 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0847 | 0
2016-11-21 02:00 | 0 | 0 | 0 | 0 | -19.6903 | -130.8081 | 117.841 | -27.841 | -126.2994 | 133.3817 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0843 | 0
2016-11-21 03:00 | 0 | 0 | 0 | 0 | -19.6997 | -115.8107 | 114.8883 | -24.8883 | -110.8817 | 119.3697 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-11-21 04:00 | 0 | 0 | 0 | 0 | -19.7091 | -100.8134 | 111.6162 | -21.6162 | -95.928 | 105.5064 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-11-21 05:00 | 0 | 0 | 0 | 0 | -19.7185 | -85.816 | 108.2533 | -18.2533 | -81.3395 | 91.8777 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-11-21 06:00 | 0 | 0 | 0 | 0 | -19.7279 | -70.8187 | 105.0173 | -15.0173 | -66.9971 | 78.6203 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0847 | 0
2016-11-21 07:00 | 0 | 0 | 0 | 0 | -19.7373 | -55.8213 | 102.1083 | -12.1083 | -52.7882 | 65.9704 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-11-21 08:00 | 0 | 0 | 0 | 0 | -19.7467 | -40.824 | 99.7029 | -9.7029 | -38.6253 | 54.3642 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-11-21 09:00 | 0 | 0 | 0 | 0 | -19.756 | -25.8266 | 97.9474 | -7.9474 | -24.4553 | 44.6326 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-11-21 10:00 | 0 | 0 | 0 | 0 | -19.7654 | -10.8293 | 96.9501 | -6.9501 | -10.2605 | 38.2413 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-11-21 11:00 | 0 | 0 | 0 | 0 | -19.7747 | 4.168 | 96.7738 | -6.7738 | 3.9495 | 36.9688 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-11-21 12:00 | 0 | 0 | 0 | 0 | -19.784 | 19.1654 | 97.4298 | -7.4298 | 18.1517 | 41.2914 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-11-21 13:00 | 0 | 0 | 0 | 0 | -19.7934 | 34.1627 | 98.8777 | -8.8777 | 32.3287 | 49.7701 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-11-21 14:00 | 0 | 0 | 0 | 0 | -19.8027 | 49.16 | 101.0286 | -11.0286 | 46.485 | 60.6834 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-11-21 15:00 | 0 | 0 | 0 | 0 | -19.812 | 64.1573 | 103.7519 | -13.7519 | 60.6582 | 72.9417 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-11-21 16:00 | 0 | 0 | 0 | 0 | -19.8213 | 79.1546 | 106.8838 | -16.8838 | 74.9219 | 85.9655 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-11-21 17:00 | 0 | 0 | 0 | 0 | -19.8305 | 94.1519 | 110.2343 | -20.2343 | 89.3801 | 99.4472 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-11-21 18:00 | 0 | 0 | 0 | 0 | -19.8398 | 109.1492 | 113.5928 | -23.5928 | 104.1528 | 113.2141 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-11-21 19:00 | 0 | 0 | 0 | 0 | -19.8491 | 124.1465 | 116.7348 | -26.7348 | 119.3532 | 127.1618 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-11-21 20:00 | 0 | 0 | 0 | 0 | -19.8583 | 139.1438 | 119.4308 | -29.4308 | 135.0549 | 141.2187 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-11-21 21:00 | 0 | 0 | 0 | 0 | -19.8675 | 154.1411 | 121.4632 | -31.4632 | 151.2557 | 155.3191 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-11-21 22:00 | 0 | 0 | 0 | 0 | -19.8768 | 169.1383 | 122.6512 | -32.6512 | 167.8499 | 169.2948 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-11-21 23:00 | 0 | 0 | 0 | 0 | -19.886 | 184.1356 | 122.8816 | -32.8816 | -175.3681 | 175.11 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-11-22 | 0 | 0 | 0 | 0 | -19.8952 | -160.8671 | 122.1324 | -32.1324 | -158.6572 | 161.6248 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-11-22 01:00 | 0 | 0 | 0 | 0 | -19.9044 | -145.8699 | 120.4778 | -30.4778 | -142.2557 | 147.5424 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-11-22 02:00 | 0 | 0 | 0 | 0 | -19.9135 | -130.8726 | 118.0718 | -28.0718 | -126.318 | 133.4615 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-11-22 03:00 | 0 | 0 | 0 | 0 | -19.9227 | -115.8754 | 115.1192 | -25.1192 | -110.892 | 119.4639 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-11-22 04:00 | 0 | 0 | 0 | 0 | -19.9319 | -100.8781 | 111.8471 | -21.8471 | -95.9345 | 105.6152 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-11-22 05:00 | 0 | 0 | 0 | 0 | -19.941 | -85.8809 | 108.484 | -18.484 | -81.3465 | 92.0023 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-11-22 06:00 | 0 | 0 | 0 | 0 | -19.9502 | -70.8837 | 105.2476 | -15.2476 | -67.0081 | 78.763 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-11-22 07:00 | 0 | 0 | 0 | 0 | -19.9593 | -55.8864 | 102.338 | -12.338 | -52.8063 | 66.1344 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-11-22 08:00 | 0 | 0 | 0 | 0 | -19.9684 | -40.8892 | 99.9313 | -9.9313 | -38.6531 | 54.5532 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-11-22 09:00 | 0 | 0 | 0 | 0 | -19.9775 | -25.892 | 98.1739 | -8.1739 | -24.4949 | 44.8475 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-11-22 10:00 | 0 | 0 | 0 | 0 | -19.9866 | -10.8948 | 97.1738 | -7.1738 | -10.3129 | 38.4709 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-11-22 11:00 | 0 | 0 | 0 | 0 | -19.9957 | 4.1024 | 96.9937 | -6.9937 | 3.8837 | 37.1813 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-11-22 12:00 | 0 | 0 | 0 | 0 | -20.0048 | 19.0996 | 97.6453 | -7.6453 | 18.0729 | 41.4564 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-11-22 13:00 | 0 | 0 | 0 | 0 | -20.0139 | 34.0968 | 99.0885 | -9.0885 | 32.2379 | 49.8835 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-11-22 14:00 | 0 | 0 | 0 | 0 | -20.0229 | 49.094 | 101.2347 | -11.2347 | 46.3837 | 60.755 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-11-22 15:00 | 0 | 0 | 0 | 0 | -20.032 | 64.0912 | 103.954 | -13.954 | 60.5482 | 72.9816 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-11-22 16:00 | 0 | 0 | 0 | 0 | -20.041 | 79.0884 | 107.0832 | -17.0832 | 74.8054 | 85.9809 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-11-22 17:00 | 0 | 0 | 0 | 0 | -20.05 | 94.0856 | 110.4324 | -20.4324 | 89.2594 | 99.4427 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-11-22 18:00 | 0 | 0 | 0 | 0 | -20.059 | 109.0827 | 113.7915 | -23.7915 | 104.0308 | 113.1926 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-11-22 19:00 | 0 | 0 | 0 | 0 | -20.068 | 124.0799 | 116.9358 | -26.9358 | 119.2333 | 127.1247 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-11-22 20:00 | 0 | 0 | 0 | 0 | -20.077 | 139.0771 | 119.6357 | -29.6357 | 134.9413 | 141.1656 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-11-22 21:00 | 0 | 0 | 0 | 0 | -20.086 | 154.0742 | 121.6729 | -31.6729 | 151.1529 | 155.2461 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0872 | 0
2016-11-22 22:00 | 0 | 0 | 0 | 0 | -20.095 | 169.0714 | 122.8659 | -32.8659 | 167.762 | 169.1793 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-11-22 23:00 | 0 | 0 | 0 | 0 | -20.1039 | 184.0685 | 123.1007 | -33.1007 | -175.4382 | 175.0284 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-11-23 | 0 | 0 | 0 | 0 | -20.1129 | -160.9343 | 122.3548 | -32.3548 | -158.7091 | 161.6634 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-11-23 01:00 | 0 | 0 | 0 | 0 | -20.1218 | -145.9372 | 120.7022 | -30.7022 | -142.2912 | 147.6069 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-11-23 02:00 | 0 | 0 | 0 | 0 | -20.1307 | -130.9401 | 118.2972 | -28.2972 | -126.3409 | 133.5425 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-11-23 03:00 | 0 | 0 | 0 | 0 | -20.1396 | -115.9429 | 115.3449 | -25.3449 | -110.9066 | 119.5593 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-11-23 04:00 | 0 | 0 | 0 | 0 | -20.1486 | -100.9458 | 112.0727 | -22.0727 | -95.9453 | 105.7249 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-11-23 05:00 | 0 | 0 | 0 | 0 | -20.1574 | -85.9487 | 108.7093 | -18.7093 | -81.3575 | 92.1275 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-11-23 06:00 | 0 | 0 | 0 | 0 | -20.1663 | -70.9516 | 105.4725 | -15.4725 | -67.023 | 78.9058 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-11-23 07:00 | 0 | 0 | 0 | 0 | -20.1752 | -55.9545 | 102.5621 | -12.5621 | -52.8282 | 66.2978 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-11-23 08:00 | 0 | 0 | 0 | 0 | -20.1841 | -40.9574 | 100.1541 | -10.1541 | -38.6846 | 54.7404 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-11-23 09:00 | 0 | 0 | 0 | 0 | -20.1929 | -25.9603 | 98.3946 | -8.3946 | -24.5377 | 45.059 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-11-23 10:00 | 0 | 0 | 0 | 0 | -20.2018 | -10.9632 | 97.3915 | -7.3915 | -10.3683 | 38.6954 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-11-23 11:00 | 0 | 0 | 0 | 0 | -20.2106 | 4.0339 | 97.2075 | -7.2075 | 3.8154 | 37.3876 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-11-23 12:00 | 0 | 0 | 0 | 0 | -20.2194 | 19.031 | 97.8545 | -7.8545 | 17.992 | 41.6154 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-11-23 13:00 | 0 | 0 | 0 | 0 | -20.2282 | 34.0281 | 99.2928 | -9.2928 | 32.1453 | 49.9914 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-11-23 14:00 | 0 | 0 | 0 | 0 | -20.237 | 49.0252 | 101.4343 | -11.4343 | 46.2808 | 60.8216 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-11-23 15:00 | 0 | 0 | 0 | 0 | -20.2458 | 64.0222 | 104.1496 | -14.1496 | 60.4369 | 73.0168 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-11-23 16:00 | 0 | 0 | 0 | 0 | -20.2546 | 79.0193 | 107.2759 | -17.2759 | 74.6875 | 85.9919 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-11-23 17:00 | 0 | 0 | 0 | 0 | -20.2633 | 94.0164 | 110.6239 | -20.6239 | 89.1373 | 99.4341 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-11-23 18:00 | 0 | 0 | 0 | 0 | -20.2721 | 109.0134 | 113.9835 | -23.9835 | 103.9072 | 113.1672 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-11-23 19:00 | 0 | 0 | 0 | 0 | -20.2808 | 124.0105 | 117.1302 | -27.1302 | 119.1116 | 127.0837 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-11-23 20:00 | 0 | 0 | 0 | 0 | -20.2896 | 139.0075 | 119.8341 | -29.8341 | 134.8255 | 141.1088 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-11-23 21:00 | 0 | 0 | 0 | 0 | -20.2983 | 154.0045 | 121.8762 | -31.8762 | 151.0474 | 155.1692 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-11-23 22:00 | 0 | 0 | 0 | 0 | -20.307 | 169.0016 | 123.0743 | -33.0743 | 167.6711 | 169.0595 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-11-23 23:00 | 0 | 0 | 0 | 0 | -20.3157 | 183.9986 | 123.3137 | -33.3137 | -175.5118 | 174.9438 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-11-24 | 0 | 0 | 0 | 0 | -20.3244 | -161.0044 | 122.5713 | -32.5713 | -158.7648 | 161.7026 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-11-24 01:00 | 0 | 0 | 0 | 0 | -20.3331 | -146.0073 | 120.9209 | -30.9209 | -142.3309 | 147.6727 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-11-24 02:00 | 0 | 0 | 0 | 0 | -20.3417 | -131.0103 | 118.5169 | -28.5169 | -126.368 | 133.6248 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-11-24 03:00 | 0 | 0 | 0 | 0 | -20.3504 | -116.0133 | 115.5651 | -25.5651 | -110.9254 | 119.6559 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-11-24 04:00 | 0 | 0 | 0 | 0 | -20.359 | -101.0163 | 112.2929 | -22.2929 | -95.9603 | 105.8355 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-11-24 05:00 | 0 | 0 | 0 | 0 | -20.3677 | -86.0193 | 108.9293 | -18.9293 | -81.3727 | 92.2533 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-11-24 06:00 | 0 | 0 | 0 | 0 | -20.3763 | -71.0223 | 105.692 | -15.692 | -67.042 | 79.0486 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-11-24 07:00 | 0 | 0 | 0 | 0 | -20.3849 | -56.0253 | 102.7806 | -12.7806 | -52.8539 | 66.4604 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-11-24 08:00 | 0 | 0 | 0 | 0 | -20.3935 | -41.0283 | 100.3712 | -10.3712 | -38.7194 | 54.9258 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-11-24 09:00 | 0 | 0 | 0 | 0 | -20.4021 | -26.0313 | 98.6094 | -8.6094 | -24.5836 | 45.2672 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-11-24 10:00 | 0 | 0 | 0 | 0 | -20.4107 | -11.0344 | 97.6031 | -7.6031 | -10.4264 | 38.9147 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.0945 | 0
2016-11-24 11:00 | 0 | 0 | 0 | 0 | -20.4192 | 3.9626 | 97.4151 | -7.4151 | 3.7446 | 37.5877 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.0945 | 0
2016-11-24 12:00 | 0 | 0 | 0 | 0 | -20.4278 | 18.9596 | 98.0574 | -8.0574 | 17.9089 | 41.7682 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-11-24 13:00 | 0 | 0 | 0 | 0 | -20.4363 | 33.9565 | 99.4906 | -9.4906 | 32.0509 | 50.0937 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-11-24 14:00 | 0 | 0 | 0 | 0 | -20.4449 | 48.9535 | 101.6273 | -11.6273 | 46.1764 | 60.8831 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.098 | 0
2016-11-24 15:00 | 0 | 0 | 0 | 0 | -20.4534 | 63.9504 | 104.3386 | -14.3386 | 60.3242 | 73.0474 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.8 | -2.8 | 1.0973 | 0
2016-11-24 16:00 | 0 | 0 | 0 | 0 | -20.4619 | 78.9474 | 107.462 | -17.462 | 74.5684 | 85.9985 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.8 | -2.8 | 1.0973 | 0
2016-11-24 17:00 | 0 | 0 | 0 | 0 | -20.4704 | 93.9443 | 110.8086 | -20.8086 | 89.014 | 99.4213 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1001 | 0
2016-11-24 18:00 | 0 | 0 | 0 | 0 | -20.4789 | 108.9413 | 114.1688 | -24.1688 | 103.7823 | 113.1378 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-11-24 19:00 | 0 | 0 | 0 | 0 | -20.4874 | 123.9382 | 117.3179 | -27.3179 | 118.9883 | 127.039 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-11-24 20:00 | 0 | 0 | 0 | 0 | -20.4959 | 138.9351 | 120.0258 | -30.0258 | 134.7077 | 141.0482 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-11-24 21:00 | 0 | 0 | 0 | 0 | -20.5043 | 153.9321 | 122.0729 | -32.0729 | 150.9396 | 155.0886 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-11-24 22:00 | 0 | 0 | 0 | 0 | -20.5128 | 168.929 | 123.2763 | -33.2763 | 167.5773 | 168.9361 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-11-24 23:00 | 0 | 0 | 0 | 0 | -20.5212 | 183.9259 | 123.5205 | -33.5205 | -175.5888 | 174.8571 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.098 | 0
2016-11-25 | 0 | 0 | 0 | 0 | -20.5296 | -161.0772 | 122.7817 | -32.7817 | -158.8244 | 161.7426 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.7 | -3.7 | 1.1004 | 0
2016-11-25 01:00 | 0 | 0 | 0 | 0 | -20.538 | -146.0803 | 121.1337 | -31.1337 | -142.3746 | 147.7396 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-11-25 02:00 | 0 | 0 | 0 | 0 | -20.5464 | -131.0834 | 118.731 | -28.731 | -126.3993 | 133.7083 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-11-25 03:00 | 0 | 0 | 0 | 0 | -20.5548 | -116.0865 | 115.7797 | -25.7797 | -110.9486 | 119.7535 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-11-25 04:00 | 0 | 0 | 0 | 0 | -20.5632 | -101.0896 | 112.5076 | -22.5076 | -95.9795 | 105.947 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-11-25 05:00 | 0 | 0 | 0 | 0 | -20.5716 | -86.0927 | 109.1437 | -19.1437 | -81.392 | 92.3794 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.1 | -5.1 | 1.1054 | 0
2016-11-25 06:00 | 0 | 0 | 0 | 0 | -20.58 | -71.0958 | 105.9058 | -15.9058 | -67.0648 | 79.1912 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.8 | -3.8 | 1.1008 | 0
2016-11-25 07:00 | 0 | 0 | 0 | 0 | -20.5883 | -56.0989 | 102.9935 | -12.9935 | -52.8833 | 66.6221 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-11-25 08:00 | 0 | 0 | 0 | 0 | -20.5966 | -41.1021 | 100.5824 | -10.5824 | -38.7578 | 55.1091 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4 | -4 | 1.1015 | 0
2016-11-25 09:00 | 0 | 0 | 0 | 0 | -20.605 | -26.1052 | 98.8182 | -8.8182 | -24.6326 | 45.4717 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-11-25 10:00 | 0 | 0 | 0 | 0 | -20.6133 | -11.1083 | 97.8086 | -7.8086 | -10.4873 | 39.1287 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1001 | 0
2016-11-25 11:00 | 0 | 0 | 0 | 0 | -20.6216 | 3.8885 | 97.6163 | -7.6163 | 3.6715 | 37.7814 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5 | -5 | 1.105 | 0
2016-11-25 12:00 | 0 | 0 | 0 | 0 | -20.6299 | 18.8854 | 98.2538 | -8.2538 | 17.8238 | 41.9148 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1036 | 0
2016-11-25 13:00 | 0 | 0 | 0 | 0 | -20.6382 | 33.8822 | 99.6819 | -9.6819 | 31.9547 | 50.1904 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4 | -4 | 1.1015 | 0
2016-11-25 14:00 | 0 | 0 | 0 | 0 | -20.6464 | 48.8791 | 101.8137 | -11.8137 | 46.0706 | 60.9395 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-11-25 15:00 | 0 | 0 | 0 | 0 | -20.6547 | 63.8759 | 104.5208 | -14.5208 | 60.2103 | 73.0733 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-11-25 16:00 | 0 | 0 | 0 | 0 | -20.6629 | 78.8728 | 107.6413 | -17.6413 | 74.4482 | 86.0008 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-11-25 17:00 | 0 | 0 | 0 | 0 | -20.6712 | 93.8696 | 110.9866 | -20.9866 | 88.8895 | 99.4046 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-11-25 18:00 | 0 | 0 | 0 | 0 | -20.6794 | 108.8664 | 114.3473 | -24.3473 | 103.6561 | 113.1047 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-11-25 19:00 | 0 | 0 | 0 | 0 | -20.6876 | 123.8632 | 117.4988 | -27.4988 | 118.8634 | 126.9907 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.3 | -3.3 | 1.0991 | 0
2016-11-25 20:00 | 0 | 0 | 0 | 0 | -20.6958 | 138.86 | 120.2107 | -30.2107 | 134.588 | 140.9842 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-11-25 21:00 | 0 | 0 | 0 | 0 | -20.704 | 153.8569 | 122.2629 | -32.2629 | 150.8293 | 155.0046 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.3 | -4.3 | 1.1025 | 0
2016-11-25 22:00 | 0 | 0 | 0 | 0 | -20.7122 | 168.8537 | 123.4718 | -33.4718 | 167.4805 | 168.8096 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1036 | 0
2016-11-25 23:00 | 0 | 0 | 0 | 0 | -20.7204 | 183.8505 | 123.7209 | -33.7209 | -175.6692 | 174.7691 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-11-26 | 0 | 0 | 0 | 0 | -20.7285 | -161.1527 | 122.9859 | -32.9859 | -158.8877 | 161.7835 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.9 | -5.9 | 1.1081 | 0
2016-11-26 01:00 | 0 | 0 | 0 | 0 | -20.7367 | -146.1559 | 121.3405 | -31.3405 | -142.4224 | 147.8079 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.8 | -6.8 | 1.1113 | 0
2016-11-26 02:00 | 0 | 0 | 0 | 0 | -20.7448 | -131.1591 | 118.9394 | -28.9394 | -126.4348 | 133.7931 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.8 | -6.8 | 1.1113 | 0
2016-11-26 03:00 | 0 | 0 | 0 | 0 | -20.7529 | -116.1624 | 115.9887 | -25.9887 | -110.9759 | 119.8522 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.8 | -6.8 | 1.1113 | 0
2016-11-26 04:00 | 0 | 0 | 0 | 0 | -20.761 | -101.1656 | 112.7167 | -22.7167 | -96.0029 | 106.0592 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.1 | -7.1 | 1.1123 | 0
2016-11-26 05:00 | 0 | 0 | 0 | 0 | -20.7691 | -86.1688 | 109.3525 | -19.3525 | -81.4154 | 92.5059 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.2 | -7.2 | 1.1127 | 0
2016-11-26 06:00 | 0 | 0 | 0 | 0 | -20.7772 | -71.172 | 106.114 | -16.114 | -67.0916 | 79.3337 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.5 | -7.5 | 1.1138 | 0
2016-11-26 07:00 | 0 | 0 | 0 | 0 | -20.7853 | -56.1753 | 103.2006 | -13.2006 | -52.9164 | 66.7828 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.8 | -7.8 | 1.1148 | 0
2016-11-26 08:00 | 0 | 0 | 0 | 0 | -20.7934 | -41.1785 | 100.7877 | -10.7877 | -38.7995 | 55.2903 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-11-26 09:00 | 0 | 0 | 0 | 0 | -20.8014 | -26.1817 | 99.0209 | -9.0209 | -24.6848 | 45.6726 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-11-26 10:00 | 0 | 0 | 0 | 0 | -20.8095 | -11.185 | 98.0078 | -8.0078 | -10.5509 | 39.3373 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.7 | -7.7 | 1.1144 | 0
2016-11-26 11:00 | 0 | 0 | 0 | 0 | -20.8175 | 3.8118 | 97.8111 | -7.8111 | 3.596 | 37.9687 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.7 | -7.7 | 1.1144 | 0
2016-11-26 12:00 | 0 | 0 | 0 | 0 | -20.8255 | 18.8085 | 98.4436 | -8.4436 | 17.7368 | 42.0551 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.7 | -7.7 | 1.1144 | 0
2016-11-26 13:00 | 0 | 0 | 0 | 0 | -20.8335 | 33.8052 | 99.8665 | -9.8665 | 31.857 | 50.2814 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.6 | -7.6 | 1.1141 | 0
2016-11-26 14:00 | 0 | 0 | 0 | 0 | -20.8416 | 48.802 | 101.9934 | -11.9934 | 45.9634 | 60.9908 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.7 | -7.7 | 1.1144 | 0
2016-11-26 15:00 | 0 | 0 | 0 | 0 | -20.8495 | 63.7987 | 104.6962 | -14.6962 | 60.0952 | 73.0945 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.3 | -7.3 | 1.1131 | 0
2016-11-26 16:00 | 0 | 0 | 0 | 0 | -20.8575 | 78.7954 | 107.8138 | -17.8138 | 74.3269 | 85.9989 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.3 | -7.3 | 1.1131 | 0
2016-11-26 17:00 | 0 | 0 | 0 | 0 | -20.8655 | 93.7921 | 111.1577 | -21.1577 | 88.764 | 99.3838 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.8 | -7.8 | 1.1148 | 0
2016-11-26 18:00 | 0 | 0 | 0 | 0 | -20.8734 | 108.7889 | 114.519 | -24.519 | 103.5287 | 113.0678 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7 | -7 | 1.112 | 0
2016-11-26 19:00 | 0 | 0 | 0 | 0 | -20.8814 | 123.7856 | 117.6729 | -27.6729 | 118.7372 | 126.9388 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-11-26 20:00 | 0 | 0 | 0 | 0 | -20.8893 | 138.7823 | 120.3888 | -30.3888 | 134.4665 | 140.9168 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.6 | -7.6 | 1.1141 | 0
2016-11-26 21:00 | 0 | 0 | 0 | 0 | -20.8972 | 153.779 | 122.4462 | -32.4462 | 150.7168 | 154.9174 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.6 | -7.6 | 1.1141 | 0
2016-11-26 22:00 | 0 | 0 | 0 | 0 | -20.9052 | 168.7757 | 123.6606 | -33.6606 | 167.381 | 168.6805 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.1 | -7.1 | 1.1123 | 0
2016-11-26 23:00 | 0 | 0 | 0 | 0 | -20.913 | 183.7724 | 123.9149 | -33.9149 | -175.7529 | 174.6804 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.7 | -7.7 | 1.1144 | 0
2016-11-27 | 0 | 0 | 0 | 0 | -20.9209 | -161.2309 | 123.184 | -33.184 | -158.9547 | 161.8254 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.5 | -7.5 | 1.1138 | 0
2016-11-27 01:00 | 0 | 0 | 0 | 0 | -20.9288 | -146.2342 | 121.5413 | -31.5413 | -142.4741 | 147.8775 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.4 | -7.4 | 1.1134 | 0
2016-11-27 02:00 | 0 | 0 | 0 | 0 | -20.9367 | -131.2376 | 119.1418 | -29.1418 | -126.4744 | 133.8792 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.4 | -8.4 | 1.1169 | 0
2016-11-27 03:00 | 0 | 0 | 0 | 0 | -20.9445 | -116.2409 | 116.1919 | -26.1919 | -111.0075 | 119.9519 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9 | -9 | 1.119 | 0
2016-11-27 04:00 | 0 | 0 | 0 | 0 | -20.9524 | -101.2442 | 112.92 | -22.92 | -96.0305 | 106.1721 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.8 | -7.8 | 1.1148 | 0
2016-11-27 05:00 | 0 | 0 | 0 | 0 | -20.9602 | -86.2476 | 109.5556 | -19.5556 | -81.4428 | 92.6327 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.8 | -7.8 | 1.1148 | 0
2016-11-27 06:00 | 0 | 0 | 0 | 0 | -20.968 | -71.2509 | 106.3164 | -16.3164 | -67.1222 | 79.4758 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.5 | -6.5 | 1.1102 | 0
2016-11-27 07:00 | 0 | 0 | 0 | 0 | -20.9758 | -56.2542 | 103.4017 | -13.4017 | -52.953 | 66.9423 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-11-27 08:00 | 0 | 0 | 0 | 0 | -20.9836 | -41.2576 | 100.987 | -10.987 | -38.8445 | 55.4692 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.8 | -6.8 | 1.1113 | 0
2016-11-27 09:00 | 0 | 0 | 0 | 0 | -20.9914 | -26.2609 | 99.2173 | -9.2173 | -24.7399 | 45.8696 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.4 | -7.4 | 1.1134 | 0
2016-11-27 10:00 | 0 | 0 | 0 | 0 | -20.9992 | -11.2643 | 98.2006 | -8.2006 | -10.6172 | 39.5404 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.1 | -8.1 | 1.1159 | 0
2016-11-27 11:00 | 0 | 0 | 0 | 0 | -21.0069 | 3.7324 | 97.9995 | -7.9995 | 3.5183 | 38.1496 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.5 | -8.5 | 1.1173 | 0
2016-11-27 12:00 | 0 | 0 | 0 | 0 | -21.0147 | 18.729 | 98.6268 | -8.6268 | 17.6479 | 42.1891 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.1 | -8.1 | 1.1159 | 0
2016-11-27 13:00 | 0 | 0 | 0 | 0 | -21.0224 | 33.7256 | 100.0444 | -10.0444 | 31.7577 | 50.3666 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.1 | -9.1 | 1.1194 | 0
2016-11-27 14:00 | 0 | 0 | 0 | 0 | -21.0302 | 48.7223 | 102.1662 | -12.1662 | 45.855 | 61.0369 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.4 | -8.4 | 1.1169 | 0
2016-11-27 15:00 | 0 | 0 | 0 | 0 | -21.0379 | 63.7189 | 104.8648 | -14.8648 | 59.979 | 73.1111 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.2 | -8.2 | 1.1162 | 0
2016-11-27 16:00 | 0 | 0 | 0 | 0 | -21.0456 | 78.7155 | 107.9793 | -17.9793 | 74.2047 | 85.9926 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.8 | -6.8 | 1.1113 | 0
2016-11-27 17:00 | 0 | 0 | 0 | 0 | -21.0533 | 93.7121 | 111.3219 | -21.3219 | 88.6376 | 99.3591 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.3 | -5.3 | 1.106 | 0
2016-11-27 18:00 | 0 | 0 | 0 | 0 | -21.061 | 108.7087 | 114.6837 | -24.6837 | 103.4003 | 113.0272 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.7 | -4.7 | 1.1039 | 0
2016-11-27 19:00 | 0 | 0 | 0 | 0 | -21.0686 | 123.7053 | 117.84 | -27.84 | 118.6096 | 126.8835 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-11-27 20:00 | 0 | 0 | 0 | 0 | -21.0763 | 138.7019 | 120.56 | -30.56 | 134.3433 | 140.8463 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.7 | -4.7 | 1.1039 | 0
2016-11-27 21:00 | 0 | 0 | 0 | 0 | -21.0839 | 153.6985 | 122.6227 | -32.6227 | 150.6021 | 154.8272 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4 | -4 | 1.1015 | 0
2016-11-27 22:00 | 0 | 0 | 0 | 0 | -21.0916 | 168.6951 | 123.8428 | -33.8428 | 167.2788 | 168.5491 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-11-27 23:00 | 0 | 0 | 0 | 0 | -21.0992 | 183.6917 | 124.1023 | -34.1023 | -175.8397 | 174.5917 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.9 | -3.9 | 1.1012 | 0
2016-11-28 | 0 | 0 | 0 | 0 | -21.1068 | -161.3117 | 123.3757 | -33.3757 | -159.0253 | 161.8684 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.8 | -3.8 | 1.1008 | 0
2016-11-28 01:00 | 0 | 0 | 0 | 0 | -21.1144 | -146.3151 | 121.736 | -31.736 | -142.5298 | 147.9485 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1001 | 0
2016-11-28 02:00 | 0 | 0 | 0 | 0 | -21.122 | -131.3186 | 119.3383 | -29.3383 | -126.5182 | 133.9665 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-11-28 03:00 | 0 | 0 | 0 | 0 | -21.1296 | -116.322 | 116.3893 | -26.3893 | -111.0432 | 120.0526 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-11-28 04:00 | 0 | 0 | 0 | 0 | -21.1372 | -101.3254 | 113.1176 | -23.1176 | -96.0622 | 106.2856 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-11-28 05:00 | 0 | 0 | 0 | 0 | -21.1447 | -86.3289 | 109.7529 | -19.7529 | -81.4743 | 92.7596 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.098 | 0
2016-11-28 06:00 | 0 | 0 | 0 | 0 | -21.1523 | -71.3323 | 106.5129 | -16.5129 | -67.1567 | 79.6174 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-11-28 07:00 | 0 | 0 | 0 | 0 | -21.1598 | -56.3358 | 103.5969 | -13.5969 | -52.9933 | 67.1006 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-11-28 08:00 | 0 | 0 | 0 | 0 | -21.1673 | -41.3392 | 101.1801 | -11.1801 | -38.8928 | 55.6457 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-11-28 09:00 | 0 | 0 | 0 | 0 | -21.1748 | -26.3427 | 99.4075 | -9.4075 | -24.7979 | 46.0627 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-11-28 10:00 | 0 | 0 | 0 | 0 | -21.1823 | -11.3461 | 98.3869 | -8.3869 | -10.686 | 39.7378 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-11-28 11:00 | 0 | 0 | 0 | 0 | -21.1898 | 3.6504 | 98.1812 | -8.1812 | 3.4383 | 38.324 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-11-28 12:00 | 0 | 0 | 0 | 0 | -21.1973 | 18.6469 | 98.8033 | -8.8033 | 17.5571 | 42.3167 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-11-28 13:00 | 0 | 0 | 0 | 0 | -21.2047 | 33.6435 | 100.2155 | -10.2155 | 31.657 | 50.4461 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-11-28 14:00 | 0 | 0 | 0 | 0 | -21.2122 | 48.64 | 102.3322 | -12.3322 | 45.7454 | 61.0779 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-11-28 15:00 | 0 | 0 | 0 | 0 | -21.2196 | 63.6365 | 105.0265 | -15.0265 | 59.8619 | 73.123 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-11-28 16:00 | 0 | 0 | 0 | 0 | -21.2271 | 78.633 | 108.1379 | -18.1379 | 74.0816 | 85.9821 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-11-28 17:00 | 0 | 0 | 0 | 0 | -21.2345 | 93.6295 | 111.4791 | -21.4791 | 88.5103 | 99.3305 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-11-28 18:00 | 0 | 0 | 0 | 0 | -21.2419 | 108.626 | 114.8414 | -24.8414 | 103.2709 | 112.9831 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-11-28 19:00 | 0 | 0 | 0 | 0 | -21.2493 | 123.6225 | 118.0001 | -28.0001 | 118.4808 | 126.825 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-11-28 20:00 | 0 | 0 | 0 | 0 | -21.2567 | 138.619 | 120.7243 | -30.7243 | 134.2186 | 140.7726 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-11-28 21:00 | 0 | 0 | 0 | 0 | -21.264 | 153.6155 | 122.7923 | -32.7923 | 150.4853 | 154.7343 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-11-28 22:00 | 0 | 0 | 0 | 0 | -21.2714 | 168.612 | 124.0182 | -34.0182 | 167.174 | 168.416 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-11-28 23:00 | 0 | 0 | 0 | 0 | -21.2787 | 183.6085 | 124.2832 | -34.2832 | -175.9298 | 174.5036 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-11-29 | 0 | 0 | 0 | 0 | -21.2861 | -161.395 | 123.561 | -33.561 | -159.0994 | 161.9128 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-11-29 01:00 | 0 | 0 | 0 | 0 | -21.2934 | -146.3985 | 121.9245 | -31.9245 | -142.5893 | 148.0208 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.2 | -2.2 | 1.0952 | 0
2016-11-29 02:00 | 0 | 0 | 0 | 0 | -21.3007 | -131.4021 | 119.5287 | -29.5287 | -126.566 | 134.0549 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-11-29 03:00 | 0 | 0 | 0 | 0 | -21.308 | -116.4056 | 116.5807 | -26.5807 | -111.083 | 120.1542 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-11-29 04:00 | 0 | 0 | 0 | 0 | -21.3153 | -101.4091 | 113.3093 | -23.3093 | -96.098 | 106.3997 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-11-29 05:00 | 0 | 0 | 0 | 0 | -21.3226 | -86.4127 | 109.9443 | -19.9443 | -81.5097 | 92.8866 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-11-29 06:00 | 0 | 0 | 0 | 0 | -21.3298 | -71.4162 | 106.7035 | -16.7035 | -67.1949 | 79.7586 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-11-29 07:00 | 0 | 0 | 0 | 0 | -21.3371 | -56.4198 | 103.786 | -13.786 | -53.0371 | 67.2575 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-11-29 08:00 | 0 | 0 | 0 | 0 | -21.3443 | -41.4233 | 101.3669 | -11.3669 | -38.9444 | 55.8197 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-11-29 09:00 | 0 | 0 | 0 | 0 | -21.3516 | -26.4269 | 99.5913 | -9.5913 | -24.8589 | 46.2518 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-11-29 10:00 | 0 | 0 | 0 | 0 | -21.3588 | -11.4305 | 98.5667 | -8.5667 | -10.7573 | 39.9296 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-11-29 11:00 | 0 | 0 | 0 | 0 | -21.366 | 3.566 | 98.3562 | -8.3562 | 3.3563 | 38.4917 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-11-29 12:00 | 0 | 0 | 0 | 0 | -21.3732 | 18.5624 | 98.973 | -8.973 | 17.4646 | 42.4379 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-11-29 13:00 | 0 | 0 | 0 | 0 | -21.3804 | 33.5588 | 100.3797 | -10.3797 | 31.5548 | 50.5197 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-11-29 14:00 | 0 | 0 | 0 | 0 | -21.3875 | 48.5553 | 102.4912 | -12.4912 | 45.6347 | 61.1137 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-11-29 15:00 | 0 | 0 | 0 | 0 | -21.3947 | 63.5517 | 105.1811 | -15.1811 | 59.7439 | 73.1302 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-11-29 16:00 | 0 | 0 | 0 | 0 | -21.4018 | 78.5481 | 108.2895 | -18.2895 | 73.9578 | 85.9674 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-11-29 17:00 | 0 | 0 | 0 | 0 | -21.409 | 93.5445 | 111.6293 | -21.6293 | 88.3822 | 99.2981 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.2 | -2.2 | 1.0952 | 0
2016-11-29 18:00 | 0 | 0 | 0 | 0 | -21.4161 | 108.5409 | 114.992 | -24.992 | 103.1406 | 112.9355 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-11-29 19:00 | 0 | 0 | 0 | 0 | -21.4232 | 123.5373 | 118.1532 | -28.1532 | 118.3509 | 126.7632 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-11-29 20:00 | 0 | 0 | 0 | 0 | -21.4303 | 138.5337 | 120.8815 | -30.8815 | 134.0923 | 140.6961 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-11-29 21:00 | 0 | 0 | 0 | 0 | -21.4374 | 153.5301 | 122.955 | -32.955 | 150.3666 | 154.6388 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-11-29 22:00 | 0 | 0 | 0 | 0 | -21.4445 | 168.5265 | 124.1868 | -34.1868 | 167.0666 | 168.2815 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-11-29 23:00 | 0 | 0 | 0 | 0 | -21.4516 | 183.5229 | 124.4573 | -34.4573 | -176.0228 | 174.4167 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-11-30 | 0 | 0 | 0 | 0 | -21.4586 | -161.4808 | 123.7398 | -33.7398 | -159.1771 | 161.9585 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.098 | 0
2016-11-30 01:00 | 0 | 0 | 0 | 0 | -21.4656 | -146.4844 | 122.1066 | -32.1066 | -142.6527 | 148.0945 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-11-30 02:00 | 0 | 0 | 0 | 0 | -21.4727 | -131.488 | 119.713 | -29.713 | -126.6178 | 134.1446 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-11-30 03:00 | 0 | 0 | 0 | 0 | -21.4797 | -116.4916 | 116.766 | -26.766 | -111.1269 | 120.2567 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-11-30 04:00 | 0 | 0 | 0 | 0 | -21.4867 | -101.4953 | 113.495 | -23.495 | -96.1378 | 106.5142 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-11-30 05:00 | 0 | 0 | 0 | 0 | -21.4937 | -86.4989 | 110.1297 | -20.1297 | -81.549 | 93.0136 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-11-30 06:00 | 0 | 0 | 0 | 0 | -21.5007 | -71.5026 | 106.888 | -16.888 | -67.2369 | 79.899 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-11-30 07:00 | 0 | 0 | 0 | 0 | -21.5077 | -56.5062 | 103.9689 | -13.9689 | -53.0844 | 67.4129 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-11-30 08:00 | 0 | 0 | 0 | 0 | -21.5146 | -41.5099 | 101.5475 | -11.5475 | -38.9992 | 55.991 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-11-30 09:00 | 0 | 0 | 0 | 0 | -21.5216 | -26.5135 | 99.7687 | -9.7687 | -24.9227 | 46.4367 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-11-30 10:00 | 0 | 0 | 0 | 0 | -21.5285 | -11.5172 | 98.7399 | -8.7399 | -10.8311 | 40.1156 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-11-30 11:00 | 0 | 0 | 0 | 0 | -21.5354 | 3.4792 | 98.5245 | -8.5245 | 3.2722 | 38.6528 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-11-30 12:00 | 0 | 0 | 0 | 0 | -21.5423 | 18.4755 | 99.1359 | -9.1359 | 17.3705 | 42.5526 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.7 | -3.7 | 1.1004 | 0
2016-11-30 13:00 | 0 | 0 | 0 | 0 | -21.5492 | 33.4718 | 100.537 | -10.537 | 31.4514 | 50.5875 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.7 | -3.7 | 1.1004 | 0
2016-11-30 14:00 | 0 | 0 | 0 | 0 | -21.5561 | 48.4681 | 102.6432 | -12.6432 | 45.523 | 61.1443 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1036 | 0
2016-11-30 15:00 | 0 | 0 | 0 | 0 | -21.563 | 63.4645 | 105.3287 | -15.3287 | 59.6252 | 73.1329 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-11-30 16:00 | 0 | 0 | 0 | 0 | -21.5699 | 78.4608 | 108.434 | -18.434 | 73.8333 | 85.9486 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.8 | -3.8 | 1.1008 | 0
2016-11-30 17:00 | 0 | 0 | 0 | 0 | -21.5767 | 93.4571 | 111.7723 | -21.7723 | 88.2535 | 99.262 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1001 | 0
2016-11-30 18:00 | 0 | 0 | 0 | 0 | -21.5836 | 108.4534 | 115.1355 | -25.1355 | 103.0096 | 112.8844 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.3 | -3.3 | 1.0991 | 0
2016-11-30 19:00 | 0 | 0 | 0 | 0 | -21.5904 | 123.4497 | 118.2991 | -28.2991 | 118.22 | 126.6983 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.9 | -3.9 | 1.1012 | 0
2016-11-30 20:00 | 0 | 0 | 0 | 0 | -21.5972 | 138.446 | 121.0316 | -31.0316 | 133.9647 | 140.6169 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1001 | 0
2016-11-30 21:00 | 0 | 0 | 0 | 0 | -21.604 | 153.4423 | 123.1105 | -33.1105 | 150.246 | 154.541 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.7 | -3.7 | 1.1004 | 0
2016-11-30 22:00 | 0 | 0 | 0 | 0 | -21.6108 | 168.4386 | 124.3484 | -34.3484 | 166.9569 | 168.1461 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.5 | -4.5 | 1.1033 | 0
2016-11-30 23:00 | 0 | 0 | 0 | 0 | -21.6176 | 183.4349 | 124.6247 | -34.6247 | -176.1188 | 174.3314 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-12-01 | 0 | 0 | 0 | 0 | -21.6243 | -161.5689 | 123.912 | -33.912 | -159.2582 | 162.0058 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-12-01 01:00 | 0 | 0 | 0 | 0 | -21.6311 | -146.5726 | 122.2824 | -32.2824 | -142.7199 | 148.1697 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6 | -6 | 1.1085 | 0
2016-12-01 02:00 | 0 | 0 | 0 | 0 | -21.6379 | -131.5763 | 119.891 | -29.891 | -126.6736 | 134.2355 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.5 | -5.5 | 1.1067 | 0
2016-12-01 03:00 | 0 | 0 | 0 | 0 | -21.6446 | -116.58 | 116.9452 | -26.9452 | -111.1749 | 120.36 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.6 | -5.6 | 1.1071 | 0
2016-12-01 04:00 | 0 | 0 | 0 | 0 | -21.6513 | -101.5838 | 113.6746 | -23.6746 | -96.1817 | 106.6292 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.7 | -5.7 | 1.1075 | 0
2016-12-01 05:00 | 0 | 0 | 0 | 0 | -21.658 | -86.5875 | 110.309 | -20.309 | -81.5922 | 93.1405 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6 | -6 | 1.1085 | 0
2016-12-01 06:00 | 0 | 0 | 0 | 0 | -21.6647 | -71.5912 | 107.0663 | -17.0663 | -67.2826 | 80.0388 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.2 | -6.2 | 1.1092 | 0
2016-12-01 07:00 | 0 | 0 | 0 | 0 | -21.6714 | -56.595 | 104.1456 | -14.1456 | -53.1351 | 67.5667 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.9 | -5.9 | 1.1081 | 0
2016-12-01 08:00 | 0 | 0 | 0 | 0 | -21.6781 | -41.5987 | 101.7217 | -11.7217 | -39.057 | 56.1595 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6 | -6 | 1.1085 | 0
2016-12-01 09:00 | 0 | 0 | 0 | 0 | -21.6847 | -26.6025 | 99.9394 | -9.9394 | -24.9893 | 46.6172 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.7 | -5.7 | 1.1075 | 0
2016-12-01 10:00 | 0 | 0 | 0 | 0 | -21.6914 | -11.6062 | 98.9065 | -8.9065 | -10.9073 | 40.2958 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.8 | -5.8 | 1.1078 | 0
2016-12-01 11:00 | 0 | 0 | 0 | 0 | -21.698 | 3.39 | 98.6859 | -8.6859 | 3.1861 | 38.8071 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6 | -6 | 1.1085 | 0
2016-12-01 12:00 | 0 | 0 | 0 | 0 | -21.7046 | 18.3862 | 99.2918 | -9.2918 | 17.2748 | 42.6608 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.3 | -6.3 | 1.1096 | 0
2016-12-01 13:00 | 0 | 0 | 0 | 0 | -21.7113 | 33.3825 | 100.6872 | -10.6872 | 31.3467 | 50.6495 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.2 | -6.2 | 1.1092 | 0
2016-12-01 14:00 | 0 | 0 | 0 | 0 | -21.7179 | 48.3787 | 102.7881 | -12.7881 | 45.4103 | 61.1697 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.4 | -6.4 | 1.1099 | 0
2016-12-01 15:00 | 0 | 0 | 0 | 0 | -21.7245 | 63.3749 | 105.4692 | -15.4692 | 59.5057 | 73.1309 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.1 | -6.1 | 1.1088 | 0
2016-12-01 16:00 | 0 | 0 | 0 | 0 | -21.731 | 78.3711 | 108.5713 | -18.5713 | 73.7083 | 85.9256 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.3 | -6.3 | 1.1096 | 0
2016-12-01 17:00 | 0 | 0 | 0 | 0 | -21.7376 | 93.3674 | 111.9082 | -21.9082 | 88.1244 | 99.2221 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.5 | -6.5 | 1.1102 | 0
2016-12-01 18:00 | 0 | 0 | 0 | 0 | -21.7442 | 108.3636 | 115.2718 | -25.2718 | 102.878 | 112.8301 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.9 | -6.9 | 1.1117 | 0
2016-12-01 19:00 | 0 | 0 | 0 | 0 | -21.7507 | 123.3598 | 118.4378 | -28.4378 | 118.0882 | 126.6305 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.2 | -7.2 | 1.1127 | 0
2016-12-01 20:00 | 0 | 0 | 0 | 0 | -21.7572 | 138.356 | 121.1746 | -31.1746 | 133.8359 | 140.535 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-12-01 21:00 | 0 | 0 | 0 | 0 | -21.7637 | 153.3522 | 123.259 | -33.259 | 150.1237 | 154.4411 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.1 | -7.1 | 1.1123 | 0
2016-12-01 22:00 | 0 | 0 | 0 | 0 | -21.7702 | 168.3484 | 124.503 | -34.503 | 166.8448 | 168.01 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7 | -7 | 1.112 | 0
2016-12-01 23:00 | 0 | 0 | 0 | 0 | -21.7767 | 183.3446 | 124.7852 | -34.7852 | -176.2177 | 174.2481 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.9 | -6.9 | 1.1117 | 0
2016-12-02 | 0 | 0 | 0 | 0 | -21.7832 | -161.6592 | 124.0774 | -34.0774 | -159.3427 | 162.0546 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.8 | -6.8 | 1.1113 | 0
2016-12-02 01:00 | 0 | 0 | 0 | 0 | -21.7897 | -146.663 | 122.4516 | -32.4516 | -142.7907 | 148.2464 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.3 | -7.3 | 1.1131 | 0
2016-12-02 02:00 | 0 | 0 | 0 | 0 | -21.7961 | -131.6669 | 120.0626 | -30.0626 | -126.7333 | 134.3274 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.2 | -7.2 | 1.1127 | 0
2016-12-02 03:00 | 0 | 0 | 0 | 0 | -21.8026 | -116.6707 | 117.1182 | -27.1182 | -111.2268 | 120.4641 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.3 | -7.3 | 1.1131 | 0
2016-12-02 04:00 | 0 | 0 | 0 | 0 | -21.809 | -101.6745 | 113.848 | -23.848 | -96.2294 | 106.7445 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.3 | -7.3 | 1.1131 | 0
2016-12-02 05:00 | 0 | 0 | 0 | 0 | -21.8154 | -86.6783 | 110.482 | -20.482 | -81.6393 | 93.2672 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.6 | -7.6 | 1.1141 | 0
2016-12-02 06:00 | 0 | 0 | 0 | 0 | -21.8219 | -71.6822 | 107.2383 | -17.2383 | -67.3319 | 80.1776 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.1 | -9.1 | 1.1194 | 0
2016-12-02 07:00 | 0 | 0 | 0 | 0 | -21.8283 | -56.686 | 104.3158 | -14.3158 | -53.1892 | 67.7188 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.4 | -9.4 | 1.1204 | 0
2016-12-02 08:00 | 0 | 0 | 0 | 0 | -21.8346 | -41.6898 | 101.8893 | -11.8893 | -39.118 | 56.3252 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.5 | -9.5 | 1.1207 | 0
2016-12-02 09:00 | 0 | 0 | 0 | 0 | -21.841 | -26.6937 | 100.1036 | -10.1036 | -25.0585 | 46.7934 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.6 | -9.6 | 1.1211 | 0
2016-12-02 10:00 | 0 | 0 | 0 | 0 | -21.8474 | -11.6975 | 99.0662 | -9.0662 | -10.9857 | 40.4699 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.2 | -9.2 | 1.1197 | 0
2016-12-02 11:00 | 0 | 0 | 0 | 0 | -21.8537 | 3.2986 | 98.8405 | -8.8405 | 3.0982 | 38.9546 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.4 | -9.4 | 1.1204 | 0
2016-12-02 12:00 | 0 | 0 | 0 | 0 | -21.8601 | 18.2948 | 99.4407 | -9.4407 | 17.1776 | 42.7624 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.1 | -9.1 | 1.1194 | 0
2016-12-02 13:00 | 0 | 0 | 0 | 0 | -21.8664 | 33.2909 | 100.8304 | -10.8304 | 31.241 | 50.7055 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.4 | -9.4 | 1.1204 | 0
2016-12-02 14:00 | 0 | 0 | 0 | 0 | -21.8727 | 48.287 | 102.9259 | -12.9259 | 45.2969 | 61.1899 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9 | -9 | 1.119 | 0
2016-12-02 15:00 | 0 | 0 | 0 | 0 | -21.879 | 63.2832 | 105.6025 | -15.6025 | 59.3857 | 73.1243 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9 | -9 | 1.119 | 0
2016-12-02 16:00 | 0 | 0 | 0 | 0 | -21.8853 | 78.2793 | 108.7014 | -18.7014 | 73.5828 | 85.8986 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.2 | -9.2 | 1.1197 | 0
2016-12-02 17:00 | 0 | 0 | 0 | 0 | -21.8916 | 93.2754 | 112.0368 | -22.0368 | 87.9948 | 99.1786 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.2 | -9.2 | 1.1197 | 0
2016-12-02 18:00 | 0 | 0 | 0 | 0 | -21.8978 | 108.2716 | 115.4008 | -25.4008 | 102.7459 | 112.7725 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.2 | -8.2 | 1.1162 | 0
2016-12-02 19:00 | 0 | 0 | 0 | 0 | -21.9041 | 123.2677 | 118.5693 | -28.5693 | 117.9558 | 126.5598 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8 | -8 | 1.1155 | 0
2016-12-02 20:00 | 0 | 0 | 0 | 0 | -21.9103 | 138.2638 | 121.3102 | -31.3102 | 133.7059 | 140.4507 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.2 | -7.2 | 1.1127 | 0
2016-12-02 21:00 | 0 | 0 | 0 | 0 | -21.9165 | 153.2599 | 123.4003 | -33.4003 | 149.9997 | 154.3393 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.4 | -7.4 | 1.1134 | 0
2016-12-02 22:00 | 0 | 0 | 0 | 0 | -21.9228 | 168.256 | 124.6505 | -34.6505 | 166.7305 | 167.8737 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.5 | -6.5 | 1.1102 | 0
2016-12-02 23:00 | 0 | 0 | 0 | 0 | -21.929 | 183.2521 | 124.9387 | -34.9387 | -176.3193 | 174.1674 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-12-03 | 0 | 0 | 0 | 0 | -21.9351 | -161.7518 | 124.2362 | -34.2362 | -159.4304 | 162.1053 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.2 | -6.2 | 1.1092 | 0
2016-12-03 01:00 | 0 | 0 | 0 | 0 | -21.9413 | -146.7557 | 122.6142 | -32.6142 | -142.8652 | 148.3245 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6 | -6 | 1.1085 | 0
2016-12-03 02:00 | 0 | 0 | 0 | 0 | -21.9475 | -131.7596 | 120.2278 | -30.2278 | -126.7969 | 134.4206 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5 | -5 | 1.105 | 0
2016-12-03 03:00 | 0 | 0 | 0 | 0 | -21.9536 | -116.7635 | 117.2848 | -27.2848 | -111.2827 | 120.5689 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1036 | 0
2016-12-03 04:00 | 0 | 0 | 0 | 0 | -21.9598 | -101.7674 | 114.0151 | -24.0151 | -96.2811 | 106.8601 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-12-03 05:00 | 0 | 0 | 0 | 0 | -21.9659 | -86.7713 | 110.6489 | -20.6489 | -81.6901 | 93.3937 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5 | -5 | 1.105 | 0
2016-12-03 06:00 | 0 | 0 | 0 | 0 | -21.972 | -71.7753 | 107.4041 | -17.4041 | -67.3848 | 80.3156 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4 | -4 | 1.1015 | 0
2016-12-03 07:00 | 0 | 0 | 0 | 0 | -21.9781 | -56.7792 | 104.4797 | -14.4797 | -53.2467 | 67.869 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.8 | -5.8 | 1.1078 | 0
2016-12-03 08:00 | 0 | 0 | 0 | 0 | -21.9842 | -41.7831 | 102.0505 | -12.0505 | -39.1819 | 56.4878 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.9 | -5.9 | 1.1081 | 0
2016-12-03 09:00 | 0 | 0 | 0 | 0 | -21.9903 | -26.787 | 100.261 | -10.261 | -25.1304 | 46.9651 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.4 | -5.4 | 1.1064 | 0
2016-12-03 10:00 | 0 | 0 | 0 | 0 | -21.9964 | -11.791 | 99.2191 | -9.2191 | -11.0664 | 40.6381 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6 | -6 | 1.1085 | 0
2016-12-03 11:00 | 0 | 0 | 0 | 0 | -22.0024 | 3.2051 | 98.9881 | -8.9881 | 3.0084 | 39.0953 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-12-03 12:00 | 0 | 0 | 0 | 0 | -22.0085 | 18.2011 | 99.5825 | -9.5825 | 17.079 | 42.8573 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-12-03 13:00 | 0 | 0 | 0 | 0 | -22.0145 | 33.1972 | 100.9664 | -10.9664 | 31.1341 | 50.7556 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-12-03 14:00 | 0 | 0 | 0 | 0 | -22.0205 | 48.1932 | 103.0565 | -13.0565 | 45.1828 | 61.2049 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-12-03 15:00 | 0 | 0 | 0 | 0 | -22.0265 | 63.1893 | 105.7286 | -15.7286 | 59.2652 | 73.1131 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-12-03 16:00 | 0 | 0 | 0 | 0 | -22.0325 | 78.1853 | 108.8243 | -18.8243 | 73.4571 | 85.8675 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-12-03 17:00 | 0 | 0 | 0 | 0 | -22.0385 | 93.1814 | 112.1582 | -22.1582 | 87.8649 | 99.1315 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-12-03 18:00 | 0 | 0 | 0 | 0 | -22.0445 | 108.1774 | 115.5226 | -25.5226 | 102.6134 | 112.7117 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-12-03 19:00 | 0 | 0 | 0 | 0 | -22.0504 | 123.1734 | 118.6934 | -28.6934 | 117.8227 | 126.4864 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.9 | -3.9 | 1.1012 | 0
2016-12-03 20:00 | 0 | 0 | 0 | 0 | -22.0564 | 138.1695 | 121.4387 | -31.4387 | 133.5749 | 140.364 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-12-03 21:00 | 0 | 0 | 0 | 0 | -22.0623 | 153.1655 | 123.5343 | -33.5343 | 149.8743 | 154.2359 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-12-03 22:00 | 0 | 0 | 0 | 0 | -22.0682 | 168.1615 | 124.7908 | -34.7908 | 166.6141 | 167.7375 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-12-03 23:00 | 0 | 0 | 0 | 0 | -22.0742 | 183.1575 | 125.0853 | -35.0853 | -176.4237 | 174.0894 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-12-04 | 0 | 0 | 0 | 0 | -22.0801 | -161.8465 | 124.388 | -34.388 | -159.5213 | 162.1577 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-12-04 01:00 | 0 | 0 | 0 | 0 | -22.0859 | -146.8505 | 122.7701 | -32.7701 | -142.9432 | 148.4041 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-12-04 02:00 | 0 | 0 | 0 | 0 | -22.0918 | -131.8544 | 120.3865 | -30.3865 | -126.8642 | 134.5148 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-12-04 03:00 | 0 | 0 | 0 | 0 | -22.0977 | -116.8584 | 117.445 | -27.445 | -111.3424 | 120.6744 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-12-04 04:00 | 0 | 0 | 0 | 0 | -22.1035 | -101.8624 | 114.1759 | -24.1759 | -96.3367 | 106.9759 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-12-04 05:00 | 0 | 0 | 0 | 0 | -22.1093 | -86.8664 | 110.8093 | -20.8093 | -81.7446 | 93.5197 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-12-04 06:00 | 0 | 0 | 0 | 0 | -22.1152 | -71.8704 | 107.5634 | -17.5634 | -67.4412 | 80.4524 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-12-04 07:00 | 0 | 0 | 0 | 0 | -22.121 | -56.8745 | 104.637 | -14.637 | -53.3074 | 68.0172 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-12-04 08:00 | 0 | 0 | 0 | 0 | -22.1268 | -41.8785 | 102.2049 | -12.2049 | -39.2488 | 56.6472 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-12-04 09:00 | 0 | 0 | 0 | 0 | -22.1326 | -26.8825 | 100.4117 | -10.4117 | -25.2049 | 47.1321 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-12-04 10:00 | 0 | 0 | 0 | 0 | -22.1383 | -11.8865 | 99.365 | -9.365 | -11.1493 | 40.8001 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-12-04 11:00 | 0 | 0 | 0 | 0 | -22.1441 | 3.1095 | 99.1286 | -9.1286 | 2.9169 | 39.2291 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-12-04 12:00 | 0 | 0 | 0 | 0 | -22.1498 | 18.1054 | 99.7172 | -9.7172 | 16.9791 | 42.9456 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.0945 | 0
2016-12-04 13:00 | 0 | 0 | 0 | 0 | -22.1556 | 33.1014 | 101.0952 | -11.0952 | 31.0264 | 50.7998 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.2 | -2.2 | 1.0952 | 0
2016-12-04 14:00 | 0 | 0 | 0 | 0 | -22.1613 | 48.0974 | 103.1799 | -13.1799 | 45.068 | 61.2147 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-12-04 15:00 | 0 | 0 | 0 | 0 | -22.167 | 63.0933 | 105.8474 | -15.8474 | 59.1443 | 73.0974 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.3 | -3.3 | 1.0991 | 0
2016-12-04 16:00 | 0 | 0 | 0 | 0 | -22.1727 | 78.0893 | 108.9399 | -18.9399 | 73.3311 | 85.8324 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-12-04 17:00 | 0 | 0 | 0 | 0 | -22.1784 | 93.0853 | 112.2722 | -22.2722 | 87.7348 | 99.0809 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.8 | -3.8 | 1.1008 | 0
2016-12-04 18:00 | 0 | 0 | 0 | 0 | -22.1841 | 108.0812 | 115.637 | -25.637 | 102.4807 | 112.6478 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.7 | -3.7 | 1.1004 | 0
2016-12-04 19:00 | 0 | 0 | 0 | 0 | -22.1897 | 123.0772 | 118.8103 | -28.8103 | 117.6891 | 126.4103 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.5 | -5.5 | 1.1067 | 0
2016-12-04 20:00 | 0 | 0 | 0 | 0 | -22.1954 | 138.0731 | 121.5597 | -31.5597 | 133.4431 | 140.2752 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.1 | -6.1 | 1.1088 | 0
2016-12-04 21:00 | 0 | 0 | 0 | 0 | -22.201 | 153.069 | 123.661 | -33.661 | 149.7474 | 154.1309 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.7 | -6.7 | 1.111 | 0
2016-12-04 22:00 | 0 | 0 | 0 | 0 | -22.2067 | 168.065 | 124.924 | -34.924 | 166.4958 | 167.6016 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.9 | -6.9 | 1.1117 | 0
2016-12-04 23:00 | 0 | 0 | 0 | 0 | -22.2123 | 183.0609 | 125.2247 | -35.2247 | -176.5306 | 174.0147 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.7 | -7.7 | 1.1144 | 0
2016-12-05 | 0 | 0 | 0 | 0 | -22.2179 | -161.9432 | 124.5329 | -34.5329 | -159.6154 | 162.2121 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.1 | -8.1 | 1.1159 | 0
2016-12-05 01:00 | 0 | 0 | 0 | 0 | -22.2235 | -146.9472 | 122.9193 | -32.9193 | -143.0248 | 148.4851 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.7 | -7.7 | 1.1144 | 0
2016-12-05 02:00 | 0 | 0 | 0 | 0 | -22.229 | -131.9513 | 120.5386 | -30.5386 | -126.9353 | 134.61 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-12-05 03:00 | 0 | 0 | 0 | 0 | -22.2346 | -116.9554 | 117.5988 | -27.5988 | -111.406 | 120.7805 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-12-05 04:00 | 0 | 0 | 0 | 0 | -22.2401 | -101.9595 | 114.3302 | -24.3302 | -96.396 | 107.0918 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.7 | -6.7 | 1.111 | 0
2016-12-05 05:00 | 0 | 0 | 0 | 0 | -22.2457 | -86.9635 | 110.9633 | -20.9633 | -81.8029 | 93.6454 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.8 | -6.8 | 1.1113 | 0
2016-12-05 06:00 | 0 | 0 | 0 | 0 | -22.2512 | -71.9676 | 107.7162 | -17.7162 | -67.5011 | 80.5881 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.6 | -5.6 | 1.1071 | 0
2016-12-05 07:00 | 0 | 0 | 0 | 0 | -22.2567 | -56.9717 | 104.7877 | -14.7877 | -53.3713 | 68.1634 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.4 | -6.4 | 1.1099 | 0
2016-12-05 08:00 | 0 | 0 | 0 | 0 | -22.2622 | -41.9758 | 102.3526 | -12.3526 | -39.3186 | 56.8034 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.5 | -6.5 | 1.1102 | 0
2016-12-05 09:00 | 0 | 0 | 0 | 0 | -22.2677 | -26.9799 | 100.5555 | -10.5555 | -25.2818 | 47.2944 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.7 | -6.7 | 1.111 | 0
2016-12-05 10:00 | 0 | 0 | 0 | 0 | -22.2732 | -11.984 | 99.504 | -9.504 | -11.2342 | 40.9559 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7 | -7 | 1.112 | 0
2016-12-05 11:00 | 0 | 0 | 0 | 0 | -22.2786 | 3.0119 | 99.262 | -9.262 | 2.8237 | 39.3559 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.7 | -6.7 | 1.111 | 0
2016-12-05 12:00 | 0 | 0 | 0 | 0 | -22.2841 | 18.0078 | 99.8447 | -9.8447 | 16.8779 | 43.0272 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.4 | -7.4 | 1.1134 | 0
2016-12-05 13:00 | 0 | 0 | 0 | 0 | -22.2895 | 33.0037 | 101.2167 | -11.2167 | 30.9178 | 50.8379 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.4 | -7.4 | 1.1134 | 0
2016-12-05 14:00 | 0 | 0 | 0 | 0 | -22.295 | 47.9995 | 103.2959 | -13.2959 | 44.9527 | 61.2192 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.2 | -9.2 | 1.1197 | 0
2016-12-05 15:00 | 0 | 0 | 0 | 0 | -22.3004 | 62.9954 | 105.9588 | -15.9588 | 59.0232 | 73.0772 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.8 | -9.8 | 1.1218 | 0
2016-12-05 16:00 | 0 | 0 | 0 | 0 | -22.3058 | 77.9913 | 109.0481 | -19.0481 | 73.2049 | 85.7933 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11 | -11 | 1.126 | 0
2016-12-05 17:00 | 0 | 0 | 0 | 0 | -22.3112 | 92.9872 | 112.3788 | -22.3788 | 87.6047 | 99.0268 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12.1 | -12.1 | 1.1299 | 0
2016-12-05 18:00 | 0 | 0 | 0 | 0 | -22.3165 | 107.9831 | 115.744 | -25.744 | 102.3478 | 112.581 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12.7 | -12.7 | 1.132 | 0
2016-12-05 19:00 | 0 | 0 | 0 | 0 | -22.3219 | 122.9789 | 118.9197 | -28.9197 | 117.5552 | 126.3317 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.6 | -13.6 | 1.1351 | 0
2016-12-05 20:00 | 0 | 0 | 0 | 0 | -22.3272 | 137.9748 | 121.6734 | -31.6734 | 133.3105 | 140.1844 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.1 | -13.1 | 1.1334 | 0
2016-12-05 21:00 | 0 | 0 | 0 | 0 | -22.3326 | 152.9707 | 123.7804 | -33.7804 | 149.6193 | 154.0245 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.7 | -11.7 | 1.1284 | 0
2016-12-05 22:00 | 0 | 0 | 0 | 0 | -22.3379 | 167.9665 | 125.0498 | -35.0498 | 166.3756 | 167.4663 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.9 | -11.9 | 1.1292 | 0
2016-12-05 23:00 | 0 | 0 | 0 | 0 | -22.3432 | 182.9624 | 125.357 | -35.357 | -176.64 | 173.9434 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.4 | -11.4 | 1.1274 | 0
2016-12-06 | 0 | 0 | 0 | 0 | -22.3485 | -162.0418 | 124.6709 | -34.6709 | -159.7124 | 162.2684 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.3 | -10.3 | 1.1236 | 0
2016-12-06 01:00 | 0 | 0 | 0 | 0 | -22.3538 | -147.0459 | 123.0616 | -33.0616 | -143.1097 | 148.5677 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.6 | -10.6 | 1.1246 | 0
2016-12-06 02:00 | 0 | 0 | 0 | 0 | -22.3591 | -132.0501 | 120.6839 | -30.6839 | -127.01 | 134.7063 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11 | -11 | 1.126 | 0
2016-12-06 03:00 | 0 | 0 | 0 | 0 | -22.3644 | -117.0542 | 117.7459 | -27.7459 | -111.4734 | 120.8872 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.6 | -11.6 | 1.1281 | 0
2016-12-06 04:00 | 0 | 0 | 0 | 0 | -22.3696 | -102.0584 | 114.4779 | -24.4779 | -96.4591 | 107.2078 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.9 | -10.9 | 1.1257 | 0
2016-12-06 05:00 | 0 | 0 | 0 | 0 | -22.3748 | -87.0626 | 111.1107 | -21.1107 | -81.8647 | 93.7704 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.7 | -10.7 | 1.1249 | 0
2016-12-06 06:00 | 0 | 0 | 0 | 0 | -22.3801 | -72.0667 | 107.8624 | -17.8624 | -67.5644 | 80.7225 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.2 | -10.2 | 1.1232 | 0
2016-12-06 07:00 | 0 | 0 | 0 | 0 | -22.3853 | -57.0709 | 104.9318 | -14.9318 | -53.4383 | 68.3074 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.8 | -9.8 | 1.1218 | 0
2016-12-06 08:00 | 0 | 0 | 0 | 0 | -22.3905 | -42.0751 | 102.4935 | -12.4935 | -39.3912 | 56.9563 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.9 | -9.9 | 1.1221 | 0
2016-12-06 09:00 | 0 | 0 | 0 | 0 | -22.3957 | -27.0792 | 100.6923 | -10.6923 | -25.3612 | 47.452 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.2 | -9.2 | 1.1197 | 0
2016-12-06 10:00 | 0 | 0 | 0 | 0 | -22.4008 | -12.0834 | 99.6359 | -9.6359 | -11.3212 | 41.1055 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.1 | -9.1 | 1.1194 | 0
2016-12-06 11:00 | 0 | 0 | 0 | 0 | -22.406 | 2.9124 | 99.3883 | -9.3883 | 2.7289 | 39.4757 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.9 | -8.9 | 1.1186 | 0
2016-12-06 12:00 | 0 | 0 | 0 | 0 | -22.4112 | 17.9082 | 99.9649 | -9.9649 | 16.7755 | 43.102 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.7 | -8.7 | 1.1179 | 0
2016-12-06 13:00 | 0 | 0 | 0 | 0 | -22.4163 | 32.904 | 101.331 | -11.331 | 30.8084 | 50.8701 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9 | -9 | 1.119 | 0
2016-12-06 14:00 | 0 | 0 | 0 | 0 | -22.4214 | 47.8998 | 103.4046 | -13.4046 | 44.837 | 61.2186 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.6 | -9.6 | 1.1211 | 0
2016-12-06 15:00 | 0 | 0 | 0 | 0 | -22.4265 | 62.8956 | 106.0629 | -16.0629 | 58.9019 | 73.0524 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.2 | -10.2 | 1.1232 | 0
2016-12-06 16:00 | 0 | 0 | 0 | 0 | -22.4316 | 77.8914 | 109.1489 | -19.1489 | 73.0788 | 85.7503 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.2 | -10.2 | 1.1232 | 0
2016-12-06 17:00 | 0 | 0 | 0 | 0 | -22.4367 | 92.8872 | 112.4781 | -22.4781 | 87.4747 | 98.9694 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.1 | -10.1 | 1.1228 | 0
2016-12-06 18:00 | 0 | 0 | 0 | 0 | -22.4418 | 107.883 | 115.8436 | -25.8436 | 102.2149 | 112.5113 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.1 | -10.1 | 1.1228 | 0
2016-12-06 19:00 | 0 | 0 | 0 | 0 | -22.4468 | 122.8788 | 119.0216 | -29.0216 | 117.421 | 126.2506 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.9 | -9.9 | 1.1221 | 0
2016-12-06 20:00 | 0 | 0 | 0 | 0 | -22.4519 | 137.8746 | 121.7796 | -31.7796 | 133.1773 | 140.0916 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.7 | -9.7 | 1.1215 | 0
2016-12-06 21:00 | 0 | 0 | 0 | 0 | -22.4569 | 152.8704 | 123.8923 | -33.8923 | 149.4901 | 153.9171 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.5 | -9.5 | 1.1207 | 0
2016-12-06 22:00 | 0 | 0 | 0 | 0 | -22.462 | 167.8662 | 125.1683 | -35.1683 | 166.2537 | 167.332 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.1 | -9.1 | 1.1194 | 0
2016-12-06 23:00 | 0 | 0 | 0 | 0 | -22.467 | 182.862 | 125.482 | -35.482 | -176.7517 | 173.8759 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.1 | -9.1 | 1.1194 | 0
2016-12-07 | 0 | 0 | 0 | 0 | -22.472 | -162.1422 | 124.8017 | -34.8017 | -159.8123 | 162.3269 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.2 | -9.2 | 1.1197 | 0
2016-12-07 01:00 | 0 | 0 | 0 | 0 | -22.477 | -147.1465 | 123.197 | -33.197 | -143.198 | 148.6518 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.9 | -9.9 | 1.1221 | 0
2016-12-07 02:00 | 0 | 0 | 0 | 0 | -22.4819 | -132.1507 | 120.8225 | -30.8225 | -127.0883 | 134.8036 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.8 | -9.8 | 1.1218 | 0
2016-12-07 03:00 | 0 | 0 | 0 | 0 | -22.4869 | -117.1549 | 117.8864 | -27.8864 | -111.5444 | 120.9943 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10 | -10 | 1.1225 | 0
2016-12-07 04:00 | 0 | 0 | 0 | 0 | -22.4918 | -102.1592 | 114.6191 | -24.6191 | -96.5259 | 107.3237 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.3 | -10.3 | 1.1236 | 0
2016-12-07 05:00 | 0 | 0 | 0 | 0 | -22.4968 | -87.1634 | 111.2516 | -21.2516 | -81.9301 | 93.8949 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.1 | -10.1 | 1.1228 | 0
2016-12-07 06:00 | 0 | 0 | 0 | 0 | -22.5017 | -72.1676 | 108.0019 | -18.0019 | -67.6311 | 80.8555 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.1 | -10.1 | 1.1228 | 0
2016-12-07 07:00 | 0 | 0 | 0 | 0 | -22.5066 | -57.1719 | 105.069 | -15.069 | -53.5084 | 68.4491 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.9 | -9.9 | 1.1221 | 0
2016-12-07 08:00 | 0 | 0 | 0 | 0 | -22.5115 | -42.1761 | 102.6276 | -12.6276 | -39.4665 | 57.1057 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.1 | -10.1 | 1.1228 | 0
2016-12-07 09:00 | 0 | 0 | 0 | 0 | -22.5164 | -27.1804 | 100.8221 | -10.8221 | -25.443 | 47.6046 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.1 | -10.1 | 1.1228 | 0
2016-12-07 10:00 | 0 | 0 | 0 | 0 | -22.5213 | -12.1846 | 99.7606 | -9.7606 | -11.4101 | 41.2487 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.1 | -10.1 | 1.1228 | 0
2016-12-07 11:00 | 0 | 0 | 0 | 0 | -22.5261 | 2.8111 | 99.5073 | -9.5073 | 2.6327 | 39.5885 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.1 | -10.1 | 1.1228 | 0
2016-12-07 12:00 | 0 | 0 | 0 | 0 | -22.531 | 17.8069 | 100.0778 | -10.0778 | 16.6721 | 43.1701 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.9 | -9.9 | 1.1221 | 0
2016-12-07 13:00 | 0 | 0 | 0 | 0 | -22.5358 | 32.8026 | 101.4378 | -11.4378 | 30.6983 | 50.8963 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.7 | -10.7 | 1.1249 | 0
2016-12-07 14:00 | 0 | 0 | 0 | 0 | -22.5406 | 47.7983 | 103.5059 | -13.5059 | 44.7209 | 61.2128 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11 | -11 | 1.126 | 0
2016-12-07 15:00 | 0 | 0 | 0 | 0 | -22.5454 | 62.7941 | 106.1596 | -16.1596 | 58.7805 | 73.0232 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.8 | -10.8 | 1.1253 | 0
2016-12-07 16:00 | 0 | 0 | 0 | 0 | -22.5502 | 77.7898 | 109.2423 | -19.2423 | 72.9528 | 85.7035 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.7 | -10.7 | 1.1249 | 0
2016-12-07 17:00 | 0 | 0 | 0 | 0 | -22.555 | 92.7855 | 112.5699 | -22.5699 | 87.3448 | 98.9086 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.8 | -10.8 | 1.1253 | 0
2016-12-07 18:00 | 0 | 0 | 0 | 0 | -22.5598 | 107.7813 | 115.9358 | -25.9358 | 102.0821 | 112.4387 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.4 | -10.4 | 1.1239 | 0
2016-12-07 19:00 | 0 | 0 | 0 | 0 | -22.5645 | 122.777 | 119.1161 | -29.1161 | 117.2867 | 126.1673 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.8 | -10.8 | 1.1253 | 0
2016-12-07 20:00 | 0 | 0 | 0 | 0 | -22.5693 | 137.7727 | 121.8783 | -31.8783 | 133.0437 | 139.9972 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11 | -11 | 1.126 | 0
2016-12-07 21:00 | 0 | 0 | 0 | 0 | -22.574 | 152.7684 | 123.9968 | -33.9968 | 149.3599 | 153.8087 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.1 | -11.1 | 1.1263 | 0
2016-12-07 22:00 | 0 | 0 | 0 | 0 | -22.5787 | 167.7641 | 125.2794 | -35.2794 | 166.1301 | 167.1987 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.9 | -10.9 | 1.1257 | 0
2016-12-07 23:00 | 0 | 0 | 0 | 0 | -22.5834 | 182.7598 | 125.5997 | -35.5997 | -176.8657 | 173.8125 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.7 | -10.7 | 1.1249 | 0
2016-12-08 | 0 | 0 | 0 | 0 | -22.5881 | -162.2444 | 124.9254 | -34.9254 | -159.9151 | 162.3876 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.2 | -11.2 | 1.1267 | 0
2016-12-08 01:00 | 0 | 0 | 0 | 0 | -22.5928 | -147.2487 | 123.3254 | -33.3254 | -143.2895 | 148.7374 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.6 | -11.6 | 1.1281 | 0
2016-12-08 02:00 | 0 | 0 | 0 | 0 | -22.5975 | -132.253 | 120.9543 | -30.9543 | -127.1702 | 134.9019 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.3 | -11.3 | 1.1271 | 0
2016-12-08 03:00 | 0 | 0 | 0 | 0 | -22.6021 | -117.2573 | 118.0201 | -28.0201 | -111.6191 | 121.102 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.2 | -11.2 | 1.1267 | 0
2016-12-08 04:00 | 0 | 0 | 0 | 0 | -22.6068 | -102.2616 | 114.7536 | -24.7536 | -96.5963 | 107.4396 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.7 | -11.7 | 1.1284 | 0
2016-12-08 05:00 | 0 | 0 | 0 | 0 | -22.6114 | -87.266 | 111.3857 | -21.3857 | -81.999 | 94.0186 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12.2 | -12.2 | 1.1302 | 0
2016-12-08 06:00 | 0 | 0 | 0 | 0 | -22.616 | -72.2703 | 108.1347 | -18.1347 | -67.701 | 80.9871 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12 | -12 | 1.1295 | 0
2016-12-08 07:00 | 0 | 0 | 0 | 0 | -22.6206 | -57.2746 | 105.1995 | -15.1995 | -53.5816 | 68.5884 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.1 | -13.1 | 1.1334 | 0
2016-12-08 08:00 | 0 | 0 | 0 | 0 | -22.6252 | -42.2789 | 102.7546 | -12.7546 | -39.5445 | 57.2515 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.3 | -13.3 | 1.1341 | 0
2016-12-08 09:00 | 0 | 0 | 0 | 0 | -22.6298 | -27.2832 | 100.9449 | -10.9449 | -25.527 | 47.7522 | 0 | 0 | 0.2 | 0 | 0 | 0 | -14.3 | -14.3 | 1.1376 | 0
2016-12-08 10:00 | 0 | 0 | 0 | 0 | -22.6344 | -12.2875 | 99.8782 | -9.8782 | -11.5008 | 41.3855 | 0 | 0 | 0.2 | 0 | 0 | 0 | -14.3 | -14.3 | 1.1376 | 0
2016-12-08 11:00 | 0 | 0 | 0 | 0 | -22.6389 | 2.7082 | 99.6191 | -9.6191 | 2.535 | 39.6941 | 0 | 0 | 0.2 | 0 | 0 | 0 | -14.4 | -14.4 | 1.1379 | 0
2016-12-08 12:00 | 0 | 0 | 0 | 0 | -22.6435 | 17.7038 | 100.1834 | -10.1834 | 16.5677 | 43.2313 | 0 | 0 | 0.2 | 0 | 0 | 0 | -14.3 | -14.3 | 1.1376 | 0
2016-12-08 13:00 | 0 | 0 | 0 | 0 | -22.648 | 32.6995 | 101.5373 | -11.5373 | 30.5877 | 50.9165 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.2 | -13.2 | 1.1337 | 0
2016-12-08 14:00 | 0 | 0 | 0 | 0 | -22.6525 | 47.6952 | 103.5998 | -13.5998 | 44.6046 | 61.2018 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12.7 | -12.7 | 1.132 | 0
2016-12-08 15:00 | 0 | 0 | 0 | 0 | -22.657 | 62.6908 | 106.2488 | -16.2488 | 58.6592 | 72.9895 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13 | -13 | 1.133 | 0
2016-12-08 16:00 | 0 | 0 | 0 | 0 | -22.6615 | 77.6865 | 109.3282 | -19.3282 | 72.8271 | 85.6529 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12.4 | -12.4 | 1.1309 | 0
2016-12-08 17:00 | 0 | 0 | 0 | 0 | -22.666 | 92.6822 | 112.6542 | -22.6542 | 87.2152 | 98.8446 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.5 | -11.5 | 1.1278 | 0
2016-12-08 18:00 | 0 | 0 | 0 | 0 | -22.6704 | 107.6778 | 116.0204 | -26.0204 | 101.9495 | 112.3635 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.1 | -11.1 | 1.1263 | 0
2016-12-08 19:00 | 0 | 0 | 0 | 0 | -22.6749 | 122.6735 | 119.2031 | -29.2031 | 117.1524 | 126.0817 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.4 | -10.4 | 1.1239 | 0
2016-12-08 20:00 | 0 | 0 | 0 | 0 | -22.6793 | 137.6691 | 121.9695 | -31.9695 | 132.9096 | 139.9011 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.2 | -9.2 | 1.1197 | 0
2016-12-08 21:00 | 0 | 0 | 0 | 0 | -22.6837 | 152.6648 | 124.0938 | -34.0938 | 149.2288 | 153.6995 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.7 | -8.7 | 1.1179 | 0
2016-12-08 22:00 | 0 | 0 | 0 | 0 | -22.6882 | 167.6604 | 125.383 | -35.383 | 166.0051 | 167.0668 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.2 | -8.2 | 1.1162 | 0
2016-12-08 23:00 | 0 | 0 | 0 | 0 | -22.6926 | 182.6561 | 125.7101 | -35.7101 | -176.9818 | 173.7533 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-12-09 | 0 | 0 | 0 | 0 | -22.6969 | -162.3483 | 125.0419 | -35.0419 | -160.0205 | 162.4506 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.2 | -7.2 | 1.1127 | 0
2016-12-09 01:00 | 0 | 0 | 0 | 0 | -22.7013 | -147.3527 | 123.4468 | -33.4468 | -143.3842 | 148.8245 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.8 | -6.8 | 1.1113 | 0
2016-12-09 02:00 | 0 | 0 | 0 | 0 | -22.7057 | -132.357 | 121.0791 | -31.0791 | -127.2554 | 135.0011 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.1 | -7.1 | 1.1123 | 0
2016-12-09 03:00 | 0 | 0 | 0 | 0 | -22.71 | -117.3614 | 118.147 | -28.147 | -111.6973 | 121.21 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.5 | -7.5 | 1.1138 | 0
2016-12-09 04:00 | 0 | 0 | 0 | 0 | -22.7144 | -102.3658 | 114.8813 | -24.8813 | -96.6702 | 107.5552 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-12-09 05:00 | 0 | 0 | 0 | 0 | -22.7187 | -87.3701 | 111.5131 | -21.5131 | -82.0714 | 94.1415 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.7 | -6.7 | 1.111 | 0
2016-12-09 06:00 | 0 | 0 | 0 | 0 | -22.723 | -72.3745 | 108.2606 | -18.2606 | -67.7742 | 81.1172 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.9 | -6.9 | 1.1117 | 0
2016-12-09 07:00 | 0 | 0 | 0 | 0 | -22.7273 | -57.3789 | 105.323 | -15.323 | -53.6576 | 68.7253 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.5 | -6.5 | 1.1102 | 0
2016-12-09 08:00 | 0 | 0 | 0 | 0 | -22.7316 | -42.3833 | 102.8747 | -12.8747 | -39.625 | 57.3937 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.4 | -6.4 | 1.1099 | 0
2016-12-09 09:00 | 0 | 0 | 0 | 0 | -22.7359 | -27.3877 | 101.0605 | -11.0605 | -25.6132 | 47.8947 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.4 | -6.4 | 1.1099 | 0
2016-12-09 10:00 | 0 | 0 | 0 | 0 | -22.7401 | -12.392 | 99.9886 | -9.9886 | -11.5934 | 41.5159 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.1 | -6.1 | 1.1088 | 0
2016-12-09 11:00 | 0 | 0 | 0 | 0 | -22.7444 | 2.6036 | 99.7235 | -9.7235 | 2.436 | 39.7926 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.6 | -7.6 | 1.1141 | 0
2016-12-09 12:00 | 0 | 0 | 0 | 0 | -22.7486 | 17.5992 | 100.2816 | -10.2816 | 16.4624 | 43.2857 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-12-09 13:00 | 0 | 0 | 0 | 0 | -22.7528 | 32.5948 | 101.6293 | -11.6293 | 30.4765 | 50.9306 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.3 | -6.3 | 1.1096 | 0
2016-12-09 14:00 | 0 | 0 | 0 | 0 | -22.757 | 47.5904 | 103.6862 | -13.6862 | 44.4882 | 61.1856 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.1 | -7.1 | 1.1123 | 0
2016-12-09 15:00 | 0 | 0 | 0 | 0 | -22.7612 | 62.586 | 106.3305 | -16.3305 | 58.538 | 72.9515 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.7 | -6.7 | 1.111 | 0
2016-12-09 16:00 | 0 | 0 | 0 | 0 | -22.7654 | 77.5816 | 109.4067 | -19.4067 | 72.7016 | 85.5985 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.7 | -6.7 | 1.111 | 0
2016-12-09 17:00 | 0 | 0 | 0 | 0 | -22.7696 | 92.5772 | 112.731 | -22.731 | 87.086 | 98.7774 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7 | -7 | 1.112 | 0
2016-12-09 18:00 | 0 | 0 | 0 | 0 | -22.7737 | 107.5728 | 116.0975 | -26.0975 | 101.8173 | 112.2856 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.2 | -7.2 | 1.1127 | 0
2016-12-09 19:00 | 0 | 0 | 0 | 0 | -22.7779 | 122.5684 | 119.2825 | -29.2825 | 117.0183 | 125.994 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.7 | -6.7 | 1.111 | 0
2016-12-09 20:00 | 0 | 0 | 0 | 0 | -22.782 | 137.564 | 122.0531 | -32.0531 | 132.7754 | 139.8035 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.4 | -7.4 | 1.1134 | 0
2016-12-09 21:00 | 0 | 0 | 0 | 0 | -22.7861 | 152.5595 | 124.1831 | -34.1831 | 149.097 | 153.5897 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.8 | -7.8 | 1.1148 | 0
2016-12-09 22:00 | 0 | 0 | 0 | 0 | -22.7902 | 167.5551 | 125.4791 | -35.4791 | 165.8787 | 166.9365 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.5 | -8.5 | 1.1173 | 0
2016-12-09 23:00 | 0 | 0 | 0 | 0 | -22.7943 | 182.5507 | 125.8131 | -35.8131 | -177.1 | 173.6986 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.5 | -8.5 | 1.1173 | 0
2016-12-10 | 0 | 0 | 0 | 0 | -22.7984 | -162.4537 | 125.151 | -35.151 | -160.1286 | 162.5158 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.7 | -8.7 | 1.1179 | 0
2016-12-10 01:00 | 0 | 0 | 0 | 0 | -22.8024 | -147.4581 | 123.561 | -33.561 | -143.4819 | 148.9132 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.8 | -8.8 | 1.1183 | 0
2016-12-10 02:00 | 0 | 0 | 0 | 0 | -22.8065 | -132.4626 | 121.1969 | -31.1969 | -127.344 | 135.1012 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.3 | -8.3 | 1.1165 | 0
2016-12-10 03:00 | 0 | 0 | 0 | 0 | -22.8105 | -117.467 | 118.267 | -28.267 | -111.779 | 121.3183 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.3 | -8.3 | 1.1165 | 0
2016-12-10 04:00 | 0 | 0 | 0 | 0 | -22.8146 | -102.4714 | 115.0021 | -25.0021 | -96.7476 | 107.6706 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-12-10 05:00 | 0 | 0 | 0 | 0 | -22.8186 | -87.4759 | 111.6336 | -21.6336 | -82.147 | 94.2635 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.1 | -8.1 | 1.1159 | 0
2016-12-10 06:00 | 0 | 0 | 0 | 0 | -22.8226 | -72.4803 | 108.3797 | -18.3797 | -67.8505 | 81.2455 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.6 | -8.6 | 1.1176 | 0
2016-12-10 07:00 | 0 | 0 | 0 | 0 | -22.8266 | -57.4847 | 105.4395 | -15.4395 | -53.7366 | 68.8595 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.6 | -8.6 | 1.1176 | 0
2016-12-10 08:00 | 0 | 0 | 0 | 0 | -22.8305 | -42.4892 | 102.9877 | -12.9877 | -39.7081 | 57.5321 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.2 | -8.2 | 1.1162 | 0
2016-12-10 09:00 | 0 | 0 | 0 | 0 | -22.8345 | -27.4936 | 101.169 | -11.169 | -25.7016 | 48.0321 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8 | -8 | 1.1155 | 0
2016-12-10 10:00 | 0 | 0 | 0 | 0 | -22.8385 | -12.4981 | 100.0916 | -10.0916 | -11.6876 | 41.6397 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.2 | -8.2 | 1.1162 | 0
2016-12-10 11:00 | 0 | 0 | 0 | 0 | -22.8424 | 2.4975 | 99.8205 | -9.8205 | 2.3358 | 39.8839 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8 | -8 | 1.1155 | 0
2016-12-10 12:00 | 0 | 0 | 0 | 0 | -22.8463 | 17.493 | 100.3723 | -10.3723 | 16.3563 | 43.3332 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-12-10 13:00 | 0 | 0 | 0 | 0 | -22.8502 | 32.4886 | 101.7139 | -11.7139 | 30.365 | 50.9386 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.1 | -8.1 | 1.1159 | 0
2016-12-10 14:00 | 0 | 0 | 0 | 0 | -22.8541 | 47.4841 | 103.7651 | -13.7651 | 44.3717 | 61.1643 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9 | -9 | 1.119 | 0
2016-12-10 15:00 | 0 | 0 | 0 | 0 | -22.858 | 62.4797 | 106.4048 | -16.4048 | 58.4171 | 72.909 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.8 | -9.8 | 1.1218 | 0
2016-12-10 16:00 | 0 | 0 | 0 | 0 | -22.8619 | 77.4752 | 109.4776 | -19.4776 | 72.5766 | 85.5404 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.1 | -11.1 | 1.1263 | 0
2016-12-10 17:00 | 0 | 0 | 0 | 0 | -22.8657 | 92.4707 | 112.8003 | -22.8003 | 86.9573 | 98.7072 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.4 | -10.4 | 1.1239 | 0
2016-12-10 18:00 | 0 | 0 | 0 | 0 | -22.8696 | 107.4663 | 116.1671 | -26.1671 | 101.6856 | 112.2051 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.1 | -9.1 | 1.1194 | 0
2016-12-10 19:00 | 0 | 0 | 0 | 0 | -22.8734 | 122.4618 | 119.3543 | -29.3543 | 116.8845 | 125.9044 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.4 | -9.4 | 1.1204 | 0
2016-12-10 20:00 | 0 | 0 | 0 | 0 | -22.8772 | 137.4573 | 122.1291 | -32.1291 | 132.6411 | 139.7045 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9 | -9 | 1.119 | 0
2016-12-10 21:00 | 0 | 0 | 0 | 0 | -22.881 | 152.4529 | 124.2649 | -34.2649 | 148.9646 | 153.4795 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.5 | -9.5 | 1.1207 | 0
2016-12-10 22:00 | 0 | 0 | 0 | 0 | -22.8848 | 167.4484 | 125.5676 | -35.5676 | 165.7511 | 166.8079 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.2 | -9.2 | 1.1197 | 0
2016-12-10 23:00 | 0 | 0 | 0 | 0 | -22.8886 | 182.4439 | 125.9086 | -35.9086 | -177.22 | 173.6485 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.7 | -7.7 | 1.1144 | 0
2016-12-11 | 0 | 0 | 0 | 0 | -22.8924 | -162.5606 | 125.2529 | -35.2529 | -160.2392 | 162.5835 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.3 | -8.3 | 1.1165 | 0
2016-12-11 01:00 | 0 | 0 | 0 | 0 | -22.8961 | -147.565 | 123.668 | -33.668 | -143.5826 | 149.0033 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.7 | -7.7 | 1.1144 | 0
2016-12-11 02:00 | 0 | 0 | 0 | 0 | -22.8999 | -132.5695 | 121.3077 | -31.3077 | -127.4359 | 135.2021 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.6 | -9.6 | 1.1211 | 0
2016-12-11 03:00 | 0 | 0 | 0 | 0 | -22.9036 | -117.574 | 118.38 | -28.38 | -111.8641 | 121.4269 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.1 | -10.1 | 1.1228 | 0
2016-12-11 04:00 | 0 | 0 | 0 | 0 | -22.9073 | -102.5785 | 115.1161 | -25.1161 | -96.8284 | 107.7857 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.2 | -10.2 | 1.1232 | 0
2016-12-11 05:00 | 0 | 0 | 0 | 0 | -22.911 | -87.583 | 111.7472 | -21.7472 | -82.226 | 94.3845 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.4 | -9.4 | 1.1204 | 0
2016-12-11 06:00 | 0 | 0 | 0 | 0 | -22.9147 | -72.5875 | 108.4918 | -18.4918 | -67.9299 | 81.3722 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.3 | -9.3 | 1.12 | 0
2016-12-11 07:00 | 0 | 0 | 0 | 0 | -22.9184 | -57.592 | 105.5491 | -15.5491 | -53.8183 | 68.9911 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.3 | -10.3 | 1.1236 | 0
2016-12-11 08:00 | 0 | 0 | 0 | 0 | -22.922 | -42.5965 | 103.0935 | -13.0935 | -39.7937 | 57.6667 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.2 | -10.2 | 1.1232 | 0
2016-12-11 09:00 | 0 | 0 | 0 | 0 | -22.9257 | -27.601 | 101.2702 | -11.2702 | -25.792 | 48.1642 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.5 | -9.5 | 1.1207 | 0
2016-12-11 10:00 | 0 | 0 | 0 | 0 | -22.9293 | -12.6055 | 100.1873 | -10.1873 | -11.7834 | 41.7569 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9 | -9 | 1.119 | 0
2016-12-11 11:00 | 0 | 0 | 0 | 0 | -22.9329 | 2.39 | 99.9101 | -9.9101 | 2.2344 | 39.968 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.4 | -8.4 | 1.1169 | 0
2016-12-11 12:00 | 0 | 0 | 0 | 0 | -22.9366 | 17.3855 | 100.4555 | -10.4555 | 16.2495 | 43.3739 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.3 | -8.3 | 1.1165 | 0
2016-12-11 13:00 | 0 | 0 | 0 | 0 | -22.9402 | 32.381 | 101.7909 | -11.7909 | 30.2532 | 50.9407 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.2 | -8.2 | 1.1162 | 0
2016-12-11 14:00 | 0 | 0 | 0 | 0 | -22.9437 | 47.3765 | 103.8364 | -13.8364 | 44.2553 | 61.1378 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-12-11 15:00 | 0 | 0 | 0 | 0 | -22.9473 | 62.372 | 106.4714 | -16.4714 | 58.2965 | 72.8622 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-12-11 16:00 | 0 | 0 | 0 | 0 | -22.9509 | 77.3674 | 109.5409 | -19.5409 | 72.4521 | 85.4787 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.5 | -7.5 | 1.1138 | 0
2016-12-11 17:00 | 0 | 0 | 0 | 0 | -22.9544 | 92.3629 | 112.862 | -22.862 | 86.8293 | 98.6339 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.7 | -5.7 | 1.1075 | 0
2016-12-11 18:00 | 0 | 0 | 0 | 0 | -22.958 | 107.3584 | 116.229 | -26.229 | 101.5544 | 112.1222 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.1 | -5.1 | 1.1054 | 0
2016-12-11 19:00 | 0 | 0 | 0 | 0 | -22.9615 | 122.3539 | 119.4185 | -29.4185 | 116.7511 | 125.8129 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5 | -5 | 1.105 | 0
2016-12-11 20:00 | 0 | 0 | 0 | 0 | -22.965 | 137.3493 | 122.1975 | -32.1975 | 132.5068 | 139.6043 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.1 | -5.1 | 1.1054 | 0
2016-12-11 21:00 | 0 | 0 | 0 | 0 | -22.9685 | 152.3448 | 124.3391 | -34.3391 | 148.8317 | 153.3689 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.5 | -5.5 | 1.1067 | 0
2016-12-11 22:00 | 0 | 0 | 0 | 0 | -22.9719 | 167.3403 | 125.6486 | -35.6486 | 165.6224 | 166.6812 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.5 | -4.5 | 1.1033 | 0
2016-12-11 23:00 | 0 | 0 | 0 | 0 | -22.9754 | 182.3358 | 125.9965 | -35.9965 | -177.3418 | 173.6033 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-12-12 | 0 | 0 | 0 | 0 | -22.9789 | -162.6688 | 125.3473 | -35.3473 | -160.3521 | 162.6537 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.5 | -4.5 | 1.1033 | 0
2016-12-12 01:00 | 0 | 0 | 0 | 0 | -22.9823 | -147.6733 | 123.7678 | -33.7678 | -143.6862 | 149.0948 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-12-12 02:00 | 0 | 0 | 0 | 0 | -22.9857 | -132.6779 | 121.4113 | -31.4113 | -127.531 | 135.3038 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4 | -4 | 1.1015 | 0
2016-12-12 03:00 | 0 | 0 | 0 | 0 | -22.9892 | -117.6824 | 118.486 | -28.486 | -111.9525 | 121.5357 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-12-12 04:00 | 0 | 0 | 0 | 0 | -22.9926 | -102.6869 | 115.2231 | -25.2231 | -96.9125 | 107.9004 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1036 | 0
2016-12-12 05:00 | 0 | 0 | 0 | 0 | -22.9959 | -87.6915 | 111.8538 | -21.8538 | -82.3082 | 94.5045 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.5 | -4.5 | 1.1033 | 0
2016-12-12 06:00 | 0 | 0 | 0 | 0 | -22.9993 | -72.696 | 108.5969 | -18.5969 | -68.0123 | 81.4969 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1036 | 0
2016-12-12 07:00 | 0 | 0 | 0 | 0 | -23.0027 | -57.7006 | 105.6515 | -15.6515 | -53.9027 | 69.1199 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.7 | -4.7 | 1.1039 | 0
2016-12-12 08:00 | 0 | 0 | 0 | 0 | -23.006 | -42.7051 | 103.1922 | -13.1922 | -39.8816 | 57.7973 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-12-12 09:00 | 0 | 0 | 0 | 0 | -23.0094 | -27.7097 | 101.364 | -11.364 | -25.8843 | 48.291 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.1 | -6.1 | 1.1088 | 0
2016-12-12 10:00 | 0 | 0 | 0 | 0 | -23.0127 | -12.7142 | 100.2756 | -10.2756 | -11.8808 | 41.8676 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-12-12 11:00 | 0 | 0 | 0 | 0 | -23.016 | 2.2812 | 99.9922 | -9.9922 | 2.1319 | 40.0448 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.1 | -5.1 | 1.1054 | 0
2016-12-12 12:00 | 0 | 0 | 0 | 0 | -23.0193 | 17.2766 | 100.5312 | -10.5312 | 16.1421 | 43.4076 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.3 | -5.3 | 1.106 | 0
2016-12-12 13:00 | 0 | 0 | 0 | 0 | -23.0226 | 32.2721 | 101.8603 | -11.8603 | 30.1412 | 50.9366 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.1 | -5.1 | 1.1054 | 0
2016-12-12 14:00 | 0 | 0 | 0 | 0 | -23.0259 | 47.2675 | 103.9002 | -13.9002 | 44.1391 | 61.1062 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-12-12 15:00 | 0 | 0 | 0 | 0 | -23.0291 | 62.263 | 106.5305 | -16.5305 | 58.1763 | 72.8111 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5 | -5 | 1.105 | 0
2016-12-12 16:00 | 0 | 0 | 0 | 0 | -23.0324 | 77.2584 | 109.5967 | -19.5967 | 72.3284 | 85.4134 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.3 | -5.3 | 1.106 | 0
2016-12-12 17:00 | 0 | 0 | 0 | 0 | -23.0356 | 92.2538 | 112.9162 | -22.9162 | 86.7021 | 98.5576 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-12-12 18:00 | 0 | 0 | 0 | 0 | -23.0388 | 107.2492 | 116.2834 | -26.2834 | 101.424 | 112.0369 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.2 | -6.2 | 1.1092 | 0
2016-12-12 19:00 | 0 | 0 | 0 | 0 | -23.042 | 122.2447 | 119.4751 | -29.4751 | 116.6182 | 125.7195 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.7 | -5.7 | 1.1075 | 0
2016-12-12 20:00 | 0 | 0 | 0 | 0 | -23.0452 | 137.2401 | 122.2582 | -32.2582 | 132.3728 | 139.503 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.8 | -5.8 | 1.1078 | 0
2016-12-12 21:00 | 0 | 0 | 0 | 0 | -23.0484 | 152.2355 | 124.4056 | -34.4056 | 148.6985 | 153.2582 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.8 | -5.8 | 1.1078 | 0
2016-12-12 22:00 | 0 | 0 | 0 | 0 | -23.0515 | 167.2309 | 125.7219 | -35.7219 | 165.4927 | 166.5566 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.8 | -5.8 | 1.1078 | 0
2016-12-12 23:00 | 0 | 0 | 0 | 0 | -23.0547 | 182.2264 | 126.0769 | -36.0769 | -177.4652 | 173.563 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6 | -6 | 1.1085 | 0
2016-12-13 | 0 | 0 | 0 | 0 | -23.0578 | -162.7782 | 125.4343 | -35.4343 | -160.4673 | 162.7264 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.3 | -6.3 | 1.1096 | 0
2016-12-13 01:00 | 0 | 0 | 0 | 0 | -23.061 | -147.7828 | 123.8602 | -33.8602 | -143.7925 | 149.1879 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.4 | -6.4 | 1.1099 | 0
2016-12-13 02:00 | 0 | 0 | 0 | 0 | -23.0641 | -132.7874 | 121.5077 | -31.5077 | -127.6291 | 135.4062 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.5 | -6.5 | 1.1102 | 0
2016-12-13 03:00 | 0 | 0 | 0 | 0 | -23.0672 | -117.792 | 118.5849 | -28.5849 | -112.0441 | 121.6446 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.3 | -6.3 | 1.1096 | 0
2016-12-13 04:00 | 0 | 0 | 0 | 0 | -23.0703 | -102.7966 | 115.323 | -25.323 | -96.9998 | 108.0145 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.2 | -6.2 | 1.1092 | 0
2016-12-13 05:00 | 0 | 0 | 0 | 0 | -23.0733 | -87.8012 | 111.9534 | -21.9534 | -82.3935 | 94.6233 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.8 | -5.8 | 1.1078 | 0
2016-12-13 06:00 | 0 | 0 | 0 | 0 | -23.0764 | -72.8058 | 108.695 | -18.695 | -68.0976 | 81.6198 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.9 | -5.9 | 1.1081 | 0
2016-12-13 07:00 | 0 | 0 | 0 | 0 | -23.0794 | -57.8104 | 105.7467 | -15.7467 | -53.9898 | 69.2458 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.9 | -5.9 | 1.1081 | 0
2016-12-13 08:00 | 0 | 0 | 0 | 0 | -23.0825 | -42.815 | 103.2836 | -13.2836 | -39.9718 | 57.9239 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.9 | -5.9 | 1.1081 | 0
2016-12-13 09:00 | 0 | 0 | 0 | 0 | -23.0855 | -27.8196 | 101.4506 | -11.4506 | -25.9786 | 48.4125 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.8 | -5.8 | 1.1078 | 0
2016-12-13 10:00 | 0 | 0 | 0 | 0 | -23.0885 | -12.8242 | 100.3564 | -10.3564 | -11.9796 | 41.9715 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.4 | -5.4 | 1.1064 | 0
2016-12-13 11:00 | 0 | 0 | 0 | 0 | -23.0915 | 2.1712 | 100.0668 | -10.0668 | 2.0284 | 40.1144 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-12-13 12:00 | 0 | 0 | 0 | 0 | -23.0945 | 17.1666 | 100.5994 | -10.5994 | 16.0342 | 43.4344 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-12-13 13:00 | 0 | 0 | 0 | 0 | -23.0975 | 32.162 | 101.9222 | -11.9222 | 30.029 | 50.9266 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.7 | -4.7 | 1.1039 | 0
2016-12-13 14:00 | 0 | 0 | 0 | 0 | -23.1004 | 47.1574 | 103.9564 | -13.9564 | 44.0231 | 61.0694 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-12-13 15:00 | 0 | 0 | 0 | 0 | -23.1034 | 62.1528 | 106.5821 | -16.5821 | 58.0568 | 72.7557 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-12-13 16:00 | 0 | 0 | 0 | 0 | -23.1063 | 77.1482 | 109.6449 | -19.6449 | 72.2053 | 85.3446 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.8 | -3.8 | 1.1008 | 0
2016-12-13 17:00 | 0 | 0 | 0 | 0 | -23.1092 | 92.1435 | 112.9627 | -22.9627 | 86.5757 | 98.4785 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.3 | -3.3 | 1.0991 | 0
2016-12-13 18:00 | 0 | 0 | 0 | 0 | -23.1121 | 107.1389 | 116.3302 | -26.3302 | 101.2945 | 111.9494 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-12-13 19:00 | 0 | 0 | 0 | 0 | -23.115 | 122.1343 | 119.524 | -29.524 | 116.486 | 125.6245 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-12-13 20:00 | 0 | 0 | 0 | 0 | -23.1179 | 137.1297 | 122.3112 | -32.3112 | 132.239 | 139.4007 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.2 | -2.2 | 1.0952 | 0
2016-12-13 21:00 | 0 | 0 | 0 | 0 | -23.1207 | 152.125 | 124.4644 | -34.4644 | 148.5651 | 153.1474 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-12-13 22:00 | 0 | 0 | 0 | 0 | -23.1236 | 167.1204 | 125.7875 | -35.7875 | 165.3622 | 166.4342 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.0945 | 0
2016-12-13 23:00 | 0 | 0 | 0 | 0 | -23.1264 | 182.1158 | 126.1497 | -36.1497 | -177.5902 | 173.5279 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-12-14 | 0 | 0 | 0 | 0 | -23.1292 | -162.8888 | 125.5138 | -35.5138 | -160.5846 | 162.8016 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-12-14 01:00 | 0 | 0 | 0 | 0 | -23.132 | -147.8935 | 123.9453 | -33.9453 | -143.9014 | 149.2823 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-12-14 02:00 | 0 | 0 | 0 | 0 | -23.1348 | -132.8981 | 121.5969 | -31.5969 | -127.7302 | 135.5094 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-12-14 03:00 | 0 | 0 | 0 | 0 | -23.1376 | -117.9027 | 118.6766 | -28.6766 | -112.1389 | 121.7535 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-12-14 04:00 | 0 | 0 | 0 | 0 | -23.1404 | -102.9074 | 115.4158 | -25.4158 | -97.0903 | 108.1281 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-12-14 05:00 | 0 | 0 | 0 | 0 | -23.1432 | -87.912 | 112.0459 | -22.0459 | -82.4818 | 94.7408 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-12-14 06:00 | 0 | 0 | 0 | 0 | -23.1459 | -72.9167 | 108.7858 | -18.7858 | -68.1857 | 81.7406 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-12-14 07:00 | 0 | 0 | 0 | 0 | -23.1486 | -57.9213 | 105.8348 | -15.8348 | -54.0794 | 69.3687 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-12-14 08:00 | 0 | 0 | 0 | 0 | -23.1513 | -42.9259 | 103.3677 | -13.3677 | -40.0642 | 58.0464 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-12-14 09:00 | 0 | 0 | 0 | 0 | -23.154 | -27.9306 | 101.5297 | -11.5297 | -26.0746 | 48.5284 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-12-14 10:00 | 0 | 0 | 0 | 0 | -23.1567 | -12.9352 | 100.4298 | -10.4298 | -12.0797 | 42.0687 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-12-14 11:00 | 0 | 0 | 0 | 0 | -23.1594 | 2.0601 | 100.1339 | -10.1339 | 1.9241 | 40.1766 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-12-14 12:00 | 0 | 0 | 0 | 0 | -23.1621 | 17.0555 | 100.6599 | -10.6599 | 15.9258 | 43.4542 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-12-14 13:00 | 0 | 0 | 0 | 0 | -23.1647 | 32.0508 | 101.9764 | -11.9764 | 29.9169 | 50.9105 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-12-14 14:00 | 0 | 0 | 0 | 0 | -23.1674 | 47.0462 | 104.0049 | -14.0049 | 43.9075 | 61.0276 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-12-14 15:00 | 0 | 0 | 0 | 0 | -23.17 | 62.0415 | 106.626 | -16.626 | 57.9379 | 72.6962 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-12-14 16:00 | 0 | 0 | 0 | 0 | -23.1726 | 77.0368 | 109.6855 | -19.6855 | 72.0832 | 85.2723 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0861 | 0
2016-12-14 17:00 | 0 | 0 | 0 | 0 | -23.1752 | 92.0322 | 113.0017 | -23.0017 | 86.4503 | 98.3965 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-12-14 18:00 | 0 | 0 | 0 | 0 | -23.1778 | 107.0275 | 116.3693 | -26.3693 | 101.1659 | 111.8596 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0843 | 0
2016-12-14 19:00 | 0 | 0 | 0 | 0 | -23.1804 | 122.0229 | 119.5653 | -29.5653 | 116.3546 | 125.5279 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.0822 | 0
2016-12-14 20:00 | 0 | 0 | 0 | 0 | -23.1829 | 137.0182 | 122.3566 | -32.3566 | 132.1057 | 139.2975 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.083 | 0
2016-12-14 21:00 | 0 | 0 | 0 | 0 | -23.1855 | 152.0135 | 124.5154 | -34.5154 | 148.4316 | 153.0367 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0861 | 0
2016-12-14 22:00 | 0 | 0 | 0 | 0 | -23.188 | 167.0089 | 125.8454 | -35.8454 | 165.231 | 166.3141 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-12-14 23:00 | 0 | 0 | 0 | 0 | -23.1905 | 182.0042 | 126.2148 | -36.2148 | -177.7165 | 173.4981 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0847 | 0
2016-12-15 | 0 | 0 | 0 | 0 | -23.193 | -163.0005 | 125.5857 | -35.5857 | -160.704 | 162.8795 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0837 | 0
2016-12-15 01:00 | 0 | 0 | 0 | 0 | -23.1955 | -148.0052 | 124.0229 | -34.0229 | -144.0129 | 149.3782 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0843 | 0
2016-12-15 02:00 | 0 | 0 | 0 | 0 | -23.198 | -133.0098 | 121.6787 | -31.6787 | -127.8342 | 135.6131 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.084 | 0
2016-12-15 03:00 | 0 | 0 | 0 | 0 | -23.2005 | -118.0145 | 118.7612 | -28.7612 | -112.2367 | 121.8625 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0847 | 0
2016-12-15 04:00 | 0 | 0 | 0 | 0 | -23.2029 | -103.0192 | 115.5014 | -25.5014 | -97.1839 | 108.2411 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-12-15 05:00 | 0 | 0 | 0 | 0 | -23.2053 | -88.0239 | 112.1313 | -22.1313 | -82.5731 | 94.857 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-12-15 06:00 | 0 | 0 | 0 | 0 | -23.2078 | -73.0285 | 108.8695 | -18.8695 | -68.2767 | 81.8593 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-12-15 07:00 | 0 | 0 | 0 | 0 | -23.2102 | -58.0332 | 105.9156 | -15.9156 | -54.1716 | 69.4886 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-12-15 08:00 | 0 | 0 | 0 | 0 | -23.2126 | -43.0379 | 103.4444 | -13.4444 | -40.1587 | 58.1646 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-12-15 09:00 | 0 | 0 | 0 | 0 | -23.215 | -28.0426 | 101.6014 | -11.6014 | -26.1724 | 48.6388 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-12-15 10:00 | 0 | 0 | 0 | 0 | -23.2173 | -13.0473 | 100.4956 | -10.4956 | -12.1811 | 42.1591 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-12-15 11:00 | 0 | 0 | 0 | 0 | -23.2197 | 1.948 | 100.1933 | -10.1933 | 1.8189 | 40.2315 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-12-15 12:00 | 0 | 0 | 0 | 0 | -23.222 | 16.9433 | 100.7128 | -10.7128 | 15.817 | 43.4671 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-12-15 13:00 | 0 | 0 | 0 | 0 | -23.2244 | 31.9386 | 102.023 | -12.023 | 29.8048 | 50.8883 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-12-15 14:00 | 0 | 0 | 0 | 0 | -23.2267 | 46.934 | 104.0459 | -14.0459 | 43.7924 | 60.9808 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-12-15 15:00 | 0 | 0 | 0 | 0 | -23.229 | 61.9293 | 106.6622 | -16.6622 | 57.8198 | 72.6324 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-12-15 16:00 | 0 | 0 | 0 | 0 | -23.2313 | 76.9246 | 109.7185 | -19.7185 | 71.9621 | 85.1966 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-12-15 17:00 | 0 | 0 | 0 | 0 | -23.2336 | 91.9199 | 113.033 | -23.033 | 86.326 | 98.3118 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-12-15 18:00 | 0 | 0 | 0 | 0 | -23.2358 | 106.9152 | 116.4008 | -26.4008 | 101.0384 | 111.7677 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-12-15 19:00 | 0 | 0 | 0 | 0 | -23.2381 | 121.9105 | 119.5989 | -29.5989 | 116.2241 | 125.4299 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-12-15 20:00 | 0 | 0 | 0 | 0 | -23.2403 | 136.9058 | 122.3942 | -32.3942 | 131.973 | 139.1935 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0861 | 0
2016-12-15 21:00 | 0 | 0 | 0 | 0 | -23.2426 | 151.9011 | 124.5587 | -34.5587 | 148.2983 | 152.9263 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-12-15 22:00 | 0 | 0 | 0 | 0 | -23.2448 | 166.8964 | 125.8956 | -35.8956 | 165.0992 | 166.1964 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-12-15 23:00 | 0 | 0 | 0 | 0 | -23.247 | 181.8916 | 126.2723 | -36.2723 | -177.844 | 173.4736 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-12-16 | 0 | 0 | 0 | 0 | -23.2492 | -163.1131 | 125.65 | -35.65 | -160.8253 | 162.96 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0847 | 0
2016-12-16 01:00 | 0 | 0 | 0 | 0 | -23.2513 | -148.1178 | 124.093 | -34.093 | -144.1268 | 149.4755 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-12-16 02:00 | 0 | 0 | 0 | 0 | -23.2535 | -133.1225 | 121.7532 | -31.7532 | -127.9409 | 135.7175 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-12-16 03:00 | 0 | 0 | 0 | 0 | -23.2556 | -118.1272 | 118.8384 | -28.8384 | -112.3375 | 121.9713 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-12-16 04:00 | 0 | 0 | 0 | 0 | -23.2578 | -103.1319 | 115.5799 | -25.5799 | -97.2804 | 108.3533 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0833 | 0
2016-12-16 05:00 | 0 | 0 | 0 | 0 | -23.2599 | -88.1366 | 112.2094 | -22.2094 | -82.6673 | 94.9718 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-12-16 06:00 | 0 | 0 | 0 | 0 | -23.262 | -73.1413 | 108.946 | -18.946 | -68.3703 | 81.9758 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-12-16 07:00 | 0 | 0 | 0 | 0 | -23.2641 | -58.1461 | 105.989 | -15.989 | -54.2661 | 69.6053 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-12-16 08:00 | 0 | 0 | 0 | 0 | -23.2662 | -43.1508 | 103.5138 | -13.5138 | -40.2553 | 58.2786 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0861 | 0
2016-12-16 09:00 | 0 | 0 | 0 | 0 | -23.2682 | -28.1555 | 101.6656 | -11.6656 | -26.2718 | 48.7437 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-12-16 10:00 | 0 | 0 | 0 | 0 | -23.2703 | -13.1602 | 100.5539 | -10.5539 | -12.2837 | 42.2427 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-12-16 11:00 | 0 | 0 | 0 | 0 | -23.2723 | 1.8351 | 100.2452 | -10.2452 | 1.713 | 40.2789 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-12-16 12:00 | 0 | 0 | 0 | 0 | -23.2744 | 16.8303 | 100.7581 | -10.7581 | 15.708 | 43.473 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-12-16 13:00 | 0 | 0 | 0 | 0 | -23.2764 | 31.8256 | 102.062 | -12.062 | 29.6929 | 50.8601 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-12-16 14:00 | 0 | 0 | 0 | 0 | -23.2784 | 46.8209 | 104.0792 | -14.0792 | 43.6778 | 60.9289 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-12-16 15:00 | 0 | 0 | 0 | 0 | -23.2804 | 61.8161 | 106.6909 | -16.6909 | 57.7025 | 72.5646 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-12-16 16:00 | 0 | 0 | 0 | 0 | -23.2823 | 76.8114 | 109.7439 | -19.7439 | 71.842 | 85.1175 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-12-16 17:00 | 0 | 0 | 0 | 0 | -23.2843 | 91.8067 | 113.0567 | -23.0567 | 86.203 | 98.2245 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-12-16 18:00 | 0 | 0 | 0 | 0 | -23.2862 | 106.8019 | 116.4246 | -26.4246 | 100.9121 | 111.6739 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-12-16 19:00 | 0 | 0 | 0 | 0 | -23.2882 | 121.7972 | 119.6248 | -29.6248 | 116.0947 | 125.3304 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.0945 | 0
2016-12-16 20:00 | 0 | 0 | 0 | 0 | -23.2901 | 136.7925 | 122.4241 | -32.4241 | 131.8411 | 139.0889 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-12-16 21:00 | 0 | 0 | 0 | 0 | -23.292 | 151.7877 | 124.5943 | -34.5943 | 148.1651 | 152.8162 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-12-16 22:00 | 0 | 0 | 0 | 0 | -23.2939 | 166.783 | 125.938 | -35.938 | 164.9671 | 166.0813 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.8 | -2.8 | 1.0973 | 0
2016-12-16 23:00 | 0 | 0 | 0 | 0 | -23.2958 | 181.7783 | 126.322 | -36.322 | -177.9727 | 173.4547 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.8 | -2.8 | 1.0973 | 0
2016-12-17 | 0 | 0 | 0 | 0 | -23.2976 | -163.2265 | 125.7067 | -35.7067 | -160.9483 | 163.0431 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-12-17 01:00 | 0 | 0 | 0 | 0 | -23.2995 | -148.2312 | 124.1556 | -34.1556 | -144.243 | 149.5741 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-12-17 02:00 | 0 | 0 | 0 | 0 | -23.3013 | -133.236 | 121.8203 | -31.8203 | -128.0503 | 135.8224 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-12-17 03:00 | 0 | 0 | 0 | 0 | -23.3031 | -118.2407 | 118.9083 | -28.9083 | -112.4412 | 122.08 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-12-17 04:00 | 0 | 0 | 0 | 0 | -23.305 | -103.2454 | 115.651 | -25.651 | -97.3798 | 108.4647 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-12-17 05:00 | 0 | 0 | 0 | 0 | -23.3068 | -88.2502 | 112.2802 | -22.2802 | -82.7643 | 95.0851 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0872 | 0
2016-12-17 06:00 | 0 | 0 | 0 | 0 | -23.3085 | -73.2549 | 109.0151 | -19.0151 | -68.4665 | 82.09 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-12-17 07:00 | 0 | 0 | 0 | 0 | -23.3103 | -58.2597 | 106.0552 | -16.0552 | -54.3629 | 69.7189 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-12-17 08:00 | 0 | 0 | 0 | 0 | -23.3121 | -43.2644 | 103.5757 | -13.5757 | -40.3538 | 58.3883 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.084 | 0
2016-12-17 09:00 | 0 | 0 | 0 | 0 | -23.3138 | -28.2692 | 101.7223 | -11.7223 | -26.3727 | 48.8429 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.0822 | 0
2016-12-17 10:00 | 0 | 0 | 0 | 0 | -23.3156 | -13.2739 | 100.6046 | -10.6046 | -12.3874 | 42.3195 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.0822 | 0
2016-12-17 11:00 | 0 | 0 | 0 | 0 | -23.3173 | 1.7213 | 100.2894 | -10.2894 | 1.6065 | 40.319 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0819 | 0
2016-12-17 12:00 | 0 | 0 | 0 | 0 | -23.319 | 16.7165 | 100.7957 | -10.7957 | 15.5989 | 43.472 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0837 | 0
2016-12-17 13:00 | 0 | 0 | 0 | 0 | -23.3207 | 31.7118 | 102.0932 | -12.0932 | 29.5813 | 50.8259 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0826 | 0
2016-12-17 14:00 | 0 | 0 | 0 | 0 | -23.3224 | 46.707 | 104.1048 | -14.1048 | 43.5638 | 60.8721 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-12-17 15:00 | 0 | 0 | 0 | 0 | -23.324 | 61.7023 | 106.7119 | -16.7119 | 57.5862 | 72.4926 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-12-17 16:00 | 0 | 0 | 0 | 0 | -23.3257 | 76.6975 | 109.7616 | -19.7616 | 71.7232 | 85.0352 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-12-17 17:00 | 0 | 0 | 0 | 0 | -23.3273 | 91.6927 | 113.0727 | -23.0727 | 86.0813 | 98.1346 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0837 | 0
2016-12-17 18:00 | 0 | 0 | 0 | 0 | -23.3289 | 106.688 | 116.4408 | -26.4408 | 100.7872 | 111.578 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0833 | 0
2016-12-17 19:00 | 0 | 0 | 0 | 0 | -23.3305 | 121.6832 | 119.6431 | -29.6431 | 115.9664 | 125.2297 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0843 | 0
2016-12-17 20:00 | 0 | 0 | 0 | 0 | -23.3321 | 136.6785 | 122.4463 | -32.4463 | 131.71 | 138.9837 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-12-17 21:00 | 0 | 0 | 0 | 0 | -23.3337 | 151.6737 | 124.6221 | -34.6221 | 148.0324 | 152.7066 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-12-17 22:00 | 0 | 0 | 0 | 0 | -23.3353 | 166.6689 | 125.9726 | -35.9726 | 164.8347 | 165.9688 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-12-17 23:00 | 0 | 0 | 0 | 0 | -23.3369 | 181.6642 | 126.364 | -36.364 | -178.1024 | 173.4413 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-12-18 | 0 | 0 | 0 | 0 | -23.3384 | -163.3406 | 125.7557 | -35.7557 | -161.073 | 163.129 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-12-18 01:00 | 0 | 0 | 0 | 0 | -23.3399 | -148.3454 | 124.2107 | -34.2107 | -144.3615 | 149.674 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-12-18 02:00 | 0 | 0 | 0 | 0 | -23.3415 | -133.3501 | 121.88 | -31.88 | -128.1623 | 135.9277 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-12-18 03:00 | 0 | 0 | 0 | 0 | -23.343 | -118.3549 | 118.9709 | -28.9709 | -112.5476 | 122.1885 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-12-18 04:00 | 0 | 0 | 0 | 0 | -23.3444 | -103.3597 | 115.7149 | -25.7149 | -97.4821 | 108.5752 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.0885 | 0
2016-12-18 05:00 | 0 | 0 | 0 | 0 | -23.3459 | -88.3645 | 112.3438 | -22.3438 | -82.864 | 95.1968 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-12-18 06:00 | 0 | 0 | 0 | 0 | -23.3474 | -73.3692 | 109.0769 | -19.0769 | -68.5652 | 82.2019 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-12-18 07:00 | 0 | 0 | 0 | 0 | -23.3488 | -58.374 | 106.1139 | -16.1139 | -54.4619 | 69.8291 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-12-18 08:00 | 0 | 0 | 0 | 0 | -23.3503 | -43.3788 | 103.6301 | -13.6301 | -40.4542 | 58.4935 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-12-18 09:00 | 0 | 0 | 0 | 0 | -23.3517 | -28.3836 | 101.7714 | -11.7714 | -26.4751 | 48.9364 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-12-18 10:00 | 0 | 0 | 0 | 0 | -23.3531 | -13.3884 | 100.6476 | -10.6476 | -12.4921 | 42.3894 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0864 | 0
2016-12-18 11:00 | 0 | 0 | 0 | 0 | -23.3545 | 1.6069 | 100.3259 | -10.3259 | 1.4995 | 40.3517 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-12-18 12:00 | 0 | 0 | 0 | 0 | -23.3559 | 16.6021 | 100.8256 | -10.8256 | 15.4896 | 43.4639 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0868 | 0
2016-12-18 13:00 | 0 | 0 | 0 | 0 | -23.3573 | 31.5973 | 102.1168 | -12.1168 | 29.4701 | 50.7857 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-12-18 14:00 | 0 | 0 | 0 | 0 | -23.3586 | 46.5925 | 104.1228 | -14.1228 | 43.4507 | 60.8103 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-12-18 15:00 | 0 | 0 | 0 | 0 | -23.36 | 61.5877 | 106.7253 | -16.7253 | 57.471 | 72.4167 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-12-18 16:00 | 0 | 0 | 0 | 0 | -23.3613 | 76.583 | 109.7718 | -19.7718 | 71.6057 | 84.9497 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-12-18 17:00 | 0 | 0 | 0 | 0 | -23.3626 | 91.5782 | 113.0812 | -23.0812 | 85.961 | 98.0421 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-12-18 18:00 | 0 | 0 | 0 | 0 | -23.3639 | 106.5734 | 116.4494 | -26.4494 | 100.6637 | 111.4804 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-12-18 19:00 | 0 | 0 | 0 | 0 | -23.3652 | 121.5686 | 119.6536 | -29.6536 | 115.8395 | 125.1278 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-12-18 20:00 | 0 | 0 | 0 | 0 | -23.3665 | 136.5638 | 122.4607 | -32.4607 | 131.5799 | 138.878 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-12-18 21:00 | 0 | 0 | 0 | 0 | -23.3677 | 151.559 | 124.6421 | -34.6421 | 147.9001 | 152.5975 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-12-18 22:00 | 0 | 0 | 0 | 0 | -23.369 | 166.5542 | 125.9994 | -35.9994 | 164.7021 | 165.859 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-12-18 23:00 | 0 | 0 | 0 | 0 | -23.3702 | 181.5494 | 126.3982 | -36.3982 | -178.2329 | 173.4336 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.2 | -2.2 | 1.0952 | 0
2016-12-19 | 0 | 0 | 0 | 0 | -23.3715 | -163.4554 | 125.797 | -35.797 | -161.1992 | 163.2175 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.3 | -3.3 | 1.0991 | 0
2016-12-19 01:00 | 0 | 0 | 0 | 0 | -23.3727 | -148.4601 | 124.2581 | -34.2581 | -144.4819 | 149.7751 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.9 | -3.9 | 1.1012 | 0
2016-12-19 02:00 | 0 | 0 | 0 | 0 | -23.3739 | -133.4649 | 121.9321 | -31.9321 | -128.2768 | 136.0334 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.0994 | 0
2016-12-19 03:00 | 0 | 0 | 0 | 0 | -23.375 | -118.4697 | 119.0261 | -29.0261 | -112.6566 | 122.2966 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-12-19 04:00 | 0 | 0 | 0 | 0 | -23.3762 | -103.4745 | 115.7714 | -25.7714 | -97.587 | 108.6847 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-12-19 05:00 | 0 | 0 | 0 | 0 | -23.3774 | -88.4793 | 112.4 | -22.4 | -82.9663 | 95.3068 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-12-19 06:00 | 0 | 0 | 0 | 0 | -23.3785 | -73.4841 | 109.1313 | -19.1313 | -68.6663 | 82.3113 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-12-19 07:00 | 0 | 0 | 0 | 0 | -23.3796 | -58.4889 | 106.1651 | -16.1651 | -54.5631 | 69.9359 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-12-19 08:00 | 0 | 0 | 0 | 0 | -23.3807 | -43.4937 | 103.677 | -13.677 | -40.5564 | 58.5943 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-12-19 09:00 | 0 | 0 | 0 | 0 | -23.3819 | -28.4985 | 101.813 | -11.813 | -26.5789 | 49.0241 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2 | 2 | 1.0805 | 0
2016-12-19 10:00 | 0 | 0 | 0 | 0 | -23.3829 | -13.5033 | 100.6831 | -10.6831 | -12.5978 | 42.4523 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0833 | 0
2016-12-19 11:00 | 0 | 0 | 0 | 0 | -23.384 | 1.4919 | 100.3548 | -10.3548 | 1.392 | 40.377 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-12-19 12:00 | 0 | 0 | 0 | 0 | -23.3851 | 16.4871 | 100.8478 | -10.8478 | 15.3804 | 43.4489 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0843 | 0
2016-12-19 13:00 | 0 | 0 | 0 | 0 | -23.3861 | 31.4823 | 102.1328 | -12.1328 | 29.3593 | 50.7395 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-12-19 14:00 | 0 | 0 | 0 | 0 | -23.3872 | 46.4775 | 104.1331 | -14.1331 | 43.3384 | 60.7436 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-12-19 15:00 | 0 | 0 | 0 | 0 | -23.3882 | 61.4727 | 106.731 | -16.731 | 57.357 | 72.3368 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0819 | 0
2016-12-19 16:00 | 0 | 0 | 0 | 0 | -23.3892 | 76.4679 | 109.7743 | -19.7743 | 71.4896 | 84.861 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0809 | 0
2016-12-19 17:00 | 0 | 0 | 0 | 0 | -23.3902 | 91.4631 | 113.082 | -23.082 | 85.8423 | 97.9473 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-12-19 18:00 | 0 | 0 | 0 | 0 | -23.3912 | 106.4582 | 116.4503 | -26.4503 | 100.5418 | 111.3809 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0826 | 0
2016-12-19 19:00 | 0 | 0 | 0 | 0 | -23.3921 | 121.4534 | 119.6565 | -29.6565 | 115.714 | 125.0247 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0833 | 0
2016-12-19 20:00 | 0 | 0 | 0 | 0 | -23.3931 | 136.4486 | 122.4674 | -32.4674 | 131.4509 | 138.772 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0837 | 0
2016-12-19 21:00 | 0 | 0 | 0 | 0 | -23.394 | 151.4438 | 124.6543 | -34.6543 | 147.7685 | 152.4891 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0837 | 0
2016-12-19 22:00 | 0 | 0 | 0 | 0 | -23.3949 | 166.439 | 126.0185 | -36.0185 | 164.5695 | 165.752 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0837 | 0
2016-12-19 23:00 | 0 | 0 | 0 | 0 | -23.3959 | 181.4342 | 126.4246 | -36.4246 | -178.3641 | 173.4316 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.083 | 0
2016-12-20 | 0 | 0 | 0 | 0 | -23.3968 | -163.5706 | 125.8306 | -35.8306 | -161.3268 | 163.3088 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-12-20 01:00 | 0 | 0 | 0 | 0 | -23.3976 | -148.5754 | 124.298 | -34.298 | -144.6044 | 149.8775 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-12-20 02:00 | 0 | 0 | 0 | 0 | -23.3985 | -133.5802 | 121.9767 | -31.9767 | -128.3936 | 136.1395 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0837 | 0
2016-12-20 03:00 | 0 | 0 | 0 | 0 | -23.3994 | -118.585 | 119.0738 | -29.0738 | -112.7682 | 122.4044 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.0822 | 0
2016-12-20 04:00 | 0 | 0 | 0 | 0 | -23.4002 | -103.5899 | 115.8204 | -25.8204 | -97.6945 | 108.7932 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0837 | 0
2016-12-20 05:00 | 0 | 0 | 0 | 0 | -23.4011 | -88.5947 | 112.4488 | -22.4488 | -83.0711 | 95.4151 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0837 | 0
2016-12-20 06:00 | 0 | 0 | 0 | 0 | -23.4019 | -73.5995 | 109.1783 | -19.1783 | -68.7697 | 82.4181 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.083 | 0
2016-12-20 07:00 | 0 | 0 | 0 | 0 | -23.4027 | -58.6043 | 106.2089 | -16.2089 | -54.6663 | 70.0393 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.084 | 0
2016-12-20 08:00 | 0 | 0 | 0 | 0 | -23.4035 | -43.6091 | 103.7164 | -13.7164 | -40.6603 | 58.6905 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-12-20 09:00 | 0 | 0 | 0 | 0 | -23.4043 | -28.6139 | 101.8469 | -11.8469 | -26.684 | 49.1061 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-12-20 10:00 | 0 | 0 | 0 | 0 | -23.405 | -13.6188 | 100.7108 | -10.7108 | -12.7042 | 42.5083 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0872 | 0
2016-12-20 11:00 | 0 | 0 | 0 | 0 | -23.4058 | 1.3764 | 100.3759 | -10.3759 | 1.2842 | 40.3948 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-12-20 12:00 | 0 | 0 | 0 | 0 | -23.4065 | 16.3716 | 100.8623 | -10.8623 | 15.2713 | 43.4269 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-12-20 13:00 | 0 | 0 | 0 | 0 | -23.4072 | 31.3668 | 102.141 | -12.141 | 29.2491 | 50.6874 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.2 | -2.2 | 1.0952 | 0
2016-12-20 14:00 | 0 | 0 | 0 | 0 | -23.4079 | 46.362 | 104.1357 | -14.1357 | 43.227 | 60.672 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-12-20 15:00 | 0 | 0 | 0 | 0 | -23.4086 | 61.3572 | 106.7291 | -16.7291 | 57.2443 | 72.253 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-12-20 16:00 | 0 | 0 | 0 | 0 | -23.4093 | 76.3523 | 109.7692 | -19.7692 | 71.375 | 84.7692 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-12-20 17:00 | 0 | 0 | 0 | 0 | -23.41 | 91.3475 | 113.0753 | -23.0753 | 85.7252 | 97.8501 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0872 | 0
2016-12-20 18:00 | 0 | 0 | 0 | 0 | -23.4107 | 106.3427 | 116.4436 | -26.4436 | 100.4216 | 111.2798 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0854 | 0
2016-12-20 19:00 | 0 | 0 | 0 | 0 | -23.4113 | 121.3379 | 119.6517 | -29.6517 | 115.5901 | 124.9207 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0843 | 0
2016-12-20 20:00 | 0 | 0 | 0 | 0 | -23.4119 | 136.333 | 122.4664 | -32.4664 | 131.3232 | 138.6657 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-12-20 21:00 | 0 | 0 | 0 | 0 | -23.4126 | 151.3282 | 124.6588 | -34.6588 | 147.6377 | 152.3815 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0861 | 0
2016-12-20 22:00 | 0 | 0 | 0 | 0 | -23.4132 | 166.3234 | 126.0297 | -36.0297 | 164.4372 | 165.6477 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.083 | 0
2016-12-20 23:00 | 0 | 0 | 0 | 0 | -23.4137 | 181.3186 | 126.4432 | -36.4432 | -178.4958 | 173.4354 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-12-21 | 0 | 0 | 0 | 0 | -23.4143 | -163.6863 | 125.8564 | -35.8564 | -161.4556 | 163.4028 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0837 | 0
2016-12-21 01:00 | 0 | 0 | 0 | 0 | -23.4149 | -148.6911 | 124.3301 | -34.3301 | -144.7286 | 149.981 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0819 | 0
2016-12-21 02:00 | 0 | 0 | 0 | 0 | -23.4154 | -133.6959 | 122.0137 | -32.0137 | -128.5125 | 136.2458 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0837 | 0
2016-12-21 03:00 | 0 | 0 | 0 | 0 | -23.416 | -118.7007 | 119.114 | -29.114 | -112.8823 | 122.5117 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0801 | 0
2016-12-21 04:00 | 0 | 0 | 0 | 0 | -23.4165 | -103.7056 | 115.8621 | -25.8621 | -97.8046 | 108.9005 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-12-21 05:00 | 0 | 0 | 0 | 0 | -23.417 | -88.7104 | 112.4902 | -22.4902 | -83.1783 | 95.5215 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0738 | 0
2016-12-21 06:00 | 0 | 0 | 0 | 0 | -23.4175 | -73.7152 | 109.2178 | -19.2178 | -68.8754 | 82.5223 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-12-21 07:00 | 0 | 0 | 0 | 0 | -23.418 | -58.72 | 106.2452 | -16.2452 | -54.7715 | 70.1392 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0759 | 0
2016-12-21 08:00 | 0 | 0 | 0 | 0 | -23.4184 | -43.7249 | 103.7482 | -13.7482 | -40.7657 | 58.782 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0777 | 0
2016-12-21 09:00 | 0 | 0 | 0 | 0 | -23.4189 | -28.7297 | 101.8732 | -11.8732 | -26.7902 | 49.1822 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0791 | 0
2016-12-21 10:00 | 0 | 0 | 0 | 0 | -23.4193 | -13.7345 | 100.7309 | -10.7309 | -12.8114 | 42.5574 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.077 | 0
2016-12-21 11:00 | 0 | 0 | 0 | 0 | -23.4198 | 1.2606 | 100.3894 | -10.3894 | 1.176 | 40.4052 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0798 | 0
2016-12-21 12:00 | 0 | 0 | 0 | 0 | -23.4202 | 16.2558 | 100.8691 | -10.8691 | 15.1624 | 43.398 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-12-21 13:00 | 0 | 0 | 0 | 0 | -23.4206 | 31.251 | 102.1415 | -12.1415 | 29.1395 | 50.6293 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.4 | 3.4 | 1.0756 | 0
2016-12-21 14:00 | 0 | 0 | 0 | 0 | -23.421 | 46.2461 | 104.1307 | -14.1307 | 43.1167 | 60.5956 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-12-21 15:00 | 0 | 0 | 0 | 0 | -23.4214 | 61.2413 | 106.7196 | -16.7196 | 57.133 | 72.1653 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0801 | 0
2016-12-21 16:00 | 0 | 0 | 0 | 0 | -23.4217 | 76.2365 | 109.7564 | -19.7564 | 71.2621 | 84.6745 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-12-21 17:00 | 0 | 0 | 0 | 0 | -23.4221 | 91.2316 | 113.0609 | -23.0609 | 85.61 | 97.7506 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0837 | 0
2016-12-21 18:00 | 0 | 0 | 0 | 0 | -23.4224 | 106.2268 | 116.4293 | -26.4293 | 100.3032 | 111.1771 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.0822 | 0
2016-12-21 19:00 | 0 | 0 | 0 | 0 | -23.4227 | 121.222 | 119.6392 | -29.6392 | 115.4679 | 124.8157 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0812 | 0
2016-12-21 20:00 | 0 | 0 | 0 | 0 | -23.423 | 136.2171 | 122.4576 | -32.4576 | 131.1969 | 138.5593 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.083 | 0
2016-12-21 21:00 | 0 | 0 | 0 | 0 | -23.4233 | 151.2123 | 124.6554 | -34.6554 | 147.5078 | 152.2747 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0816 | 0
2016-12-21 22:00 | 0 | 0 | 0 | 0 | -23.4236 | 166.2075 | 126.033 | -36.033 | 164.3051 | 165.5464 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0816 | 0
2016-12-21 23:00 | 0 | 0 | 0 | 0 | -23.4239 | 181.2026 | 126.4539 | -36.4539 | -178.628 | 173.445 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0826 | 0
2016-12-22 | 0 | 0 | 0 | 0 | -23.4241 | -163.8022 | 125.8745 | -35.8745 | -161.5856 | 163.4994 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.0857 | 0
2016-12-22 01:00 | 0 | 0 | 0 | 0 | -23.4244 | -148.807 | 124.3546 | -34.3546 | -144.8545 | 150.0856 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.083 | 0
2016-12-22 02:00 | 0 | 0 | 0 | 0 | -23.4246 | -133.8119 | 122.0431 | -32.0431 | -128.6336 | 136.3522 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0795 | 0
2016-12-22 03:00 | 0 | 0 | 0 | 0 | -23.4248 | -118.8167 | 119.1466 | -29.1466 | -112.9986 | 122.6185 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-12-22 04:00 | 0 | 0 | 0 | 0 | -23.425 | -103.8215 | 115.8962 | -25.8962 | -97.917 | 109.0067 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0872 | 0
2016-12-22 05:00 | 0 | 0 | 0 | 0 | -23.4252 | -88.8264 | 112.5241 | -22.5241 | -83.2879 | 95.6261 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0837 | 0
2016-12-22 06:00 | 0 | 0 | 0 | 0 | -23.4253 | -73.8312 | 109.2499 | -19.2499 | -68.9832 | 82.6239 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0861 | 0
2016-12-22 07:00 | 0 | 0 | 0 | 0 | -23.4255 | -58.836 | 106.274 | -16.274 | -54.8786 | 70.2354 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0843 | 0
2016-12-22 08:00 | 0 | 0 | 0 | 0 | -23.4257 | -43.8409 | 103.7724 | -13.7724 | -40.8727 | 58.8689 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0819 | 0
2016-12-22 09:00 | 0 | 0 | 0 | 0 | -23.4258 | -28.8457 | 101.8918 | -11.8918 | -26.8975 | 49.2524 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0833 | 0
2016-12-22 10:00 | 0 | 0 | 0 | 0 | -23.4259 | -13.8506 | 100.7433 | -10.7433 | -12.9192 | 42.5994 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0851 | 0
2016-12-22 11:00 | 0 | 0 | 0 | 0 | -23.426 | 1.1446 | 100.3951 | -10.3951 | 1.0678 | 40.4082 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0833 | 0
2016-12-22 12:00 | 0 | 0 | 0 | 0 | -23.4261 | 16.1398 | 100.8682 | -10.8682 | 15.0539 | 43.3621 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-12-22 13:00 | 0 | 0 | 0 | 0 | -23.4262 | 31.1349 | 102.1343 | -12.1343 | 29.0307 | 50.5654 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-12-22 14:00 | 0 | 0 | 0 | 0 | -23.4262 | 46.1301 | 104.118 | -14.118 | 43.0075 | 60.5144 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-12-22 15:00 | 0 | 0 | 0 | 0 | -23.4263 | 61.1252 | 106.7025 | -16.7025 | 57.0231 | 72.0739 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-12-22 16:00 | 0 | 0 | 0 | 0 | -23.4263 | 76.1204 | 109.7361 | -19.7361 | 71.1509 | 84.5768 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-12-22 17:00 | 0 | 0 | 0 | 0 | -23.4263 | 91.1156 | 113.039 | -23.039 | 85.4966 | 97.649 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0833 | 0
2016-12-22 18:00 | 0 | 0 | 0 | 0 | -23.4264 | 106.1107 | 116.4073 | -26.4073 | 100.1867 | 111.0729 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0861 | 0
2016-12-22 19:00 | 0 | 0 | 0 | 0 | -23.4264 | 121.1059 | 119.6191 | -29.6191 | 115.3475 | 124.7099 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-12-22 20:00 | 0 | 0 | 0 | 0 | -23.4263 | 136.1011 | 122.4412 | -32.4412 | 131.0721 | 138.4527 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.0893 | 0
2016-12-22 21:00 | 0 | 0 | 0 | 0 | -23.4263 | 151.0962 | 124.6443 | -34.6443 | 147.379 | 152.1688 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.0906 | 0
2016-12-22 22:00 | 0 | 0 | 0 | 0 | -23.4263 | 166.0914 | 126.0286 | -36.0286 | 164.1734 | 165.4479 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-12-22 23:00 | 0 | 0 | 0 | 0 | -23.4262 | 181.0865 | 126.4569 | -36.4569 | -178.7604 | 173.4606 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-12-23 | 0 | 0 | 0 | 0 | -23.4261 | -163.9183 | 125.8847 | -35.8847 | -161.7165 | 163.5987 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-12-23 01:00 | 0 | 0 | 0 | 0 | -23.4261 | -148.9231 | 124.3713 | -34.3713 | -144.982 | 150.1913 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-12-23 02:00 | 0 | 0 | 0 | 0 | -23.426 | -133.928 | 122.0649 | -32.0649 | -128.7567 | 136.4588 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-12-23 03:00 | 0 | 0 | 0 | 0 | -23.4258 | -118.9328 | 119.1718 | -29.1718 | -113.1172 | 122.7246 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.0903 | 0
2016-12-23 04:00 | 0 | 0 | 0 | 0 | -23.4257 | -103.9377 | 115.9229 | -25.9229 | -98.0317 | 109.1115 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-12-23 05:00 | 0 | 0 | 0 | 0 | -23.4256 | -88.9425 | 112.5505 | -22.5505 | -83.3997 | 95.7286 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-12-23 06:00 | 0 | 0 | 0 | 0 | -23.4254 | -73.9474 | 109.2744 | -19.2744 | -69.0931 | 82.7226 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-12-23 07:00 | 0 | 0 | 0 | 0 | -23.4253 | -58.9522 | 106.2952 | -16.2952 | -54.9874 | 70.328 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-12-23 08:00 | 0 | 0 | 0 | 0 | -23.4251 | -43.957 | 103.789 | -13.789 | -40.9811 | 58.9511 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-12-23 09:00 | 0 | 0 | 0 | 0 | -23.4249 | -28.9619 | 101.9028 | -11.9028 | -27.0059 | 49.3167 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.2 | -2.2 | 1.0952 | 0
2016-12-23 10:00 | 0 | 0 | 0 | 0 | -23.4247 | -13.9667 | 100.7479 | -10.7479 | -13.0276 | 42.6345 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.8 | -2.8 | 1.0973 | 0
2016-12-23 11:00 | 0 | 0 | 0 | 0 | -23.4245 | 1.0284 | 100.3931 | -10.3931 | 0.95942 | 40.4036 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-12-23 12:00 | 0 | 0 | 0 | 0 | -23.4242 | 16.0236 | 100.8596 | -10.8596 | 14.9457 | 43.3192 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.1 | -5.1 | 1.1054 | 0
2016-12-23 13:00 | 0 | 0 | 0 | 0 | -23.424 | 31.0188 | 102.1194 | -12.1194 | 28.9227 | 50.4955 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.3 | -4.3 | 1.1025 | 0
2016-12-23 14:00 | 0 | 0 | 0 | 0 | -23.4237 | 46.0139 | 104.0977 | -14.0977 | 42.8996 | 60.4285 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.9 | -3.9 | 1.1012 | 0
2016-12-23 15:00 | 0 | 0 | 0 | 0 | -23.4235 | 61.0091 | 106.6777 | -16.6777 | 56.9148 | 71.9787 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.3 | -4.3 | 1.1025 | 0
2016-12-23 16:00 | 0 | 0 | 0 | 0 | -23.4232 | 76.0042 | 109.7083 | -19.7083 | 71.0416 | 84.4762 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-12-23 17:00 | 0 | 0 | 0 | 0 | -23.4229 | 90.9994 | 113.0095 | -23.0095 | 85.3853 | 97.5452 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.7 | -5.7 | 1.1075 | 0
2016-12-23 18:00 | 0 | 0 | 0 | 0 | -23.4226 | 105.9946 | 116.3779 | -26.3779 | 100.0723 | 110.9673 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5 | -5 | 1.105 | 0
2016-12-23 19:00 | 0 | 0 | 0 | 0 | -23.4222 | 120.9897 | 119.5914 | -29.5914 | 115.229 | 124.6033 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.1 | -5.1 | 1.1054 | 0
2016-12-23 20:00 | 0 | 0 | 0 | 0 | -23.4219 | 135.9849 | 122.417 | -32.417 | 130.949 | 138.3461 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.3 | -5.3 | 1.106 | 0
2016-12-23 21:00 | 0 | 0 | 0 | 0 | -23.4215 | 150.98 | 124.6254 | -34.6254 | 147.2513 | 152.0639 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.3 | -5.3 | 1.106 | 0
2016-12-23 22:00 | 0 | 0 | 0 | 0 | -23.4212 | 165.9752 | 126.0163 | -36.0163 | 164.0423 | 165.3523 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-12-23 23:00 | 0 | 0 | 0 | 0 | -23.4208 | 180.9703 | 126.452 | -36.452 | -178.893 | 173.482 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.5 | -6.5 | 1.1102 | 0
2016-12-24 | 0 | 0 | 0 | 0 | -23.4204 | -164.0345 | 125.8872 | -35.8872 | -161.8482 | 163.7007 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.1 | -5.1 | 1.1054 | 0
2016-12-24 01:00 | 0 | 0 | 0 | 0 | -23.42 | -149.0393 | 124.3803 | -34.3803 | -145.1109 | 150.2979 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.7 | -4.7 | 1.1039 | 0
2016-12-24 02:00 | 0 | 0 | 0 | 0 | -23.4196 | -134.0442 | 122.0791 | -32.0791 | -128.8816 | 136.5654 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1001 | 0
2016-12-24 03:00 | 0 | 0 | 0 | 0 | -23.4191 | -119.049 | 119.1893 | -29.1893 | -113.2379 | 122.83 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1001 | 0
2016-12-24 04:00 | 0 | 0 | 0 | 0 | -23.4187 | -104.0539 | 115.942 | -25.942 | -98.1486 | 109.2149 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-12-24 05:00 | 0 | 0 | 0 | 0 | -23.4182 | -89.0587 | 112.5693 | -22.5693 | -83.5136 | 95.829 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-12-24 06:00 | 0 | 0 | 0 | 0 | -23.4177 | -74.0635 | 109.2914 | -19.2914 | -69.2049 | 82.8185 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.2 | -2.2 | 1.0952 | 0
2016-12-24 07:00 | 0 | 0 | 0 | 0 | -23.4172 | -59.0684 | 106.3088 | -16.3088 | -55.0979 | 70.4169 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-12-24 08:00 | 0 | 0 | 0 | 0 | -23.4167 | -44.0732 | 103.798 | -13.798 | -41.0908 | 59.0285 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-12-24 09:00 | 0 | 0 | 0 | 0 | -23.4162 | -29.0781 | 101.9061 | -11.9061 | -27.1151 | 49.375 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-12-24 10:00 | 0 | 0 | 0 | 0 | -23.4157 | -14.0829 | 100.7449 | -10.7449 | -13.1365 | 42.6625 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-12-24 11:00 | 0 | 0 | 0 | 0 | -23.4151 | 0.91227 | 100.3833 | -10.3833 | 0.85107 | 40.3917 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-12-24 12:00 | 0 | 0 | 0 | 0 | -23.4146 | 15.9074 | 100.8432 | -10.8432 | 14.838 | 43.2694 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-12-24 13:00 | 0 | 0 | 0 | 0 | -23.414 | 30.9026 | 102.0969 | -12.0969 | 28.8157 | 50.4198 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-12-24 14:00 | 0 | 0 | 0 | 0 | -23.4134 | 45.8977 | 104.0697 | -14.0697 | 42.793 | 60.3379 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.0977 | 0
2016-12-24 15:00 | 0 | 0 | 0 | 0 | -23.4128 | 60.8929 | 106.6454 | -16.6454 | 56.8082 | 71.8799 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-12-24 16:00 | 0 | 0 | 0 | 0 | -23.4122 | 75.8881 | 109.6729 | -19.6729 | 70.9342 | 84.3729 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-12-24 17:00 | 0 | 0 | 0 | 0 | -23.4116 | 90.8832 | 112.9724 | -22.9724 | 85.276 | 97.4394 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-12-24 18:00 | 0 | 0 | 0 | 0 | -23.411 | 105.8784 | 116.3408 | -26.3408 | 99.96 | 110.8603 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-12-24 19:00 | 0 | 0 | 0 | 0 | -23.4103 | 120.8736 | 119.5561 | -29.5561 | 115.1126 | 124.4961 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.0966 | 0
2016-12-24 20:00 | 0 | 0 | 0 | 0 | -23.4096 | 135.8687 | 122.3852 | -32.3852 | 130.8277 | 138.2397 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-12-24 21:00 | 0 | 0 | 0 | 0 | -23.409 | 150.8639 | 124.5988 | -34.5988 | 147.125 | 151.96 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.098 | 0
2016-12-24 22:00 | 0 | 0 | 0 | 0 | -23.4083 | 165.859 | 125.9962 | -35.9962 | 163.9119 | 165.2596 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.0998 | 0
2016-12-24 23:00 | 0 | 0 | 0 | 0 | -23.4076 | 180.8542 | 126.4393 | -36.4393 | -179.0256 | 173.5095 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-12-25 | 0 | 0 | 0 | 0 | -23.4069 | -164.1506 | 125.8818 | -35.8818 | -161.9807 | 163.8053 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4 | -4 | 1.1015 | 0
2016-12-25 01:00 | 0 | 0 | 0 | 0 | -23.4061 | -149.1555 | 124.3815 | -34.3815 | -145.2412 | 150.4053 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.3 | -3.3 | 1.0991 | 0
2016-12-25 02:00 | 0 | 0 | 0 | 0 | -23.4054 | -134.1603 | 122.0855 | -32.0855 | -129.0083 | 136.6719 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.3 | -3.3 | 1.0991 | 0
2016-12-25 03:00 | 0 | 0 | 0 | 0 | -23.4046 | -119.1651 | 119.1992 | -29.1992 | -113.3606 | 122.9346 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.098 | 0
2016-12-25 04:00 | 0 | 0 | 0 | 0 | -23.4038 | -104.17 | 115.9535 | -25.9535 | -98.2676 | 109.3169 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.8 | -2.8 | 1.0973 | 0
2016-12-25 05:00 | 0 | 0 | 0 | 0 | -23.4031 | -89.1748 | 112.5807 | -22.5807 | -83.6295 | 95.9273 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-12-25 06:00 | 0 | 0 | 0 | 0 | -23.4023 | -74.1796 | 109.3009 | -19.3009 | -69.3185 | 82.9115 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.098 | 0
2016-12-25 07:00 | 0 | 0 | 0 | 0 | -23.4014 | -59.1845 | 106.3148 | -16.3148 | -55.2099 | 70.502 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-12-25 08:00 | 0 | 0 | 0 | 0 | -23.4006 | -44.1893 | 103.7993 | -13.7993 | -41.2018 | 59.1011 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.3 | -4.3 | 1.1025 | 0
2016-12-25 09:00 | 0 | 0 | 0 | 0 | -23.3998 | -29.1942 | 101.9018 | -11.9018 | -27.2252 | 49.4274 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-12-25 10:00 | 0 | 0 | 0 | 0 | -23.3989 | -14.199 | 100.7341 | -10.7341 | -13.2457 | 42.6835 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.9 | -3.9 | 1.1012 | 0
2016-12-25 11:00 | 0 | 0 | 0 | 0 | -23.3981 | 0.79618 | 100.3659 | -10.3659 | 0.74283 | 40.3722 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.8 | -5.8 | 1.1078 | 0
2016-12-25 12:00 | 0 | 0 | 0 | 0 | -23.3972 | 15.7913 | 100.8192 | -10.8192 | 14.7308 | 43.2127 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6 | -6 | 1.1085 | 0
2016-12-25 13:00 | 0 | 0 | 0 | 0 | -23.3963 | 30.7865 | 102.0667 | -12.0667 | 28.7096 | 50.3383 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.1 | -6.1 | 1.1088 | 0
2016-12-25 14:00 | 0 | 0 | 0 | 0 | -23.3954 | 45.7817 | 104.0341 | -14.0341 | 42.6879 | 60.2426 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.2 | -6.2 | 1.1092 | 0
2016-12-25 15:00 | 0 | 0 | 0 | 0 | -23.3945 | 60.7768 | 106.6055 | -16.6055 | 56.7034 | 71.7775 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.7 | -5.7 | 1.1075 | 0
2016-12-25 16:00 | 0 | 0 | 0 | 0 | -23.3935 | 75.772 | 109.63 | -19.63 | 70.8288 | 84.2668 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.6 | -5.6 | 1.1071 | 0
2016-12-25 17:00 | 0 | 0 | 0 | 0 | -23.3926 | 90.7672 | 112.9279 | -22.9279 | 85.1689 | 97.3317 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.9 | -4.9 | 1.1046 | 0
2016-12-25 18:00 | 0 | 0 | 0 | 0 | -23.3916 | 105.7624 | 116.2963 | -26.2963 | 99.85 | 110.7521 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.7 | -4.7 | 1.1039 | 0
2016-12-25 19:00 | 0 | 0 | 0 | 0 | -23.3906 | 120.7575 | 119.5132 | -29.5132 | 114.9983 | 124.3883 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1036 | 0
2016-12-25 20:00 | 0 | 0 | 0 | 0 | -23.3896 | 135.7527 | 122.3457 | -32.3457 | 130.7082 | 138.1333 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1001 | 0
2016-12-25 21:00 | 0 | 0 | 0 | 0 | -23.3886 | 150.7479 | 124.5644 | -34.5644 | 147.0001 | 151.8573 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.2 | -3.2 | 1.0987 | 0
2016-12-25 22:00 | 0 | 0 | 0 | 0 | -23.3876 | 165.743 | 125.9683 | -35.9683 | 163.7824 | 165.1699 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.7 | -4.7 | 1.1039 | 0
2016-12-25 23:00 | 0 | 0 | 0 | 0 | -23.3866 | 180.7382 | 126.4187 | -36.4187 | -179.158 | 173.5428 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-12-26 | 0 | 0 | 0 | 0 | -23.3856 | -164.2666 | 125.8686 | -35.8686 | -162.1136 | 163.9125 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5 | -5 | 1.105 | 0
2016-12-26 01:00 | 0 | 0 | 0 | 0 | -23.3845 | -149.2714 | 124.375 | -34.375 | -145.3725 | 150.5136 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.3 | -7.3 | 1.1131 | 0
2016-12-26 02:00 | 0 | 0 | 0 | 0 | -23.3834 | -134.2763 | 122.0843 | -32.0843 | -129.1366 | 136.7782 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.9 | -5.9 | 1.1081 | 0
2016-12-26 03:00 | 0 | 0 | 0 | 0 | -23.3823 | -119.2811 | 119.2015 | -29.2015 | -113.4851 | 123.0384 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7 | -7 | 1.112 | 0
2016-12-26 04:00 | 0 | 0 | 0 | 0 | -23.3813 | -104.2859 | 115.9575 | -25.9575 | -98.3885 | 109.4173 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.8 | -7.8 | 1.1148 | 0
2016-12-26 05:00 | 0 | 0 | 0 | 0 | -23.3801 | -89.2908 | 112.5845 | -22.5845 | -83.7473 | 96.0233 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7 | -7 | 1.112 | 0
2016-12-26 06:00 | 0 | 0 | 0 | 0 | -23.379 | -74.2956 | 109.3027 | -19.3027 | -69.4339 | 83.0015 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-12-26 07:00 | 0 | 0 | 0 | 0 | -23.3779 | -59.3004 | 106.3132 | -16.3132 | -55.3235 | 70.5832 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.1 | -8.1 | 1.1159 | 0
2016-12-26 08:00 | 0 | 0 | 0 | 0 | -23.3767 | -44.3052 | 103.793 | -13.793 | -41.3139 | 59.1688 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.2 | -8.2 | 1.1162 | 0
2016-12-26 09:00 | 0 | 0 | 0 | 0 | -23.3756 | -29.3101 | 101.8897 | -11.8897 | -27.336 | 49.4737 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.8 | -8.8 | 1.1183 | 0
2016-12-26 10:00 | 0 | 0 | 0 | 0 | -23.3744 | -14.3149 | 100.7156 | -10.7156 | -13.3552 | 42.6975 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.8 | -7.8 | 1.1148 | 0
2016-12-26 11:00 | 0 | 0 | 0 | 0 | -23.3732 | 0.6803 | 100.3407 | -10.3407 | 0.63478 | 40.3453 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-12-26 12:00 | 0 | 0 | 0 | 0 | -23.372 | 15.6755 | 100.7874 | -10.7874 | 14.6244 | 43.1491 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.4 | -6.4 | 1.1099 | 0
2016-12-26 13:00 | 0 | 0 | 0 | 0 | -23.3708 | 30.6707 | 102.0288 | -12.0288 | 28.6047 | 50.2511 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8 | -8 | 1.1155 | 0
2016-12-26 14:00 | 0 | 0 | 0 | 0 | -23.3695 | 45.6658 | 103.991 | -13.991 | 42.5842 | 60.1428 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.6 | -7.6 | 1.1141 | 0
2016-12-26 15:00 | 0 | 0 | 0 | 0 | -23.3683 | 60.661 | 106.5581 | -16.5581 | 56.6004 | 71.6716 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.8 | -7.8 | 1.1148 | 0
2016-12-26 16:00 | 0 | 0 | 0 | 0 | -23.367 | 75.6562 | 109.5795 | -19.5795 | 70.7255 | 84.1582 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.8 | -7.8 | 1.1148 | 0
2016-12-26 17:00 | 0 | 0 | 0 | 0 | -23.3658 | 90.6514 | 112.8759 | -22.8759 | 85.0642 | 97.2221 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.2 | -8.2 | 1.1162 | 0
2016-12-26 18:00 | 0 | 0 | 0 | 0 | -23.3645 | 105.6466 | 116.2442 | -26.2442 | 99.7423 | 110.6427 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8 | -8 | 1.1155 | 0
2016-12-26 19:00 | 0 | 0 | 0 | 0 | -23.3632 | 120.6417 | 119.4628 | -29.4628 | 114.8863 | 124.28 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.2 | -8.2 | 1.1162 | 0
2016-12-26 20:00 | 0 | 0 | 0 | 0 | -23.3619 | 135.6369 | 122.2986 | -32.2986 | 130.5908 | 138.0272 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.7 | -7.7 | 1.1144 | 0
2016-12-26 21:00 | 0 | 0 | 0 | 0 | -23.3606 | 150.6321 | 124.5223 | -34.5223 | 146.8769 | 151.7557 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8 | -8 | 1.1155 | 0
2016-12-26 22:00 | 0 | 0 | 0 | 0 | -23.3592 | 165.6273 | 125.9327 | -35.9327 | 163.6539 | 165.083 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.6 | -5.6 | 1.1071 | 0
2016-12-26 23:00 | 0 | 0 | 0 | 0 | -23.3579 | 180.6225 | 126.3903 | -36.3903 | -179.2901 | 173.5822 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-12-27 | 0 | 0 | 0 | 0 | -23.3565 | -164.3824 | 125.8477 | -35.8477 | -162.247 | 164.0221 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.7 | -3.7 | 1.1004 | 0
2016-12-27 01:00 | 0 | 0 | 0 | 0 | -23.3551 | -149.3872 | 124.3607 | -34.3607 | -145.5049 | 150.6225 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.092 | 0
2016-12-27 02:00 | 0 | 0 | 0 | 0 | -23.3537 | -134.392 | 122.0753 | -32.0753 | -129.2663 | 136.8843 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-12-27 03:00 | 0 | 0 | 0 | 0 | -23.3523 | -119.3968 | 119.1962 | -29.1962 | -113.6114 | 123.1411 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-12-27 04:00 | 0 | 0 | 0 | 0 | -23.3509 | -104.4016 | 115.9538 | -25.9538 | -98.5112 | 109.5161 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.0949 | 0
2016-12-27 05:00 | 0 | 0 | 0 | 0 | -23.3495 | -89.4064 | 112.5806 | -22.5806 | -83.8669 | 96.1171 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.2 | -2.2 | 1.0952 | 0
2016-12-27 06:00 | 0 | 0 | 0 | 0 | -23.348 | -74.4112 | 109.297 | -19.297 | -69.5509 | 83.0885 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-12-27 07:00 | 0 | 0 | 0 | 0 | -23.3466 | -59.416 | 106.304 | -16.304 | -55.4384 | 70.6605 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-12-27 08:00 | 0 | 0 | 0 | 0 | -23.3451 | -44.4209 | 103.779 | -13.779 | -41.427 | 59.2316 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.097 | 0
2016-12-27 09:00 | 0 | 0 | 0 | 0 | -23.3436 | -29.4257 | 101.8699 | -11.8699 | -27.4475 | 49.5141 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.0962 | 0
2016-12-27 10:00 | 0 | 0 | 0 | 0 | -23.3421 | -14.4305 | 100.6894 | -10.6894 | -13.4649 | 42.7044 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.098 | 0
2016-12-27 11:00 | 0 | 0 | 0 | 0 | -23.3406 | 0.56472 | 100.3078 | -10.3078 | 0.52701 | 40.311 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.0994 | 0
2016-12-27 12:00 | 0 | 0 | 0 | 0 | -23.3391 | 15.5599 | 100.748 | -10.748 | 14.5186 | 43.0786 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-12-27 13:00 | 0 | 0 | 0 | 0 | -23.3375 | 30.5551 | 101.9833 | -11.9833 | 28.501 | 50.1581 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-12-27 14:00 | 0 | 0 | 0 | 0 | -23.336 | 45.5503 | 103.9402 | -13.9402 | 42.4822 | 60.0386 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-12-27 15:00 | 0 | 0 | 0 | 0 | -23.3344 | 60.5455 | 106.5032 | -16.5032 | 56.4994 | 71.5623 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.1 | -5.1 | 1.1054 | 0
2016-12-27 16:00 | 0 | 0 | 0 | 0 | -23.3328 | 75.5407 | 109.5217 | -19.5217 | 70.6245 | 84.0469 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1036 | 0
2016-12-27 17:00 | 0 | 0 | 0 | 0 | -23.3312 | 90.5359 | 112.8164 | -22.8164 | 84.9618 | 97.1107 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.6 | -5.6 | 1.1071 | 0
2016-12-27 18:00 | 0 | 0 | 0 | 0 | -23.3296 | 105.5311 | 116.1847 | -26.1847 | 99.637 | 110.5321 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1036 | 0
2016-12-27 19:00 | 0 | 0 | 0 | 0 | -23.328 | 120.5263 | 119.4048 | -29.4048 | 114.7766 | 124.1712 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.3 | -4.3 | 1.1025 | 0
2016-12-27 20:00 | 0 | 0 | 0 | 0 | -23.3264 | 135.5215 | 122.244 | -32.244 | 130.4755 | 137.9214 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-12-27 21:00 | 0 | 0 | 0 | 0 | -23.3247 | 150.5167 | 124.4725 | -34.4725 | 146.7553 | 151.6553 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.3 | -3.3 | 1.0991 | 0
2016-12-27 22:00 | 0 | 0 | 0 | 0 | -23.323 | 165.5119 | 125.8893 | -35.8893 | 163.5265 | 164.9991 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.5 | -4.5 | 1.1033 | 0
2016-12-27 23:00 | 0 | 0 | 0 | 0 | -23.3214 | 180.5071 | 126.3541 | -36.3541 | -179.4218 | 173.6275 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-12-28 | 0 | 0 | 0 | 0 | -23.3197 | -164.4977 | 125.8189 | -35.8189 | -162.3807 | 164.1342 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-12-28 01:00 | 0 | 0 | 0 | 0 | -23.318 | -149.5025 | 124.3386 | -34.3386 | -145.6382 | 150.7321 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.4 | -5.4 | 1.1064 | 0
2016-12-28 02:00 | 0 | 0 | 0 | 0 | -23.3163 | -134.5073 | 122.0587 | -32.0587 | -129.3974 | 136.99 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-12-28 03:00 | 0 | 0 | 0 | 0 | -23.3145 | -119.5121 | 119.1832 | -29.1832 | -113.7393 | 123.2428 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.1 | -6.1 | 1.1088 | 0
2016-12-28 04:00 | 0 | 0 | 0 | 0 | -23.3128 | -104.5169 | 115.9426 | -25.9426 | -98.6357 | 109.6131 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.8 | -5.8 | 1.1078 | 0
2016-12-28 05:00 | 0 | 0 | 0 | 0 | -23.311 | -89.5217 | 112.5692 | -22.5692 | -83.9883 | 96.2084 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.7 | -5.7 | 1.1075 | 0
2016-12-28 06:00 | 0 | 0 | 0 | 0 | -23.3093 | -74.5265 | 109.2836 | -19.2836 | -69.6695 | 83.1723 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-12-28 07:00 | 0 | 0 | 0 | 0 | -23.3075 | -59.5313 | 106.2872 | -16.2872 | -55.5546 | 70.7338 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.1 | -4.1 | 1.1018 | 0
2016-12-28 08:00 | 0 | 0 | 0 | 0 | -23.3057 | -44.5361 | 103.7573 | -13.7573 | -41.5411 | 59.2894 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.0956 | 0
2016-12-28 09:00 | 0 | 0 | 0 | 0 | -23.3039 | -29.5409 | 101.8424 | -11.8424 | -27.5595 | 49.5483 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.4 | -2.4 | 1.0959 | 0
2016-12-28 10:00 | 0 | 0 | 0 | 0 | -23.3021 | -14.5456 | 100.6555 | -10.6555 | -13.5747 | 42.7042 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-12-28 11:00 | 0 | 0 | 0 | 0 | -23.3002 | 0.44957 | 100.2673 | -10.2673 | 0.41962 | 40.2693 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-12-28 12:00 | 0 | 0 | 0 | 0 | -23.2984 | 15.4448 | 100.7009 | -10.7009 | 14.4138 | 43.0013 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-12-28 13:00 | 0 | 0 | 0 | 0 | -23.2965 | 30.44 | 101.9303 | -11.9303 | 28.3986 | 50.0594 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.0889 | 0
2016-12-28 14:00 | 0 | 0 | 0 | 0 | -23.2946 | 45.4352 | 103.882 | -13.882 | 42.3819 | 59.9298 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-12-28 15:00 | 0 | 0 | 0 | 0 | -23.2927 | 60.4304 | 106.4408 | -16.4408 | 56.4004 | 71.4496 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-12-28 16:00 | 0 | 0 | 0 | 0 | -23.2908 | 75.4256 | 109.4564 | -19.4564 | 70.5257 | 83.9333 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.0917 | 0
2016-12-28 17:00 | 0 | 0 | 0 | 0 | -23.2889 | 90.4209 | 112.7496 | -22.7496 | 84.8619 | 96.9976 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-12-28 18:00 | 0 | 0 | 0 | 0 | -23.287 | 105.4161 | 116.1178 | -26.1178 | 99.5343 | 110.4206 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-12-28 19:00 | 0 | 0 | 0 | 0 | -23.2851 | 120.4113 | 119.3394 | -29.3394 | 114.6695 | 124.0621 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-12-28 20:00 | 0 | 0 | 0 | 0 | -23.2831 | 135.4065 | 122.1817 | -32.1817 | 130.3624 | 137.8159 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-12-28 21:00 | 0 | 0 | 0 | 0 | -23.2811 | 150.4017 | 124.4151 | -34.4151 | 146.6356 | 151.5563 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-12-28 22:00 | 0 | 0 | 0 | 0 | -23.2791 | 165.397 | 125.8381 | -35.8381 | 163.4003 | 164.918 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-12-28 23:00 | 0 | 0 | 0 | 0 | -23.2772 | 180.3922 | 126.3101 | -36.3101 | -179.5529 | 173.6788 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.0878 | 0
2016-12-29 | 0 | 0 | 0 | 0 | -23.2751 | -164.6126 | 125.7822 | -35.7822 | -162.5145 | 164.2487 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-12-29 01:00 | 0 | 0 | 0 | 0 | -23.2731 | -149.6174 | 124.3088 | -34.3088 | -145.7722 | 150.8422 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.0875 | 0
2016-12-29 02:00 | 0 | 0 | 0 | 0 | -23.2711 | -134.6221 | 122.0343 | -32.0343 | -129.5297 | 137.0953 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.0882 | 0
2016-12-29 03:00 | 0 | 0 | 0 | 0 | -23.269 | -119.6269 | 119.1625 | -29.1625 | -113.8687 | 123.3433 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.0896 | 0
2016-12-29 04:00 | 0 | 0 | 0 | 0 | -23.267 | -104.6317 | 115.9237 | -25.9237 | -98.7618 | 109.7083 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-12-29 05:00 | 0 | 0 | 0 | 0 | -23.2649 | -89.6365 | 112.5502 | -22.5502 | -84.1112 | 96.2973 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-12-29 06:00 | 0 | 0 | 0 | 0 | -23.2628 | -74.6412 | 109.2627 | -19.2627 | -69.7895 | 83.2529 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.0938 | 0
2016-12-29 07:00 | 0 | 0 | 0 | 0 | -23.2607 | -59.646 | 106.2627 | -16.2627 | -55.672 | 70.8031 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-12-29 08:00 | 0 | 0 | 0 | 0 | -23.2586 | -44.6508 | 103.728 | -13.728 | -41.656 | 59.3422 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-12-29 09:00 | 0 | 0 | 0 | 0 | -23.2564 | -29.6555 | 101.8073 | -11.8073 | -27.6719 | 49.5765 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-12-29 10:00 | 0 | 0 | 0 | 0 | -23.2543 | -14.6603 | 100.6139 | -10.6139 | -13.6845 | 42.697 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-12-29 11:00 | 0 | 0 | 0 | 0 | -23.2521 | 0.33494 | 100.219 | -10.219 | 0.3127 | 40.2201 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.0924 | 0
2016-12-29 12:00 | 0 | 0 | 0 | 0 | -23.25 | 15.3302 | 100.6462 | -10.6462 | 14.3098 | 42.9171 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-12-29 13:00 | 0 | 0 | 0 | 0 | -23.2478 | 30.3254 | 101.8696 | -11.8696 | 28.2976 | 49.9552 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-12-29 14:00 | 0 | 0 | 0 | 0 | -23.2456 | 45.3207 | 103.8162 | -13.8162 | 42.2833 | 59.8168 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-12-29 15:00 | 0 | 0 | 0 | 0 | -23.2434 | 60.3159 | 106.371 | -16.371 | 56.3035 | 71.3336 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-12-29 16:00 | 0 | 0 | 0 | 0 | -23.2412 | 75.3111 | 109.3837 | -19.3837 | 70.4294 | 83.8172 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-12-29 17:00 | 0 | 0 | 0 | 0 | -23.2389 | 90.3064 | 112.6754 | -22.6754 | 84.7646 | 96.8829 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-12-29 18:00 | 0 | 0 | 0 | 0 | -23.2367 | 105.3016 | 116.0435 | -26.0435 | 99.4343 | 110.3081 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.0928 | 0
2016-12-29 19:00 | 0 | 0 | 0 | 0 | -23.2344 | 120.2969 | 119.2666 | -29.2666 | 114.5649 | 123.9527 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.0914 | 0
2016-12-29 20:00 | 0 | 0 | 0 | 0 | -23.2321 | 135.2921 | 122.112 | -32.112 | 130.2518 | 137.7108 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.091 | 0
2016-12-29 21:00 | 0 | 0 | 0 | 0 | -23.2298 | 150.2874 | 124.3501 | -34.3501 | 146.5178 | 151.4585 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.0899 | 0
2016-12-29 22:00 | 0 | 0 | 0 | 0 | -23.2275 | 165.2826 | 125.7792 | -35.7792 | 163.2756 | 164.8397 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-12-29 23:00 | 0 | 0 | 0 | 0 | -23.2252 | 180.2779 | 126.2584 | -36.2584 | -179.6833 | 173.736 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-12-30 | 0 | 0 | 0 | 0 | -23.2229 | -164.7269 | 125.7378 | -35.7378 | -162.6483 | 164.3654 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.0941 | 0
2016-12-30 01:00 | 0 | 0 | 0 | 0 | -23.2205 | -149.7316 | 124.2712 | -34.2712 | -145.9069 | 150.9527 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.0935 | 0
2016-12-30 02:00 | 0 | 0 | 0 | 0 | -23.2182 | -134.7364 | 122.0022 | -32.0022 | -129.663 | 137.2001 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.0931 | 0
2016-12-30 03:00 | 0 | 0 | 0 | 0 | -23.2158 | -119.7411 | 119.1342 | -29.1342 | -113.9995 | 123.4426 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.0983 | 0
2016-12-30 04:00 | 0 | 0 | 0 | 0 | -23.2134 | -104.7459 | 115.8972 | -25.8972 | -98.8894 | 109.8017 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.0994 | 0
2016-12-30 05:00 | 0 | 0 | 0 | 0 | -23.211 | -89.7506 | 112.5236 | -22.5236 | -84.2355 | 96.3836 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1001 | 0
2016-12-30 06:00 | 0 | 0 | 0 | 0 | -23.2086 | -74.7554 | 109.2341 | -19.2341 | -69.9108 | 83.3303 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.2 | -4.2 | 1.1022 | 0
2016-12-30 07:00 | 0 | 0 | 0 | 0 | -23.2062 | -59.7601 | 106.2306 | -16.2306 | -55.7904 | 70.8683 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-12-30 08:00 | 0 | 0 | 0 | 0 | -23.2037 | -44.7648 | 103.691 | -13.691 | -41.7717 | 59.39 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.4 | -4.4 | 1.1029 | 0
2016-12-30 09:00 | 0 | 0 | 0 | 0 | -23.2013 | -29.7696 | 101.7645 | -11.7645 | -27.7847 | 49.5986 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1036 | 0
2016-12-30 10:00 | 0 | 0 | 0 | 0 | -23.1988 | -14.7743 | 100.5647 | -10.5647 | -13.7942 | 42.6828 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.8 | -4.8 | 1.1043 | 0
2016-12-30 11:00 | 0 | 0 | 0 | 0 | -23.1964 | 0.22095 | 100.1631 | -10.1631 | 0.20632 | 40.1636 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.2 | -5.2 | 1.1057 | 0
2016-12-30 12:00 | 0 | 0 | 0 | 0 | -23.1939 | 15.2162 | 100.5838 | -10.5838 | 14.2069 | 42.8262 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.1 | -5.1 | 1.1054 | 0
2016-12-30 13:00 | 0 | 0 | 0 | 0 | -23.1914 | 30.2115 | 101.8014 | -11.8014 | 28.198 | 49.8454 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.3 | -5.3 | 1.106 | 0
2016-12-30 14:00 | 0 | 0 | 0 | 0 | -23.1888 | 45.2067 | 103.743 | -13.743 | 42.1866 | 59.6994 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.8 | -5.8 | 1.1078 | 0
2016-12-30 15:00 | 0 | 0 | 0 | 0 | -23.1863 | 60.202 | 106.2937 | -16.2937 | 56.2089 | 71.2144 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6 | -6 | 1.1085 | 0
2016-12-30 16:00 | 0 | 0 | 0 | 0 | -23.1838 | 75.1973 | 109.3037 | -19.3037 | 70.3356 | 83.6988 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.8 | -5.8 | 1.1078 | 0
2016-12-30 17:00 | 0 | 0 | 0 | 0 | -23.1812 | 90.1926 | 112.5939 | -22.5939 | 84.67 | 96.7666 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.1 | -6.1 | 1.1088 | 0
2016-12-30 18:00 | 0 | 0 | 0 | 0 | -23.1786 | 105.1878 | 115.9619 | -25.9619 | 99.3371 | 110.1948 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.7 | -6.7 | 1.111 | 0
2016-12-30 19:00 | 0 | 0 | 0 | 0 | -23.176 | 120.1831 | 119.1864 | -29.1864 | 114.4631 | 123.8431 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.1 | -7.1 | 1.1123 | 0
2016-12-30 20:00 | 0 | 0 | 0 | 0 | -23.1734 | 135.1784 | 122.0348 | -32.0348 | 130.1436 | 137.6062 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.3 | -7.3 | 1.1131 | 0
2016-12-30 21:00 | 0 | 0 | 0 | 0 | -23.1708 | 150.1737 | 124.2775 | -34.2775 | 146.4021 | 151.362 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.4 | -7.4 | 1.1134 | 0
2016-12-30 22:00 | 0 | 0 | 0 | 0 | -23.1682 | 165.1689 | 125.7126 | -35.7126 | 163.1524 | 164.7642 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7 | -7 | 1.112 | 0
2016-12-30 23:00 | 0 | 0 | 0 | 0 | -23.1656 | 180.1642 | 126.1988 | -36.1988 | -179.8129 | 173.7992 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.8 | -7.8 | 1.1148 | 0
2016-12-31 | 0 | 0 | 0 | 0 | -23.1629 | -164.8405 | 125.6857 | -35.6857 | -162.782 | 164.4843 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.5 | -7.5 | 1.1138 | 0
2016-12-31 01:00 | 0 | 0 | 0 | 0 | -23.1603 | -149.8452 | 124.2258 | -34.2258 | -146.042 | 151.0635 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.6 | -7.6 | 1.1141 | 0
2016-12-31 02:00 | 0 | 0 | 0 | 0 | -23.1576 | -134.8499 | 121.9624 | -31.9624 | -129.7974 | 137.3042 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.5 | -7.5 | 1.1138 | 0
2016-12-31 03:00 | 0 | 0 | 0 | 0 | -23.1549 | -119.8546 | 119.0982 | -29.0982 | -114.1315 | 123.5405 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.5 | -7.5 | 1.1138 | 0
2016-12-31 04:00 | 0 | 0 | 0 | 0 | -23.1522 | -104.8594 | 115.8631 | -25.8631 | -99.0184 | 109.893 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.9 | -7.9 | 1.1152 | 0
2016-12-31 05:00 | 0 | 0 | 0 | 0 | -23.1495 | -89.8641 | 112.4894 | -22.4894 | -84.3613 | 96.4672 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.7 | -7.7 | 1.1144 | 0
2016-12-31 06:00 | 0 | 0 | 0 | 0 | -23.1467 | -74.8688 | 109.1979 | -19.1979 | -70.0334 | 83.4043 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.2 | -7.2 | 1.1127 | 0
2016-12-31 07:00 | 0 | 0 | 0 | 0 | -23.144 | -59.8735 | 106.1908 | -16.1908 | -55.9098 | 70.9294 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.3 | -7.3 | 1.1131 | 0
2016-12-31 08:00 | 0 | 0 | 0 | 0 | -23.1412 | -44.8782 | 103.6464 | -13.6464 | -41.888 | 59.4328 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.2 | -7.2 | 1.1127 | 0
2016-12-31 09:00 | 0 | 0 | 0 | 0 | -23.1385 | -29.8829 | 101.714 | -11.714 | -27.8978 | 49.6146 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.5 | -7.5 | 1.1138 | 0
2016-12-31 10:00 | 0 | 0 | 0 | 0 | -23.1357 | -14.8876 | 100.5077 | -10.5077 | -13.9037 | 42.6615 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.6 | -6.6 | 1.1106 | 0
2016-12-31 11:00 | 0 | 0 | 0 | 0 | -23.1329 | 0.10769 | 100.0996 | -10.0996 | 0.10059 | 40.0997 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.5 | -6.5 | 1.1102 | 0
2016-12-31 12:00 | 0 | 0 | 0 | 0 | -23.1301 | 15.103 | 100.5139 | -10.5139 | 14.1051 | 42.7286 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.3 | -6.3 | 1.1096 | 0
2016-12-31 13:00 | 0 | 0 | 0 | 0 | -23.1272 | 30.0983 | 101.7257 | -11.7257 | 28.1 | 49.7301 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.7 | -6.7 | 1.111 | 0
2016-12-31 14:00 | 0 | 0 | 0 | 0 | -23.1244 | 45.0936 | 103.6623 | -13.6623 | 42.0919 | 59.5778 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.9 | -6.9 | 1.1117 | 0
2016-12-31 15:00 | 0 | 0 | 0 | 0 | -23.1216 | 60.0889 | 106.2092 | -16.2092 | 56.1166 | 71.092 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.2 | -6.2 | 1.1092 | 0
2016-12-31 16:00 | 0 | 0 | 0 | 0 | -23.1187 | 75.0842 | 109.2163 | -19.2163 | 70.2443 | 83.5782 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.9 | -6.9 | 1.1117 | 0
2016-12-31 17:00 | 0 | 0 | 0 | 0 | -23.1158 | 90.0795 | 112.5051 | -22.5051 | 84.5781 | 96.6489 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.9 | -6.9 | 1.1117 | 0
2016-12-31 18:00 | 0 | 0 | 0 | 0 | -23.1129 | 105.0748 | 115.873 | -25.873 | 99.2426 | 110.0807 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.9 | -6.9 | 1.1117 | 0
2016-12-31 19:00 | 0 | 0 | 0 | 0 | -23.11 | 120.0701 | 119.0988 | -29.0988 | 114.364 | 123.7334 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7 | -7 | 1.112 | 0
2016-12-31 20:00 | 0 | 0 | 0 | 0 | -23.1071 | 135.0654 | 121.9501 | -31.9501 | 130.038 | 137.5022 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.4 | -7.4 | 1.1134 | 0
2016-12-31 21:00 | 0 | 0 | 0 | 0 | -23.1042 | 150.0607 | 124.1973 | -34.1973 | 146.2887 | 151.2669 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.5 | -7.5 | 1.1138 | 0
2016-12-31 22:00 | 0 | 0 | 0 | 0 | -23.1012 | 165.0561 | 125.6384 | -35.6384 | 163.0308 | 164.6915 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.3 | -7.3 | 1.1131 | 0
2016-12-31 23:00 | 0 | 0 | 0 | 0 | -23.0983 | 180.0514 | 126.1316 | -36.1316 | -179.9415 | 173.8682 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.7 | -7.7 | 1.1144 | 0