## Summary
Hornsund photovoltaic capacity factor
Site | Hornsund
Latitude [deg] | 76.9667
Longitude [deg E] | 15.7167
Surface tilt [deg] | 60
Surface azimuth [deg] | 0
Minimum ground albedo [-] | 0.2
Maximum ground albedo [-] | 0.8
Albedo model | rho(t) from 2015 Hornsund/Fuglebekken snow-cover reference
2015 snow-cover points | 17 May 90%; 10 Jun 75%; 15 Jun 50%; 20 Jun 25%; 27 Jun 10%; 06 Jul <2%
Interpolation | Linear between observed 2015 SCE points
Before 17 May | SCE = 1.0 -> rho = rho_max
From 06 July onward | SCE = 0.0 -> rho = rho_min; autumn return not imposed
Derating factor [-] | 0.82
Hourly conversion | linear
Direct input interpretation | BHI
Temperature correction | ON - SEKLIMA hourly air temperature
NOCT [°C] | 45
Temperature coefficient [1/°C] | -0.004
Reference cell temperature [°C] | 25
NOCT reference ambient temperature [°C] | 20
NOCT reference irradiance [W/m²] | 800
Temperature source UTC offset [h] | 1
Year | Processed hours | Specific production (kWh/kWp) | Mean CF | Maximum CF | Mean POA irradiance (W/m²)
2015 | 8760 | 612.068 | 0.069871 | 0.75437 | 80.9604

## Hourly 2015
Date and time UTC | GHI horizontal (W/m²) | DHI horizontal (W/m²) | BHI horizontal / source Direct (W/m²) | Derived DNI (W/m²) | Solar declination (°) | Hour angle (°) | Solar zenith (°) | Solar elevation (°) | Solar azimuth (°) | PV incidence angle (°) | POA direct (W/m²) | POA diffuse (W/m²) | Ground albedo rho(t) (-) | Snow cover fraction - 2015 reference (-) | POA ground reflected (W/m²) | POA global (W/m²) | Air temperature (°C) | Cell temperature (°C) | Temperature factor (-) | Capacity factor (kW/kWp)
2015-01-01 | 0 | 0 | 0 | 0 | -23.0954 | -164.9532 | 125.6258 | -35.6258 | -162.9151 | 164.6051 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.4 | -5.4 | 1.1216 | 0
2015-01-01 01:00 | 0 | 0 | 0 | 0 | -23.0924 | -149.9578 | 124.1728 | -34.1728 | -146.1773 | 151.1743 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.1 | -6.1 | 1.1244 | 0
2015-01-01 02:00 | 0 | 0 | 0 | 0 | -23.0894 | -134.9625 | 121.9149 | -31.9149 | -129.9323 | 137.4075 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.9 | -6.9 | 1.1276 | 0
2015-01-01 03:00 | 0 | 0 | 0 | 0 | -23.0864 | -119.9672 | 119.0546 | -29.0546 | -114.2645 | 123.6369 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.5 | -6.5 | 1.126 | 0
2015-01-01 04:00 | 0 | 0 | 0 | 0 | -23.0834 | -104.9719 | 115.8214 | -25.8214 | -99.1485 | 109.9822 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.4 | -6.4 | 1.1256 | 0
2015-01-01 05:00 | 0 | 0 | 0 | 0 | -23.0803 | -89.9766 | 112.4475 | -22.4475 | -84.4882 | 96.5482 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.9 | -5.9 | 1.1236 | 0
2015-01-01 06:00 | 0 | 0 | 0 | 0 | -23.0773 | -74.9813 | 109.1542 | -19.1542 | -70.1569 | 83.4749 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.7 | -5.7 | 1.1228 | 0
2015-01-01 07:00 | 0 | 0 | 0 | 0 | -23.0742 | -59.986 | 106.1435 | -16.1435 | -56.0301 | 70.9863 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.9 | -5.9 | 1.1236 | 0
2015-01-01 08:00 | 0 | 0 | 0 | 0 | -23.0711 | -44.9907 | 103.5942 | -13.5942 | -42.0048 | 59.4704 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2 | -4.2 | 1.1168 | 0
2015-01-01 09:00 | 0 | 0 | 0 | 0 | -23.068 | -29.9953 | 101.6559 | -11.6559 | -28.0109 | 49.6245 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1148 | 0
2015-01-01 10:00 | 0 | 0 | 0 | 0 | -23.0649 | -15 | 100.4432 | -10.4432 | -14.0129 | 42.6332 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-01-01 11:00 | 0 | 0 | 0 | 0 | -23.0618 | -0.0046998 | 100.0284 | -10.0284 | -0.0043913 | 40.0284 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.6 | -5.6 | 1.1224 | 0
2015-01-01 12:00 | 0 | 0 | 0 | 0 | -23.0586 | 14.9906 | 100.4364 | -10.4364 | 14.0045 | 42.6242 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6 | -6 | 1.124 | 0
2015-01-01 13:00 | 0 | 0 | 0 | 0 | -23.0555 | 29.9859 | 101.6425 | -11.6425 | 28.0036 | 49.6093 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-01-01 14:00 | 0 | 0 | 0 | 0 | -23.0523 | 44.9813 | 103.5742 | -13.5742 | 41.9992 | 59.452 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.8 | -5.8 | 1.1232 | 0
2015-01-01 15:00 | 0 | 0 | 0 | 0 | -23.0491 | 59.9766 | 106.1172 | -16.1172 | 56.0266 | 70.9666 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6 | -6 | 1.124 | 0
2015-01-01 16:00 | 0 | 0 | 0 | 0 | -23.0459 | 74.9719 | 109.1217 | -19.1217 | 70.1557 | 83.4554 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1196 | 0
2015-01-01 17:00 | 0 | 0 | 0 | 0 | -23.0427 | 89.9673 | 112.409 | -22.409 | 84.4891 | 96.5297 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-01-01 18:00 | 0 | 0 | 0 | 0 | -23.0395 | 104.9626 | 115.7768 | -25.7768 | 99.1511 | 109.9658 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.8 | -4.8 | 1.1192 | 0
2015-01-01 19:00 | 0 | 0 | 0 | 0 | -23.0363 | 119.9579 | 119.0039 | -29.0039 | 114.2678 | 123.6235 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.6 | -5.6 | 1.1224 | 0
2015-01-01 20:00 | 0 | 0 | 0 | 0 | -23.033 | 134.9533 | 121.858 | -31.858 | 129.9349 | 137.3986 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1196 | 0
2015-01-01 21:00 | 0 | 0 | 0 | 0 | -23.0298 | 149.9486 | 124.1096 | -34.1096 | 146.1774 | 151.1731 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-01-01 22:00 | 0 | 0 | 0 | 0 | -23.0265 | 164.944 | 125.5565 | -35.5565 | 162.9109 | 164.6214 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-01-01 23:00 | 0 | 0 | 0 | 0 | -23.0232 | 179.9393 | 126.0566 | -36.0566 | 179.9309 | 173.9432 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-01-02 | 0 | 0 | 0 | 0 | -23.0199 | -165.0654 | 125.5579 | -35.5579 | -163.0484 | 164.7283 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-01-02 01:00 | 0 | 0 | 0 | 0 | -23.0166 | -150.07 | 124.1118 | -34.1118 | -146.3133 | 151.2856 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-01-02 02:00 | 0 | 0 | 0 | 0 | -23.0133 | -135.0747 | 121.8596 | -31.8596 | -130.0685 | 137.5102 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.2 | -2.2 | 1.1088 | 0
2015-01-02 03:00 | 0 | 0 | 0 | 0 | -23.01 | -120.0793 | 119.0032 | -29.0032 | -114.399 | 123.7321 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-01-02 04:00 | 0 | 0 | 0 | 0 | -23.0066 | -105.084 | 115.7718 | -25.7718 | -99.2803 | 110.0696 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.4 | -2.4 | 1.1096 | 0
2015-01-02 05:00 | 0 | 0 | 0 | 0 | -23.0033 | -90.0886 | 112.398 | -22.398 | -84.6166 | 96.6266 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.2 | -2.2 | 1.1088 | 0
2015-01-02 06:00 | 0 | 0 | 0 | 0 | -22.9999 | -75.0933 | 109.1027 | -19.1027 | -70.2819 | 83.5423 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.2 | -2.2 | 1.1088 | 0
2015-01-02 07:00 | 0 | 0 | 0 | 0 | -22.9965 | -60.0979 | 106.0884 | -16.0884 | -56.1515 | 71.0391 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.8 | -2.8 | 1.1112 | 0
2015-01-02 08:00 | 0 | 0 | 0 | 0 | -22.9931 | -45.1025 | 103.5341 | -13.5341 | -42.1225 | 59.503 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-01-02 09:00 | 0 | 0 | 0 | 0 | -22.9897 | -30.1072 | 101.5899 | -11.5899 | -28.1245 | 49.6283 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-01-02 10:00 | 0 | 0 | 0 | 0 | -22.9862 | -15.1118 | 100.3708 | -10.3708 | -14.1221 | 42.5978 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-01-02 11:00 | 0 | 0 | 0 | 0 | -22.9828 | -0.11646 | 99.9495 | -9.9495 | -0.10885 | 39.9496 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-01-02 12:00 | 0 | 0 | 0 | 0 | -22.9793 | 14.8789 | 100.3512 | -10.3512 | 13.9049 | 42.5129 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-01-02 13:00 | 0 | 0 | 0 | 0 | -22.9759 | 29.8743 | 101.5516 | -11.5516 | 27.9087 | 49.4829 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.2 | -2.2 | 1.1088 | 0
2015-01-02 14:00 | 0 | 0 | 0 | 0 | -22.9724 | 44.8696 | 103.4785 | -13.4785 | 41.9085 | 59.3218 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-01-02 15:00 | 0 | 0 | 0 | 0 | -22.9689 | 59.865 | 106.0178 | -16.0178 | 55.9389 | 70.8379 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-01-02 16:00 | 0 | 0 | 0 | 0 | -22.9654 | 74.8604 | 109.0197 | -19.0197 | 70.0696 | 83.3303 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.1064 | 0
2015-01-02 17:00 | 0 | 0 | 0 | 0 | -22.9619 | 89.8558 | 112.3055 | -22.3055 | 84.4027 | 96.409 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-01-02 18:00 | 0 | 0 | 0 | 0 | -22.9583 | 104.8511 | 115.6731 | -25.6731 | 99.0624 | 109.8501 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.1064 | 0
2015-01-02 19:00 | 0 | 0 | 0 | 0 | -22.9548 | 119.8465 | 118.9015 | -28.9015 | 114.1743 | 123.5134 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-01-02 20:00 | 0 | 0 | 0 | 0 | -22.9512 | 134.8419 | 121.7583 | -31.7583 | 129.8346 | 137.2955 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-01-02 21:00 | 0 | 0 | 0 | 0 | -22.9476 | 149.8373 | 124.0142 | -34.0142 | 146.0684 | 151.0806 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-01-02 22:00 | 0 | 0 | 0 | 0 | -22.9441 | 164.8327 | 125.4668 | -35.4668 | 162.7927 | 164.5538 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-01-02 23:00 | 0 | 0 | 0 | 0 | -22.9405 | 179.8281 | 125.9737 | -35.9737 | 179.8043 | 174.024 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-01-03 | 0 | 0 | 0 | 0 | -22.9368 | -165.1766 | 125.4823 | -35.4823 | -163.1812 | 164.8534 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-01-03 01:00 | 0 | 0 | 0 | 0 | -22.9332 | -150.1812 | 124.043 | -34.043 | -146.4493 | 151.3969 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-01-03 02:00 | 0 | 0 | 0 | 0 | -22.9296 | -135.1858 | 121.7965 | -31.7965 | -130.2052 | 137.612 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1 | 1 | 1.096 | 0
2015-01-03 03:00 | 0 | 0 | 0 | 0 | -22.9259 | -120.1904 | 118.944 | -28.944 | -114.5344 | 123.8256 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-01-03 04:00 | 0 | 0 | 0 | 0 | -22.9222 | -105.195 | 115.7147 | -25.7147 | -99.413 | 110.1547 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.3 | 1.3 | 1.0948 | 0
2015-01-03 05:00 | 0 | 0 | 0 | 0 | -22.9186 | -90.1996 | 112.3407 | -22.3407 | -84.7461 | 96.7022 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.4 | 1.4 | 1.0944 | 0
2015-01-03 06:00 | 0 | 0 | 0 | 0 | -22.9149 | -75.2042 | 109.0435 | -19.0435 | -70.4078 | 83.6062 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-01-03 07:00 | 0 | 0 | 0 | 0 | -22.9112 | -60.2088 | 106.0256 | -16.0256 | -56.2736 | 71.0877 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-01-03 08:00 | 0 | 0 | 0 | 0 | -22.9074 | -45.2134 | 103.4664 | -13.4664 | -42.2405 | 59.5305 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-01-03 09:00 | 0 | 0 | 0 | 0 | -22.9037 | -30.218 | 101.5164 | -11.5164 | -28.2381 | 49.626 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-01-03 10:00 | 0 | 0 | 0 | 0 | -22.9 | -15.2226 | 100.2908 | -10.2908 | -14.2309 | 42.5554 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-01-03 11:00 | 0 | 0 | 0 | 0 | -22.8962 | -0.22716 | 99.863 | -9.863 | -0.2124 | 39.8635 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-01-03 12:00 | 0 | 0 | 0 | 0 | -22.8924 | 14.7683 | 100.2585 | -10.2585 | 13.8067 | 42.395 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-01-03 13:00 | 0 | 0 | 0 | 0 | -22.8886 | 29.7637 | 101.4533 | -11.4533 | 27.8157 | 49.3511 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-01-03 14:00 | 0 | 0 | 0 | 0 | -22.8848 | 44.7591 | 103.3755 | -13.3755 | 41.8199 | 59.1877 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.8 | -0.8 | 1.1032 | 0
2015-01-03 15:00 | 0 | 0 | 0 | 0 | -22.881 | 59.7545 | 105.9111 | -15.9111 | 55.8538 | 70.7064 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-01-03 16:00 | 0 | 0 | 0 | 0 | -22.8772 | 74.7499 | 108.9105 | -18.9105 | 69.9864 | 83.2032 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-01-03 17:00 | 0 | 0 | 0 | 0 | -22.8734 | 89.7453 | 112.1949 | -22.1949 | 84.3195 | 96.2871 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-01-03 18:00 | 0 | 0 | 0 | 0 | -22.8695 | 104.7408 | 115.5624 | -25.5624 | 98.9768 | 109.7337 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-01-03 19:00 | 0 | 0 | 0 | 0 | -22.8656 | 119.7362 | 118.7919 | -28.7919 | 114.084 | 123.4033 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.1064 | 0
2015-01-03 20:00 | 0 | 0 | 0 | 0 | -22.8618 | 134.7316 | 121.6514 | -31.6514 | 129.7371 | 137.1931 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-01-03 21:00 | 0 | 0 | 0 | 0 | -22.8579 | 149.7271 | 123.9114 | -33.9114 | 145.9619 | 150.9894 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-01-03 22:00 | 0 | 0 | 0 | 0 | -22.854 | 164.7225 | 125.3696 | -35.3696 | 162.6765 | 164.4888 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-01-03 23:00 | 0 | 0 | 0 | 0 | -22.8501 | 179.7179 | 125.8832 | -35.8832 | 179.6792 | 174.1106 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.2 | -2.2 | 1.1088 | 0
2015-01-04 | 0 | 0 | 0 | 0 | -22.8461 | -165.2866 | 125.399 | -35.399 | -163.3132 | 164.9801 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-01-04 01:00 | 0 | 0 | 0 | 0 | -22.8422 | -150.2912 | 123.9665 | -33.9665 | -146.5853 | 151.5079 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.11 | 0
2015-01-04 02:00 | 0 | 0 | 0 | 0 | -22.8382 | -135.2958 | 121.7256 | -31.7256 | -130.3424 | 137.7127 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-01-04 03:00 | 0 | 0 | 0 | 0 | -22.8343 | -120.3003 | 118.8772 | -28.8772 | -114.6705 | 123.9174 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-01-04 04:00 | 0 | 0 | 0 | 0 | -22.8303 | -105.3049 | 115.6499 | -25.6499 | -99.5467 | 110.2375 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.8 | -2.8 | 1.1112 | 0
2015-01-04 05:00 | 0 | 0 | 0 | 0 | -22.8263 | -90.3094 | 112.2759 | -22.2759 | -84.8765 | 96.7748 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-01-04 06:00 | 0 | 0 | 0 | 0 | -22.8223 | -75.314 | 108.9767 | -18.9767 | -70.5345 | 83.6665 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-01-04 07:00 | 0 | 0 | 0 | 0 | -22.8182 | -60.3185 | 105.9553 | -15.9553 | -56.3963 | 71.1319 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-01-04 08:00 | 0 | 0 | 0 | 0 | -22.8142 | -45.3231 | 103.3911 | -13.3911 | -42.3588 | 59.5528 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-01-04 09:00 | 0 | 0 | 0 | 0 | -22.8102 | -30.3276 | 101.4352 | -11.4352 | -28.3516 | 49.6175 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-01-04 10:00 | 0 | 0 | 0 | 0 | -22.8061 | -15.3322 | 100.2032 | -10.2032 | -14.3391 | 42.5059 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.1132 | 0
2015-01-04 11:00 | 0 | 0 | 0 | 0 | -22.802 | -0.33669 | 99.7689 | -9.7689 | -0.31495 | 39.7701 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-01-04 12:00 | 0 | 0 | 0 | 0 | -22.7979 | 14.6588 | 100.1583 | -10.1583 | 13.71 | 42.2705 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-01-04 13:00 | 0 | 0 | 0 | 0 | -22.7938 | 29.6542 | 101.3476 | -11.3476 | 27.7245 | 49.214 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-01-04 14:00 | 0 | 0 | 0 | 0 | -22.7897 | 44.6497 | 103.2652 | -13.2652 | 41.7336 | 59.0496 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3 | -3 | 1.112 | 0
2015-01-04 15:00 | 0 | 0 | 0 | 0 | -22.7856 | 59.6452 | 105.7973 | -15.7973 | 55.7713 | 70.572 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-01-04 16:00 | 0 | 0 | 0 | 0 | -22.7814 | 74.6406 | 108.7941 | -18.7941 | 69.9061 | 83.0742 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-01-04 17:00 | 0 | 0 | 0 | 0 | -22.7773 | 89.6361 | 112.0772 | -22.0772 | 84.2393 | 96.1641 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-01-04 18:00 | 0 | 0 | 0 | 0 | -22.7731 | 104.6316 | 115.4445 | -25.4445 | 98.8944 | 109.617 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-01-04 19:00 | 0 | 0 | 0 | 0 | -22.7689 | 119.6271 | 118.6752 | -28.6752 | 113.9968 | 123.2934 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-01-04 20:00 | 0 | 0 | 0 | 0 | -22.7648 | 134.6226 | 121.5372 | -31.5372 | 129.6426 | 137.0914 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-01-04 21:00 | 0 | 0 | 0 | 0 | -22.7606 | 149.618 | 123.8012 | -33.8012 | 145.8581 | 150.8997 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.1132 | 0
2015-01-04 22:00 | 0 | 0 | 0 | 0 | -22.7563 | 164.6135 | 125.2649 | -35.2649 | 162.5624 | 164.4262 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.1132 | 0
2015-01-04 23:00 | 0 | 0 | 0 | 0 | -22.7521 | 179.609 | 125.7851 | -35.7851 | 179.5555 | 174.2029 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-01-05 | 0 | 0 | 0 | 0 | -22.7479 | -165.3955 | 125.308 | -35.308 | -163.4444 | 165.1083 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1148 | 0
2015-01-05 01:00 | 0 | 0 | 0 | 0 | -22.7436 | -150.4 | 123.8823 | -33.8823 | -146.7211 | 151.6185 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.118 | 0
2015-01-05 02:00 | 0 | 0 | 0 | 0 | -22.7393 | -135.4045 | 121.6472 | -31.6472 | -130.4798 | 137.8121 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.7 | -4.7 | 1.1188 | 0
2015-01-05 03:00 | 0 | 0 | 0 | 0 | -22.735 | -120.409 | 118.8027 | -28.8027 | -114.8072 | 124.0074 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.1 | -6.1 | 1.1244 | 0
2015-01-05 04:00 | 0 | 0 | 0 | 0 | -22.7307 | -105.4135 | 115.5774 | -25.5774 | -99.6811 | 110.3179 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7 | -7 | 1.128 | 0
2015-01-05 05:00 | 0 | 0 | 0 | 0 | -22.7264 | -90.418 | 112.2035 | -22.2035 | -85.0077 | 96.8444 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.5 | -6.5 | 1.126 | 0
2015-01-05 06:00 | 0 | 0 | 0 | 0 | -22.7221 | -75.4225 | 108.9024 | -18.9024 | -70.6619 | 83.7231 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.8 | -6.8 | 1.1272 | 0
2015-01-05 07:00 | 0 | 0 | 0 | 0 | -22.7178 | -60.427 | 105.8773 | -15.8773 | -56.5194 | 71.1718 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.9 | -5.9 | 1.1236 | 0
2015-01-05 08:00 | 0 | 0 | 0 | 0 | -22.7134 | -45.4315 | 103.3082 | -13.3082 | -42.4772 | 59.5699 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.5 | -5.5 | 1.122 | 0
2015-01-05 09:00 | 0 | 0 | 0 | 0 | -22.7091 | -30.436 | 101.3464 | -11.3464 | -28.4648 | 49.6029 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.7 | -4.7 | 1.1188 | 0
2015-01-05 10:00 | 0 | 0 | 0 | 0 | -22.7047 | -15.4405 | 100.1081 | -10.1081 | -14.4466 | 42.4495 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1196 | 0
2015-01-05 11:00 | 0 | 0 | 0 | 0 | -22.7003 | -0.44496 | 99.6673 | -9.6673 | -0.41641 | 39.6694 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.6 | -4.6 | 1.1184 | 0
2015-01-05 12:00 | 0 | 0 | 0 | 0 | -22.6959 | 14.5506 | 100.0506 | -10.0506 | 13.6148 | 42.1394 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-01-05 13:00 | 0 | 0 | 0 | 0 | -22.6915 | 29.5461 | 101.2345 | -11.2345 | 27.6353 | 49.0718 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2 | -4.2 | 1.1168 | 0
2015-01-05 14:00 | 0 | 0 | 0 | 0 | -22.6871 | 44.5416 | 103.1477 | -13.1477 | 41.6497 | 58.9077 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.3 | -4.3 | 1.1172 | 0
2015-01-05 15:00 | 0 | 0 | 0 | 0 | -22.6826 | 59.5371 | 105.6763 | -15.6763 | 55.6915 | 70.435 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2 | -4.2 | 1.1168 | 0
2015-01-05 16:00 | 0 | 0 | 0 | 0 | -22.6782 | 74.5327 | 108.6707 | -18.6707 | 69.8287 | 82.9434 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.9 | -3.9 | 1.1156 | 0
2015-01-05 17:00 | 0 | 0 | 0 | 0 | -22.6737 | 89.5282 | 111.9525 | -21.9525 | 84.1623 | 96.04 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2 | -4.2 | 1.1168 | 0
2015-01-05 18:00 | 0 | 0 | 0 | 0 | -22.6692 | 104.5237 | 115.3197 | -25.3197 | 98.8153 | 109.4998 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.1132 | 0
2015-01-05 19:00 | 0 | 0 | 0 | 0 | -22.6647 | 119.5192 | 118.5514 | -28.5514 | 113.9129 | 123.1836 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-01-05 20:00 | 0 | 0 | 0 | 0 | -22.6602 | 134.5148 | 121.4158 | -31.4158 | 129.5512 | 136.9904 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.6 | -3.6 | 1.1144 | 0
2015-01-05 21:00 | 0 | 0 | 0 | 0 | -22.6557 | 149.5103 | 123.6837 | -33.6837 | 145.7571 | 150.8115 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1148 | 0
2015-01-05 22:00 | 0 | 0 | 0 | 0 | -22.6512 | 164.5059 | 125.1527 | -35.1527 | 162.4507 | 164.3661 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.7 | -4.7 | 1.1188 | 0
2015-01-05 23:00 | 0 | 0 | 0 | 0 | -22.6466 | 179.5014 | 125.6794 | -35.6794 | 179.4335 | 174.3007 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.8 | -3.8 | 1.1152 | 0
2015-01-06 | 0 | 0 | 0 | 0 | -22.6421 | -165.503 | 125.2093 | -35.2093 | -163.5746 | 165.2379 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3 | -3 | 1.112 | 0
2015-01-06 01:00 | 0 | 0 | 0 | 0 | -22.6375 | -150.5075 | 123.7904 | -33.7904 | -146.8565 | 151.7287 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.1132 | 0
2015-01-06 02:00 | 0 | 0 | 0 | 0 | -22.6329 | -135.5119 | 121.561 | -31.561 | -130.6174 | 137.9103 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1148 | 0
2015-01-06 03:00 | 0 | 0 | 0 | 0 | -22.6283 | -120.5164 | 118.7206 | -28.7206 | -114.9444 | 124.0954 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.8 | -3.8 | 1.1152 | 0
2015-01-06 04:00 | 0 | 0 | 0 | 0 | -22.6237 | -105.5208 | 115.4974 | -25.4974 | -99.8162 | 110.3957 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-01-06 05:00 | 0 | 0 | 0 | 0 | -22.6191 | -90.5253 | 112.1235 | -22.1235 | -85.1396 | 96.911 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-01-06 06:00 | 0 | 0 | 0 | 0 | -22.6144 | -75.5297 | 108.8204 | -18.8204 | -70.7899 | 83.7761 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-01-06 07:00 | 0 | 0 | 0 | 0 | -22.6098 | -60.5341 | 105.7918 | -15.7918 | -56.6429 | 71.2073 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-01-06 08:00 | 0 | 0 | 0 | 0 | -22.6051 | -45.5386 | 103.2177 | -13.2177 | -42.5957 | 59.5818 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.1064 | 0
2015-01-06 09:00 | 0 | 0 | 0 | 0 | -22.6005 | -30.543 | 101.25 | -11.25 | -28.5778 | 49.5821 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-01-06 10:00 | 0 | 0 | 0 | 0 | -22.5958 | -15.5474 | 100.0054 | -10.0054 | -14.5534 | 42.3861 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-01-06 11:00 | 0 | 0 | 0 | 0 | -22.5911 | -0.55187 | 99.5583 | -9.5583 | -0.51669 | 39.5614 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-01-06 12:00 | 0 | 0 | 0 | 0 | -22.5864 | 14.4437 | 99.9356 | -9.9356 | 13.5212 | 42.0019 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-01-06 13:00 | 0 | 0 | 0 | 0 | -22.5816 | 29.4393 | 101.1143 | -11.1143 | 27.5481 | 48.9244 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-01-06 14:00 | 0 | 0 | 0 | 0 | -22.5769 | 44.4349 | 103.0231 | -13.0231 | 41.5683 | 58.762 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-01-06 15:00 | 0 | 0 | 0 | 0 | -22.5721 | 59.4305 | 105.5482 | -15.5482 | 55.6145 | 70.2953 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.5 | -0.5 | 1.102 | 0
2015-01-06 16:00 | 0 | 0 | 0 | 0 | -22.5674 | 74.426 | 108.5403 | -18.5403 | 69.7545 | 82.811 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-01-06 17:00 | 0 | 0 | 0 | 0 | -22.5626 | 89.4216 | 111.8209 | -21.8209 | 84.0886 | 95.9149 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-01-06 18:00 | 0 | 0 | 0 | 0 | -22.5578 | 104.4172 | 115.1878 | -25.1878 | 98.7396 | 109.3823 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-01-06 19:00 | 0 | 0 | 0 | 0 | -22.553 | 119.4128 | 118.4205 | -28.4205 | 113.8324 | 123.0741 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-01-06 20:00 | 0 | 0 | 0 | 0 | -22.5482 | 134.4084 | 121.2872 | -31.2872 | 129.463 | 136.8903 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-01-06 21:00 | 0 | 0 | 0 | 0 | -22.5434 | 149.404 | 123.5589 | -33.5589 | 145.6589 | 150.7246 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-01-06 22:00 | 0 | 0 | 0 | 0 | -22.5385 | 164.3996 | 125.0331 | -35.0331 | 162.3413 | 164.3082 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-01-06 23:00 | 0 | 0 | 0 | 0 | -22.5337 | 179.3952 | 125.5662 | -35.5662 | 179.3133 | 174.404 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-01-07 | 0 | 0 | 0 | 0 | -22.5288 | -165.6092 | 125.1031 | -35.1031 | -163.7037 | 165.3685 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.7 | 0.7 | 1.0972 | 0
2015-01-07 01:00 | 0 | 0 | 0 | 0 | -22.5239 | -150.6136 | 123.6909 | -33.6909 | -146.9914 | 151.8382 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1 | 1 | 1.096 | 0
2015-01-07 02:00 | 0 | 0 | 0 | 0 | -22.519 | -135.6179 | 121.4672 | -31.4672 | -130.7549 | 138.0069 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-01-07 03:00 | 0 | 0 | 0 | 0 | -22.5141 | -120.6223 | 118.6309 | -28.6309 | -115.0819 | 124.1813 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-01-07 04:00 | 0 | 0 | 0 | 0 | -22.5092 | -105.6267 | 115.4098 | -25.4098 | -99.9518 | 110.471 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-01-07 05:00 | 0 | 0 | 0 | 0 | -22.5043 | -90.6311 | 112.0359 | -22.0359 | -85.272 | 96.9744 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-01-07 06:00 | 0 | 0 | 0 | 0 | -22.4993 | -75.6355 | 108.7309 | -18.7309 | -70.9183 | 83.8253 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-01-07 07:00 | 0 | 0 | 0 | 0 | -22.4944 | -60.6398 | 105.6987 | -15.6987 | -56.7667 | 71.2384 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-01-07 08:00 | 0 | 0 | 0 | 0 | -22.4894 | -45.6442 | 103.1197 | -13.1197 | -42.7142 | 59.5885 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-01-07 09:00 | 0 | 0 | 0 | 0 | -22.4844 | -30.6486 | 101.1462 | -11.1462 | -28.6903 | 49.5553 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-01-07 10:00 | 0 | 0 | 0 | 0 | -22.4794 | -15.6529 | 99.8953 | -9.8953 | -14.6595 | 42.3158 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-01-07 11:00 | 0 | 0 | 0 | 0 | -22.4744 | -0.65731 | 99.4419 | -9.4419 | -0.61572 | 39.4463 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-01-07 12:00 | 0 | 0 | 0 | 0 | -22.4694 | 14.3383 | 99.8133 | -9.8133 | 13.4293 | 41.8579 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-01-07 13:00 | 0 | 0 | 0 | 0 | -22.4644 | 29.334 | 100.9867 | -10.9867 | 27.4631 | 48.7721 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-01-07 14:00 | 0 | 0 | 0 | 0 | -22.4593 | 44.3296 | 102.8913 | -12.8913 | 41.4894 | 58.6128 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-01-07 15:00 | 0 | 0 | 0 | 0 | -22.4542 | 59.3253 | 105.4132 | -15.4132 | 55.5404 | 70.1532 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-01-07 16:00 | 0 | 0 | 0 | 0 | -22.4492 | 74.3209 | 108.403 | -18.403 | 69.6833 | 82.6769 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-01-07 17:00 | 0 | 0 | 0 | 0 | -22.4441 | 89.3166 | 111.6823 | -21.6823 | 84.0182 | 95.789 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-01-07 18:00 | 0 | 0 | 0 | 0 | -22.439 | 104.3122 | 115.0491 | -25.0491 | 98.6673 | 109.2645 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-01-07 19:00 | 0 | 0 | 0 | 0 | -22.4339 | 119.3079 | 118.2828 | -28.2828 | 113.7552 | 122.9649 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-01-07 20:00 | 0 | 0 | 0 | 0 | -22.4287 | 134.3036 | 121.1517 | -31.1517 | 129.3781 | 136.791 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-01-07 21:00 | 0 | 0 | 0 | 0 | -22.4236 | 149.2992 | 123.427 | -33.427 | 145.5637 | 150.6392 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-01-07 22:00 | 0 | 0 | 0 | 0 | -22.4185 | 164.2949 | 124.9062 | -34.9062 | 162.2344 | 164.2526 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-01-07 23:00 | 0 | 0 | 0 | 0 | -22.4133 | 179.2906 | 125.4455 | -35.4455 | 179.1949 | 174.5126 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-01-08 | 0 | 0 | 0 | 0 | -22.4081 | -165.7138 | 124.9893 | -34.9893 | -163.8315 | 165.5001 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.6 | -3.6 | 1.1144 | 0
2015-01-08 01:00 | 0 | 0 | 0 | 0 | -22.4029 | -150.7181 | 123.5838 | -33.5838 | -147.1257 | 151.9468 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2 | -4.2 | 1.1168 | 0
2015-01-08 02:00 | 0 | 0 | 0 | 0 | -22.3977 | -135.7224 | 121.3658 | -31.3658 | -130.8924 | 138.1019 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.6 | -3.6 | 1.1144 | 0
2015-01-08 03:00 | 0 | 0 | 0 | 0 | -22.3925 | -120.7267 | 118.5336 | -28.5336 | -115.2197 | 124.265 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1148 | 0
2015-01-08 04:00 | 0 | 0 | 0 | 0 | -22.3873 | -105.7311 | 115.3146 | -25.3146 | -100.0878 | 110.5435 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-01-08 05:00 | 0 | 0 | 0 | 0 | -22.3821 | -90.7354 | 111.9408 | -21.9408 | -85.4049 | 97.0346 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.11 | 0
2015-01-08 06:00 | 0 | 0 | 0 | 0 | -22.3768 | -75.7397 | 108.6339 | -18.6339 | -71.0471 | 83.8707 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.1132 | 0
2015-01-08 07:00 | 0 | 0 | 0 | 0 | -22.3715 | -60.744 | 105.5981 | -15.5981 | -56.8906 | 71.265 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-01-08 08:00 | 0 | 0 | 0 | 0 | -22.3663 | -45.7483 | 103.0142 | -13.0142 | -42.8326 | 59.59 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-01-08 09:00 | 0 | 0 | 0 | 0 | -22.361 | -30.7526 | 101.0349 | -11.0349 | -28.8024 | 49.5223 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-01-08 10:00 | 0 | 0 | 0 | 0 | -22.3557 | -15.7569 | 99.7777 | -9.7777 | -14.7646 | 42.2385 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-01-08 11:00 | 0 | 0 | 0 | 0 | -22.3503 | -0.76118 | 99.3181 | -9.3181 | -0.71341 | 39.3241 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-01-08 12:00 | 0 | 0 | 0 | 0 | -22.345 | 14.2345 | 99.6837 | -9.6837 | 13.3392 | 41.7076 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-01-08 13:00 | 0 | 0 | 0 | 0 | -22.3397 | 29.2302 | 100.8521 | -10.8521 | 27.3803 | 48.6148 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-01-08 14:00 | 0 | 0 | 0 | 0 | -22.3343 | 44.2259 | 102.7525 | -12.7525 | 41.413 | 58.4599 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-01-08 15:00 | 0 | 0 | 0 | 0 | -22.329 | 59.2217 | 105.2712 | -15.2712 | 55.4692 | 70.0087 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-01-08 16:00 | 0 | 0 | 0 | 0 | -22.3236 | 74.2174 | 108.2589 | -18.2589 | 69.6154 | 82.5414 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-01-08 17:00 | 0 | 0 | 0 | 0 | -22.3182 | 89.2131 | 111.537 | -21.537 | 83.9512 | 95.6623 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-01-08 18:00 | 0 | 0 | 0 | 0 | -22.3128 | 104.2088 | 114.9036 | -24.9036 | 98.5985 | 109.1466 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-01-08 19:00 | 0 | 0 | 0 | 0 | -22.3074 | 119.2046 | 118.1381 | -28.1381 | 113.6816 | 122.8561 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-01-08 20:00 | 0 | 0 | 0 | 0 | -22.3019 | 134.2003 | 121.0091 | -31.0091 | 129.2965 | 136.6926 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-01-08 21:00 | 0 | 0 | 0 | 0 | -22.2965 | 149.196 | 123.2879 | -33.2879 | 145.4716 | 150.5552 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1 | 1 | 1.096 | 0
2015-01-08 22:00 | 0 | 0 | 0 | 0 | -22.291 | 164.1918 | 124.772 | -34.772 | 162.1301 | 164.1991 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-01-08 23:00 | 0 | 0 | 0 | 0 | -22.2856 | 179.1875 | 125.3174 | -35.3174 | 179.0786 | 174.6264 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-01-09 | 0 | 0 | 0 | 0 | -22.2801 | -165.8168 | 124.868 | -34.868 | -163.958 | 165.6324 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-01-09 01:00 | 0 | 0 | 0 | 0 | -22.2746 | -150.821 | 123.4692 | -33.4692 | -147.2593 | 152.0545 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-01-09 02:00 | 0 | 0 | 0 | 0 | -22.2691 | -135.8253 | 121.2569 | -31.2569 | -131.0295 | 138.1952 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-01-09 03:00 | 0 | 0 | 0 | 0 | -22.2636 | -120.8295 | 118.4288 | -28.4288 | -115.3575 | 124.3465 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.7 | 0.7 | 1.0972 | 0
2015-01-09 04:00 | 0 | 0 | 0 | 0 | -22.258 | -105.8338 | 115.2119 | -25.2119 | -100.2241 | 110.6133 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-01-09 05:00 | 0 | 0 | 0 | 0 | -22.2525 | -90.838 | 111.8382 | -21.8382 | -85.5381 | 97.0915 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-01-09 06:00 | 0 | 0 | 0 | 0 | -22.2469 | -75.8423 | 108.5294 | -18.5294 | -71.1761 | 83.9123 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-01-09 07:00 | 0 | 0 | 0 | 0 | -22.2414 | -60.8465 | 105.49 | -15.49 | -57.0146 | 71.2871 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-01-09 08:00 | 0 | 0 | 0 | 0 | -22.2358 | -45.8507 | 102.9013 | -12.9013 | -42.9507 | 59.5862 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-01-09 09:00 | 0 | 0 | 0 | 0 | -22.2302 | -30.855 | 100.9162 | -10.9162 | -28.9139 | 49.4833 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-01-09 10:00 | 0 | 0 | 0 | 0 | -22.2246 | -15.8592 | 99.6528 | -9.6528 | -14.8687 | 42.1544 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-01-09 11:00 | 0 | 0 | 0 | 0 | -22.219 | -0.86341 | 99.187 | -9.187 | -0.80968 | 39.1947 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-01-09 12:00 | 0 | 0 | 0 | 0 | -22.2133 | 14.1324 | 99.5469 | -9.5469 | 13.2509 | 41.551 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-01-09 13:00 | 0 | 0 | 0 | 0 | -22.2077 | 29.1282 | 100.7103 | -10.7103 | 27.2998 | 48.4527 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-01-09 14:00 | 0 | 0 | 0 | 0 | -22.202 | 44.1239 | 102.6067 | -12.6067 | 41.3394 | 58.3037 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-01-09 15:00 | 0 | 0 | 0 | 0 | -22.1963 | 59.1197 | 105.1223 | -15.1223 | 55.401 | 69.8618 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-01-09 16:00 | 0 | 0 | 0 | 0 | -22.1907 | 74.1155 | 108.1079 | -18.1079 | 69.5508 | 82.4044 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-01-09 17:00 | 0 | 0 | 0 | 0 | -22.185 | 89.1113 | 111.3849 | -21.3849 | 83.8877 | 95.5349 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-01-09 18:00 | 0 | 0 | 0 | 0 | -22.1793 | 104.1071 | 114.7513 | -24.7513 | 98.5333 | 109.0285 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-01-09 19:00 | 0 | 0 | 0 | 0 | -22.1735 | 119.1029 | 117.9867 | -27.9867 | 113.6115 | 122.7477 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-01-09 20:00 | 0 | 0 | 0 | 0 | -22.1678 | 134.0987 | 120.8597 | -30.8597 | 129.2183 | 136.5951 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-01-09 21:00 | 0 | 0 | 0 | 0 | -22.1621 | 149.0945 | 123.1417 | -33.1417 | 145.3825 | 150.4726 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-01-09 22:00 | 0 | 0 | 0 | 0 | -22.1563 | 164.0903 | 124.6306 | -34.6306 | 162.0285 | 164.1476 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-01-09 23:00 | 0 | 0 | 0 | 0 | -22.1505 | 179.0861 | 125.182 | -35.182 | 178.9644 | 174.7452 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-01-10 | 0 | 0 | 0 | 0 | -22.1447 | -165.9181 | 124.7392 | -34.7392 | -164.083 | 165.7652 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-01-10 01:00 | 0 | 0 | 0 | 0 | -22.1389 | -150.9222 | 123.347 | -33.347 | -147.3919 | 152.161 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-01-10 02:00 | 0 | 0 | 0 | 0 | -22.1331 | -135.9264 | 121.1404 | -31.1404 | -131.1663 | 138.2867 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-01-10 03:00 | 0 | 0 | 0 | 0 | -22.1273 | -120.9306 | 118.3165 | -28.3165 | -115.4953 | 124.4256 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-01-10 04:00 | 0 | 0 | 0 | 0 | -22.1215 | -105.9348 | 115.1018 | -25.1018 | -100.3606 | 110.6802 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-01-10 05:00 | 0 | 0 | 0 | 0 | -22.1156 | -90.9389 | 111.7281 | -21.7281 | -85.6715 | 97.1451 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-01-10 06:00 | 0 | 0 | 0 | 0 | -22.1098 | -75.9431 | 108.4175 | -18.4175 | -71.3052 | 83.95 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-01-10 07:00 | 0 | 0 | 0 | 0 | -22.1039 | -60.9473 | 105.3746 | -15.3746 | -57.1385 | 71.3048 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.8 | -0.8 | 1.1032 | 0
2015-01-10 08:00 | 0 | 0 | 0 | 0 | -22.098 | -45.9514 | 102.7809 | -12.7809 | -43.0685 | 59.5772 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.8 | -0.8 | 1.1032 | 0
2015-01-10 09:00 | 0 | 0 | 0 | 0 | -22.0921 | -30.9556 | 100.79 | -10.79 | -29.0247 | 49.4382 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-01-10 10:00 | 0 | 0 | 0 | 0 | -22.0862 | -15.9597 | 99.5205 | -9.5205 | -14.9718 | 42.0635 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-01-10 11:00 | 0 | 0 | 0 | 0 | -22.0803 | -0.96388 | 99.0487 | -9.0487 | -0.90444 | 39.0583 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-01-10 12:00 | 0 | 0 | 0 | 0 | -22.0743 | 14.032 | 99.403 | -9.403 | 13.1646 | 41.3882 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.8 | -0.8 | 1.1032 | 0
2015-01-10 13:00 | 0 | 0 | 0 | 0 | -22.0684 | 29.0278 | 100.5616 | -10.5616 | 27.2216 | 48.2858 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-01-10 14:00 | 0 | 0 | 0 | 0 | -22.0624 | 44.0237 | 102.454 | -12.454 | 41.2685 | 58.1441 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-01-10 15:00 | 0 | 0 | 0 | 0 | -22.0565 | 59.0195 | 104.9667 | -14.9667 | 55.3359 | 69.7128 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.4 | -1.4 | 1.1056 | 0
2015-01-10 16:00 | 0 | 0 | 0 | 0 | -22.0505 | 74.0154 | 107.9503 | -17.9503 | 69.4894 | 82.2661 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-01-10 17:00 | 0 | 0 | 0 | 0 | -22.0445 | 89.0113 | 111.2262 | -21.2262 | 83.8277 | 95.4069 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.1064 | 0
2015-01-10 18:00 | 0 | 0 | 0 | 0 | -22.0385 | 104.0072 | 114.5924 | -24.5924 | 98.4717 | 108.9104 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-01-10 19:00 | 0 | 0 | 0 | 0 | -22.0324 | 119.003 | 117.8285 | -27.8285 | 113.545 | 122.6397 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.11 | 0
2015-01-10 20:00 | 0 | 0 | 0 | 0 | -22.0264 | 133.9989 | 120.7034 | -30.7034 | 129.1437 | 136.4985 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.11 | 0
2015-01-10 21:00 | 0 | 0 | 0 | 0 | -22.0204 | 148.9948 | 122.9886 | -32.9886 | 145.2968 | 150.3915 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.11 | 0
2015-01-10 22:00 | 0 | 0 | 0 | 0 | -22.0143 | 163.9907 | 124.4821 | -34.4821 | 161.9297 | 164.0979 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.1 | -2.1 | 1.1084 | 0
2015-01-10 23:00 | 0 | 0 | 0 | 0 | -22.0082 | 178.9866 | 125.0393 | -35.0393 | 178.8524 | 174.8688 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-01-11 | 0 | 0 | 0 | 0 | -22.0021 | -166.0175 | 124.6031 | -34.6031 | -164.2064 | 165.8981 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-01-11 01:00 | 0 | 0 | 0 | 0 | -21.9961 | -151.0216 | 123.2174 | -33.2174 | -147.5235 | 152.2661 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-01-11 02:00 | 0 | 0 | 0 | 0 | -21.9899 | -136.0257 | 121.0165 | -31.0165 | -131.3026 | 138.3761 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-01-11 03:00 | 0 | 0 | 0 | 0 | -21.9838 | -121.0298 | 118.1967 | -28.1967 | -115.633 | 124.5022 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.1132 | 0
2015-01-11 04:00 | 0 | 0 | 0 | 0 | -21.9777 | -106.0339 | 114.9841 | -24.9841 | -100.4971 | 110.7442 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-01-11 05:00 | 0 | 0 | 0 | 0 | -21.9715 | -91.038 | 111.6106 | -21.6106 | -85.805 | 97.1952 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.6 | -3.6 | 1.1144 | 0
2015-01-11 06:00 | 0 | 0 | 0 | 0 | -21.9654 | -76.0421 | 108.2982 | -18.2982 | -71.4344 | 83.9838 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.6 | -3.6 | 1.1144 | 0
2015-01-11 07:00 | 0 | 0 | 0 | 0 | -21.9592 | -61.0462 | 105.2517 | -15.2517 | -57.2622 | 71.3179 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.1132 | 0
2015-01-11 08:00 | 0 | 0 | 0 | 0 | -21.953 | -46.0503 | 102.6532 | -12.6532 | -43.1858 | 59.5629 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.11 | 0
2015-01-11 09:00 | 0 | 0 | 0 | 0 | -21.9468 | -31.0544 | 100.6566 | -10.6566 | -29.1347 | 49.387 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.8 | -2.8 | 1.1112 | 0
2015-01-11 10:00 | 0 | 0 | 0 | 0 | -21.9406 | -16.0584 | 99.381 | -9.381 | -15.0737 | 41.9657 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.8 | -2.8 | 1.1112 | 0
2015-01-11 11:00 | 0 | 0 | 0 | 0 | -21.9344 | -1.0625 | 98.9031 | -8.9031 | -0.99762 | 38.915 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-01-11 12:00 | 0 | 0 | 0 | 0 | -21.9282 | 13.9334 | 99.252 | -9.252 | 13.0804 | 41.2193 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-01-11 13:00 | 0 | 0 | 0 | 0 | -21.9219 | 28.9294 | 100.4058 | -10.4058 | 27.1459 | 48.1143 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-01-11 14:00 | 0 | 0 | 0 | 0 | -21.9157 | 43.9253 | 102.2945 | -12.2945 | 41.2004 | 57.9814 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-01-11 15:00 | 0 | 0 | 0 | 0 | -21.9094 | 58.9212 | 104.8044 | -14.8044 | 55.2739 | 69.5617 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-01-11 16:00 | 0 | 0 | 0 | 0 | -21.9031 | 73.9172 | 107.786 | -17.786 | 69.4315 | 82.1266 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3 | -3 | 1.112 | 0
2015-01-11 17:00 | 0 | 0 | 0 | 0 | -21.8968 | 88.9131 | 111.0609 | -21.0609 | 83.7713 | 95.2784 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-01-11 18:00 | 0 | 0 | 0 | 0 | -21.8905 | 103.9091 | 114.4268 | -24.4268 | 98.4137 | 108.7924 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4 | -4 | 1.116 | 0
2015-01-11 19:00 | 0 | 0 | 0 | 0 | -21.8842 | 118.905 | 117.6637 | -27.6637 | 113.4823 | 122.5323 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.6 | -4.6 | 1.1184 | 0
2015-01-11 20:00 | 0 | 0 | 0 | 0 | -21.8778 | 133.901 | 120.5403 | -30.5403 | 129.0726 | 136.4029 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.7 | -4.7 | 1.1188 | 0
2015-01-11 21:00 | 0 | 0 | 0 | 0 | -21.8715 | 148.897 | 122.8286 | -32.8286 | 145.2143 | 150.3116 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.1 | -5.1 | 1.1204 | 0
2015-01-11 22:00 | 0 | 0 | 0 | 0 | -21.8651 | 163.8929 | 124.3265 | -34.3265 | 161.8338 | 164.05 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-01-11 23:00 | 0 | 0 | 0 | 0 | -21.8588 | 178.8889 | 124.8894 | -34.8894 | 178.7428 | 174.997 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.4 | -5.4 | 1.1216 | 0
2015-01-12 | 0 | 0 | 0 | 0 | -21.8524 | -166.1151 | 124.4596 | -34.4596 | -164.328 | 166.031 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1208 | 0
2015-01-12 01:00 | 0 | 0 | 0 | 0 | -21.846 | -151.1192 | 123.0804 | -33.0804 | -147.654 | 152.3697 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.3 | -5.3 | 1.1212 | 0
2015-01-12 02:00 | 0 | 0 | 0 | 0 | -21.8396 | -136.1232 | 120.8852 | -30.8852 | -131.4382 | 138.4634 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-01-12 03:00 | 0 | 0 | 0 | 0 | -21.8332 | -121.1272 | 118.0695 | -28.0695 | -115.7704 | 124.5762 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.1 | -5.1 | 1.1204 | 0
2015-01-12 04:00 | 0 | 0 | 0 | 0 | -21.8267 | -106.1312 | 114.8591 | -24.8591 | -100.6335 | 110.8052 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-01-12 05:00 | 0 | 0 | 0 | 0 | -21.8203 | -91.1352 | 111.4857 | -21.4857 | -85.9385 | 97.2419 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1208 | 0
2015-01-12 06:00 | 0 | 0 | 0 | 0 | -21.8138 | -76.1392 | 108.1715 | -18.1715 | -71.5635 | 84.0136 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1196 | 0
2015-01-12 07:00 | 0 | 0 | 0 | 0 | -21.8074 | -61.1432 | 105.1215 | -15.1215 | -57.3857 | 71.3265 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1208 | 0
2015-01-12 08:00 | 0 | 0 | 0 | 0 | -21.8009 | -46.1472 | 102.5181 | -12.5181 | -43.3027 | 59.5434 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.8 | -4.8 | 1.1192 | 0
2015-01-12 09:00 | 0 | 0 | 0 | 0 | -21.7944 | -31.1512 | 100.5159 | -10.5159 | -29.2439 | 49.3299 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1196 | 0
2015-01-12 10:00 | 0 | 0 | 0 | 0 | -21.7879 | -16.1552 | 99.2342 | -9.2342 | -15.1743 | 41.8612 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.1 | -5.1 | 1.1204 | 0
2015-01-12 11:00 | 0 | 0 | 0 | 0 | -21.7814 | -1.1592 | 98.7505 | -8.7505 | -1.0891 | 38.7647 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.2 | -6.2 | 1.1248 | 0
2015-01-12 12:00 | 0 | 0 | 0 | 0 | -21.7748 | 13.8368 | 99.094 | -9.094 | 12.9982 | 41.0443 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.2 | -6.2 | 1.1248 | 0
2015-01-12 13:00 | 0 | 0 | 0 | 0 | -21.7683 | 28.8328 | 100.2432 | -10.2432 | 27.0727 | 47.9383 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.3 | -6.3 | 1.1252 | 0
2015-01-12 14:00 | 0 | 0 | 0 | 0 | -21.7617 | 43.8288 | 102.1282 | -12.1282 | 41.1351 | 57.8155 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.1 | -6.1 | 1.1244 | 0
2015-01-12 15:00 | 0 | 0 | 0 | 0 | -21.7552 | 58.8249 | 104.6354 | -14.6354 | 55.215 | 69.4086 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.2 | -6.2 | 1.1248 | 0
2015-01-12 16:00 | 0 | 0 | 0 | 0 | -21.7486 | 73.8209 | 107.6153 | -17.6153 | 69.377 | 81.986 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.5 | -6.5 | 1.126 | 0
2015-01-12 17:00 | 0 | 0 | 0 | 0 | -21.742 | 88.8169 | 110.8891 | -20.8891 | 83.7185 | 95.1494 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.7 | -5.7 | 1.1228 | 0
2015-01-12 18:00 | 0 | 0 | 0 | 0 | -21.7354 | 103.8129 | 114.2548 | -24.2548 | 98.3596 | 108.6745 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.4 | -5.4 | 1.1216 | 0
2015-01-12 19:00 | 0 | 0 | 0 | 0 | -21.7288 | 118.809 | 117.4923 | -27.4923 | 113.4233 | 122.4254 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.1 | -6.1 | 1.1244 | 0
2015-01-12 20:00 | 0 | 0 | 0 | 0 | -21.7221 | 133.805 | 120.3706 | -30.3706 | 129.0052 | 136.3082 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.6 | -6.6 | 1.1264 | 0
2015-01-12 21:00 | 0 | 0 | 0 | 0 | -21.7155 | 148.8011 | 122.6618 | -32.6618 | 145.1352 | 150.2332 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.2 | -7.2 | 1.1288 | 0
2015-01-12 22:00 | 0 | 0 | 0 | 0 | -21.7089 | 163.7971 | 124.1639 | -34.1639 | 161.7408 | 164.0038 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.5 | -6.5 | 1.126 | 0
2015-01-12 23:00 | 0 | 0 | 0 | 0 | -21.7022 | 178.7932 | 124.7323 | -34.7323 | 178.6356 | 175.1296 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.9 | -8.9 | 1.1356 | 0
2015-01-13 | 0 | 0 | 0 | 0 | -21.6955 | -166.2108 | 124.3089 | -34.3089 | -164.4478 | 166.1635 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.7 | -8.7 | 1.1348 | 0
2015-01-13 01:00 | 0 | 0 | 0 | 0 | -21.6888 | -151.2147 | 122.9361 | -32.9361 | -147.7832 | 152.4716 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7 | -7 | 1.128 | 0
2015-01-13 02:00 | 0 | 0 | 0 | 0 | -21.6821 | -136.2186 | 120.7465 | -30.7465 | -131.5731 | 138.5484 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.3 | -6.3 | 1.1252 | 0
2015-01-13 03:00 | 0 | 0 | 0 | 0 | -21.6754 | -121.2226 | 117.9349 | -27.9349 | -115.9073 | 124.6475 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.3 | -5.3 | 1.1212 | 0
2015-01-13 04:00 | 0 | 0 | 0 | 0 | -21.6687 | -106.2265 | 114.7268 | -24.7268 | -100.7697 | 110.863 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.1 | -5.1 | 1.1204 | 0
2015-01-13 05:00 | 0 | 0 | 0 | 0 | -21.6619 | -91.2304 | 111.3535 | -21.3535 | -86.0719 | 97.2851 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1208 | 0
2015-01-13 06:00 | 0 | 0 | 0 | 0 | -21.6552 | -76.2344 | 108.0375 | -18.0375 | -71.6924 | 84.0394 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.118 | 0
2015-01-13 07:00 | 0 | 0 | 0 | 0 | -21.6484 | -61.2383 | 104.984 | -14.984 | -57.5089 | 71.3304 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-01-13 08:00 | 0 | 0 | 0 | 0 | -21.6417 | -46.2422 | 102.3758 | -12.3758 | -43.4189 | 59.5187 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.8 | -5.8 | 1.1232 | 0
2015-01-13 09:00 | 0 | 0 | 0 | 0 | -21.6349 | -31.2461 | 100.368 | -10.368 | -29.3522 | 49.2667 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.7 | -6.7 | 1.1268 | 0
2015-01-13 10:00 | 0 | 0 | 0 | 0 | -21.6281 | -16.25 | 99.0804 | -9.0804 | -15.2736 | 41.7501 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.5 | -7.5 | 1.13 | 0
2015-01-13 11:00 | 0 | 0 | 0 | 0 | -21.6213 | -1.2539 | 98.5908 | -8.5908 | -1.1789 | 38.6075 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.5 | -8.5 | 1.134 | 0
2015-01-13 12:00 | 0 | 0 | 0 | 0 | -21.6144 | 13.7422 | 98.929 | -8.929 | 12.9181 | 40.8634 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.9 | -7.9 | 1.1316 | 0
2015-01-13 13:00 | 0 | 0 | 0 | 0 | -21.6076 | 28.7383 | 100.0738 | -10.0738 | 27.002 | 47.7578 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.5 | -7.5 | 1.13 | 0
2015-01-13 14:00 | 0 | 0 | 0 | 0 | -21.6008 | 43.7344 | 101.9553 | -11.9553 | 41.0728 | 57.6466 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.9 | -6.9 | 1.1276 | 0
2015-01-13 15:00 | 0 | 0 | 0 | 0 | -21.5939 | 58.7305 | 104.4599 | -14.4599 | 55.1595 | 69.2536 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.2 | -6.2 | 1.1248 | 0
2015-01-13 16:00 | 0 | 0 | 0 | 0 | -21.587 | 73.7266 | 107.438 | -17.438 | 69.326 | 81.8444 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.2 | -6.2 | 1.1248 | 0
2015-01-13 17:00 | 0 | 0 | 0 | 0 | -21.5801 | 88.7227 | 110.7109 | -20.7109 | 83.6694 | 95.0201 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.8 | -5.8 | 1.1232 | 0
2015-01-13 18:00 | 0 | 0 | 0 | 0 | -21.5732 | 103.7189 | 114.0764 | -24.0764 | 98.3092 | 108.5567 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.3 | -6.3 | 1.1252 | 0
2015-01-13 19:00 | 0 | 0 | 0 | 0 | -21.5663 | 118.715 | 117.3145 | -27.3145 | 113.3681 | 122.3191 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.1 | -6.1 | 1.1244 | 0
2015-01-13 20:00 | 0 | 0 | 0 | 0 | -21.5594 | 133.7111 | 120.1943 | -30.1943 | 128.9415 | 136.2146 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.8 | -6.8 | 1.1272 | 0
2015-01-13 21:00 | 0 | 0 | 0 | 0 | -21.5525 | 148.7073 | 122.4882 | -32.4882 | 145.0595 | 150.156 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.1 | -7.1 | 1.1284 | 0
2015-01-13 22:00 | 0 | 0 | 0 | 0 | -21.5455 | 163.7034 | 123.9944 | -33.9944 | 161.6509 | 163.959 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.2 | -7.2 | 1.1288 | 0
2015-01-13 23:00 | 0 | 0 | 0 | 0 | -21.5386 | 178.6995 | 124.5681 | -34.5681 | 178.531 | 175.2662 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.8 | -6.8 | 1.1272 | 0
2015-01-14 | 0 | 0 | 0 | 0 | -21.5316 | -166.3043 | 124.151 | -34.151 | -164.5657 | 166.2954 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.1 | -7.1 | 1.1284 | 0
2015-01-14 01:00 | 0 | 0 | 0 | 0 | -21.5246 | -151.3082 | 122.7845 | -32.7845 | -147.9111 | 152.5716 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.8 | -6.8 | 1.1272 | 0
2015-01-14 02:00 | 0 | 0 | 0 | 0 | -21.5176 | -136.312 | 120.6004 | -30.6004 | -131.707 | 138.631 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.7 | -6.7 | 1.1268 | 0
2015-01-14 03:00 | 0 | 0 | 0 | 0 | -21.5106 | -121.3159 | 117.793 | -27.793 | -116.0437 | 124.716 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.6 | -7.6 | 1.1304 | 0
2015-01-14 04:00 | 0 | 0 | 0 | 0 | -21.5036 | -106.3197 | 114.5871 | -24.5871 | -100.9056 | 110.9177 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.9 | -7.9 | 1.1316 | 0
2015-01-14 05:00 | 0 | 0 | 0 | 0 | -21.4966 | -91.3236 | 111.214 | -21.214 | -86.205 | 97.3246 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.4 | -8.4 | 1.1336 | 0
2015-01-14 06:00 | 0 | 0 | 0 | 0 | -21.4895 | -76.3274 | 107.8962 | -17.8962 | -71.821 | 84.0611 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.8 | -8.8 | 1.1352 | 0
2015-01-14 07:00 | 0 | 0 | 0 | 0 | -21.4825 | -61.3312 | 104.8392 | -14.8392 | -57.6316 | 71.3299 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.6 | -9.6 | 1.1384 | 0
2015-01-14 08:00 | 0 | 0 | 0 | 0 | -21.4754 | -46.335 | 102.2263 | -12.2263 | -43.5345 | 59.4888 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.3 | -9.3 | 1.1372 | 0
2015-01-14 09:00 | 0 | 0 | 0 | 0 | -21.4683 | -31.3389 | 100.2129 | -10.2129 | -29.4594 | 49.1976 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.7 | -8.7 | 1.1348 | 0
2015-01-14 10:00 | 0 | 0 | 0 | 0 | -21.4612 | -16.3427 | 98.9194 | -8.9194 | -15.3716 | 41.6322 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.1 | -9.1 | 1.1364 | 0
2015-01-14 11:00 | 0 | 0 | 0 | 0 | -21.4541 | -1.3465 | 98.4242 | -8.4242 | -1.2669 | 38.4435 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.6 | -8.6 | 1.1344 | 0
2015-01-14 12:00 | 0 | 0 | 0 | 0 | -21.447 | 13.6497 | 98.7572 | -8.7572 | 12.8403 | 40.6765 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.4 | -8.4 | 1.1336 | 0
2015-01-14 13:00 | 0 | 0 | 0 | 0 | -21.4399 | 28.6459 | 99.8977 | -9.8977 | 26.934 | 47.573 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8 | -8 | 1.132 | 0
2015-01-14 14:00 | 0 | 0 | 0 | 0 | -21.4328 | 43.6421 | 101.7758 | -11.7758 | 41.0135 | 57.4748 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.1 | -8.1 | 1.1324 | 0
2015-01-14 15:00 | 0 | 0 | 0 | 0 | -21.4256 | 58.6383 | 104.2779 | -14.2779 | 55.1072 | 69.0969 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8 | -8 | 1.132 | 0
2015-01-14 16:00 | 0 | 0 | 0 | 0 | -21.4185 | 73.6345 | 107.2544 | -17.2544 | 69.2786 | 81.7019 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8 | -8 | 1.132 | 0
2015-01-14 17:00 | 0 | 0 | 0 | 0 | -21.4113 | 88.6307 | 110.5264 | -20.5264 | 83.624 | 94.8905 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.9 | -7.9 | 1.1316 | 0
2015-01-14 18:00 | 0 | 0 | 0 | 0 | -21.4041 | 103.6269 | 113.8917 | -23.8917 | 98.2627 | 108.4392 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.3 | -8.3 | 1.1332 | 0
2015-01-14 19:00 | 0 | 0 | 0 | 0 | -21.3969 | 118.6231 | 117.1303 | -27.1303 | 113.3167 | 122.2136 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9 | -9 | 1.136 | 0
2015-01-14 20:00 | 0 | 0 | 0 | 0 | -21.3897 | 133.6193 | 120.0116 | -30.0116 | 128.8815 | 136.1219 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.9 | -7.9 | 1.1316 | 0
2015-01-14 21:00 | 0 | 0 | 0 | 0 | -21.3825 | 148.6156 | 122.308 | -32.308 | 144.9874 | 150.0802 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9 | -9 | 1.136 | 0
2015-01-14 22:00 | 0 | 0 | 0 | 0 | -21.3752 | 163.6118 | 123.8181 | -33.8181 | 161.5642 | 163.9156 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.2 | -9.2 | 1.1368 | 0
2015-01-14 23:00 | 0 | 0 | 0 | 0 | -21.368 | 178.608 | 124.397 | -34.397 | 178.429 | 175.4066 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9 | -9 | 1.136 | 0
2015-01-15 | 0 | 0 | 0 | 0 | -21.3607 | -166.3957 | 123.9859 | -33.9859 | -164.6814 | 166.4263 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.9 | -8.9 | 1.1356 | 0
2015-01-15 01:00 | 0 | 0 | 0 | 0 | -21.3535 | -151.3995 | 122.6257 | -32.6257 | -148.0374 | 152.6694 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.2 | -9.2 | 1.1368 | 0
2015-01-15 02:00 | 0 | 0 | 0 | 0 | -21.3462 | -136.4033 | 120.4471 | -30.4471 | -131.8399 | 138.711 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.3 | -9.3 | 1.1372 | 0
2015-01-15 03:00 | 0 | 0 | 0 | 0 | -21.3389 | -121.407 | 117.6438 | -27.6438 | -116.1795 | 124.7815 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.7 | -9.7 | 1.1388 | 0
2015-01-15 04:00 | 0 | 0 | 0 | 0 | -21.3316 | -106.4108 | 114.4402 | -24.4402 | -101.041 | 110.9691 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.2 | -9.2 | 1.1368 | 0
2015-01-15 05:00 | 0 | 0 | 0 | 0 | -21.3243 | -91.4145 | 111.0673 | -21.0673 | -86.3377 | 97.3605 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.7 | -9.7 | 1.1388 | 0
2015-01-15 06:00 | 0 | 0 | 0 | 0 | -21.3169 | -76.4183 | 107.7477 | -17.7477 | -71.9493 | 84.0787 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.6 | -9.6 | 1.1384 | 0
2015-01-15 07:00 | 0 | 0 | 0 | 0 | -21.3096 | -61.422 | 104.6873 | -14.6873 | -57.7538 | 71.3247 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10 | -10 | 1.14 | 0
2015-01-15 08:00 | 0 | 0 | 0 | 0 | -21.3022 | -46.4257 | 102.0697 | -12.0697 | -43.6492 | 59.4537 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.7 | -10.7 | 1.1428 | 0
2015-01-15 09:00 | 0 | 0 | 0 | 0 | -21.2949 | -31.4295 | 100.0507 | -10.0507 | -29.5655 | 49.1226 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.4 | -10.4 | 1.1416 | 0
2015-01-15 10:00 | 0 | 0 | 0 | 0 | -21.2875 | -16.4332 | 98.7514 | -8.7514 | -15.468 | 41.5078 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.3 | -10.3 | 1.1412 | 0
2015-01-15 11:00 | 0 | 0 | 0 | 0 | -21.2801 | -1.4369 | 98.2506 | -8.2506 | -1.3529 | 38.2727 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11 | -11 | 1.144 | 0
2015-01-15 12:00 | 0 | 0 | 0 | 0 | -21.2727 | 13.5594 | 98.5786 | -8.5786 | 12.7648 | 40.4839 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.9 | -10.9 | 1.1436 | 0
2015-01-15 13:00 | 0 | 0 | 0 | 0 | -21.2653 | 28.5557 | 99.715 | -9.715 | 26.8686 | 47.384 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.6 | -10.6 | 1.1424 | 0
2015-01-15 14:00 | 0 | 0 | 0 | 0 | -21.2579 | 43.5519 | 101.5898 | -11.5898 | 40.9572 | 57.3003 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.1 | -11.1 | 1.1444 | 0
2015-01-15 15:00 | 0 | 0 | 0 | 0 | -21.2504 | 58.5482 | 104.0896 | -14.0896 | 55.0583 | 68.9386 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12 | -12 | 1.148 | 0
2015-01-15 16:00 | 0 | 0 | 0 | 0 | -21.243 | 73.5445 | 107.0645 | -17.0645 | 69.2347 | 81.5585 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.6 | -11.6 | 1.1464 | 0
2015-01-15 17:00 | 0 | 0 | 0 | 0 | -21.2355 | 88.5408 | 110.3357 | -20.3357 | 83.5824 | 94.7607 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.6 | -11.6 | 1.1464 | 0
2015-01-15 18:00 | 0 | 0 | 0 | 0 | -21.2281 | 103.5371 | 113.7008 | -23.7008 | 98.22 | 108.322 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.1 | -12.1 | 1.1484 | 0
2015-01-15 19:00 | 0 | 0 | 0 | 0 | -21.2206 | 118.5335 | 116.9398 | -26.9398 | 113.2693 | 122.1087 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12 | -12 | 1.148 | 0
2015-01-15 20:00 | 0 | 0 | 0 | 0 | -21.2131 | 133.5298 | 119.8224 | -29.8224 | 128.8254 | 136.0303 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.3 | -12.3 | 1.1492 | 0
2015-01-15 21:00 | 0 | 0 | 0 | 0 | -21.2056 | 148.5261 | 122.1213 | -32.1213 | 144.9189 | 150.0056 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.3 | -12.3 | 1.1492 | 0
2015-01-15 22:00 | 0 | 0 | 0 | 0 | -21.198 | 163.5224 | 123.6351 | -33.6351 | 161.4807 | 163.8734 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.7 | -11.7 | 1.1468 | 0
2015-01-15 23:00 | 0 | 0 | 0 | 0 | -21.1905 | 178.5187 | 124.219 | -34.219 | 178.3297 | 175.5503 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.8 | -11.8 | 1.1472 | 0
2015-01-16 | 0 | 0 | 0 | 0 | -21.183 | -166.4849 | 123.8138 | -33.8138 | -164.795 | 166.5559 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12 | -12 | 1.148 | 0
2015-01-16 01:00 | 0 | 0 | 0 | 0 | -21.1754 | -151.4886 | 122.4597 | -32.4597 | -148.1621 | 152.7649 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.1 | -12.1 | 1.1484 | 0
2015-01-16 02:00 | 0 | 0 | 0 | 0 | -21.1679 | -136.4923 | 120.2867 | -30.2867 | -131.9717 | 138.7884 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.3 | -12.3 | 1.1492 | 0
2015-01-16 03:00 | 0 | 0 | 0 | 0 | -21.1603 | -121.4959 | 117.4874 | -27.4874 | -116.3144 | 124.8441 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.7 | -12.7 | 1.1508 | 0
2015-01-16 04:00 | 0 | 0 | 0 | 0 | -21.1527 | -106.4996 | 114.286 | -24.286 | -101.1759 | 111.0171 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.9 | -12.9 | 1.1516 | 0
2015-01-16 05:00 | 0 | 0 | 0 | 0 | -21.1451 | -91.5032 | 110.9134 | -20.9134 | -86.47 | 97.3927 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.8 | -12.8 | 1.1512 | 0
2015-01-16 06:00 | 0 | 0 | 0 | 0 | -21.1375 | -76.5069 | 107.5921 | -17.5921 | -72.077 | 84.0923 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.6 | -13.6 | 1.1544 | 0
2015-01-16 07:00 | 0 | 0 | 0 | 0 | -21.1298 | -61.5105 | 104.5283 | -14.5283 | -57.8753 | 71.3149 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.7 | -13.7 | 1.1548 | 0
2015-01-16 08:00 | 0 | 0 | 0 | 0 | -21.1222 | -46.5142 | 101.906 | -11.906 | -43.7631 | 59.4134 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.5 | -13.5 | 1.154 | 0
2015-01-16 09:00 | 0 | 0 | 0 | 0 | -21.1146 | -31.5178 | 99.8816 | -9.8816 | -29.6704 | 49.0417 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.6 | -13.6 | 1.1544 | 0
2015-01-16 10:00 | 0 | 0 | 0 | 0 | -21.1069 | -16.5214 | 98.5765 | -8.5765 | -15.5629 | 41.3767 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.2 | -13.2 | 1.1528 | 0
2015-01-16 11:00 | 0 | 0 | 0 | 0 | -21.0992 | -1.5251 | 98.0702 | -8.0702 | -1.437 | 38.0953 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.4 | -13.4 | 1.1536 | 0
2015-01-16 12:00 | 0 | 0 | 0 | 0 | -21.0915 | 13.4713 | 98.3933 | -8.3933 | 12.6917 | 40.2855 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.5 | -13.5 | 1.154 | 0
2015-01-16 13:00 | 0 | 0 | 0 | 0 | -21.0838 | 28.4677 | 99.5256 | -9.5256 | 26.806 | 47.1908 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.3 | -13.3 | 1.1532 | 0
2015-01-16 14:00 | 0 | 0 | 0 | 0 | -21.0761 | 43.4641 | 101.3973 | -11.3973 | 40.904 | 57.1232 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.3 | -13.3 | 1.1532 | 0
2015-01-16 15:00 | 0 | 0 | 0 | 0 | -21.0684 | 58.4605 | 103.8949 | -13.8949 | 55.0128 | 68.7787 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.7 | -13.7 | 1.1548 | 0
2015-01-16 16:00 | 0 | 0 | 0 | 0 | -21.0607 | 73.4569 | 106.8685 | -16.8685 | 69.1946 | 81.4145 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15 | -15 | 1.16 | 0
2015-01-16 17:00 | 0 | 0 | 0 | 0 | -21.0529 | 88.4533 | 110.1388 | -20.1388 | 83.5447 | 94.6308 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.1 | -15.1 | 1.1604 | 0
2015-01-16 18:00 | 0 | 0 | 0 | 0 | -21.0452 | 103.4497 | 113.5037 | -23.5037 | 98.1814 | 108.2052 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.6 | -15.6 | 1.1624 | 0
2015-01-16 19:00 | 0 | 0 | 0 | 0 | -21.0374 | 118.4461 | 116.7431 | -26.7431 | 113.2259 | 122.0046 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.4 | -16.4 | 1.1656 | 0
2015-01-16 20:00 | 0 | 0 | 0 | 0 | -21.0296 | 133.4425 | 119.6269 | -29.6269 | 128.7731 | 135.9398 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.4 | -16.4 | 1.1656 | 0
2015-01-16 21:00 | 0 | 0 | 0 | 0 | -21.0219 | 148.4389 | 121.928 | -31.928 | 144.854 | 149.9322 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.2 | -16.2 | 1.1648 | 0
2015-01-16 22:00 | 0 | 0 | 0 | 0 | -21.014 | 163.4353 | 123.4454 | -33.4454 | 161.4005 | 163.8323 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.7 | -15.7 | 1.1628 | 0
2015-01-16 23:00 | 0 | 0 | 0 | 0 | -21.0062 | 178.4317 | 124.0341 | -34.0341 | 178.2333 | 175.697 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.2 | -15.2 | 1.1608 | 0
2015-01-17 | 0 | 0 | 0 | 0 | -20.9984 | -166.5718 | 123.6347 | -33.6347 | -164.9063 | 166.6837 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.6 | -15.6 | 1.1624 | 0
2015-01-17 01:00 | 0 | 0 | 0 | 0 | -20.9906 | -151.5754 | 122.2867 | -32.2867 | -148.2851 | 152.858 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16 | -16 | 1.164 | 0
2015-01-17 02:00 | 0 | 0 | 0 | 0 | -20.9827 | -136.579 | 120.1191 | -30.1191 | -132.1023 | 138.8628 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.7 | -15.7 | 1.1628 | 0
2015-01-17 03:00 | 0 | 0 | 0 | 0 | -20.9749 | -121.5825 | 117.3239 | -27.3239 | -116.4485 | 124.9035 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.2 | -15.2 | 1.1608 | 0
2015-01-17 04:00 | 0 | 0 | 0 | 0 | -20.967 | -106.5861 | 114.1248 | -24.1248 | -101.3102 | 111.0617 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.2 | -15.2 | 1.1608 | 0
2015-01-17 05:00 | 0 | 0 | 0 | 0 | -20.9591 | -91.5896 | 110.7523 | -20.7523 | -86.6018 | 97.4211 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.3 | -15.3 | 1.1612 | 0
2015-01-17 06:00 | 0 | 0 | 0 | 0 | -20.9512 | -76.5932 | 107.4293 | -17.4293 | -72.2041 | 84.1016 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.7 | -15.7 | 1.1628 | 0
2015-01-17 07:00 | 0 | 0 | 0 | 0 | -20.9433 | -61.5967 | 104.3621 | -14.3621 | -57.996 | 71.3005 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.1 | -15.1 | 1.1604 | 0
2015-01-17 08:00 | 0 | 0 | 0 | 0 | -20.9354 | -46.6003 | 101.7352 | -11.7352 | -43.876 | 59.3679 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.4 | -14.4 | 1.1576 | 0
2015-01-17 09:00 | 0 | 0 | 0 | 0 | -20.9275 | -31.6038 | 99.7054 | -9.7054 | -29.774 | 48.955 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.8 | -13.8 | 1.1552 | 0
2015-01-17 10:00 | 0 | 0 | 0 | 0 | -20.9195 | -16.6073 | 98.3948 | -8.3948 | -15.6561 | 41.2392 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.2 | -15.2 | 1.1608 | 0
2015-01-17 11:00 | 0 | 0 | 0 | 0 | -20.9116 | -1.6109 | 97.883 | -7.883 | -1.5191 | 37.9112 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.5 | -14.5 | 1.158 | 0
2015-01-17 12:00 | 0 | 0 | 0 | 0 | -20.9036 | 13.3856 | 98.2014 | -8.2014 | 12.621 | 40.0815 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.1 | -14.1 | 1.1564 | 0
2015-01-17 13:00 | 0 | 0 | 0 | 0 | -20.8956 | 28.3821 | 99.3298 | -9.3298 | 26.7462 | 46.9937 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14 | -14 | 1.156 | 0
2015-01-17 14:00 | 0 | 0 | 0 | 0 | -20.8876 | 43.3786 | 101.1986 | -11.1986 | 40.854 | 56.9435 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.3 | -14.3 | 1.1572 | 0
2015-01-17 15:00 | 0 | 0 | 0 | 0 | -20.8796 | 58.3751 | 103.6941 | -13.6941 | 54.9708 | 68.6174 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.4 | -14.4 | 1.1576 | 0
2015-01-17 16:00 | 0 | 0 | 0 | 0 | -20.8716 | 73.3716 | 106.6663 | -16.6663 | 69.1581 | 81.2698 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.8 | -14.8 | 1.1592 | 0
2015-01-17 17:00 | 0 | 0 | 0 | 0 | -20.8636 | 88.3681 | 109.9359 | -19.9359 | 83.5108 | 94.5009 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.2 | -15.2 | 1.1608 | 0
2015-01-17 18:00 | 0 | 0 | 0 | 0 | -20.8556 | 103.3646 | 113.3006 | -23.3006 | 98.1466 | 108.0888 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.7 | -14.7 | 1.1588 | 0
2015-01-17 19:00 | 0 | 0 | 0 | 0 | -20.8475 | 118.3611 | 116.5403 | -26.5403 | 113.1864 | 121.9012 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.3 | -16.3 | 1.1652 | 0
2015-01-17 20:00 | 0 | 0 | 0 | 0 | -20.8395 | 133.3576 | 119.4252 | -29.4252 | 128.7247 | 135.8503 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.5 | -16.5 | 1.166 | 0
2015-01-17 21:00 | 0 | 0 | 0 | 0 | -20.8314 | 148.3541 | 121.7284 | -31.7284 | 144.7929 | 149.8601 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.1 | -16.1 | 1.1644 | 0
2015-01-17 22:00 | 0 | 0 | 0 | 0 | -20.8233 | 163.3506 | 123.2491 | -33.2491 | 161.3237 | 163.7921 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.8 | -14.8 | 1.1592 | 0
2015-01-17 23:00 | 0 | 0 | 0 | 0 | -20.8152 | 178.3471 | 123.8425 | -33.8425 | 178.1398 | 175.846 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.2 | -15.2 | 1.1608 | 0
2015-01-18 | 0 | 0 | 0 | 0 | -20.8071 | -166.6563 | 123.4488 | -33.4488 | -165.0152 | 166.8095 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.3 | -15.3 | 1.1612 | 0
2015-01-18 01:00 | 0 | 0 | 0 | 0 | -20.799 | -151.6598 | 122.1066 | -32.1066 | -148.4062 | 152.9482 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.9 | -13.9 | 1.1556 | 0
2015-01-18 02:00 | 0 | 0 | 0 | 0 | -20.7909 | -136.6633 | 119.9444 | -29.9444 | -132.2314 | 138.9343 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.8 | -13.8 | 1.1552 | 0
2015-01-18 03:00 | 0 | 0 | 0 | 0 | -20.7827 | -121.6667 | 117.1533 | -27.1533 | -116.5816 | 124.9596 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.5 | -13.5 | 1.154 | 0
2015-01-18 04:00 | 0 | 0 | 0 | 0 | -20.7746 | -106.6702 | 113.9564 | -23.9564 | -101.4436 | 111.1028 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.9 | -12.9 | 1.1516 | 0
2015-01-18 05:00 | 0 | 0 | 0 | 0 | -20.7664 | -91.6736 | 110.5842 | -20.5842 | -86.7328 | 97.4457 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.8 | -11.8 | 1.1472 | 0
2015-01-18 06:00 | 0 | 0 | 0 | 0 | -20.7583 | -76.6771 | 107.2596 | -17.2596 | -72.3305 | 84.1068 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.5 | -11.5 | 1.146 | 0
2015-01-18 07:00 | 0 | 0 | 0 | 0 | -20.7501 | -61.6805 | 104.189 | -14.189 | -58.116 | 71.2815 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.3 | -11.3 | 1.1452 | 0
2015-01-18 08:00 | 0 | 0 | 0 | 0 | -20.7419 | -46.684 | 101.5576 | -11.5576 | -43.9878 | 59.3172 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.2 | -11.2 | 1.1448 | 0
2015-01-18 09:00 | 0 | 0 | 0 | 0 | -20.7337 | -31.6874 | 99.5224 | -9.5224 | -29.8763 | 48.8624 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.1 | -10.1 | 1.1404 | 0
2015-01-18 10:00 | 0 | 0 | 0 | 0 | -20.7255 | -16.6908 | 98.2062 | -8.2062 | -15.7476 | 41.0953 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.8 | -9.8 | 1.1392 | 0
2015-01-18 11:00 | 0 | 0 | 0 | 0 | -20.7172 | -1.6943 | 97.6892 | -7.6892 | -1.5991 | 37.7205 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.8 | -8.8 | 1.1352 | 0
2015-01-18 12:00 | 0 | 0 | 0 | 0 | -20.709 | 13.3023 | 98.003 | -8.003 | 12.5528 | 39.872 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.4 | -8.4 | 1.1336 | 0
2015-01-18 13:00 | 0 | 0 | 0 | 0 | -20.7007 | 28.2989 | 99.1277 | -9.1277 | 26.6893 | 46.7927 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.6 | -7.6 | 1.1304 | 0
2015-01-18 14:00 | 0 | 0 | 0 | 0 | -20.6925 | 43.2955 | 100.9936 | -10.9936 | 40.8072 | 56.7614 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.118 | 0
2015-01-18 15:00 | 0 | 0 | 0 | 0 | -20.6842 | 58.2921 | 103.4872 | -13.4872 | 54.9322 | 68.4548 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.118 | 0
2015-01-18 16:00 | 0 | 0 | 0 | 0 | -20.6759 | 73.2887 | 106.4581 | -16.4581 | 69.1253 | 81.1246 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.7 | -4.7 | 1.1188 | 0
2015-01-18 17:00 | 0 | 0 | 0 | 0 | -20.6676 | 88.2853 | 109.7271 | -19.7271 | 83.4809 | 94.3711 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.4 | -5.4 | 1.1216 | 0
2015-01-18 18:00 | 0 | 0 | 0 | 0 | -20.6593 | 103.2819 | 113.0915 | -23.0915 | 98.1159 | 107.9729 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.5 | -5.5 | 1.122 | 0
2015-01-18 19:00 | 0 | 0 | 0 | 0 | -20.651 | 118.2785 | 116.3316 | -26.3316 | 113.151 | 121.7987 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.1 | -6.1 | 1.1244 | 0
2015-01-18 20:00 | 0 | 0 | 0 | 0 | -20.6426 | 133.2751 | 119.2174 | -29.2174 | 128.6803 | 135.7618 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.4 | -6.4 | 1.1256 | 0
2015-01-18 21:00 | 0 | 0 | 0 | 0 | -20.6343 | 148.2717 | 121.5225 | -31.5225 | 144.7355 | 149.789 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.4 | -6.4 | 1.1256 | 0
2015-01-18 22:00 | 0 | 0 | 0 | 0 | -20.6259 | 163.2683 | 123.0464 | -33.0464 | 161.2503 | 163.7527 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.4 | -6.4 | 1.1256 | 0
2015-01-18 23:00 | 0 | 0 | 0 | 0 | -20.6176 | 178.265 | 123.6443 | -33.6443 | 178.0493 | 175.9968 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.5 | -6.5 | 1.126 | 0
2015-01-19 | 0 | 0 | 0 | 0 | -20.6092 | -166.7384 | 123.256 | -33.256 | -165.1216 | 166.9328 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.6 | -6.6 | 1.1264 | 0
2015-01-19 01:00 | 0 | 0 | 0 | 0 | -20.6008 | -151.7418 | 121.9197 | -31.9197 | -148.5253 | 153.0356 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.2 | -6.2 | 1.1248 | 0
2015-01-19 02:00 | 0 | 0 | 0 | 0 | -20.5924 | -136.7451 | 119.7628 | -29.7628 | -132.3591 | 139.0027 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.3 | -6.3 | 1.1252 | 0
2015-01-19 03:00 | 0 | 0 | 0 | 0 | -20.584 | -121.7485 | 116.9757 | -26.9757 | -116.7135 | 125.0124 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.6 | -5.6 | 1.1224 | 0
2015-01-19 04:00 | 0 | 0 | 0 | 0 | -20.5756 | -106.7518 | 113.7811 | -23.7811 | -101.5762 | 111.1403 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.3 | -5.3 | 1.1212 | 0
2015-01-19 05:00 | 0 | 0 | 0 | 0 | -20.5671 | -91.7552 | 110.4092 | -20.4092 | -86.8631 | 97.4664 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.9 | -5.9 | 1.1236 | 0
2015-01-19 06:00 | 0 | 0 | 0 | 0 | -20.5587 | -76.7585 | 107.0828 | -17.0828 | -72.4561 | 84.1078 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.9 | -5.9 | 1.1236 | 0
2015-01-19 07:00 | 0 | 0 | 0 | 0 | -20.5502 | -61.7619 | 104.009 | -14.009 | -58.235 | 71.2578 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-01-19 08:00 | 0 | 0 | 0 | 0 | -20.5418 | -46.7652 | 101.373 | -11.373 | -44.0984 | 59.2614 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3 | -3 | 1.112 | 0
2015-01-19 09:00 | 0 | 0 | 0 | 0 | -20.5333 | -31.7685 | 99.3326 | -9.3326 | -29.9771 | 48.7641 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.11 | 0
2015-01-19 10:00 | 0 | 0 | 0 | 0 | -20.5248 | -16.7719 | 98.011 | -8.011 | -15.8373 | 40.9449 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-01-19 11:00 | 0 | 0 | 0 | 0 | -20.5163 | -1.7752 | 97.4888 | -7.4888 | -1.6769 | 37.5234 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-01-19 12:00 | 0 | 0 | 0 | 0 | -20.5078 | 13.2215 | 97.7981 | -7.7981 | 12.4872 | 39.657 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-01-19 13:00 | 0 | 0 | 0 | 0 | -20.4992 | 28.2182 | 98.9192 | -8.9192 | 26.6353 | 46.588 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-01-19 14:00 | 0 | 0 | 0 | 0 | -20.4907 | 43.2149 | 100.7825 | -10.7825 | 40.7637 | 56.5771 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-01-19 15:00 | 0 | 0 | 0 | 0 | -20.4822 | 58.2116 | 103.2743 | -13.2743 | 54.8972 | 68.2911 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.1064 | 0
2015-01-19 16:00 | 0 | 0 | 0 | 0 | -20.4736 | 73.2083 | 106.2441 | -16.2441 | 69.0964 | 80.9791 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-01-19 17:00 | 0 | 0 | 0 | 0 | -20.465 | 88.205 | 109.5124 | -19.5124 | 83.4549 | 94.2414 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-01-19 18:00 | 0 | 0 | 0 | 0 | -20.4565 | 103.2017 | 112.8766 | -22.8766 | 98.0893 | 107.8576 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-01-19 19:00 | 0 | 0 | 0 | 0 | -20.4479 | 118.1984 | 116.1169 | -26.1169 | 113.1196 | 121.6971 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-01-19 20:00 | 0 | 0 | 0 | 0 | -20.4393 | 133.1951 | 119.0035 | -29.0035 | 128.6399 | 135.6745 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-01-19 21:00 | 0 | 0 | 0 | 0 | -20.4306 | 148.1919 | 121.3104 | -31.3104 | 144.6819 | 149.7191 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-01-19 22:00 | 0 | 0 | 0 | 0 | -20.422 | 163.1886 | 122.8372 | -32.8372 | 161.1804 | 163.7139 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-01-19 23:00 | 0 | 0 | 0 | 0 | -20.4134 | 178.1853 | 123.4394 | -33.4394 | 177.9618 | 176.1486 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-01-20 | 0 | 0 | 0 | 0 | -20.4047 | -166.8179 | 123.0565 | -33.0565 | -165.2255 | 167.0533 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-01-20 01:00 | 0 | 0 | 0 | 0 | -20.3961 | -151.8212 | 121.7259 | -31.7259 | -148.6425 | 153.1197 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-01-20 02:00 | 0 | 0 | 0 | 0 | -20.3874 | -136.8245 | 119.5742 | -29.5742 | -132.4852 | 139.0677 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-01-20 03:00 | 0 | 0 | 0 | 0 | -20.3787 | -121.8277 | 116.7912 | -26.7912 | -116.8443 | 125.0618 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-01-20 04:00 | 0 | 0 | 0 | 0 | -20.37 | -106.8309 | 113.5988 | -23.5988 | -101.7078 | 111.1741 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.1048 | 0
2015-01-20 05:00 | 0 | 0 | 0 | 0 | -20.3613 | -91.8342 | 110.2272 | -20.2272 | -86.9924 | 97.4832 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-01-20 06:00 | 0 | 0 | 0 | 0 | -20.3526 | -76.8374 | 106.8992 | -16.8992 | -72.5808 | 84.1045 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-01-20 07:00 | 0 | 0 | 0 | 0 | -20.3439 | -61.8407 | 103.8221 | -13.8221 | -58.353 | 71.2295 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-01-20 08:00 | 0 | 0 | 0 | 0 | -20.3351 | -46.8439 | 101.1817 | -11.1817 | -44.2079 | 59.2005 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-01-20 09:00 | 0 | 0 | 0 | 0 | -20.3264 | -31.8471 | 99.1361 | -9.1361 | -30.0764 | 48.6601 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-01-20 10:00 | 0 | 0 | 0 | 0 | -20.3176 | -16.8503 | 97.8091 | -7.8091 | -15.9252 | 40.7883 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.4 | -1.4 | 1.1056 | 0
2015-01-20 11:00 | 0 | 0 | 0 | 0 | -20.3088 | -1.8535 | 97.2819 | -7.2819 | -1.7524 | 37.3199 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-01-20 12:00 | 0 | 0 | 0 | 0 | -20.3001 | 13.1433 | 97.5869 | -7.5869 | 12.4241 | 39.4368 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-01-20 13:00 | 0 | 0 | 0 | 0 | -20.2913 | 28.1401 | 98.7045 | -8.7045 | 26.5843 | 46.3797 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.1064 | 0
2015-01-20 14:00 | 0 | 0 | 0 | 0 | -20.2825 | 43.1369 | 100.5653 | -10.5653 | 40.7234 | 56.3907 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-01-20 15:00 | 0 | 0 | 0 | 0 | -20.2736 | 58.1337 | 103.0555 | -13.0555 | 54.8658 | 68.1263 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-01-20 16:00 | 0 | 0 | 0 | 0 | -20.2648 | 73.1305 | 106.0242 | -16.0242 | 69.0712 | 80.8332 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.4 | -2.4 | 1.1096 | 0
2015-01-20 17:00 | 0 | 0 | 0 | 0 | -20.256 | 88.1273 | 109.292 | -19.292 | 83.4328 | 94.112 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-01-20 18:00 | 0 | 0 | 0 | 0 | -20.2471 | 103.1241 | 112.656 | -22.656 | 98.0667 | 107.7429 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-01-20 19:00 | 0 | 0 | 0 | 0 | -20.2383 | 118.1209 | 115.8964 | -25.8964 | 113.0924 | 121.5964 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3 | -3 | 1.112 | 0
2015-01-20 20:00 | 0 | 0 | 0 | 0 | -20.2294 | 133.1177 | 118.7838 | -28.7838 | 128.6036 | 135.5882 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-01-20 21:00 | 0 | 0 | 0 | 0 | -20.2205 | 148.1146 | 121.0922 | -31.0922 | 144.6322 | 149.6502 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.6 | -3.6 | 1.1144 | 0
2015-01-20 22:00 | 0 | 0 | 0 | 0 | -20.2116 | 163.1114 | 122.6219 | -32.6219 | 161.1141 | 163.6756 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-01-20 23:00 | 0 | 0 | 0 | 0 | -20.2027 | 178.1083 | 123.2281 | -33.2281 | 177.8775 | 176.3005 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-01-21 | 0 | 0 | 0 | 0 | -20.1938 | -166.8949 | 122.8504 | -32.8504 | -165.3267 | 167.1704 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.8 | -2.8 | 1.1112 | 0
2015-01-21 01:00 | 0 | 0 | 0 | 0 | -20.1849 | -151.898 | 121.5253 | -31.5253 | -148.7574 | 153.2005 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-01-21 02:00 | 0 | 0 | 0 | 0 | -20.1759 | -136.9012 | 119.3789 | -29.3789 | -132.6096 | 139.1293 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1196 | 0
2015-01-21 03:00 | 0 | 0 | 0 | 0 | -20.167 | -121.9043 | 116.5998 | -26.5998 | -116.9737 | 125.1076 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.1 | -5.1 | 1.1204 | 0
2015-01-21 04:00 | 0 | 0 | 0 | 0 | -20.158 | -106.9075 | 113.4096 | -23.4096 | -101.8383 | 111.2041 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.118 | 0
2015-01-21 05:00 | 0 | 0 | 0 | 0 | -20.149 | -91.9106 | 110.0383 | -20.0383 | -87.1208 | 97.496 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.9 | -5.9 | 1.1236 | 0
2015-01-21 06:00 | 0 | 0 | 0 | 0 | -20.1401 | -76.9137 | 106.7088 | -16.7088 | -72.7045 | 84.097 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-01-21 07:00 | 0 | 0 | 0 | 0 | -20.1311 | -61.9168 | 103.6285 | -13.6285 | -58.4698 | 71.1966 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.5 | -5.5 | 1.122 | 0
2015-01-21 08:00 | 0 | 0 | 0 | 0 | -20.1221 | -46.92 | 100.9836 | -10.9836 | -44.316 | 59.1345 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.7 | -5.7 | 1.1228 | 0
2015-01-21 09:00 | 0 | 0 | 0 | 0 | -20.113 | -31.9231 | 98.9329 | -8.9329 | -30.1741 | 48.5504 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.9 | -3.9 | 1.1156 | 0
2015-01-21 10:00 | 0 | 0 | 0 | 0 | -20.104 | -16.9262 | 97.6007 | -7.6007 | -16.0111 | 40.6254 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-01-21 11:00 | 0 | 0 | 0 | 0 | -20.095 | -1.9293 | 97.0686 | -7.0686 | -1.8257 | 37.11 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.8 | -3.8 | 1.1152 | 0
2015-01-21 12:00 | 0 | 0 | 0 | 0 | -20.0859 | 13.0676 | 97.3694 | -7.3694 | 12.3638 | 39.2113 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-01-21 13:00 | 0 | 0 | 0 | 0 | -20.0769 | 28.0645 | 98.4837 | -8.4837 | 26.5363 | 46.1678 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.11 | 0
2015-01-21 14:00 | 0 | 0 | 0 | 0 | -20.0678 | 43.0614 | 100.3422 | -10.3422 | 40.6866 | 56.2023 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-01-21 15:00 | 0 | 0 | 0 | 0 | -20.0587 | 58.0584 | 102.8308 | -12.8308 | 54.838 | 67.9605 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-01-21 16:00 | 0 | 0 | 0 | 0 | -20.0496 | 73.0553 | 105.7987 | -15.7987 | 69.0499 | 80.6871 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.1048 | 0
2015-01-21 17:00 | 0 | 0 | 0 | 0 | -20.0405 | 88.0522 | 109.0659 | -19.0659 | 83.4148 | 93.9829 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-01-21 18:00 | 0 | 0 | 0 | 0 | -20.0314 | 103.0491 | 112.4297 | -22.4297 | 98.0482 | 107.629 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-01-21 19:00 | 0 | 0 | 0 | 0 | -20.0223 | 118.0461 | 115.6702 | -25.6702 | 113.0692 | 121.4967 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-01-21 20:00 | 0 | 0 | 0 | 0 | -20.0131 | 133.043 | 118.5582 | -28.5582 | 128.5713 | 135.5029 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-01-21 21:00 | 0 | 0 | 0 | 0 | -20.004 | 148.0399 | 120.8681 | -30.8681 | 144.5864 | 149.5823 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-01-21 22:00 | 0 | 0 | 0 | 0 | -19.9948 | 163.0369 | 122.4003 | -32.4003 | 161.0514 | 163.6375 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-01-21 23:00 | 0 | 0 | 0 | 0 | -19.9857 | 178.0338 | 123.0105 | -33.0105 | 177.7964 | 176.4517 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-01-22 | 0 | 0 | 0 | 0 | -19.9765 | -166.9692 | 122.6377 | -32.6377 | -165.4252 | 167.2838 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-01-22 01:00 | 0 | 0 | 0 | 0 | -19.9673 | -151.9722 | 121.3181 | -31.3181 | -148.8701 | 153.2777 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-01-22 02:00 | 0 | 0 | 0 | 0 | -19.9581 | -136.9753 | 119.1767 | -29.1767 | -132.7322 | 139.1874 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-01-22 03:00 | 0 | 0 | 0 | 0 | -19.9489 | -121.9783 | 116.4016 | -26.4016 | -117.1016 | 125.1497 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-01-22 04:00 | 0 | 0 | 0 | 0 | -19.9397 | -106.9813 | 113.2137 | -23.2137 | -101.9676 | 111.2304 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-01-22 05:00 | 0 | 0 | 0 | 0 | -19.9304 | -91.9843 | 109.8427 | -19.8427 | -87.2481 | 97.5048 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-01-22 06:00 | 0 | 0 | 0 | 0 | -19.9212 | -76.9873 | 106.5116 | -16.5116 | -72.8272 | 84.0852 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-01-22 07:00 | 0 | 0 | 0 | 0 | -19.9119 | -61.9904 | 103.4281 | -13.4281 | -58.5855 | 71.1591 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-01-22 08:00 | 0 | 0 | 0 | 0 | -19.9027 | -46.9934 | 100.7789 | -10.7789 | -44.4228 | 59.0634 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-01-22 09:00 | 0 | 0 | 0 | 0 | -19.8934 | -31.9964 | 98.7232 | -8.7232 | -30.2702 | 48.4351 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-01-22 10:00 | 0 | 0 | 0 | 0 | -19.8841 | -16.9994 | 97.3858 | -7.3858 | -16.095 | 40.4562 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-01-22 11:00 | 0 | 0 | 0 | 0 | -19.8748 | -2.0023 | 96.8489 | -6.8489 | -1.8966 | 36.8939 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-01-22 12:00 | 0 | 0 | 0 | 0 | -19.8655 | 12.9947 | 97.1457 | -7.1457 | 12.3061 | 38.9807 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-01-22 13:00 | 0 | 0 | 0 | 0 | -19.8562 | 27.9917 | 98.257 | -8.257 | 26.4914 | 45.9527 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-01-22 14:00 | 0 | 0 | 0 | 0 | -19.8468 | 42.9887 | 100.1133 | -10.1133 | 40.6531 | 56.012 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-01-22 15:00 | 0 | 0 | 0 | 0 | -19.8375 | 57.9857 | 102.6005 | -12.6005 | 54.8139 | 67.794 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-01-22 16:00 | 0 | 0 | 0 | 0 | -19.8281 | 72.9828 | 105.5676 | -15.5676 | 69.0324 | 80.541 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-01-22 17:00 | 0 | 0 | 0 | 0 | -19.8188 | 87.9798 | 108.8343 | -18.8343 | 83.4008 | 93.8543 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.7 | 0.7 | 1.0972 | 0
2015-01-22 18:00 | 0 | 0 | 0 | 0 | -19.8094 | 102.9769 | 112.1979 | -22.1979 | 98.0339 | 107.5157 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-01-22 19:00 | 0 | 0 | 0 | 0 | -19.8 | 117.9739 | 115.4385 | -25.4385 | 113.0503 | 121.3979 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-01-22 20:00 | 0 | 0 | 0 | 0 | -19.7906 | 132.971 | 118.3269 | -28.3269 | 128.5431 | 135.4188 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.7 | 0.7 | 1.0972 | 0
2015-01-22 21:00 | 0 | 0 | 0 | 0 | -19.7812 | 147.968 | 120.638 | -30.638 | 144.5445 | 149.5154 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-01-22 22:00 | 0 | 0 | 0 | 0 | -19.7718 | 162.9651 | 122.1726 | -32.1726 | 160.9923 | 163.5995 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-01-22 23:00 | 0 | 0 | 0 | 0 | -19.7623 | 177.9621 | 122.7865 | -32.7865 | 177.7186 | 176.6007 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-01-23 | 0 | 0 | 0 | 0 | -19.7529 | -167.0408 | 122.4186 | -32.4186 | -165.5208 | 167.3929 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-01-23 01:00 | 0 | 0 | 0 | 0 | -19.7435 | -152.0437 | 121.1043 | -31.1043 | -148.9805 | 153.3511 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-01-23 02:00 | 0 | 0 | 0 | 0 | -19.734 | -137.0466 | 118.9679 | -28.9679 | -132.8529 | 139.2417 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-01-23 03:00 | 0 | 0 | 0 | 0 | -19.7245 | -122.0495 | 116.1967 | -26.1967 | -117.228 | 125.1881 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-01-23 04:00 | 0 | 0 | 0 | 0 | -19.715 | -107.0524 | 113.011 | -23.011 | -102.0955 | 111.2528 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-01-23 05:00 | 0 | 0 | 0 | 0 | -19.7055 | -92.0553 | 109.6403 | -19.6403 | -87.3742 | 97.5095 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-01-23 06:00 | 0 | 0 | 0 | 0 | -19.696 | -77.0582 | 106.3077 | -16.3077 | -72.9486 | 84.0691 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-01-23 07:00 | 0 | 0 | 0 | 0 | -19.6865 | -62.0611 | 103.2211 | -13.2211 | -58.6999 | 71.1169 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-01-23 08:00 | 0 | 0 | 0 | 0 | -19.677 | -47.064 | 100.5676 | -10.5676 | -44.528 | 58.9874 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.7 | 0.7 | 1.0972 | 0
2015-01-23 09:00 | 0 | 0 | 0 | 0 | -19.6675 | -32.0669 | 98.5069 | -8.5069 | -30.3645 | 48.3142 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-01-23 10:00 | 0 | 0 | 0 | 0 | -19.6579 | -17.0698 | 97.1645 | -7.1645 | -16.1769 | 40.281 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-01-23 11:00 | 0 | 0 | 0 | 0 | -19.6484 | -2.0727 | 96.623 | -6.623 | -1.9651 | 36.6716 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-01-23 12:00 | 0 | 0 | 0 | 0 | -19.6388 | 12.9245 | 96.9159 | -6.9159 | 12.2513 | 38.745 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-01-23 13:00 | 0 | 0 | 0 | 0 | -19.6292 | 27.9216 | 98.0243 | -8.0243 | 26.4497 | 45.7343 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-01-23 14:00 | 0 | 0 | 0 | 0 | -19.6196 | 42.9187 | 99.8786 | -9.8786 | 40.623 | 55.8199 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-01-23 15:00 | 0 | 0 | 0 | 0 | -19.61 | 57.9159 | 102.3646 | -12.3646 | 54.7934 | 67.6267 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-01-23 16:00 | 0 | 0 | 0 | 0 | -19.6004 | 72.913 | 105.3309 | -15.3309 | 69.0189 | 80.3948 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-01-23 17:00 | 0 | 0 | 0 | 0 | -19.5908 | 87.9102 | 108.5973 | -18.5973 | 83.3908 | 93.726 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-01-23 18:00 | 0 | 0 | 0 | 0 | -19.5812 | 102.9073 | 111.9607 | -21.9607 | 98.0237 | 107.4033 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-01-23 19:00 | 0 | 0 | 0 | 0 | -19.5715 | 117.9045 | 115.2012 | -25.2012 | 113.0355 | 121.3001 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-01-23 20:00 | 0 | 0 | 0 | 0 | -19.5619 | 132.9017 | 118.09 | -28.09 | 128.519 | 135.3357 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-01-23 21:00 | 0 | 0 | 0 | 0 | -19.5522 | 147.8989 | 120.4022 | -30.4022 | 144.5066 | 149.4493 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.7 | 0.7 | 1.0972 | 0
2015-01-23 22:00 | 0 | 0 | 0 | 0 | -19.5425 | 162.896 | 121.939 | -31.939 | 160.9369 | 163.5615 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-01-23 23:00 | 0 | 0 | 0 | 0 | -19.5328 | 177.8932 | 122.5564 | -32.5564 | 177.6442 | 176.7461 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-01-24 | 0 | 0 | 0 | 0 | -19.5232 | -167.1096 | 122.1931 | -32.1931 | -165.6136 | 167.4974 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-01-24 01:00 | 0 | 0 | 0 | 0 | -19.5134 | -152.1124 | 120.884 | -30.884 | -149.0885 | 153.4204 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-01-24 02:00 | 0 | 0 | 0 | 0 | -19.5037 | -137.1152 | 118.7526 | -28.7526 | -132.9716 | 139.2922 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.7 | 0.7 | 1.0972 | 0
2015-01-24 03:00 | 0 | 0 | 0 | 0 | -19.494 | -122.118 | 115.9852 | -25.9852 | -117.3528 | 125.2226 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-01-24 04:00 | 0 | 0 | 0 | 0 | -19.4843 | -107.1208 | 112.8017 | -22.8017 | -102.2221 | 111.2712 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-01-24 05:00 | 0 | 0 | 0 | 0 | -19.4745 | -92.1236 | 109.4314 | -19.4314 | -87.4991 | 97.5102 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-01-24 06:00 | 0 | 0 | 0 | 0 | -19.4648 | -77.1264 | 106.0973 | -16.0973 | -73.0688 | 84.0487 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-01-24 07:00 | 0 | 0 | 0 | 0 | -19.455 | -62.1291 | 103.0076 | -13.0076 | -58.813 | 71.0702 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-01-24 08:00 | 0 | 0 | 0 | 0 | -19.4452 | -47.1319 | 100.3498 | -10.3498 | -44.6317 | 58.9063 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-01-24 09:00 | 0 | 0 | 0 | 0 | -19.4354 | -32.1347 | 98.2843 | -8.2843 | -30.4569 | 48.1879 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-01-24 10:00 | 0 | 0 | 0 | 0 | -19.4256 | -17.1374 | 96.937 | -6.937 | -16.2566 | 40.0997 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-01-24 11:00 | 0 | 0 | 0 | 0 | -19.4158 | -2.1402 | 96.391 | -6.391 | -2.0311 | 36.4432 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-01-24 12:00 | 0 | 0 | 0 | 0 | -19.406 | 12.8571 | 96.6802 | -6.6802 | 12.1993 | 38.5045 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-01-24 13:00 | 0 | 0 | 0 | 0 | -19.3962 | 27.8543 | 97.7858 | -7.7858 | 26.4111 | 45.5128 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-01-24 14:00 | 0 | 0 | 0 | 0 | -19.3863 | 42.8516 | 99.6383 | -9.6383 | 40.5964 | 55.6263 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-01-24 15:00 | 0 | 0 | 0 | 0 | -19.3765 | 57.8488 | 102.1232 | -12.1232 | 54.7767 | 67.4589 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-01-24 16:00 | 0 | 0 | 0 | 0 | -19.3666 | 72.8461 | 105.0889 | -15.0889 | 69.0093 | 80.2488 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-01-24 17:00 | 0 | 0 | 0 | 0 | -19.3567 | 87.8434 | 108.355 | -18.355 | 83.3849 | 93.5984 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-01-24 18:00 | 0 | 0 | 0 | 0 | -19.3468 | 102.8406 | 111.7181 | -21.7181 | 98.0177 | 107.2918 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-01-24 19:00 | 0 | 0 | 0 | 0 | -19.337 | 117.8379 | 114.9586 | -24.9586 | 113.0248 | 121.2034 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-01-24 20:00 | 0 | 0 | 0 | 0 | -19.327 | 132.8352 | 117.8476 | -27.8476 | 128.499 | 135.2537 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-01-24 21:00 | 0 | 0 | 0 | 0 | -19.3171 | 147.8325 | 120.1607 | -30.1607 | 144.4726 | 149.3842 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-01-24 22:00 | 0 | 0 | 0 | 0 | -19.3072 | 162.8298 | 121.6995 | -31.6995 | 160.8853 | 163.5233 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-01-24 23:00 | 0 | 0 | 0 | 0 | -19.2973 | 177.8271 | 122.3202 | -32.3202 | 177.5731 | 176.8863 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-01-25 | 0 | 0 | 0 | 0 | -19.2873 | -167.1756 | 121.9614 | -31.9614 | -165.7034 | 167.5966 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-01-25 01:00 | 0 | 0 | 0 | 0 | -19.2774 | -152.1783 | 120.6574 | -30.6574 | -149.194 | 153.4855 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-01-25 02:00 | 0 | 0 | 0 | 0 | -19.2674 | -137.181 | 118.5307 | -28.5307 | -133.0883 | 139.3387 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-01-25 03:00 | 0 | 0 | 0 | 0 | -19.2574 | -122.1836 | 115.7671 | -25.7671 | -117.4758 | 125.2532 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-01-25 04:00 | 0 | 0 | 0 | 0 | -19.2474 | -107.1863 | 112.5859 | -22.5859 | -102.3472 | 111.2857 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3 | -3 | 1.112 | 0
2015-01-25 05:00 | 0 | 0 | 0 | 0 | -19.2374 | -92.189 | 109.2159 | -19.2159 | -87.6226 | 97.5067 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-01-25 06:00 | 0 | 0 | 0 | 0 | -19.2274 | -77.1916 | 105.8803 | -15.8803 | -73.1876 | 84.0239 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.6 | -3.6 | 1.1144 | 0
2015-01-25 07:00 | 0 | 0 | 0 | 0 | -19.2174 | -62.1943 | 102.7876 | -12.7876 | -58.9246 | 71.0189 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.8 | -3.8 | 1.1152 | 0
2015-01-25 08:00 | 0 | 0 | 0 | 0 | -19.2074 | -47.1969 | 100.1257 | -10.1257 | -44.7338 | 58.8203 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2 | -4.2 | 1.1168 | 0
2015-01-25 09:00 | 0 | 0 | 0 | 0 | -19.1973 | -32.1996 | 98.0554 | -8.0554 | -30.5475 | 48.0561 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-01-25 10:00 | 0 | 0 | 0 | 0 | -19.1873 | -17.2022 | 96.7033 | -6.7033 | -16.3342 | 39.9125 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-01-25 11:00 | 0 | 0 | 0 | 0 | -19.1772 | -2.2049 | 96.153 | -6.153 | -2.0945 | 36.2088 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-01-25 12:00 | 0 | 0 | 0 | 0 | -19.1672 | 12.7925 | 96.4386 | -6.4386 | 12.1501 | 38.2593 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.118 | 0
2015-01-25 13:00 | 0 | 0 | 0 | 0 | -19.1571 | 27.7899 | 97.5416 | -7.5416 | 26.3756 | 45.2884 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.118 | 0
2015-01-25 14:00 | 0 | 0 | 0 | 0 | -19.147 | 42.7872 | 99.3924 | -9.3924 | 40.5733 | 55.4313 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.8 | -4.8 | 1.1192 | 0
2015-01-25 15:00 | 0 | 0 | 0 | 0 | -19.1369 | 57.7846 | 101.8764 | -11.8764 | 54.7637 | 67.2906 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1208 | 0
2015-01-25 16:00 | 0 | 0 | 0 | 0 | -19.1268 | 72.782 | 104.8417 | -14.8417 | 69.0036 | 80.103 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.4 | -5.4 | 1.1216 | 0
2015-01-25 17:00 | 0 | 0 | 0 | 0 | -19.1167 | 87.7794 | 108.1074 | -18.1074 | 83.3832 | 93.4714 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.3 | -5.3 | 1.1212 | 0
2015-01-25 18:00 | 0 | 0 | 0 | 0 | -19.1065 | 102.7768 | 111.4704 | -21.4704 | 98.0158 | 107.1812 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.7 | -5.7 | 1.1228 | 0
2015-01-25 19:00 | 0 | 0 | 0 | 0 | -19.0964 | 117.7742 | 114.7106 | -24.7106 | 113.0184 | 121.1077 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.7 | -5.7 | 1.1228 | 0
2015-01-25 20:00 | 0 | 0 | 0 | 0 | -19.0862 | 132.7716 | 117.5998 | -27.5998 | 128.4832 | 135.1728 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.1 | -5.1 | 1.1204 | 0
2015-01-25 21:00 | 0 | 0 | 0 | 0 | -19.0761 | 147.769 | 119.9137 | -29.9137 | 144.4427 | 149.3197 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.8 | -4.8 | 1.1192 | 0
2015-01-25 22:00 | 0 | 0 | 0 | 0 | -19.0659 | 162.7665 | 121.4543 | -31.4543 | 160.8375 | 163.4846 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.5 | -5.5 | 1.122 | 0
2015-01-25 23:00 | 0 | 0 | 0 | 0 | -19.0557 | 177.7639 | 122.0781 | -32.0781 | 177.5054 | 177.0191 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.1 | -5.1 | 1.1204 | 0
2015-01-26 | 0 | 0 | 0 | 0 | -19.0455 | -167.2387 | 121.7235 | -31.7235 | -165.7902 | 167.6902 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.7 | -4.7 | 1.1188 | 0
2015-01-26 01:00 | 0 | 0 | 0 | 0 | -19.0353 | -152.2413 | 120.4244 | -30.4244 | -149.2968 | 153.5461 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1196 | 0
2015-01-26 02:00 | 0 | 0 | 0 | 0 | -19.0251 | -137.2438 | 118.3025 | -28.3025 | -133.2027 | 139.381 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.1 | -5.1 | 1.1204 | 0
2015-01-26 03:00 | 0 | 0 | 0 | 0 | -19.0149 | -122.2464 | 115.5426 | -25.5426 | -117.5971 | 125.2797 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1196 | 0
2015-01-26 04:00 | 0 | 0 | 0 | 0 | -19.0046 | -107.2489 | 112.3636 | -22.3636 | -102.4707 | 111.296 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.8 | -4.8 | 1.1192 | 0
2015-01-26 05:00 | 0 | 0 | 0 | 0 | -18.9944 | -92.2515 | 108.9939 | -18.9939 | -87.7446 | 97.499 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.3 | -4.3 | 1.1172 | 0
2015-01-26 06:00 | 0 | 0 | 0 | 0 | -18.9841 | -77.254 | 105.6569 | -15.6569 | -73.3051 | 83.9948 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.1 | -4.1 | 1.1164 | 0
2015-01-26 07:00 | 0 | 0 | 0 | 0 | -18.9739 | -62.2566 | 102.5613 | -12.5613 | -59.0346 | 70.9629 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.1 | -4.1 | 1.1164 | 0
2015-01-26 08:00 | 0 | 0 | 0 | 0 | -18.9636 | -47.2591 | 99.8953 | -9.8953 | -44.8342 | 58.7293 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1148 | 0
2015-01-26 09:00 | 0 | 0 | 0 | 0 | -18.9533 | -32.2616 | 97.8203 | -7.8203 | -30.6362 | 47.9189 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1148 | 0
2015-01-26 10:00 | 0 | 0 | 0 | 0 | -18.943 | -17.2641 | 96.4635 | -6.4635 | -16.4095 | 39.7193 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-01-26 11:00 | 0 | 0 | 0 | 0 | -18.9327 | -2.2666 | 95.909 | -5.909 | -2.1554 | 35.9685 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.1132 | 0
2015-01-26 12:00 | 0 | 0 | 0 | 0 | -18.9224 | 12.7308 | 96.1912 | -6.1912 | 12.1039 | 38.0093 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.6 | -3.6 | 1.1144 | 0
2015-01-26 13:00 | 0 | 0 | 0 | 0 | -18.9121 | 27.7283 | 97.2918 | -7.2918 | 26.3435 | 45.0613 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.9 | -3.9 | 1.1156 | 0
2015-01-26 14:00 | 0 | 0 | 0 | 0 | -18.9017 | 42.7258 | 99.1411 | -9.1411 | 40.5537 | 55.2349 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.1 | -4.1 | 1.1164 | 0
2015-01-26 15:00 | 0 | 0 | 0 | 0 | -18.8914 | 57.7233 | 101.6243 | -11.6243 | 54.7545 | 67.122 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-01-26 16:00 | 0 | 0 | 0 | 0 | -18.881 | 72.7209 | 104.5892 | -14.5892 | 69.0019 | 79.9574 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.3 | -5.3 | 1.1212 | 0
2015-01-26 17:00 | 0 | 0 | 0 | 0 | -18.8707 | 87.7184 | 107.8548 | -17.8548 | 83.3855 | 93.3452 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.9 | -5.9 | 1.1236 | 0
2015-01-26 18:00 | 0 | 0 | 0 | 0 | -18.8603 | 102.7159 | 111.2175 | -21.2175 | 98.0181 | 107.0715 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.7 | -6.7 | 1.1268 | 0
2015-01-26 19:00 | 0 | 0 | 0 | 0 | -18.8499 | 117.7134 | 114.4576 | -24.4576 | 113.0162 | 121.0131 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.6 | -7.6 | 1.1304 | 0
2015-01-26 20:00 | 0 | 0 | 0 | 0 | -18.8395 | 132.7109 | 117.3467 | -27.3467 | 128.4716 | 135.0929 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.3 | -6.3 | 1.1252 | 0
2015-01-26 21:00 | 0 | 0 | 0 | 0 | -18.8291 | 147.7085 | 119.6612 | -29.6612 | 144.4168 | 149.2561 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.75 | -7.75 | 1.131 | 0
2015-01-26 22:00 | 0 | 0 | 0 | 0 | -18.8187 | 162.706 | 121.2034 | -31.2034 | 160.7934 | 163.4454 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.2 | -9.2 | 1.1368 | 0
2015-01-26 23:00 | 0 | 0 | 0 | 0 | -18.8083 | 177.7036 | 121.83 | -31.83 | 177.4413 | 177.1422 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.3 | -9.3 | 1.1372 | 0
2015-01-27 | 0 | 0 | 0 | 0 | -18.7978 | -167.2989 | 121.4795 | -31.4795 | -165.8739 | 167.7775 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.1 | -10.1 | 1.1404 | 0
2015-01-27 01:00 | 0 | 0 | 0 | 0 | -18.7874 | -152.3013 | 120.1852 | -30.1852 | -149.3971 | 153.602 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.8 | -10.8 | 1.1432 | 0
2015-01-27 02:00 | 0 | 0 | 0 | 0 | -18.7769 | -137.3038 | 118.0679 | -28.0679 | -133.315 | 139.4191 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.6 | -12.6 | 1.1504 | 0
2015-01-27 03:00 | 0 | 0 | 0 | 0 | -18.7665 | -122.3062 | 115.3117 | -25.3117 | -117.7164 | 125.302 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.8 | -12.8 | 1.1512 | 0
2015-01-27 04:00 | 0 | 0 | 0 | 0 | -18.756 | -107.3086 | 112.1349 | -22.1349 | -102.5926 | 111.3022 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.8 | -12.8 | 1.1512 | 0
2015-01-27 05:00 | 0 | 0 | 0 | 0 | -18.7455 | -92.311 | 108.7656 | -18.7656 | -87.8651 | 97.4871 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.1 | -12.1 | 1.1484 | 0
2015-01-27 06:00 | 0 | 0 | 0 | 0 | -18.735 | -77.3135 | 105.4272 | -15.4272 | -73.4209 | 83.9614 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13 | -13 | 1.152 | 0
2015-01-27 07:00 | 0 | 0 | 0 | 0 | -18.7245 | -62.3159 | 102.3286 | -12.3286 | -59.1431 | 70.9024 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.7 | -12.7 | 1.1508 | 0
2015-01-27 08:00 | 0 | 0 | 0 | 0 | -18.714 | -47.3183 | 99.6586 | -9.6586 | -44.9329 | 58.6335 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.1 | -13.1 | 1.1524 | 0
2015-01-27 09:00 | 0 | 0 | 0 | 0 | -18.7035 | -32.3207 | 97.5791 | -7.5791 | -30.7229 | 47.7764 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.9 | -12.9 | 1.1516 | 0
2015-01-27 10:00 | 0 | 0 | 0 | 0 | -18.6929 | -17.3231 | 96.2178 | -6.2178 | -16.4825 | 39.5204 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.4 | -13.4 | 1.1536 | 0
2015-01-27 11:00 | 0 | 0 | 0 | 0 | -18.6824 | -2.3255 | 95.6592 | -5.6592 | -2.2137 | 35.7223 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14 | -14 | 1.156 | 0
2015-01-27 12:00 | 0 | 0 | 0 | 0 | -18.6718 | 12.6721 | 95.9382 | -5.9382 | 12.0606 | 37.7549 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.1 | -14.1 | 1.1564 | 0
2015-01-27 13:00 | 0 | 0 | 0 | 0 | -18.6613 | 27.6698 | 97.0366 | -7.0366 | 26.3146 | 44.8314 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.9 | -14.9 | 1.1596 | 0
2015-01-27 14:00 | 0 | 0 | 0 | 0 | -18.6507 | 42.6674 | 98.8845 | -8.8845 | 40.5377 | 55.0374 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.1 | -15.1 | 1.1604 | 0
2015-01-27 15:00 | 0 | 0 | 0 | 0 | -18.6401 | 57.665 | 101.367 | -11.367 | 54.7491 | 66.9532 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.1 | -16.1 | 1.1644 | 0
2015-01-27 16:00 | 0 | 0 | 0 | 0 | -18.6295 | 72.6626 | 104.3317 | -14.3317 | 69.0041 | 79.8123 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16 | -16 | 1.164 | 0
2015-01-27 17:00 | 0 | 0 | 0 | 0 | -18.6189 | 87.6603 | 107.5971 | -17.5971 | 83.3919 | 93.2197 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.9 | -15.9 | 1.1636 | 0
2015-01-27 18:00 | 0 | 0 | 0 | 0 | -18.6083 | 102.6579 | 110.9596 | -20.9596 | 98.0247 | 106.9629 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.9 | -15.9 | 1.1636 | 0
2015-01-27 19:00 | 0 | 0 | 0 | 0 | -18.5977 | 117.6556 | 114.1994 | -24.1994 | 113.0183 | 120.9197 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.6 | -16.6 | 1.1664 | 0
2015-01-27 20:00 | 0 | 0 | 0 | 0 | -18.587 | 132.6532 | 117.0884 | -27.0884 | 128.4642 | 135.0141 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.9 | -16.9 | 1.1676 | 0
2015-01-27 21:00 | 0 | 0 | 0 | 0 | -18.5764 | 147.6509 | 119.4033 | -29.4033 | 144.395 | 149.193 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.7 | -16.7 | 1.1668 | 0
2015-01-27 22:00 | 0 | 0 | 0 | 0 | -18.5657 | 162.6486 | 120.9469 | -30.9469 | 160.7532 | 163.4055 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.9 | -16.9 | 1.1676 | 0
2015-01-27 23:00 | 0 | 0 | 0 | 0 | -18.5551 | 177.6462 | 121.5763 | -31.5763 | 177.3806 | 177.2528 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.7 | -16.7 | 1.1668 | 0
2015-01-28 | 0 | 0 | 0 | 0 | -18.5444 | -167.3561 | 121.2297 | -31.2297 | -165.9545 | 167.8582 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.2 | -17.2 | 1.1688 | 0
2015-01-28 01:00 | 0 | 0 | 0 | 0 | -18.5337 | -152.3584 | 119.9399 | -29.9399 | -149.4946 | 153.653 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17 | -17 | 1.168 | 0
2015-01-28 02:00 | 0 | 0 | 0 | 0 | -18.523 | -137.3607 | 117.8271 | -27.8271 | -133.4249 | 139.4527 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.7 | -17.7 | 1.1708 | 0
2015-01-28 03:00 | 0 | 0 | 0 | 0 | -18.5123 | -122.363 | 115.0746 | -25.0746 | -117.8337 | 125.3202 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.3 | -18.3 | 1.1732 | 0
2015-01-28 04:00 | 0 | 0 | 0 | 0 | -18.5016 | -107.3653 | 111.8999 | -21.8999 | -102.7127 | 111.3042 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.8 | -17.8 | 1.1712 | 0
2015-01-28 05:00 | 0 | 0 | 0 | 0 | -18.4909 | -92.3676 | 108.5311 | -18.5311 | -87.984 | 97.471 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.6 | -17.6 | 1.1704 | 0
2015-01-28 06:00 | 0 | 0 | 0 | 0 | -18.4801 | -77.3699 | 105.1913 | -15.1913 | -73.5353 | 83.9235 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.4 | -17.4 | 1.1696 | 0
2015-01-28 07:00 | 0 | 0 | 0 | 0 | -18.4694 | -62.3722 | 102.0898 | -12.0898 | -59.25 | 70.8374 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.8 | -17.8 | 1.1712 | 0
2015-01-28 08:00 | 0 | 0 | 0 | 0 | -18.4586 | -47.3745 | 99.4159 | -9.4159 | -45.0297 | 58.5329 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.5 | -17.5 | 1.17 | 0
2015-01-28 09:00 | 0 | 0 | 0 | 0 | -18.4479 | -32.3768 | 97.3319 | -7.3319 | -30.8075 | 47.6287 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.2 | -17.2 | 1.1688 | 0
2015-01-28 10:00 | 0 | 0 | 0 | 0 | -18.4371 | -17.3791 | 95.9661 | -5.9661 | -16.5531 | 39.3156 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.7 | -17.7 | 1.1708 | 0
2015-01-28 11:00 | 0 | 0 | 0 | 0 | -18.4263 | -2.3813 | 95.4036 | -5.4036 | -2.2693 | 35.4704 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.5 | -17.5 | 1.17 | 0
2015-01-28 12:00 | 0 | 0 | 0 | 0 | -18.4155 | 12.6164 | 95.6796 | -5.6796 | 12.0204 | 37.496 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.5 | -16.5 | 1.166 | 0
2015-01-28 13:00 | 0 | 0 | 0 | 0 | -18.4047 | 27.6142 | 96.7759 | -6.7759 | 26.289 | 44.5991 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.5 | -16.5 | 1.166 | 0
2015-01-28 14:00 | 0 | 0 | 0 | 0 | -18.3939 | 42.6119 | 98.6227 | -8.6227 | 40.5253 | 54.8389 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.6 | -16.6 | 1.1664 | 0
2015-01-28 15:00 | 0 | 0 | 0 | 0 | -18.3831 | 57.6097 | 101.1047 | -11.1047 | 54.7475 | 66.7844 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.5 | -16.5 | 1.166 | 0
2015-01-28 16:00 | 0 | 0 | 0 | 0 | -18.3723 | 72.6074 | 104.0693 | -14.0693 | 69.0104 | 79.6677 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.7 | -16.7 | 1.1668 | 0
2015-01-28 17:00 | 0 | 0 | 0 | 0 | -18.3614 | 87.6052 | 107.3346 | -17.3346 | 83.4024 | 93.0951 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.3 | -16.3 | 1.1652 | 0
2015-01-28 18:00 | 0 | 0 | 0 | 0 | -18.3506 | 102.603 | 110.6969 | -20.6969 | 98.0354 | 106.8553 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.9 | -15.9 | 1.1636 | 0
2015-01-28 19:00 | 0 | 0 | 0 | 0 | -18.3397 | 117.6007 | 113.9364 | -23.9364 | 113.0245 | 120.8274 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.7 | -15.7 | 1.1628 | 0
2015-01-28 20:00 | 0 | 0 | 0 | 0 | -18.3288 | 132.5985 | 116.8251 | -26.8251 | 128.4609 | 134.9363 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.4 | -15.4 | 1.1616 | 0
2015-01-28 21:00 | 0 | 0 | 0 | 0 | -18.318 | 147.5963 | 119.1402 | -29.1402 | 144.3772 | 149.1306 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.7 | -16.7 | 1.1668 | 0
2015-01-28 22:00 | 0 | 0 | 0 | 0 | -18.3071 | 162.5941 | 120.685 | -30.685 | 160.7169 | 163.3646 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.3 | -15.3 | 1.1612 | 0
2015-01-28 23:00 | 0 | 0 | 0 | 0 | -18.2962 | 177.5919 | 121.3168 | -31.3168 | 177.3235 | 177.3478 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.4 | -15.4 | 1.1616 | 0
2015-01-29 | 0 | 0 | 0 | 0 | -18.2853 | -167.4103 | 120.9739 | -30.9739 | -166.0318 | 167.9317 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16 | -16 | 1.164 | 0
2015-01-29 01:00 | 0 | 0 | 0 | 0 | -18.2744 | -152.4125 | 119.6886 | -29.6886 | -149.5893 | 153.6988 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.8 | -14.8 | 1.1592 | 0
2015-01-29 02:00 | 0 | 0 | 0 | 0 | -18.2634 | -137.4147 | 117.5803 | -27.5803 | -133.5324 | 139.4819 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.1 | -16.1 | 1.1644 | 0
2015-01-29 03:00 | 0 | 0 | 0 | 0 | -18.2525 | -122.4169 | 114.8313 | -24.8313 | -117.949 | 125.334 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.9 | -14.9 | 1.1596 | 0
2015-01-29 04:00 | 0 | 0 | 0 | 0 | -18.2415 | -107.419 | 111.6587 | -21.6587 | -102.831 | 111.302 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.3 | -15.3 | 1.1612 | 0
2015-01-29 05:00 | 0 | 0 | 0 | 0 | -18.2306 | -92.4212 | 108.2903 | -18.2903 | -88.1012 | 97.4506 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.6 | -14.6 | 1.1584 | 0
2015-01-29 06:00 | 0 | 0 | 0 | 0 | -18.2196 | -77.4234 | 104.9492 | -14.9492 | -73.6479 | 83.8814 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.3 | -14.3 | 1.1572 | 0
2015-01-29 07:00 | 0 | 0 | 0 | 0 | -18.2086 | -62.4255 | 101.8449 | -11.8449 | -59.3551 | 70.7679 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.5 | -14.5 | 1.158 | 0
2015-01-29 08:00 | 0 | 0 | 0 | 0 | -18.1977 | -47.4277 | 99.1671 | -9.1671 | -45.1246 | 58.4274 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.2 | -14.2 | 1.1568 | 0
2015-01-29 09:00 | 0 | 0 | 0 | 0 | -18.1867 | -32.4298 | 97.0788 | -7.0788 | -30.8899 | 47.4757 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.4 | -14.4 | 1.1576 | 0
2015-01-29 10:00 | 0 | 0 | 0 | 0 | -18.1757 | -17.432 | 95.7087 | -5.7087 | -16.6213 | 39.1052 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.8 | -14.8 | 1.1592 | 0
2015-01-29 11:00 | 0 | 0 | 0 | 0 | -18.1646 | -2.4341 | 95.1424 | -5.1424 | -2.3221 | 35.2129 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.2 | -15.2 | 1.1608 | 0
2015-01-29 12:00 | 0 | 0 | 0 | 0 | -18.1536 | 12.5637 | 95.4155 | -5.4155 | 11.9832 | 37.2329 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16 | -16 | 1.164 | 0
2015-01-29 13:00 | 0 | 0 | 0 | 0 | -18.1426 | 27.5616 | 96.51 | -6.51 | 26.2668 | 44.3645 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16 | -16 | 1.164 | 0
2015-01-29 14:00 | 0 | 0 | 0 | 0 | -18.1315 | 42.5595 | 98.3558 | -8.3558 | 40.5165 | 54.6394 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.6 | -16.6 | 1.1664 | 0
2015-01-29 15:00 | 0 | 0 | 0 | 0 | -18.1205 | 57.5574 | 100.8375 | -10.8375 | 54.7498 | 66.6156 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.8 | -16.8 | 1.1672 | 0
2015-01-29 16:00 | 0 | 0 | 0 | 0 | -18.1094 | 72.5553 | 103.802 | -13.802 | 69.0206 | 79.5237 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.4 | -17.4 | 1.1696 | 0
2015-01-29 17:00 | 0 | 0 | 0 | 0 | -18.0984 | 87.5531 | 107.0673 | -17.0673 | 83.4171 | 92.9714 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.8 | -17.8 | 1.1712 | 0
2015-01-29 18:00 | 0 | 0 | 0 | 0 | -18.0873 | 102.551 | 110.4294 | -20.4294 | 98.0503 | 106.7489 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.7 | -18.7 | 1.1748 | 0
2015-01-29 19:00 | 0 | 0 | 0 | 0 | -18.0762 | 117.5489 | 113.6685 | -23.6685 | 113.035 | 120.7363 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.2 | -19.2 | 1.1768 | 0
2015-01-29 20:00 | 0 | 0 | 0 | 0 | -18.0651 | 132.5469 | 116.5568 | -26.5568 | 128.4618 | 134.8595 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19 | -19 | 1.176 | 0
2015-01-29 21:00 | 0 | 0 | 0 | 0 | -18.054 | 147.5448 | 118.872 | -28.872 | 144.3635 | 149.0687 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.7 | -19.7 | 1.1788 | 0
2015-01-29 22:00 | 0 | 0 | 0 | 0 | -18.0429 | 162.5427 | 120.4178 | -30.4178 | 160.6844 | 163.3225 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.7 | -19.7 | 1.1788 | 0
2015-01-29 23:00 | 0 | 0 | 0 | 0 | -18.0317 | 177.5406 | 121.0519 | -31.0519 | 177.27 | 177.424 | 0 | 0 | 0.8 | 1 | 0 | 0 | -20.2 | -20.2 | 1.1808 | 0
2015-01-30 | 0 | 0 | 0 | 0 | -18.0206 | -167.4615 | 120.7125 | -30.7125 | -166.106 | 167.9974 | 0 | 0 | 0.8 | 1 | 0 | 0 | -20 | -20 | 1.18 | 0
2015-01-30 01:00 | 0 | 0 | 0 | 0 | -18.0095 | -152.4635 | 119.4315 | -29.4315 | -149.6812 | 153.7393 | 0 | 0 | 0.8 | 1 | 0 | 0 | -20.1 | -20.1 | 1.1804 | 0
2015-01-30 02:00 | 0 | 0 | 0 | 0 | -17.9983 | -137.4656 | 117.3274 | -27.3274 | -133.6375 | 139.5063 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.9 | -19.9 | 1.1796 | 0
2015-01-30 03:00 | 0 | 0 | 0 | 0 | -17.9871 | -122.4676 | 114.582 | -24.582 | -118.0621 | 125.3435 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.9 | -19.9 | 1.1796 | 0
2015-01-30 04:00 | 0 | 0 | 0 | 0 | -17.976 | -107.4697 | 111.4115 | -21.4115 | -102.9474 | 111.2955 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.9 | -19.9 | 1.1796 | 0
2015-01-30 05:00 | 0 | 0 | 0 | 0 | -17.9648 | -92.4717 | 108.0435 | -18.0435 | -88.2166 | 97.4259 | 0 | 0 | 0.8 | 1 | 0 | 0 | -20.2 | -20.2 | 1.1808 | 0
2015-01-30 06:00 | 0 | 0 | 0 | 0 | -17.9536 | -77.4738 | 104.701 | -14.701 | -73.7588 | 83.8349 | 0 | 0 | 0.8 | 1 | 0 | 0 | -20.2 | -20.2 | 1.1808 | 0
2015-01-30 07:00 | 0 | 0 | 0 | 0 | -17.9424 | -62.4758 | 101.594 | -11.594 | -59.4583 | 70.6938 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.6 | -19.6 | 1.1784 | 0
2015-01-30 08:00 | 0 | 0 | 0 | 0 | -17.9312 | -47.4778 | 98.9124 | -8.9124 | -45.2175 | 58.3173 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.8 | -19.8 | 1.1792 | 0
2015-01-30 09:00 | 0 | 0 | 0 | 0 | -17.9199 | -32.4798 | 96.8199 | -6.8199 | -30.9702 | 47.3177 | 0 | 0 | 0.8 | 1 | 0 | 0 | -20.1 | -20.1 | 1.1804 | 0
2015-01-30 10:00 | 0 | 0 | 0 | 0 | -17.9087 | -17.4819 | 95.4456 | -5.4456 | -16.6871 | 38.8893 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.7 | -19.7 | 1.1788 | 0
2015-01-30 11:00 | 0 | 0 | 0 | 0 | -17.8975 | -2.4839 | 94.8757 | -4.8757 | -2.3722 | 34.9498 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.6 | -19.6 | 1.1784 | 0
2015-01-30 12:00 | 0 | 0 | 0 | 0 | -17.8862 | 12.5141 | 95.1461 | -5.1461 | 11.9491 | 36.9656 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.4 | -19.4 | 1.1776 | 0
2015-01-30 13:00 | 0 | 0 | 0 | 0 | -17.875 | 27.5121 | 96.2389 | -6.2389 | 26.248 | 44.1276 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.7 | -19.7 | 1.1788 | 0
2015-01-30 14:00 | 0 | 0 | 0 | 0 | -17.8637 | 42.5101 | 98.0839 | -8.0839 | 40.5113 | 54.4393 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.3 | -19.3 | 1.1772 | 0
2015-01-30 15:00 | 0 | 0 | 0 | 0 | -17.8524 | 57.5081 | 100.5654 | -10.5654 | 54.7559 | 66.4469 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.4 | -19.4 | 1.1776 | 0
2015-01-30 16:00 | 0 | 0 | 0 | 0 | -17.8411 | 72.5062 | 103.53 | -13.53 | 69.0349 | 79.3805 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.4 | -19.4 | 1.1776 | 0
2015-01-30 17:00 | 0 | 0 | 0 | 0 | -17.8298 | 87.5042 | 106.7954 | -16.7954 | 83.4359 | 92.8488 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.1 | -19.1 | 1.1764 | 0
2015-01-30 18:00 | 0 | 0 | 0 | 0 | -17.8185 | 102.5022 | 110.1572 | -20.1572 | 98.0694 | 106.6437 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.8 | -18.8 | 1.1752 | 0
2015-01-30 19:00 | 0 | 0 | 0 | 0 | -17.8072 | 117.5002 | 113.3958 | -23.3958 | 113.0496 | 120.6463 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.3 | -19.3 | 1.1772 | 0
2015-01-30 20:00 | 0 | 0 | 0 | 0 | -17.7959 | 132.4983 | 116.2837 | -26.2837 | 128.4668 | 134.7837 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.3 | -18.3 | 1.1732 | 0
2015-01-30 21:00 | 0 | 0 | 0 | 0 | -17.7845 | 147.4963 | 118.5988 | -28.5988 | 144.3539 | 149.0073 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.9 | -18.9 | 1.1756 | 0
2015-01-30 22:00 | 0 | 0 | 0 | 0 | -17.7732 | 162.4944 | 120.1453 | -30.1453 | 160.6558 | 163.2792 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.4 | -16.4 | 1.1656 | 0
2015-01-30 23:00 | 0 | 0 | 0 | 0 | -17.7618 | 177.4924 | 120.7815 | -30.7815 | 177.2202 | 177.4781 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.5 | -17.5 | 1.17 | 0
2015-01-31 | 0 | 0 | 0 | 0 | -17.7505 | -167.5095 | 120.4454 | -30.4454 | -166.1768 | 168.0549 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.4 | -17.4 | 1.1696 | 0
2015-01-31 01:00 | 0 | 0 | 0 | 0 | -17.7391 | -152.5115 | 119.1685 | -29.1685 | -149.7701 | 153.7743 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.1 | -17.1 | 1.1684 | 0
2015-01-31 02:00 | 0 | 0 | 0 | 0 | -17.7277 | -137.5134 | 117.0687 | -27.0687 | -133.74 | 139.526 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.2 | -16.2 | 1.1648 | 0
2015-01-31 03:00 | 0 | 0 | 0 | 0 | -17.7163 | -122.5153 | 114.3266 | -24.3266 | -118.173 | 125.3484 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.4 | -16.4 | 1.1656 | 0
2015-01-31 04:00 | 0 | 0 | 0 | 0 | -17.7049 | -107.5172 | 111.1582 | -21.1582 | -103.0618 | 111.2846 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.9 | -15.9 | 1.1636 | 0
2015-01-31 05:00 | 0 | 0 | 0 | 0 | -17.6935 | -92.5191 | 107.7906 | -17.7906 | -88.3302 | 97.3969 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.9 | -15.9 | 1.1636 | 0
2015-01-31 06:00 | 0 | 0 | 0 | 0 | -17.6821 | -77.521 | 104.4469 | -14.4469 | -73.8679 | 83.784 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.5 | -15.5 | 1.162 | 0
2015-01-31 07:00 | 0 | 0 | 0 | 0 | -17.6707 | -62.523 | 101.3372 | -11.3372 | -59.5598 | 70.6153 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.4 | -15.4 | 1.1616 | 0
2015-01-31 08:00 | 0 | 0 | 0 | 0 | -17.6593 | -47.5248 | 98.6519 | -8.6519 | -45.3085 | 58.2024 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.4 | -15.4 | 1.1616 | 0
2015-01-31 09:00 | 0 | 0 | 0 | 0 | -17.6478 | -32.5267 | 96.5552 | -6.5552 | -31.0483 | 47.1547 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.8 | -14.8 | 1.1592 | 0
2015-01-31 10:00 | 0 | 0 | 0 | 0 | -17.6364 | -17.5286 | 95.1769 | -5.1769 | -16.7503 | 38.6678 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.5 | -14.5 | 1.158 | 0
2015-01-31 11:00 | 0 | 0 | 0 | 0 | -17.6249 | -2.5305 | 94.6036 | -4.6036 | -2.4195 | 34.6812 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.5 | -14.5 | 1.158 | 0
2015-01-31 12:00 | 0 | 0 | 0 | 0 | -17.6134 | 12.4676 | 94.8715 | -4.8715 | 11.9181 | 36.6942 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15 | -15 | 1.16 | 0
2015-01-31 13:00 | 0 | 0 | 0 | 0 | -17.6019 | 27.4657 | 95.9627 | -5.9627 | 26.2326 | 43.8887 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.6 | -14.6 | 1.1584 | 0
2015-01-31 14:00 | 0 | 0 | 0 | 0 | -17.5904 | 42.4639 | 97.8072 | -7.8072 | 40.5098 | 54.2386 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.3 | -14.3 | 1.1572 | 0
2015-01-31 15:00 | 0 | 0 | 0 | 0 | -17.5789 | 57.462 | 100.2886 | -10.2886 | 54.7658 | 66.2786 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.5 | -14.5 | 1.158 | 0
2015-01-31 16:00 | 0 | 0 | 0 | 0 | -17.5674 | 72.4602 | 103.2534 | -13.2534 | 69.0532 | 79.238 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.5 | -14.5 | 1.158 | 0
2015-01-31 17:00 | 0 | 0 | 0 | 0 | -17.5559 | 87.4583 | 106.5189 | -16.5189 | 83.4588 | 92.7273 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.4 | -14.4 | 1.1576 | 0
2015-01-31 18:00 | 0 | 0 | 0 | 0 | -17.5444 | 102.4565 | 109.8805 | -19.8805 | 98.0927 | 106.5397 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15 | -15 | 1.16 | 0
2015-01-31 19:00 | 0 | 0 | 0 | 0 | -17.5329 | 117.4546 | 113.1186 | -23.1186 | 113.0685 | 120.5575 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.6 | -14.6 | 1.1584 | 0
2015-01-31 20:00 | 0 | 0 | 0 | 0 | -17.5213 | 132.4528 | 116.0059 | -26.0059 | 128.4761 | 134.7089 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.9 | -14.9 | 1.1596 | 0
2015-01-31 21:00 | 0 | 0 | 0 | 0 | -17.5098 | 147.451 | 118.3207 | -28.3207 | 144.3483 | 148.9463 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15 | -15 | 1.16 | 0
2015-01-31 22:00 | 0 | 0 | 0 | 0 | -17.4982 | 162.4492 | 119.8678 | -29.8678 | 160.6311 | 163.2345 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.2 | -15.2 | 1.1608 | 0
2015-01-31 23:00 | 0 | 0 | 0 | 0 | -17.4866 | 177.4473 | 120.5058 | -30.5058 | 177.1739 | 177.5071 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.1 | -15.1 | 1.1604 | 0
2015-02-01 | 0 | 0 | 0 | 0 | -17.475 | -167.5545 | 120.1728 | -30.1728 | -166.2444 | 168.1036 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.5 | -15.5 | 1.162 | 0
2015-02-01 01:00 | 0 | 0 | 0 | 0 | -17.4634 | -152.5563 | 118.8999 | -28.8999 | -149.8562 | 153.8035 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.9 | -15.9 | 1.1636 | 0
2015-02-01 02:00 | 0 | 0 | 0 | 0 | -17.4518 | -137.5581 | 116.8041 | -26.8041 | -133.8399 | 139.5408 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.2 | -16.2 | 1.1648 | 0
2015-02-01 03:00 | 0 | 0 | 0 | 0 | -17.4402 | -122.5599 | 114.0654 | -24.0654 | -118.2817 | 125.3488 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.2 | -16.2 | 1.1648 | 0
2015-02-01 04:00 | 0 | 0 | 0 | 0 | -17.4286 | -107.5617 | 110.8991 | -20.8991 | -103.1741 | 111.2694 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.6 | -16.6 | 1.1664 | 0
2015-02-01 05:00 | 0 | 0 | 0 | 0 | -17.417 | -92.5634 | 107.5319 | -17.5319 | -88.4419 | 97.3635 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.5 | -17.5 | 1.17 | 0
2015-02-01 06:00 | 0 | 0 | 0 | 0 | -17.4053 | -77.5652 | 104.187 | -14.187 | -73.9751 | 83.7288 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.6 | -17.6 | 1.1704 | 0
2015-02-01 07:00 | 0 | 0 | 0 | 0 | -17.3937 | -62.567 | 101.0746 | -11.0746 | -59.6593 | 70.5323 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.8 | -17.8 | 1.1712 | 0
2015-02-01 08:00 | 0 | 0 | 0 | 0 | -17.382 | -47.5688 | 98.3857 | -8.3857 | -45.3974 | 58.083 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.9 | -17.9 | 1.1716 | 0
2015-02-01 09:00 | 0 | 0 | 0 | 0 | -17.3704 | -32.5705 | 96.285 | -6.285 | -31.1241 | 46.9867 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.1 | -18.1 | 1.1724 | 0
2015-02-01 10:00 | 0 | 0 | 0 | 0 | -17.3587 | -17.5723 | 94.9027 | -4.9027 | -16.8111 | 38.441 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.4 | -18.4 | 1.1736 | 0
2015-02-01 11:00 | 0 | 0 | 0 | 0 | -17.347 | -2.574 | 94.3262 | -4.3262 | -2.4639 | 34.4072 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.1 | -18.1 | 1.1724 | 0
2015-02-01 12:00 | 0 | 0 | 0 | 0 | -17.3353 | 12.4242 | 94.5917 | -4.5917 | 11.8902 | 36.419 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.7 | -18.7 | 1.1748 | 0
2015-02-01 13:00 | 0 | 0 | 0 | 0 | -17.3236 | 27.4225 | 95.6816 | -5.6816 | 26.2205 | 43.648 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.6 | -18.6 | 1.1744 | 0
2015-02-01 14:00 | 0 | 0 | 0 | 0 | -17.3119 | 42.4208 | 97.5256 | -7.5256 | 40.512 | 54.0374 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19 | -19 | 1.176 | 0
2015-02-01 15:00 | 0 | 0 | 0 | 0 | -17.3002 | 57.419 | 100.0072 | -10.0072 | 54.7796 | 66.1106 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.2 | -19.2 | 1.1768 | 0
2015-02-01 16:00 | 0 | 0 | 0 | 0 | -17.2885 | 72.4173 | 102.9723 | -12.9723 | 69.0754 | 79.0964 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.1 | -19.1 | 1.1764 | 0
2015-02-01 17:00 | 0 | 0 | 0 | 0 | -17.2768 | 87.4156 | 106.2379 | -16.2379 | 83.4858 | 92.6069 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.7 | -18.7 | 1.1748 | 0
2015-02-01 18:00 | 0 | 0 | 0 | 0 | -17.265 | 102.4139 | 109.5994 | -19.5994 | 98.1202 | 106.4369 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18 | -18 | 1.172 | 0
2015-02-01 19:00 | 0 | 0 | 0 | 0 | -17.2533 | 117.4122 | 112.8369 | -22.8369 | 113.0916 | 120.47 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.7 | -17.7 | 1.1708 | 0
2015-02-01 20:00 | 0 | 0 | 0 | 0 | -17.2415 | 132.4105 | 115.7234 | -25.7234 | 128.4895 | 134.6351 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.7 | -17.7 | 1.1708 | 0
2015-02-01 21:00 | 0 | 0 | 0 | 0 | -17.2297 | 147.4088 | 118.0377 | -28.0377 | 144.3468 | 148.8856 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.4 | -17.4 | 1.1696 | 0
2015-02-01 22:00 | 0 | 0 | 0 | 0 | -17.2179 | 162.4071 | 119.5852 | -29.5852 | 160.6103 | 163.188 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.2 | -17.2 | 1.1688 | 0
2015-02-01 23:00 | 0 | 0 | 0 | 0 | -17.2062 | 177.4054 | 120.2248 | -30.2248 | 177.1314 | 177.5084 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.5 | -16.5 | 1.166 | 0
2015-02-02 | 0 | 0 | 0 | 0 | -17.1944 | -167.5963 | 119.8948 | -29.8948 | -166.3086 | 168.1432 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.3 | -16.3 | 1.1652 | 0
2015-02-02 01:00 | 0 | 0 | 0 | 0 | -17.1825 | -152.5979 | 118.6257 | -28.6257 | -149.9392 | 153.8268 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.4 | -15.4 | 1.1616 | 0
2015-02-02 02:00 | 0 | 0 | 0 | 0 | -17.1707 | -137.5996 | 116.5338 | -26.5338 | -133.9372 | 139.5505 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.3 | -15.3 | 1.1612 | 0
2015-02-02 03:00 | 0 | 0 | 0 | 0 | -17.1589 | -122.6013 | 113.7985 | -23.7985 | -118.388 | 125.3446 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.3 | -14.3 | 1.1572 | 0
2015-02-02 04:00 | 0 | 0 | 0 | 0 | -17.1471 | -107.6029 | 110.6342 | -20.6342 | -103.2844 | 111.2497 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.2 | -14.2 | 1.1568 | 0
2015-02-02 05:00 | 0 | 0 | 0 | 0 | -17.1352 | -92.6046 | 107.2674 | -17.2674 | -88.5516 | 97.3259 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.7 | -13.7 | 1.1548 | 0
2015-02-02 06:00 | 0 | 0 | 0 | 0 | -17.1234 | -77.6062 | 103.9213 | -13.9213 | -74.0805 | 83.6692 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.2 | -13.2 | 1.1528 | 0
2015-02-02 07:00 | 0 | 0 | 0 | 0 | -17.1115 | -62.6079 | 100.8063 | -10.8063 | -59.7568 | 70.445 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.6 | -13.6 | 1.1544 | 0
2015-02-02 08:00 | 0 | 0 | 0 | 0 | -17.0997 | -47.6095 | 98.1139 | -8.1139 | -45.4842 | 57.9589 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.9 | -12.9 | 1.1516 | 0
2015-02-02 09:00 | 0 | 0 | 0 | 0 | -17.0878 | -32.6111 | 96.0092 | -6.0092 | -31.1975 | 46.8138 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.7 | -12.7 | 1.1508 | 0
2015-02-02 10:00 | 0 | 0 | 0 | 0 | -17.0759 | -17.6128 | 94.6232 | -4.6232 | -16.8692 | 38.2088 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.2 | -13.2 | 1.1528 | 0
2015-02-02 11:00 | 0 | 0 | 0 | 0 | -17.064 | -2.6144 | 94.0436 | -4.0436 | -2.5054 | 34.128 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.5 | -14.5 | 1.158 | 0
2015-02-02 12:00 | 0 | 0 | 0 | 0 | -17.0521 | 12.384 | 94.307 | -4.307 | 11.8655 | 36.1401 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.4 | -14.4 | 1.1576 | 0
2015-02-02 13:00 | 0 | 0 | 0 | 0 | -17.0402 | 27.3824 | 95.3957 | -5.3957 | 26.212 | 43.4055 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.7 | -14.7 | 1.1588 | 0
2015-02-02 14:00 | 0 | 0 | 0 | 0 | -17.0283 | 42.3808 | 97.2395 | -7.2395 | 40.5178 | 53.8359 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15 | -15 | 1.16 | 0
2015-02-02 15:00 | 0 | 0 | 0 | 0 | -17.0163 | 57.3792 | 99.7213 | -9.7213 | 54.7973 | 65.9432 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.1 | -15.1 | 1.1604 | 0
2015-02-02 16:00 | 0 | 0 | 0 | 0 | -17.0044 | 72.3776 | 102.6869 | -12.6869 | 69.1017 | 78.9558 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.8 | -14.8 | 1.1592 | 0
2015-02-02 17:00 | 0 | 0 | 0 | 0 | -16.9924 | 87.376 | 105.9527 | -15.9527 | 83.517 | 92.4877 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15 | -15 | 1.16 | 0
2015-02-02 18:00 | 0 | 0 | 0 | 0 | -16.9805 | 102.3745 | 109.3139 | -19.3139 | 98.1518 | 106.3354 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.7 | -14.7 | 1.1588 | 0
2015-02-02 19:00 | 0 | 0 | 0 | 0 | -16.9685 | 117.3729 | 112.5508 | -22.5508 | 113.1188 | 120.3836 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.3 | -14.3 | 1.1572 | 0
2015-02-02 20:00 | 0 | 0 | 0 | 0 | -16.9565 | 132.3713 | 115.4365 | -25.4365 | 128.507 | 134.5622 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.6 | -14.6 | 1.1584 | 0
2015-02-02 21:00 | 0 | 0 | 0 | 0 | -16.9446 | 147.3698 | 117.7502 | -27.7502 | 144.3494 | 148.8251 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.4 | -14.4 | 1.1576 | 0
2015-02-02 22:00 | 0 | 0 | 0 | 0 | -16.9326 | 162.3682 | 119.2978 | -29.2978 | 160.5934 | 163.1398 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.4 | -14.4 | 1.1576 | 0
2015-02-02 23:00 | 0 | 0 | 0 | 0 | -16.9206 | 177.3666 | 119.9388 | -29.9388 | 177.0925 | 177.4805 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.5 | -14.5 | 1.158 | 0
2015-02-03 | 0 | 0 | 0 | 0 | -16.9086 | -167.6349 | 119.6115 | -29.6115 | -166.3694 | 168.1731 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.2 | -14.2 | 1.1568 | 0
2015-02-03 01:00 | 0 | 0 | 0 | 0 | -16.8965 | -152.6364 | 118.346 | -28.346 | -150.0192 | 153.844 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14 | -14 | 1.156 | 0
2015-02-03 02:00 | 0 | 0 | 0 | 0 | -16.8845 | -137.638 | 116.258 | -26.258 | -134.0318 | 139.5552 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12 | -12 | 1.148 | 0
2015-02-03 03:00 | 0 | 0 | 0 | 0 | -16.8725 | -122.6395 | 113.5259 | -23.5259 | -118.4919 | 125.3357 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.9 | -13.9 | 1.1556 | 0
2015-02-03 04:00 | 0 | 0 | 0 | 0 | -16.8604 | -107.641 | 110.3636 | -20.3636 | -103.3925 | 111.2256 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.8 | -13.8 | 1.1552 | 0
2015-02-03 05:00 | 0 | 0 | 0 | 0 | -16.8484 | -92.6425 | 106.9972 | -16.9972 | -88.6593 | 97.2839 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.5 | -13.5 | 1.154 | 0
2015-02-03 06:00 | 0 | 0 | 0 | 0 | -16.8363 | -77.6441 | 103.6499 | -13.6499 | -74.1838 | 83.6053 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.6 | -13.6 | 1.1544 | 0
2015-02-03 07:00 | 0 | 0 | 0 | 0 | -16.8243 | -62.6456 | 100.5325 | -10.5325 | -59.8523 | 70.3533 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.7 | -13.7 | 1.1548 | 0
2015-02-03 08:00 | 0 | 0 | 0 | 0 | -16.8122 | -47.6471 | 97.8366 | -7.8366 | -45.5688 | 57.8304 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.7 | -12.7 | 1.1508 | 0
2015-02-03 09:00 | 0 | 0 | 0 | 0 | -16.8001 | -32.6486 | 95.7281 | -5.7281 | -31.2686 | 46.6361 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.9 | -12.9 | 1.1516 | 0
2015-02-03 10:00 | 0 | 0 | 0 | 0 | -16.788 | -17.6501 | 94.3385 | -4.3385 | -16.9247 | 37.9714 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.1 | -12.1 | 1.1484 | 0
2015-02-03 11:00 | 0 | 0 | 0 | 0 | -16.7759 | -2.6515 | 93.7558 | -3.7558 | -2.5441 | 33.8436 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.7 | -11.7 | 1.1468 | 0
2015-02-03 12:00 | 0 | 0 | 0 | 0 | -16.7638 | 12.347 | 94.0173 | -4.0173 | 11.844 | 35.8575 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.8 | -10.8 | 1.1432 | 0
2015-02-03 13:00 | 0 | 0 | 0 | 0 | -16.7517 | 27.3455 | 95.1051 | -5.1051 | 26.2069 | 43.1615 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.3 | -10.3 | 1.1412 | 0
2015-02-03 14:00 | 0 | 0 | 0 | 0 | -16.7395 | 42.344 | 96.9488 | -6.9488 | 40.5273 | 53.6343 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.7 | -10.7 | 1.1428 | 0
2015-02-03 15:00 | 0 | 0 | 0 | 0 | -16.7274 | 57.3426 | 99.4311 | -9.4311 | 54.8188 | 65.7764 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10 | -10 | 1.14 | 0
2015-02-03 16:00 | 0 | 0 | 0 | 0 | -16.7153 | 72.3411 | 102.3971 | -12.3971 | 69.132 | 78.8163 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.7 | -9.7 | 1.1388 | 0
2015-02-03 17:00 | 0 | 0 | 0 | 0 | -16.7031 | 87.3397 | 105.6632 | -15.6632 | 83.5522 | 92.3698 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.6 | -8.6 | 1.1344 | 0
2015-02-03 18:00 | 0 | 0 | 0 | 0 | -16.6909 | 102.3382 | 109.0243 | -19.0243 | 98.1876 | 106.2353 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.3 | -6.3 | 1.1252 | 0
2015-02-03 19:00 | 0 | 0 | 0 | 0 | -16.6788 | 117.3368 | 112.2604 | -22.2604 | 113.1502 | 120.2986 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-02-03 20:00 | 0 | 0 | 0 | 0 | -16.6666 | 132.3353 | 115.1451 | -25.1451 | 128.5287 | 134.4902 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.4 | -2.4 | 1.1096 | 0
2015-02-03 21:00 | 0 | 0 | 0 | 0 | -16.6544 | 147.3339 | 117.458 | -27.458 | 144.356 | 148.7648 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.1064 | 0
2015-02-03 22:00 | 0 | 0 | 0 | 0 | -16.6422 | 162.3325 | 119.0057 | -29.0057 | 160.5805 | 163.0895 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6 | -1.6 | 1.1064 | 0
2015-02-03 23:00 | 0 | 0 | 0 | 0 | -16.63 | 177.3311 | 119.6479 | -29.6479 | 177.0572 | 177.4229 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-02-04 | 0 | 0 | 0 | 0 | -16.6178 | -167.6703 | 119.323 | -29.323 | -166.4268 | 168.1929 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-02-04 01:00 | 0 | 0 | 0 | 0 | -16.6056 | -152.6718 | 118.061 | -28.061 | -150.0961 | 153.8549 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-02-04 02:00 | 0 | 0 | 0 | 0 | -16.5933 | -137.6732 | 115.9767 | -25.9767 | -134.1236 | 139.5546 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-02-04 03:00 | 0 | 0 | 0 | 0 | -16.5811 | -122.6745 | 113.2477 | -23.2477 | -118.5933 | 125.3221 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.1 | -2.1 | 1.1084 | 0
2015-02-04 04:00 | 0 | 0 | 0 | 0 | -16.5688 | -107.6759 | 110.0874 | -20.0874 | -103.4983 | 111.1969 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-02-04 05:00 | 0 | 0 | 0 | 0 | -16.5566 | -92.6773 | 106.7214 | -16.7214 | -88.7649 | 97.2375 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.2 | -2.2 | 1.1088 | 0
2015-02-04 06:00 | 0 | 0 | 0 | 0 | -16.5443 | -77.6787 | 103.373 | -13.373 | -74.2851 | 83.5371 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-02-04 07:00 | 0 | 0 | 0 | 0 | -16.532 | -62.6801 | 100.2531 | -10.2531 | -59.9457 | 70.2572 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-02-04 08:00 | 0 | 0 | 0 | 0 | -16.5198 | -47.6814 | 97.5538 | -7.5538 | -45.6512 | 57.6974 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.1 | -2.1 | 1.1084 | 0
2015-02-04 09:00 | 0 | 0 | 0 | 0 | -16.5075 | -32.6828 | 95.4416 | -5.4416 | -31.3373 | 46.4537 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-02-04 10:00 | 0 | 0 | 0 | 0 | -16.4952 | -17.6842 | 94.0486 | -4.0486 | -16.9775 | 37.7288 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-02-04 11:00 | 0 | 0 | 0 | 0 | -16.4829 | -2.6855 | 93.4632 | -3.4632 | -2.5798 | 33.5541 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-02-04 12:00 | 0 | 0 | 0 | 0 | -16.4706 | 12.3131 | 93.7228 | -3.7228 | 11.8258 | 35.5714 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.11 | 0
2015-02-04 13:00 | 0 | 0 | 0 | 0 | -16.4582 | 27.3118 | 94.8099 | -4.8099 | 26.2052 | 42.916 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.1 | -2.1 | 1.1084 | 0
2015-02-04 14:00 | 0 | 0 | 0 | 0 | -16.4459 | 42.3105 | 96.6537 | -6.6537 | 40.5405 | 53.4327 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-02-04 15:00 | 0 | 0 | 0 | 0 | -16.4336 | 57.3091 | 99.1365 | -9.1365 | 54.8442 | 65.6104 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-02-04 16:00 | 0 | 0 | 0 | 0 | -16.4212 | 72.3078 | 102.1032 | -12.1032 | 69.1663 | 78.6779 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-02-04 17:00 | 0 | 0 | 0 | 0 | -16.4088 | 87.3065 | 105.3697 | -15.3697 | 83.5915 | 92.2533 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-02-04 18:00 | 0 | 0 | 0 | 0 | -16.3965 | 102.3052 | 108.7306 | -18.7306 | 98.2275 | 106.1365 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-02-04 19:00 | 0 | 0 | 0 | 0 | -16.3841 | 117.3039 | 111.9659 | -21.9659 | 113.1858 | 120.2147 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.5 | -0.5 | 1.102 | 0
2015-02-04 20:00 | 0 | 0 | 0 | 0 | -16.3717 | 132.3026 | 114.8495 | -24.8495 | 128.5545 | 134.4192 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-02-04 21:00 | 0 | 0 | 0 | 0 | -16.3593 | 147.3013 | 117.1615 | -27.1615 | 144.3666 | 148.7047 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-02-04 22:00 | 0 | 0 | 0 | 0 | -16.3469 | 162.3 | 118.7089 | -28.7089 | 160.5713 | 163.0371 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-02-04 23:00 | 0 | 0 | 0 | 0 | -16.3345 | 177.2987 | 119.3521 | -29.3521 | 177.0257 | 177.3359 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-02-05 | 0 | 0 | 0 | 0 | -16.3221 | -167.7026 | 119.0295 | -29.0295 | -166.4808 | 168.2021 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-02-05 01:00 | 0 | 0 | 0 | 0 | -16.3097 | -152.7039 | 117.7708 | -27.7708 | -150.1699 | 153.8593 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-02-05 02:00 | 0 | 0 | 0 | 0 | -16.2973 | -137.7051 | 115.69 | -25.69 | -134.2127 | 139.5487 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-02-05 03:00 | 0 | 0 | 0 | 0 | -16.2848 | -122.7064 | 112.9641 | -22.9641 | -118.6923 | 125.3036 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-02-05 04:00 | 0 | 0 | 0 | 0 | -16.2724 | -107.7076 | 109.8057 | -19.8057 | -103.6019 | 111.1638 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-02-05 05:00 | 0 | 0 | 0 | 0 | -16.2599 | -92.7089 | 106.4402 | -16.4402 | -88.8684 | 97.1867 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-02-05 06:00 | 0 | 0 | 0 | 0 | -16.2474 | -77.7101 | 103.0907 | -13.0907 | -74.3843 | 83.4647 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.5 | -0.5 | 1.102 | 0
2015-02-05 07:00 | 0 | 0 | 0 | 0 | -16.235 | -62.7114 | 99.9684 | -9.9684 | -60.037 | 70.1569 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-02-05 08:00 | 0 | 0 | 0 | 0 | -16.2225 | -47.7126 | 97.2658 | -7.2658 | -45.7313 | 57.56 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-02-05 09:00 | 0 | 0 | 0 | 0 | -16.21 | -32.7138 | 95.1501 | -5.1501 | -31.4035 | 46.2667 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2 | -4.2 | 1.1168 | 0
2015-02-05 10:00 | 0 | 0 | 0 | 0 | -16.1975 | -17.7151 | 93.7536 | -3.7536 | -17.0277 | 37.4813 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.1 | -5.1 | 1.1204 | 0
2015-02-05 11:00 | 0 | 0 | 0 | 0 | -16.185 | -2.7163 | 93.1656 | -3.1656 | -2.6125 | 33.2596 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.3 | -5.3 | 1.1212 | 0
2015-02-05 12:00 | 0 | 0 | 0 | 0 | -16.1725 | 12.2825 | 93.4237 | -3.4237 | 11.8107 | 35.2821 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.6 | -5.6 | 1.1224 | 0
2015-02-05 13:00 | 0 | 0 | 0 | 0 | -16.16 | 27.2813 | 94.5102 | -4.5102 | 26.2071 | 42.6694 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6 | -6 | 1.124 | 0
2015-02-05 14:00 | 0 | 0 | 0 | 0 | -16.1474 | 42.2801 | 96.3542 | -6.3542 | 40.5574 | 53.2312 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.6 | -6.6 | 1.1264 | 0
2015-02-05 15:00 | 0 | 0 | 0 | 0 | -16.1349 | 57.2789 | 98.8379 | -8.8379 | 54.8735 | 65.4453 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.9 | -6.9 | 1.1276 | 0
2015-02-05 16:00 | 0 | 0 | 0 | 0 | -16.1223 | 72.2777 | 101.8053 | -11.8053 | 69.2046 | 78.5408 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.7 | -7.7 | 1.1308 | 0
2015-02-05 17:00 | 0 | 0 | 0 | 0 | -16.1098 | 87.2765 | 105.0722 | -15.0722 | 83.6349 | 92.1382 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.6 | -8.6 | 1.1344 | 0
2015-02-05 18:00 | 0 | 0 | 0 | 0 | -16.0972 | 102.2754 | 108.4328 | -18.4328 | 98.2715 | 106.0392 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.4 | -9.4 | 1.1376 | 0
2015-02-05 19:00 | 0 | 0 | 0 | 0 | -16.0847 | 117.2742 | 111.6674 | -21.6674 | 113.2254 | 120.1321 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.2 | -10.2 | 1.1408 | 0
2015-02-05 20:00 | 0 | 0 | 0 | 0 | -16.0721 | 132.273 | 114.5497 | -24.5497 | 128.5844 | 134.349 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.4 | -10.4 | 1.1416 | 0
2015-02-05 21:00 | 0 | 0 | 0 | 0 | -16.0595 | 147.2719 | 116.8606 | -26.8606 | 144.3812 | 148.6445 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11 | -11 | 1.144 | 0
2015-02-05 22:00 | 0 | 0 | 0 | 0 | -16.0469 | 162.2707 | 118.4076 | -28.4076 | 160.5661 | 162.9823 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11 | -11 | 1.144 | 0
2015-02-05 23:00 | 0 | 0 | 0 | 0 | -16.0343 | 177.2696 | 119.0515 | -29.0515 | 176.9979 | 177.221 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.4 | -11.4 | 1.1456 | 0
2015-02-06 | 0 | 0 | 0 | 0 | -16.0217 | -167.7316 | 118.7311 | -28.7311 | -166.5314 | 168.2005 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.6 | -11.6 | 1.1464 | 0
2015-02-06 01:00 | 0 | 0 | 0 | 0 | -16.0091 | -152.7327 | 117.4755 | -27.4755 | -150.2406 | 153.8571 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.1 | -12.1 | 1.1484 | 0
2015-02-06 02:00 | 0 | 0 | 0 | 0 | -15.9964 | -137.7339 | 115.3981 | -25.3981 | -134.2989 | 139.5373 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.4 | -12.4 | 1.1496 | 0
2015-02-06 03:00 | 0 | 0 | 0 | 0 | -15.9838 | -122.735 | 112.6752 | -22.6752 | -118.7887 | 125.2803 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.7 | -12.7 | 1.1508 | 0
2015-02-06 04:00 | 0 | 0 | 0 | 0 | -15.9712 | -107.7361 | 109.5186 | -19.5186 | -103.7031 | 111.1261 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.8 | -12.8 | 1.1512 | 0
2015-02-06 05:00 | 0 | 0 | 0 | 0 | -15.9585 | -92.7372 | 106.1536 | -16.1536 | -88.9697 | 97.1316 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.7 | -12.7 | 1.1508 | 0
2015-02-06 06:00 | 0 | 0 | 0 | 0 | -15.9458 | -77.7383 | 102.803 | -12.803 | -74.4813 | 83.3879 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.8 | -12.8 | 1.1512 | 0
2015-02-06 07:00 | 0 | 0 | 0 | 0 | -15.9332 | -62.7394 | 99.6783 | -9.6783 | -60.1261 | 70.0523 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.8 | -12.8 | 1.1512 | 0
2015-02-06 08:00 | 0 | 0 | 0 | 0 | -15.9205 | -47.7405 | 96.9727 | -6.9727 | -45.8092 | 57.4183 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.8 | -12.8 | 1.1512 | 0
2015-02-06 09:00 | 0 | 0 | 0 | 0 | -15.9078 | -32.7416 | 94.8534 | -4.8534 | -31.4672 | 46.0751 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.8 | -12.8 | 1.1512 | 0
2015-02-06 10:00 | 0 | 0 | 0 | 0 | -15.8951 | -17.7427 | 93.4538 | -3.4538 | -17.0751 | 37.2288 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.3 | -13.3 | 1.1532 | 0
2015-02-06 11:00 | 0 | 0 | 0 | 0 | -15.8824 | -2.7438 | 92.8634 | -2.8634 | -2.6423 | 32.9603 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.3 | -13.3 | 1.1532 | 0
2015-02-06 12:00 | 0 | 0 | 0 | 0 | -15.8697 | 12.2551 | 93.12 | -3.12 | 11.7989 | 34.9895 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.6 | -13.6 | 1.1544 | 0
2015-02-06 13:00 | 0 | 0 | 0 | 0 | -15.857 | 27.254 | 94.2062 | -4.2062 | 26.2124 | 42.4217 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.8 | -13.8 | 1.1552 | 0
2015-02-06 14:00 | 0 | 0 | 0 | 0 | -15.8443 | 42.253 | 96.0507 | -6.0507 | 40.578 | 53.03 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.8 | -13.8 | 1.1552 | 0
2015-02-06 15:00 | 0 | 0 | 0 | 0 | -15.8315 | 57.2519 | 98.5352 | -8.5352 | 54.9066 | 65.2812 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.2 | -14.2 | 1.1568 | 0
2015-02-06 16:00 | 0 | 0 | 0 | 0 | -15.8188 | 72.2509 | 101.5035 | -11.5035 | 69.2469 | 78.4051 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.3 | -14.3 | 1.1572 | 0
2015-02-06 17:00 | 0 | 0 | 0 | 0 | -15.8061 | 87.2498 | 104.7708 | -14.7708 | 83.6823 | 92.0245 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.1 | -15.1 | 1.1604 | 0
2015-02-06 18:00 | 0 | 0 | 0 | 0 | -15.7933 | 102.2488 | 108.1313 | -18.1313 | 98.3196 | 105.9432 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16 | -16 | 1.164 | 0
2015-02-06 19:00 | 0 | 0 | 0 | 0 | -15.7805 | 117.2477 | 111.3649 | -21.3649 | 113.2692 | 120.0507 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.6 | -16.6 | 1.1664 | 0
2015-02-06 20:00 | 0 | 0 | 0 | 0 | -15.7678 | 132.2467 | 114.2459 | -24.2459 | 128.6183 | 134.2796 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.3 | -18.3 | 1.1732 | 0
2015-02-06 21:00 | 0 | 0 | 0 | 0 | -15.755 | 147.2457 | 116.5555 | -26.5555 | 144.3998 | 148.5844 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18 | -18 | 1.172 | 0
2015-02-06 22:00 | 0 | 0 | 0 | 0 | -15.7422 | 162.2447 | 118.1018 | -28.1018 | 160.5648 | 162.925 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.9 | -17.9 | 1.1716 | 0
2015-02-06 23:00 | 0 | 0 | 0 | 0 | -15.7294 | 177.2436 | 118.7463 | -28.7463 | 176.9737 | 177.0801 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.5 | -18.5 | 1.174 | 0
2015-02-07 | 0 | 0 | 0 | 0 | -15.7166 | -167.7574 | 118.4278 | -28.4278 | -166.5785 | 168.1877 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.4 | -18.4 | 1.1736 | 0
2015-02-07 01:00 | 0 | 0 | 0 | 0 | -15.7038 | -152.7584 | 117.1751 | -27.1751 | -150.3081 | 153.8481 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.1 | -19.1 | 1.1764 | 0
2015-02-07 02:00 | 0 | 0 | 0 | 0 | -15.691 | -137.7594 | 115.1011 | -25.1011 | -134.3823 | 139.5205 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19 | -19 | 1.176 | 0
2015-02-07 03:00 | 0 | 0 | 0 | 0 | -15.6781 | -122.7604 | 112.3811 | -22.3811 | -118.8825 | 125.2521 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.1 | -19.1 | 1.1764 | 0
2015-02-07 04:00 | 0 | 0 | 0 | 0 | -15.6653 | -107.7613 | 109.2264 | -19.2264 | -103.802 | 111.0838 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.2 | -19.2 | 1.1768 | 0
2015-02-07 05:00 | 0 | 0 | 0 | 0 | -15.6525 | -92.7623 | 105.8617 | -15.8617 | -89.0687 | 97.0721 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.5 | -19.5 | 1.178 | 0
2015-02-07 06:00 | 0 | 0 | 0 | 0 | -15.6396 | -77.7633 | 102.5101 | -12.5101 | -74.5762 | 83.3069 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.1 | -18.1 | 1.1724 | 0
2015-02-07 07:00 | 0 | 0 | 0 | 0 | -15.6268 | -62.7643 | 99.3832 | -9.3832 | -60.213 | 69.9435 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.7 | -18.7 | 1.1748 | 0
2015-02-07 08:00 | 0 | 0 | 0 | 0 | -15.6139 | -47.7652 | 96.6744 | -6.6744 | -45.8847 | 57.2724 | 0 | 0 | 0.8 | 1 | 0 | 0 | -20.4 | -20.4 | 1.1816 | 0
2015-02-07 09:00 | 0 | 0 | 0 | 0 | -15.601 | -32.7662 | 94.5518 | -4.5518 | -31.5285 | 45.8791 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.5 | -18.5 | 1.174 | 0
2015-02-07 10:00 | 0 | 0 | 0 | 0 | -15.5881 | -17.7672 | 93.1492 | -3.1492 | -17.1198 | 36.9714 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.7 | -19.7 | 1.1788 | 0
2015-02-07 11:00 | 0 | 0 | 0 | 0 | -15.5752 | -2.7681 | 92.5564 | -2.5564 | -2.669 | 32.6562 | 0 | 0 | 0.8 | 1 | 0 | 0 | -20 | -20 | 1.18 | 0
2015-02-07 12:00 | 0 | 0 | 0 | 0 | -15.5623 | 12.231 | 92.8119 | -2.8119 | 11.7904 | 34.6939 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.6 | -18.6 | 1.1744 | 0
2015-02-07 13:00 | 0 | 0 | 0 | 0 | -15.5494 | 27.23 | 93.8979 | -3.8979 | 26.2213 | 42.1731 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.1 | -16.1 | 1.1644 | 0
2015-02-07 14:00 | 0 | 0 | 0 | 0 | -15.5365 | 42.2291 | 95.743 | -5.743 | 40.6023 | 52.8293 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.8 | -16.8 | 1.1672 | 0
2015-02-07 15:00 | 0 | 0 | 0 | 0 | -15.5236 | 57.2282 | 98.2286 | -8.2286 | 54.9436 | 65.1182 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.2 | -15.2 | 1.1608 | 0
2015-02-07 16:00 | 0 | 0 | 0 | 0 | -15.5107 | 72.2272 | 101.1979 | -11.1979 | 69.2931 | 78.2707 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.2 | -14.2 | 1.1568 | 0
2015-02-07 17:00 | 0 | 0 | 0 | 0 | -15.4977 | 87.2263 | 104.4657 | -14.4657 | 83.7337 | 91.9124 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.2 | -14.2 | 1.1568 | 0
2015-02-07 18:00 | 0 | 0 | 0 | 0 | -15.4848 | 102.2254 | 107.826 | -17.826 | 98.3718 | 105.8488 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.3 | -14.3 | 1.1572 | 0
2015-02-07 19:00 | 0 | 0 | 0 | 0 | -15.4718 | 117.2245 | 111.0587 | -21.0587 | 113.317 | 119.9706 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.8 | -13.8 | 1.1552 | 0
2015-02-07 20:00 | 0 | 0 | 0 | 0 | -15.4589 | 132.2236 | 113.9382 | -23.9382 | 128.6562 | 134.2111 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.6 | -13.6 | 1.1544 | 0
2015-02-07 21:00 | 0 | 0 | 0 | 0 | -15.4459 | 147.2227 | 116.2463 | -26.2463 | 144.4224 | 148.5241 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.8 | -13.8 | 1.1552 | 0
2015-02-07 22:00 | 0 | 0 | 0 | 0 | -15.4329 | 162.2218 | 117.7918 | -27.7918 | 160.5672 | 162.865 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.5 | -13.5 | 1.154 | 0
2015-02-07 23:00 | 0 | 0 | 0 | 0 | -15.42 | 177.221 | 118.4366 | -28.4366 | 176.9532 | 176.9155 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.9 | -13.9 | 1.1556 | 0
2015-02-08 | 0 | 0 | 0 | 0 | -15.407 | -167.7799 | 118.1198 | -28.1198 | -166.6222 | 168.1633 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14 | -14 | 1.156 | 0
2015-02-08 01:00 | 0 | 0 | 0 | 0 | -15.394 | -152.7808 | 116.8699 | -26.8699 | -150.3724 | 153.8322 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14 | -14 | 1.156 | 0
2015-02-08 02:00 | 0 | 0 | 0 | 0 | -15.381 | -137.7816 | 114.7991 | -24.7991 | -134.4628 | 139.4981 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.2 | -15.2 | 1.1608 | 0
2015-02-08 03:00 | 0 | 0 | 0 | 0 | -15.368 | -122.7825 | 112.0819 | -22.0819 | -118.9737 | 125.219 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.2 | -15.2 | 1.1608 | 0
2015-02-08 04:00 | 0 | 0 | 0 | 0 | -15.3549 | -107.7833 | 108.9289 | -18.9289 | -103.8985 | 111.0369 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.1 | -17.1 | 1.1684 | 0
2015-02-08 05:00 | 0 | 0 | 0 | 0 | -15.3419 | -92.7842 | 105.5647 | -15.5647 | -89.1655 | 97.0083 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.3 | -16.3 | 1.1652 | 0
2015-02-08 06:00 | 0 | 0 | 0 | 0 | -15.3289 | -77.785 | 102.2121 | -12.2121 | -74.6689 | 83.2217 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.4 | -16.4 | 1.1656 | 0
2015-02-08 07:00 | 0 | 0 | 0 | 0 | -15.3158 | -62.7859 | 99.083 | -9.083 | -60.2977 | 69.8306 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.9 | -16.9 | 1.1676 | 0
2015-02-08 08:00 | 0 | 0 | 0 | 0 | -15.3028 | -47.7867 | 96.3712 | -6.3712 | -45.9578 | 57.1223 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.2 | -17.2 | 1.1688 | 0
2015-02-08 09:00 | 0 | 0 | 0 | 0 | -15.2897 | -32.7875 | 94.2454 | -4.2454 | -31.5872 | 45.6788 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.7 | -16.7 | 1.1668 | 0
2015-02-08 10:00 | 0 | 0 | 0 | 0 | -15.2767 | -17.7883 | 92.8398 | -2.8398 | -17.1617 | 36.7093 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.1 | -17.1 | 1.1684 | 0
2015-02-08 11:00 | 0 | 0 | 0 | 0 | -15.2636 | -2.7892 | 92.245 | -2.245 | -2.6928 | 32.3475 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.2 | -17.2 | 1.1688 | 0
2015-02-08 12:00 | 0 | 0 | 0 | 0 | -15.2505 | 12.21 | 92.4994 | -2.4994 | 11.7852 | 34.3954 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.5 | -17.5 | 1.17 | 0
2015-02-08 13:00 | 0 | 0 | 0 | 0 | -15.2374 | 27.2092 | 93.5854 | -3.5854 | 26.2336 | 41.9237 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.6 | -17.6 | 1.1704 | 0
2015-02-08 14:00 | 0 | 0 | 0 | 0 | -15.2243 | 42.2084 | 95.4314 | -5.4314 | 40.6303 | 52.6291 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18 | -18 | 1.172 | 0
2015-02-08 15:00 | 0 | 0 | 0 | 0 | -15.2112 | 57.2077 | 97.9182 | -7.9182 | 54.9844 | 64.9564 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.4 | -17.4 | 1.1696 | 0
2015-02-08 16:00 | 0 | 0 | 0 | 0 | -15.1981 | 72.2069 | 100.8886 | -10.8886 | 69.3432 | 78.1379 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.6 | -18.6 | 1.1744 | 0
2015-02-08 17:00 | 0 | 0 | 0 | 0 | -15.185 | 87.2061 | 104.157 | -14.157 | 83.7892 | 91.8018 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.5 | -18.5 | 1.174 | 0
2015-02-08 18:00 | 0 | 0 | 0 | 0 | -15.1719 | 102.2053 | 107.517 | -17.517 | 98.4279 | 105.7558 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.3 | -18.3 | 1.1732 | 0
2015-02-08 19:00 | 0 | 0 | 0 | 0 | -15.1587 | 117.2046 | 110.7487 | -20.7487 | 113.3688 | 119.8918 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.7 | -18.7 | 1.1748 | 0
2015-02-08 20:00 | 0 | 0 | 0 | 0 | -15.1456 | 132.2038 | 113.6267 | -23.6267 | 128.6982 | 134.1433 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.7 | -18.7 | 1.1748 | 0
2015-02-08 21:00 | 0 | 0 | 0 | 0 | -15.1324 | 147.203 | 115.9331 | -25.9331 | 144.4489 | 148.4636 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.2 | -18.2 | 1.1728 | 0
2015-02-08 22:00 | 0 | 0 | 0 | 0 | -15.1193 | 162.2023 | 117.4776 | -27.4776 | 160.5735 | 162.8021 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.2 | -19.2 | 1.1768 | 0
2015-02-08 23:00 | 0 | 0 | 0 | 0 | -15.1061 | 177.2015 | 118.1226 | -28.1226 | 176.9363 | 176.7298 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.5 | -18.5 | 1.174 | 0
2015-02-09 | 0 | 0 | 0 | 0 | -15.0929 | -167.7992 | 117.8072 | -27.8072 | -166.6624 | 168.1272 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.2 | -19.2 | 1.1768 | 0
2015-02-09 01:00 | 0 | 0 | 0 | 0 | -15.0798 | -152.7999 | 116.5599 | -26.5599 | -150.4336 | 153.8092 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.1 | -19.1 | 1.1764 | 0
2015-02-09 02:00 | 0 | 0 | 0 | 0 | -15.0666 | -137.8007 | 114.4921 | -24.4921 | -134.5403 | 139.47 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.1 | -18.1 | 1.1724 | 0
2015-02-09 03:00 | 0 | 0 | 0 | 0 | -15.0534 | -122.8014 | 111.7776 | -21.7776 | -119.0622 | 125.1808 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.3 | -18.3 | 1.1732 | 0
2015-02-09 04:00 | 0 | 0 | 0 | 0 | -15.0402 | -107.8021 | 108.6265 | -18.6265 | -103.9925 | 110.9855 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.6 | -19.6 | 1.1784 | 0
2015-02-09 05:00 | 0 | 0 | 0 | 0 | -15.027 | -92.8028 | 105.2627 | -15.2627 | -89.2599 | 96.9401 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.6 | -18.6 | 1.1744 | 0
2015-02-09 06:00 | 0 | 0 | 0 | 0 | -15.0138 | -77.8035 | 101.9091 | -11.9091 | -74.7593 | 83.1323 | 0 | 0 | 0.8 | 1 | 0 | 0 | -21 | -21 | 1.184 | 0
2015-02-09 07:00 | 0 | 0 | 0 | 0 | -15.0005 | -62.8042 | 98.7778 | -8.7778 | -60.38 | 69.7136 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19 | -19 | 1.176 | 0
2015-02-09 08:00 | 0 | 0 | 0 | 0 | -14.9873 | -47.8049 | 96.0632 | -6.0632 | -46.0286 | 56.9682 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.5 | -19.5 | 1.178 | 0
2015-02-09 09:00 | 0 | 0 | 0 | 0 | -14.9741 | -32.8056 | 93.9342 | -3.9342 | -31.6433 | 45.4741 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.7 | -18.7 | 1.1748 | 0
2015-02-09 10:00 | 0 | 0 | 0 | 0 | -14.9608 | -17.8063 | 92.5259 | -2.5259 | -17.2008 | 36.4426 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.2 | -19.2 | 1.1768 | 0
2015-02-09 11:00 | 0 | 0 | 0 | 0 | -14.9476 | -2.807 | 91.9292 | -1.9292 | -2.7134 | 32.0342 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.6 | -18.6 | 1.1744 | 0
2015-02-09 12:00 | 0 | 0 | 0 | 0 | -14.9343 | 12.1924 | 92.1828 | -2.1828 | 11.7832 | 34.0942 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.1 | -18.1 | 1.1724 | 0
2015-02-09 13:00 | 0 | 0 | 0 | 0 | -14.921 | 27.1917 | 93.269 | -3.269 | 26.2495 | 41.6738 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.5 | -18.5 | 1.174 | 0
2015-02-09 14:00 | 0 | 0 | 0 | 0 | -14.9078 | 42.191 | 95.116 | -5.116 | 40.662 | 52.4296 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.2 | -18.2 | 1.1728 | 0
2015-02-09 15:00 | 0 | 0 | 0 | 0 | -14.8945 | 57.1904 | 97.6041 | -7.6041 | 55.029 | 64.7959 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.1 | -18.1 | 1.1724 | 0
2015-02-09 16:00 | 0 | 0 | 0 | 0 | -14.8812 | 72.1897 | 100.5757 | -10.5757 | 69.3973 | 78.0067 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.9 | -17.9 | 1.1716 | 0
2015-02-09 17:00 | 0 | 0 | 0 | 0 | -14.8679 | 87.1891 | 103.8448 | -13.8448 | 83.8486 | 91.6929 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.2 | -18.2 | 1.1728 | 0
2015-02-09 18:00 | 0 | 0 | 0 | 0 | -14.8546 | 102.1885 | 107.2046 | -17.2046 | 98.4881 | 105.6643 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.1 | -18.1 | 1.1724 | 0
2015-02-09 19:00 | 0 | 0 | 0 | 0 | -14.8413 | 117.1878 | 110.4352 | -20.4352 | 113.4246 | 119.8142 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.1 | -18.1 | 1.1724 | 0
2015-02-09 20:00 | 0 | 0 | 0 | 0 | -14.828 | 132.1872 | 113.3115 | -23.3115 | 128.7441 | 134.0763 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.2 | -18.2 | 1.1728 | 0
2015-02-09 21:00 | 0 | 0 | 0 | 0 | -14.8146 | 147.1866 | 115.6161 | -25.6161 | 144.4793 | 148.4028 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.2 | -18.2 | 1.1728 | 0
2015-02-09 22:00 | 0 | 0 | 0 | 0 | -14.8013 | 162.186 | 117.1594 | -27.1594 | 160.5836 | 162.7363 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.9 | -17.9 | 1.1716 | 0
2015-02-09 23:00 | 0 | 0 | 0 | 0 | -14.788 | 177.1853 | 117.8043 | -27.8043 | 176.9231 | 176.5251 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.5 | -17.5 | 1.17 | 0
2015-02-10 | 0 | 0 | 0 | 0 | -14.7746 | -167.8153 | 117.4902 | -27.4902 | -166.6993 | 168.079 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17 | -17 | 1.168 | 0
2015-02-10 01:00 | 0 | 0 | 0 | 0 | -14.7613 | -152.8159 | 116.2453 | -26.2453 | -150.4916 | 153.779 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.6 | -17.6 | 1.1704 | 0
2015-02-10 02:00 | 0 | 0 | 0 | 0 | -14.7479 | -137.8164 | 114.1804 | -24.1804 | -134.615 | 139.4362 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.5 | -16.5 | 1.166 | 0
2015-02-10 03:00 | 0 | 0 | 0 | 0 | -14.7345 | -122.817 | 111.4686 | -21.4686 | -119.1481 | 125.1377 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.1 | -17.1 | 1.1684 | 0
2015-02-10 04:00 | 0 | 0 | 0 | 0 | -14.7212 | -107.8176 | 108.3191 | -18.3191 | -104.084 | 110.9294 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18 | -18 | 1.172 | 0
2015-02-10 05:00 | 0 | 0 | 0 | 0 | -14.7078 | -92.8182 | 104.9558 | -14.9558 | -89.352 | 96.8676 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.1 | -18.1 | 1.1724 | 0
2015-02-10 06:00 | 0 | 0 | 0 | 0 | -14.6944 | -77.8188 | 101.6013 | -11.6013 | -74.8474 | 83.0388 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.7 | -17.7 | 1.1708 | 0
2015-02-10 07:00 | 0 | 0 | 0 | 0 | -14.681 | -62.8193 | 98.4679 | -8.4679 | -60.4601 | 69.5925 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.8 | -17.8 | 1.1712 | 0
2015-02-10 08:00 | 0 | 0 | 0 | 0 | -14.6676 | -47.8199 | 95.7504 | -5.7504 | -46.0969 | 56.81 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.8 | -17.8 | 1.1712 | 0
2015-02-10 09:00 | 0 | 0 | 0 | 0 | -14.6542 | -32.8204 | 93.6185 | -3.6185 | -31.6968 | 45.2654 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.9 | -16.9 | 1.1676 | 0
2015-02-10 10:00 | 0.0033333 | 0.0033333 | 0 | 0 | -14.6407 | -17.821 | 92.2076 | -2.2076 | -17.2371 | 36.1714 | 0 | 0.0025 | 0.8 | 1 | 0.00066667 | 0.0031667 | -16.7 | -16.6999 | 1.1668 | 3.0298e-06
2015-02-10 11:00 | 0.0066667 | 0.0066667 | 0 | 0 | -14.6273 | -2.8215 | 91.6091 | -1.6091 | -2.7311 | 31.7165 | 0 | 0.005 | 0.8 | 1 | 0.0013333 | 0.0063333 | -15.4 | -15.3998 | 1.1616 | 6.0326e-06
2015-02-10 12:00 | 0.01 | 0.01 | 0 | 0 | -14.6139 | 12.1779 | 91.862 | -1.862 | 11.7845 | 33.7904 | 0 | 0.0075 | 0.8 | 1 | 0.002 | 0.0095 | -16 | -15.9997 | 1.164 | 9.0676e-06
2015-02-10 13:00 | 0.0066667 | 0.0066667 | 0 | 0 | -14.6004 | 27.1774 | 92.9487 | -2.9487 | 26.2688 | 41.4235 | 0 | 0.005 | 0.8 | 1 | 0.0013333 | 0.0063333 | -16.2 | -16.1998 | 1.1648 | 6.0492e-06
2015-02-10 14:00 | 0.0033333 | 0.0033333 | 0 | 0 | -14.587 | 42.1769 | 94.7968 | -4.7968 | 40.6973 | 52.2311 | 0 | 0.0025 | 0.8 | 1 | 0.00066667 | 0.0031667 | -16.1 | -16.0999 | 1.1644 | 3.0236e-06
2015-02-10 15:00 | 0 | 0 | 0 | 0 | -14.5735 | 57.1764 | 97.2865 | -7.2865 | 55.0775 | 64.6369 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.5 | -14.5 | 1.158 | 0
2015-02-10 16:00 | 0 | 0 | 0 | 0 | -14.5601 | 72.1758 | 100.2594 | -10.2594 | 69.4552 | 77.877 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.1 | -14.1 | 1.1564 | 0
2015-02-10 17:00 | 0 | 0 | 0 | 0 | -14.5466 | 87.1753 | 103.5291 | -13.5291 | 83.9119 | 91.5856 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.7 | -13.7 | 1.1548 | 0
2015-02-10 18:00 | 0 | 0 | 0 | 0 | -14.5331 | 102.1748 | 106.8887 | -16.8887 | 98.5522 | 105.5744 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.7 | -13.7 | 1.1548 | 0
2015-02-10 19:00 | 0 | 0 | 0 | 0 | -14.5196 | 117.1743 | 110.1182 | -20.1182 | 113.4843 | 119.7378 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.8 | -13.8 | 1.1552 | 0
2015-02-10 20:00 | 0 | 0 | 0 | 0 | -14.5061 | 132.1738 | 112.9927 | -22.9927 | 128.7939 | 134.01 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.8 | -13.8 | 1.1552 | 0
2015-02-10 21:00 | 0 | 0 | 0 | 0 | -14.4926 | 147.1734 | 115.2954 | -25.2954 | 144.5135 | 148.3417 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.9 | -13.9 | 1.1556 | 0
2015-02-10 22:00 | 0 | 0 | 0 | 0 | -14.4791 | 162.1729 | 116.8372 | -26.8372 | 160.5974 | 162.6673 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.4 | -14.4 | 1.1576 | 0
2015-02-10 23:00 | 0 | 0 | 0 | 0 | -14.4656 | 177.1724 | 117.4818 | -27.4818 | 176.9135 | 176.3037 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.4 | -15.4 | 1.1616 | 0
2015-02-11 | 0 | 0 | 0 | 0 | -14.4521 | -167.8281 | 117.1688 | -27.1688 | -166.7326 | 168.0187 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.5 | -15.5 | 1.162 | 0
2015-02-11 01:00 | 0 | 0 | 0 | 0 | -14.4386 | -152.8285 | 115.9262 | -25.9262 | -150.5464 | 153.7416 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.4 | -15.4 | 1.1616 | 0
2015-02-11 02:00 | 0 | 0 | 0 | 0 | -14.4251 | -137.829 | 113.8641 | -23.8641 | -134.6867 | 139.3966 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.4 | -15.4 | 1.1616 | 0
2015-02-11 03:00 | 0 | 0 | 0 | 0 | -14.4115 | -122.8294 | 111.1547 | -21.1547 | -119.2312 | 125.0895 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.6 | -15.6 | 1.1624 | 0
2015-02-11 04:00 | 0 | 0 | 0 | 0 | -14.398 | -107.8299 | 108.007 | -18.007 | -104.1731 | 110.8687 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.6 | -16.6 | 1.1664 | 0
2015-02-11 05:00 | 0 | 0 | 0 | 0 | -14.3844 | -92.8303 | 104.644 | -14.644 | -89.4418 | 96.7907 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.5 | -16.5 | 1.166 | 0
2015-02-11 06:00 | 0 | 0 | 0 | 0 | -14.3708 | -77.8308 | 101.2886 | -11.2886 | -74.9332 | 82.9412 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.6 | -16.6 | 1.1664 | 0
2015-02-11 07:00 | 0 | 0 | 0 | 0 | -14.3573 | -62.8312 | 98.1532 | -8.1532 | -60.5378 | 69.4675 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.2 | -16.2 | 1.1648 | 0
2015-02-11 08:00 | 0 | 0 | 0 | 0 | -14.3437 | -47.8316 | 95.4331 | -5.4331 | -46.1628 | 56.6479 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16 | -16 | 1.164 | 0
2015-02-11 09:00 | 0 | 0 | 0 | 0 | -14.3301 | -32.832 | 93.2983 | -3.2983 | -31.7477 | 45.0526 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.6 | -15.6 | 1.1624 | 0
2015-02-11 10:00 | 0.013333 | 0.013333 | 0 | 0 | -14.3165 | -17.8325 | 91.8849 | -1.8849 | -17.2706 | 35.8957 | 0 | 0.01 | 0.8 | 1 | 0.0026667 | 0.012667 | -15.8 | -15.7996 | 1.1632 | 1.2082e-05
2015-02-11 11:00 | 0.026667 | 0.026667 | 0 | 0 | -14.3029 | -2.8329 | 91.2849 | -1.2849 | -2.7457 | 31.3944 | 0 | 0.02 | 0.8 | 1 | 0.0053333 | 0.025333 | -16.3 | -16.2992 | 1.1652 | 2.4205e-05
2015-02-11 12:00 | 0.04 | 0.04 | 0 | 0 | -14.2893 | 12.1667 | 91.5373 | -1.5373 | 11.7891 | 33.4842 | 0 | 0.03 | 0.8 | 1 | 0.008 | 0.038 | -16.2 | -16.1988 | 1.1648 | 3.6295e-05
2015-02-11 13:00 | 0.026667 | 0.026667 | 0 | 0 | -14.2757 | 27.1663 | 92.6246 | -2.6246 | 26.2917 | 41.173 | 0 | 0.02 | 0.8 | 1 | 0.0053333 | 0.025333 | -15.9 | -15.8992 | 1.1636 | 2.4172e-05
2015-02-11 14:00 | 0.013333 | 0.013333 | 0 | 0 | -14.2621 | 42.1659 | 94.4741 | -4.4741 | 40.7363 | 52.0335 | 0 | 0.01 | 0.8 | 1 | 0.0026667 | 0.012667 | -15.8 | -15.7996 | 1.1632 | 1.2082e-05
2015-02-11 15:00 | 0 | 0 | 0 | 0 | -14.2485 | 57.1656 | 96.9654 | -6.9654 | 55.1297 | 64.4794 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.9 | -13.9 | 1.1556 | 0
2015-02-11 16:00 | 0 | 0 | 0 | 0 | -14.2348 | 72.1652 | 99.9398 | -9.9398 | 69.517 | 77.7491 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15 | -15 | 1.16 | 0
2015-02-11 17:00 | 0 | 0 | 0 | 0 | -14.2212 | 87.1648 | 103.2102 | -13.2102 | 83.9792 | 91.48 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.3 | -14.3 | 1.1572 | 0
2015-02-11 18:00 | 0 | 0 | 0 | 0 | -14.2076 | 102.1644 | 106.5696 | -16.5696 | 98.6202 | 105.486 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.8 | -13.8 | 1.1552 | 0
2015-02-11 19:00 | 0 | 0 | 0 | 0 | -14.1939 | 117.1641 | 109.7978 | -19.7978 | 113.548 | 119.6627 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.4 | -13.4 | 1.1536 | 0
2015-02-11 20:00 | 0 | 0 | 0 | 0 | -14.1803 | 132.1637 | 112.6704 | -22.6704 | 128.8475 | 133.9443 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.1 | -13.1 | 1.1524 | 0
2015-02-11 21:00 | 0 | 0 | 0 | 0 | -14.1666 | 147.1634 | 114.971 | -24.971 | 144.5516 | 148.2801 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.6 | -12.6 | 1.1504 | 0
2015-02-11 22:00 | 0 | 0 | 0 | 0 | -14.1529 | 162.163 | 116.5112 | -26.5112 | 160.615 | 162.5949 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.7 | -12.7 | 1.1508 | 0
2015-02-11 23:00 | 0 | 0 | 0 | 0 | -14.1392 | 177.1627 | 117.1553 | -27.1553 | 176.9075 | 176.0676 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.5 | -12.5 | 1.15 | 0
2015-02-12 | 0 | 0 | 0 | 0 | -14.1255 | -167.8377 | 116.8432 | -26.8432 | -166.7626 | 167.9461 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.4 | -13.4 | 1.1536 | 0
2015-02-12 01:00 | 0 | 0 | 0 | 0 | -14.1119 | -152.838 | 115.6026 | -25.6026 | -150.5979 | 153.6968 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.7 | -13.7 | 1.1548 | 0
2015-02-12 02:00 | 0 | 0 | 0 | 0 | -14.0982 | -137.8383 | 113.5432 | -23.5432 | -134.7555 | 139.3512 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.6 | -13.6 | 1.1544 | 0
2015-02-12 03:00 | 0 | 0 | 0 | 0 | -14.0844 | -122.8386 | 110.8363 | -20.8363 | -119.3117 | 125.0362 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14 | -14 | 1.156 | 0
2015-02-12 04:00 | 0 | 0 | 0 | 0 | -14.0707 | -107.8389 | 107.6902 | -17.6902 | -104.2596 | 110.8035 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.1 | -14.1 | 1.1564 | 0
2015-02-12 05:00 | 0 | 0 | 0 | 0 | -14.057 | -92.8393 | 104.3276 | -14.3276 | -89.5291 | 96.7096 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.3 | -14.3 | 1.1572 | 0
2015-02-12 06:00 | 0 | 0 | 0 | 0 | -14.0433 | -77.8396 | 100.9714 | -10.9714 | -75.0167 | 82.8395 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.3 | -14.3 | 1.1572 | 0
2015-02-12 07:00 | 0.0066667 | 0.0066667 | 0 | 0 | -14.0296 | -62.8399 | 97.834 | -7.834 | -60.6131 | 69.3386 | 0 | 0.005 | 0.8 | 1 | 0.0013333 | 0.0063333 | -14.7 | -14.6998 | 1.1588 | 6.018e-06
2015-02-12 08:00 | 0.013333 | 0.013333 | 0 | 0 | -14.0158 | -47.8401 | 95.1112 | -5.1112 | -46.2263 | 56.4819 | 0 | 0.01 | 0.8 | 1 | 0.0026667 | 0.012667 | -14.4 | -14.3996 | 1.1576 | 1.2024e-05
2015-02-12 09:00 | 0.02 | 0.02 | 0 | 0 | -14.0021 | -32.8404 | 92.9737 | -2.9737 | -31.7961 | 44.8358 | 0 | 0.015 | 0.8 | 1 | 0.004 | 0.019 | -14.7 | -14.6994 | 1.1588 | 1.8054e-05
2015-02-12 10:00 | 0.04 | 0.04 | 0 | 0 | -13.9883 | -17.8407 | 91.5581 | -1.5581 | -17.3013 | 35.6157 | 0 | 0.03 | 0.8 | 1 | 0.008 | 0.038 | -14.8 | -14.7988 | 1.1592 | 3.6121e-05
2015-02-12 11:00 | 0.06 | 0.06 | 0 | 0 | -13.9745 | -2.841 | 90.9566 | -0.95663 | -2.7572 | 31.0681 | 0 | 0.045 | 0.8 | 1 | 0.012 | 0.057 | -14.8 | -14.7982 | 1.1592 | 5.4181e-05
2015-02-12 12:00 | 0.08 | 0.08 | 0 | 0 | -13.9608 | 12.1588 | 91.2088 | -1.2088 | 11.797 | 33.1757 | 0 | 0.06 | 0.8 | 1 | 0.016 | 0.076 | -14.8 | -14.7976 | 1.1592 | 7.2241e-05
2015-02-12 13:00 | 0.053333 | 0.053333 | 0 | 0 | -13.947 | 27.1585 | 92.2968 | -2.2968 | 26.318 | 40.9224 | 0 | 0.04 | 0.8 | 1 | 0.010667 | 0.050667 | -15.2 | -15.1984 | 1.1608 | 4.8227e-05
2015-02-12 14:00 | 0.026667 | 0.026667 | 0 | 0 | -13.9332 | 42.1582 | 94.1479 | -4.1479 | 40.779 | 51.837 | 0 | 0.02 | 0.8 | 1 | 0.0053333 | 0.025333 | -15.3 | -15.2992 | 1.1612 | 2.4122e-05
2015-02-12 15:00 | 0 | 0 | 0 | 0 | -13.9194 | 57.158 | 96.641 | -6.641 | 55.1856 | 64.3235 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.2 | -15.2 | 1.1608 | 0
2015-02-12 16:00 | 0 | 0 | 0 | 0 | -13.9056 | 72.1577 | 99.6169 | -9.6169 | 69.5826 | 77.623 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.9 | -15.9 | 1.1636 | 0
2015-02-12 17:00 | 0 | 0 | 0 | 0 | -13.8918 | 87.1575 | 102.8881 | -12.8881 | 84.0503 | 91.3762 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.9 | -15.9 | 1.1636 | 0
2015-02-12 18:00 | 0 | 0 | 0 | 0 | -13.878 | 102.1573 | 106.2473 | -16.2473 | 98.6921 | 105.3992 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.2 | -16.2 | 1.1648 | 0
2015-02-12 19:00 | 0 | 0 | 0 | 0 | -13.8642 | 117.157 | 109.4743 | -19.4743 | 113.6155 | 119.5887 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16 | -16 | 1.164 | 0
2015-02-12 20:00 | 0 | 0 | 0 | 0 | -13.8504 | 132.1568 | 112.3448 | -22.3448 | 128.905 | 133.8793 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.9 | -15.9 | 1.1636 | 0
2015-02-12 21:00 | 0 | 0 | 0 | 0 | -13.8366 | 147.1566 | 114.6431 | -24.6431 | 144.5934 | 148.218 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.5 | -15.5 | 1.162 | 0
2015-02-12 22:00 | 0 | 0 | 0 | 0 | -13.8227 | 162.1564 | 116.1815 | -26.1815 | 160.6362 | 162.5192 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.3 | -16.3 | 1.1652 | 0
2015-02-12 23:00 | 0 | 0 | 0 | 0 | -13.8089 | 177.1562 | 116.8249 | -26.8249 | 176.9051 | 175.8183 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.3 | -17.3 | 1.1692 | 0
2015-02-13 | 0 | 0 | 0 | 0 | -13.795 | -167.844 | 116.5135 | -26.5135 | -166.7892 | 167.8611 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.3 | -17.3 | 1.1692 | 0
2015-02-13 01:00 | 0 | 0 | 0 | 0 | -13.7812 | -152.8442 | 115.2748 | -25.2748 | -150.6463 | 153.6445 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.7 | -16.7 | 1.1668 | 0
2015-02-13 02:00 | 0 | 0 | 0 | 0 | -13.7673 | -137.8444 | 113.2178 | -23.2178 | -134.8213 | 139.2999 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.3 | -17.3 | 1.1692 | 0
2015-02-13 03:00 | 0 | 0 | 0 | 0 | -13.7535 | -122.8446 | 110.5133 | -20.5133 | -119.3894 | 124.9778 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.1 | -17.1 | 1.1684 | 0
2015-02-13 04:00 | 0 | 0 | 0 | 0 | -13.7396 | -107.8448 | 107.3688 | -17.3688 | -104.3436 | 110.7336 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.6 | -17.6 | 1.1704 | 0
2015-02-13 05:00 | 0 | 0 | 0 | 0 | -13.7257 | -92.845 | 104.0067 | -14.0067 | -89.6141 | 96.6242 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.9 | -17.9 | 1.1716 | 0
2015-02-13 06:00 | 0 | 0 | 0 | 0 | -13.7118 | -77.8451 | 100.6496 | -10.6496 | -75.0978 | 82.7338 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.8 | -17.8 | 1.1712 | 0
2015-02-13 07:00 | 0.013333 | 0.013333 | 0 | 0 | -13.6979 | -62.8453 | 97.5103 | -7.5103 | -60.6861 | 69.2058 | 0 | 0.01 | 0.8 | 1 | 0.0026667 | 0.012667 | -17.4 | -17.3996 | 1.1696 | 1.2148e-05
2015-02-13 08:00 | 0.026667 | 0.026667 | 0 | 0 | -13.684 | -47.8454 | 94.785 | -4.785 | -46.2873 | 56.3122 | 0 | 0.02 | 0.8 | 1 | 0.0053333 | 0.025333 | -17.5 | -17.4992 | 1.17 | 2.4305e-05
2015-02-13 09:00 | 0.04 | 0.04 | 0 | 0 | -13.6701 | -32.8456 | 92.6448 | -2.6448 | -31.8417 | 44.6152 | 0 | 0.03 | 0.8 | 1 | 0.008 | 0.038 | -16.8 | -16.7988 | 1.1672 | 3.637e-05
2015-02-13 10:00 | 0.13333 | 0.13333 | 0 | 0 | -13.6562 | -17.8457 | 91.2271 | -1.2271 | -17.3291 | 35.3316 | 0 | 0.1 | 0.8 | 1 | 0.026667 | 0.12667 | -18 | -17.996 | 1.172 | 0.00012173
2015-02-13 11:00 | 0.22667 | 0.22667 | 0 | 0 | -13.6423 | -2.8459 | 90.6244 | -0.62443 | -2.7657 | 30.7377 | 0 | 0.17 | 0.8 | 1 | 0.045333 | 0.21533 | -17.8 | -17.7933 | 1.1712 | 0.0002068
2015-02-13 12:00 | 0.32 | 0.32 | 0 | 0 | -13.6284 | 12.154 | 90.8765 | -0.87651 | 11.8082 | 32.8651 | 0 | 0.24 | 0.8 | 1 | 0.064 | 0.304 | -18 | -17.9905 | 1.172 | 0.00029215
2015-02-13 13:00 | 0.21333 | 0.21333 | 0 | 0 | -13.6144 | 27.1539 | 91.9656 | -1.9656 | 26.3478 | 40.672 | 0 | 0.16 | 0.8 | 1 | 0.042667 | 0.20267 | -17.3 | -17.2937 | 1.1692 | 0.0001943
2015-02-13 14:00 | 0.10667 | 0.10667 | 0 | 0 | -13.6005 | 42.1537 | 93.8184 | -3.8184 | 40.8253 | 51.6418 | 0 | 0.08 | 0.8 | 1 | 0.021333 | 0.10133 | -14.9 | -14.8968 | 1.1596 | 9.6354e-05
2015-02-13 15:00 | 0 | 0 | 0 | 0 | -13.5865 | 57.1536 | 96.3134 | -6.3134 | 55.2454 | 64.1694 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.1 | -15.1 | 1.1604 | 0
2015-02-13 16:00 | 0 | 0 | 0 | 0 | -13.5726 | 72.1535 | 99.2909 | -9.2909 | 69.6521 | 77.4988 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.8 | -14.8 | 1.1592 | 0
2015-02-13 17:00 | 0 | 0 | 0 | 0 | -13.5586 | 87.1534 | 102.563 | -12.563 | 84.1252 | 91.2742 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.3 | -15.3 | 1.1612 | 0
2015-02-13 18:00 | 0 | 0 | 0 | 0 | -13.5447 | 102.1533 | 105.9219 | -15.9219 | 98.7678 | 105.314 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.4 | -15.4 | 1.1616 | 0
2015-02-13 19:00 | 0 | 0 | 0 | 0 | -13.5307 | 117.1532 | 109.1476 | -19.1476 | 113.6868 | 119.516 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.5 | -15.5 | 1.162 | 0
2015-02-13 20:00 | 0 | 0 | 0 | 0 | -13.5167 | 132.1531 | 112.0159 | -22.0159 | 128.9663 | 133.8148 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.7 | -15.7 | 1.1628 | 0
2015-02-13 21:00 | 0 | 0 | 0 | 0 | -13.5027 | 147.153 | 114.3118 | -24.3118 | 144.6389 | 148.1552 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.4 | -16.4 | 1.1656 | 0
2015-02-13 22:00 | 0 | 0 | 0 | 0 | -13.4887 | 162.153 | 115.8483 | -25.8483 | 160.6611 | 162.4398 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.2 | -16.2 | 1.1648 | 0
2015-02-13 23:00 | 0 | 0 | 0 | 0 | -13.4747 | 177.1529 | 116.4907 | -26.4907 | 176.9062 | 175.5572 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.3 | -16.3 | 1.1652 | 0
2015-02-14 | 0 | 0 | 0 | 0 | -13.4607 | -167.8472 | 116.1798 | -26.1798 | -166.8124 | 167.7638 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.2 | -17.2 | 1.1688 | 0
2015-02-14 01:00 | 0 | 0 | 0 | 0 | -13.4467 | -152.8473 | 114.9428 | -24.9428 | -150.6916 | 153.5847 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.6 | -15.6 | 1.1624 | 0
2015-02-14 02:00 | 0 | 0 | 0 | 0 | -13.4327 | -137.8473 | 112.8882 | -22.8882 | -134.8841 | 139.2428 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.2 | -17.2 | 1.1688 | 0
2015-02-14 03:00 | 0 | 0 | 0 | 0 | -13.4187 | -122.8474 | 110.186 | -20.186 | -119.4644 | 124.9144 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.8 | -17.8 | 1.1712 | 0
2015-02-14 04:00 | 0 | 0 | 0 | 0 | -13.4046 | -107.8474 | 107.043 | -17.043 | -104.425 | 110.6591 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.4 | -17.4 | 1.1696 | 0
2015-02-14 05:00 | 0 | 0 | 0 | 0 | -13.3906 | -92.8474 | 103.6813 | -13.6813 | -89.6966 | 96.5346 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.7 | -17.7 | 1.1708 | 0
2015-02-14 06:00 | 0 | 0 | 0 | 0 | -13.3766 | -77.8475 | 100.3234 | -10.3234 | -75.1765 | 82.6241 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.9 | -17.9 | 1.1716 | 0
2015-02-14 07:00 | 0.066667 | 0.063333 | 0.0033333 | 0 | -13.3625 | -62.8475 | 97.1823 | -7.1823 | -60.7566 | 69.0693 | 0 | 0.0475 | 0.8 | 1 | 0.013333 | 0.060833 | -16 | -15.9981 | 1.164 | 5.8064e-05
2015-02-14 08:00 | 0.13333 | 0.12667 | 0.0066667 | 0 | -13.3485 | -47.8475 | 94.4545 | -4.4545 | -46.3457 | 56.1389 | 0 | 0.095 | 0.8 | 1 | 0.026667 | 0.12167 | -15.5 | -15.4962 | 1.162 | 0.00011593
2015-02-14 09:00 | 0.2 | 0.19 | 0.01 | 0 | -13.3344 | -32.8476 | 92.3119 | -2.3119 | -31.8848 | 44.3908 | 0 | 0.1425 | 0.8 | 1 | 0.04 | 0.1825 | -15.3 | -15.2943 | 1.1612 | 0.00017377
2015-02-14 10:00 | 0.57333 | 0.53333 | 0.04 | 0 | -13.3203 | -17.8476 | 90.8921 | -0.89212 | -17.3541 | 35.0433 | 0 | 0.4 | 0.8 | 1 | 0.11467 | 0.51467 | -13.8 | -13.7839 | 1.1551 | 0.0004875
2015-02-14 11:00 | 0.94667 | 0.87667 | 0.07 | 0 | -13.3062 | -2.8476 | 90.2884 | -0.28844 | -2.7711 | 30.4033 | 0 | 0.6575 | 0.8 | 1 | 0.18933 | 0.84683 | -13.6 | -13.5735 | 1.1543 | 0.00080155
2015-02-14 12:00 | 1.32 | 1.22 | 0.1 | 0 | -13.2922 | 12.1524 | 90.5406 | -0.54063 | 11.8226 | 32.5525 | 0 | 0.915 | 0.8 | 1 | 0.264 | 1.179 | -10.4 | -10.3632 | 1.1415 | 0.0011035
2015-02-14 13:00 | 0.88 | 0.81333 | 0.066667 | 0 | -13.2781 | 27.1524 | 91.6309 | -1.6309 | 26.3811 | 40.4218 | 0 | 0.61 | 0.8 | 1 | 0.176 | 0.786 | -10.6 | -10.5754 | 1.1423 | 0.00073624
2015-02-14 14:00 | 0.44 | 0.40667 | 0.033333 | 0 | -13.264 | 42.1524 | 93.4856 | -3.4856 | 40.8752 | 51.448 | 0 | 0.305 | 0.8 | 1 | 0.088 | 0.393 | -10.7 | -10.6877 | 1.1428 | 0.00036826
2015-02-14 15:00 | 0 | 0 | 0 | 0 | -13.2499 | 57.1525 | 95.9827 | -5.9827 | 55.3088 | 64.0171 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.2 | -10.2 | 1.1408 | 0
2015-02-14 16:00 | 0 | 0 | 0 | 0 | -13.2358 | 72.1525 | 98.962 | -8.962 | 69.7252 | 77.3764 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.9 | -10.9 | 1.1436 | 0
2015-02-14 17:00 | 0 | 0 | 0 | 0 | -13.2217 | 87.1525 | 102.2349 | -12.2349 | 84.2039 | 91.1739 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.9 | -10.9 | 1.1436 | 0
2015-02-14 18:00 | 0 | 0 | 0 | 0 | -13.2075 | 102.1525 | 105.5936 | -15.5936 | 98.8473 | 105.2303 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.5 | -10.5 | 1.142 | 0
2015-02-14 19:00 | 0 | 0 | 0 | 0 | -13.1934 | 117.1526 | 108.8178 | -18.8178 | 113.7618 | 119.4445 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.5 | -10.5 | 1.142 | 0
2015-02-14 20:00 | 0 | 0 | 0 | 0 | -13.1793 | 132.1526 | 111.6839 | -21.6839 | 129.0312 | 133.7509 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10 | -10 | 1.14 | 0
2015-02-14 21:00 | 0 | 0 | 0 | 0 | -13.1652 | 147.1527 | 113.9772 | -23.9772 | 144.6881 | 148.0918 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.9 | -9.9 | 1.1396 | 0
2015-02-14 22:00 | 0 | 0 | 0 | 0 | -13.151 | 162.1527 | 115.5115 | -25.5115 | 160.6896 | 162.3567 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.5 | -9.5 | 1.138 | 0
2015-02-14 23:00 | 0 | 0 | 0 | 0 | -13.1369 | 177.1528 | 116.1529 | -26.1529 | 176.9108 | 175.2858 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.9 | -9.9 | 1.1396 | 0
2015-02-15 | 0 | 0 | 0 | 0 | -13.1227 | -167.8472 | 115.8423 | -25.8423 | -166.8322 | 167.6542 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.5 | -10.5 | 1.142 | 0
2015-02-15 01:00 | 0 | 0 | 0 | 0 | -13.1085 | -152.8471 | 114.6068 | -24.6068 | -150.7336 | 153.5173 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.5 | -10.5 | 1.142 | 0
2015-02-15 02:00 | 0 | 0 | 0 | 0 | -13.0944 | -137.847 | 112.5544 | -22.5544 | -134.944 | 139.1796 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.1 | -10.1 | 1.1404 | 0
2015-02-15 03:00 | 0 | 0 | 0 | 0 | -13.0802 | -122.8469 | 109.8544 | -19.8544 | -119.5366 | 124.8458 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.3 | -10.3 | 1.1412 | 0
2015-02-15 04:00 | 0 | 0 | 0 | 0 | -13.066 | -107.8469 | 106.7129 | -16.7129 | -104.5038 | 110.5801 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.4 | -8.4 | 1.1336 | 0
2015-02-15 05:00 | 0 | 0 | 0 | 0 | -13.0518 | -92.8468 | 103.3516 | -13.3516 | -89.7766 | 96.4408 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.1 | -8.1 | 1.1324 | 0
2015-02-15 06:00 | 0 | 0 | 0 | 0 | -13.0376 | -77.8467 | 99.9929 | -9.9929 | -75.2528 | 82.5105 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.4 | -7.4 | 1.1296 | 0
2015-02-15 07:00 | 0.15 | 0.15 | 0 | 0 | -13.0234 | -62.8466 | 96.85 | -6.85 | -60.8248 | 68.9291 | 0 | 0.1125 | 0.8 | 1 | 0.03 | 0.1425 | -7.5 | -7.4955 | 1.13 | 0.00013204
2015-02-15 08:00 | 0.3 | 0.3 | 0 | 0 | -13.0092 | -47.8465 | 94.1199 | -4.1199 | -46.4017 | 55.9619 | 0 | 0.225 | 0.8 | 1 | 0.06 | 0.285 | -7.3 | -7.2911 | 1.1292 | 0.00026389
2015-02-15 09:00 | 0.45 | 0.45 | 0 | 0 | -12.995 | -32.8463 | 91.9749 | -1.9749 | -31.9252 | 44.1629 | 0 | 0.3375 | 0.8 | 1 | 0.09 | 0.4275 | -7.2 | -7.1866 | 1.1287 | 0.00039568
2015-02-15 10:00 | 0.97 | 0.97 | 0 | 0 | -12.9808 | -17.8462 | 90.5533 | -0.55332 | -17.3763 | 34.7511 | 0 | 0.7275 | 0.8 | 1 | 0.194 | 0.9215 | -7.1 | -7.0712 | 1.1283 | 0.00085257
2015-02-15 11:00 | 1.49 | 1.49 | 0 | 0 | -12.9666 | -2.8461 | 89.9488 | 0.051233 | -2.7735 | 30.065 | 0 | 1.1175 | 0.8 | 1 | 0.298 | 1.4155 | -6.6 | -6.5558 | 1.1262 | 0.0013072
2015-02-15 12:00 | 2.01 | 2.01 | 0 | 0 | -12.9523 | 12.154 | 90.2013 | -0.20126 | 11.8403 | 32.2382 | 0 | 1.5075 | 0.8 | 1 | 0.402 | 1.9095 | -4.8 | -4.7403 | 1.119 | 0.0017521
2015-02-15 13:00 | 1.34 | 1.34 | 0 | 0 | -12.9381 | 27.1542 | 91.2929 | -1.2929 | 26.4178 | 40.1721 | 0 | 1.005 | 0.8 | 1 | 0.268 | 1.273 | -3.2 | -3.1602 | 1.1126 | 0.0011614
2015-02-15 14:00 | 0.67 | 0.67 | 0 | 0 | -12.9239 | 42.1543 | 93.1497 | -3.1497 | 40.9286 | 51.2558 | 0 | 0.5025 | 0.8 | 1 | 0.134 | 0.6365 | -2 | -1.9801 | 1.1079 | 0.00057826
2015-02-15 15:00 | 0 | 0 | 0 | 0 | -12.9096 | 57.1545 | 95.649 | -5.649 | 55.3758 | 63.8667 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.1048 | 0
2015-02-15 16:00 | 0 | 0 | 0 | 0 | -12.8954 | 72.1546 | 98.6301 | -8.6301 | 69.8021 | 77.2561 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.9 | 2.9 | 1.0884 | 0
2015-02-15 17:00 | 0 | 0 | 0 | 0 | -12.8811 | 87.1548 | 101.904 | -11.904 | 84.2863 | 91.0756 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.6 | 2.6 | 1.0896 | 0
2015-02-15 18:00 | 0 | 0 | 0 | 0 | -12.8668 | 102.1549 | 105.2625 | -15.2625 | 98.9305 | 105.1483 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2 | 2 | 1.092 | 0
2015-02-15 19:00 | 0 | 0 | 0 | 0 | -12.8526 | 117.1551 | 108.4852 | -18.4852 | 113.8405 | 119.3742 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.4 | 1.4 | 1.0944 | 0
2015-02-15 20:00 | 0 | 0 | 0 | 0 | -12.8383 | 132.1553 | 111.3489 | -21.3489 | 129.0998 | 133.6875 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.9 | 1.9 | 1.0924 | 0
2015-02-15 21:00 | 0 | 0 | 0 | 0 | -12.824 | 147.1555 | 113.6395 | -23.6395 | 144.7409 | 148.0277 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.9 | 1.9 | 1.0924 | 0
2015-02-15 22:00 | 0 | 0 | 0 | 0 | -12.8097 | 162.1556 | 115.1714 | -25.1714 | 160.7216 | 162.2697 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.7 | 1.7 | 1.0932 | 0
2015-02-15 23:00 | 0 | 0 | 0 | 0 | -12.7954 | 177.1558 | 115.8115 | -25.8115 | 176.9189 | 175.0049 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.3 | 1.3 | 1.0948 | 0
2015-02-16 | 0 | 0 | 0 | 0 | -12.7811 | -167.844 | 115.501 | -25.501 | -166.8487 | 167.5323 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-02-16 01:00 | 0 | 0 | 0 | 0 | -12.7668 | -152.8438 | 114.2669 | -24.2669 | -150.7725 | 153.4423 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-02-16 02:00 | 0 | 0 | 0 | 0 | -12.7525 | -137.8436 | 112.2166 | -22.2166 | -135.0009 | 139.1106 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-02-16 03:00 | 0 | 0 | 0 | 0 | -12.7382 | -122.8434 | 109.5186 | -19.5186 | -119.606 | 124.7722 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-02-16 04:00 | 0 | 0 | 0 | 0 | -12.7238 | -107.8431 | 106.3786 | -16.3786 | -104.5801 | 110.4966 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-02-16 05:00 | 0 | 0 | 0 | 0 | -12.7095 | -92.8429 | 103.0177 | -13.0177 | -89.8542 | 96.3429 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-02-16 06:00 | 0 | 0 | 0 | 0 | -12.6952 | -77.8427 | 99.6582 | -9.6582 | -75.3267 | 82.3931 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.8 | 0.8 | 1.0968 | 0
2015-02-16 07:00 | 0.40667 | 0.40667 | 0 | 0 | -12.6808 | -62.8425 | 96.5137 | -6.5137 | -60.8905 | 68.7853 | 0 | 0.305 | 0.8 | 1 | 0.081333 | 0.38633 | 1.6 | 1.6121 | 1.0936 | 0.00034643
2015-02-16 08:00 | 0.81333 | 0.81333 | 0 | 0 | -12.6665 | -47.8422 | 93.7813 | -3.7813 | -46.4552 | 55.7815 | 0 | 0.61 | 0.8 | 1 | 0.16267 | 0.77267 | 1.8 | 1.8241 | 1.0927 | 0.00069232
2015-02-16 09:00 | 1.22 | 1.22 | 0 | 0 | -12.6521 | -32.842 | 91.634 | -1.634 | -31.9629 | 43.9314 | 0 | 0.915 | 0.8 | 1 | 0.244 | 1.159 | 1.9 | 1.9362 | 1.0923 | 0.0010381
2015-02-16 10:00 | 2.2267 | 2.15 | 0.076667 | 0 | -12.6377 | -17.8417 | 90.2108 | -0.21078 | -17.3956 | 34.455 | 0 | 1.6125 | 0.8 | 1 | 0.44533 | 2.0578 | 1.9 | 1.9643 | 1.0921 | 0.0018429
2015-02-16 11:00 | 3.2333 | 3.08 | 0.15333 | 0 | -12.6234 | -2.8415 | 89.6055 | 0.39446 | -2.7728 | 29.7229 | 0 | 2.31 | 0.8 | 1 | 0.64667 | 2.9567 | 1.7 | 1.7924 | 1.0928 | 0.0026495
2015-02-16 12:00 | 4.24 | 4.01 | 0.23 | 0 | -12.609 | 12.1588 | 89.8585 | 0.14147 | 11.8613 | 31.9223 | 0 | 3.0075 | 0.8 | 1 | 0.848 | 3.8555 | 1.5 | 1.6205 | 1.0935 | 0.0034572
2015-02-16 13:00 | 2.8267 | 2.6733 | 0.15333 | 0 | -12.5946 | 27.1591 | 90.9517 | -0.9517 | 26.4579 | 39.923 | 0 | 2.005 | 0.8 | 1 | 0.56533 | 2.5703 | 1.2 | 1.2803 | 1.0949 | 0.0023076
2015-02-16 14:00 | 1.4133 | 1.3367 | 0.076667 | 0 | -12.5802 | 42.1593 | 92.8107 | -2.8107 | 40.9856 | 51.0652 | 0 | 1.0025 | 0.8 | 1 | 0.28267 | 1.2852 | 2.3 | 2.3402 | 1.0906 | 0.0011494
2015-02-16 15:00 | 0 | 0 | 0 | 0 | -12.5658 | 57.1596 | 95.3125 | -5.3125 | 55.4465 | 63.7183 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.1 | 2.1 | 1.0916 | 0
2015-02-16 16:00 | 0 | 0 | 0 | 0 | -12.5514 | 72.1599 | 98.2955 | -8.2955 | 69.8827 | 77.1377 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2 | 2 | 1.092 | 0
2015-02-16 17:00 | 0 | 0 | 0 | 0 | -12.537 | 87.1602 | 101.5704 | -11.5704 | 84.3724 | 90.9791 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.3 | 2.3 | 1.0908 | 0
2015-02-16 18:00 | 0 | 0 | 0 | 0 | -12.5226 | 102.1605 | 104.9286 | -14.9286 | 99.0174 | 105.0678 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-02-16 19:00 | 0 | 0 | 0 | 0 | -12.5082 | 117.1608 | 108.1498 | -18.1498 | 113.9229 | 119.305 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-02-16 20:00 | 0 | 0 | 0 | 0 | -12.4938 | 132.1611 | 111.011 | -21.011 | 129.172 | 133.6245 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-02-16 21:00 | 0 | 0 | 0 | 0 | -12.4794 | 147.1614 | 113.2987 | -23.2987 | 144.7973 | 147.9626 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-02-16 22:00 | 0 | 0 | 0 | 0 | -12.4649 | 162.1617 | 114.8281 | -24.8281 | 160.7572 | 162.1788 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-02-16 23:00 | 0 | 0 | 0 | 0 | -12.4505 | 177.162 | 115.4667 | -25.4667 | 176.9303 | 174.7155 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-02-17 | 0 | 0 | 0 | 0 | -12.436 | -167.8376 | 115.1561 | -25.1561 | -166.862 | 167.3983 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-02-17 01:00 | 0 | 0 | 0 | 0 | -12.4216 | -152.8373 | 113.9232 | -23.9232 | -150.8083 | 153.3597 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.5 | -0.5 | 1.102 | 0
2015-02-17 02:00 | 0 | 0 | 0 | 0 | -12.4071 | -137.837 | 111.8748 | -21.8748 | -135.0549 | 139.0355 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-02-17 03:00 | 0 | 0 | 0 | 0 | -12.3927 | -122.8366 | 109.1789 | -19.1789 | -119.6728 | 124.6935 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-02-17 04:00 | 0 | 0 | 0 | 0 | -12.3782 | -107.8363 | 106.0402 | -16.0402 | -104.6537 | 110.4085 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-02-17 05:00 | 0 | 0 | 0 | 0 | -12.3637 | -92.8359 | 102.6797 | -12.6797 | -89.9293 | 96.2408 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-02-17 06:00 | 0 | 0 | 0 | 0 | -12.3492 | -77.8356 | 99.3195 | -9.3195 | -75.3983 | 82.2719 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-02-17 07:00 | 0.69333 | 0.6 | 0.093333 | 0 | -12.3348 | -62.8352 | 96.1733 | -6.1733 | -60.9539 | 68.6379 | 0 | 0.45 | 0.8 | 1 | 0.13867 | 0.58867 | 0.5 | 0.5184 | 1.0979 | 0.00052998
2015-02-17 08:00 | 1.3867 | 1.2 | 0.18667 | 0 | -12.3203 | -47.8348 | 93.4388 | -3.4388 | -46.5062 | 55.5977 | 0 | 0.9 | 0.8 | 1 | 0.27733 | 1.1773 | 0.9 | 0.93679 | 1.0963 | 0.0010583
2015-02-17 09:00 | 2.08 | 1.8 | 0.28 | 0 | -12.3058 | -32.8345 | 91.2894 | -1.2894 | -31.998 | 43.6965 | 0 | 1.35 | 0.8 | 1 | 0.416 | 1.766 | 0.1 | 0.15519 | 1.0994 | 0.001592
2015-02-17 10:00 | 3.0033 | 2.6567 | 0.34667 | 0 | -12.2913 | -17.8341 | 89.8646 | 0.13538 | -17.4121 | 34.1551 | 0 | 1.9925 | 0.8 | 1 | 0.60067 | 2.5932 | 0.5 | 0.58104 | 1.0977 | 0.0023341
2015-02-17 11:00 | 3.9267 | 3.5133 | 0.41333 | 0 | -12.2768 | -2.8337 | 89.2589 | 0.74113 | -2.7691 | 29.3772 | 0 | 2.635 | 0.8 | 1 | 0.78533 | 3.4203 | -1 | -0.89311 | 1.1036 | 0.0030952
2015-02-17 12:00 | 4.85 | 4.37 | 0.48 | 0 | -12.2622 | 12.1667 | 89.5125 | 0.48746 | 11.8854 | 31.6049 | 0 | 3.2775 | 0.8 | 1 | 0.97 | 4.2475 | 0.2 | 0.33273 | 1.0987 | 0.0038266
2015-02-17 13:00 | 3.2333 | 2.9133 | 0.32 | 0 | -12.2477 | 27.1671 | 90.6075 | -0.60747 | 26.5014 | 39.6747 | 0 | 2.185 | 0.8 | 1 | 0.64667 | 2.8317 | -0.7 | -0.61151 | 1.1024 | 0.0025598
2015-02-17 14:00 | 1.6167 | 1.4567 | 0.16 | 0 | -12.2332 | 42.1675 | 92.4689 | -2.4689 | 41.0461 | 50.8764 | 0 | 1.0925 | 0.8 | 1 | 0.32333 | 1.4158 | -0.3 | -0.25576 | 1.101 | 0.0012783
2015-02-17 15:00 | 0 | 0 | 0 | 0 | -12.2187 | 57.1679 | 94.9732 | -4.9732 | 55.5208 | 63.572 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-02-17 16:00 | 0 | 0 | 0 | 0 | -12.2041 | 72.1683 | 97.9583 | -7.9583 | 69.9668 | 77.0215 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-02-17 17:00 | 0 | 0 | 0 | 0 | -12.1896 | 87.1687 | 101.2342 | -11.2342 | 84.4621 | 90.8845 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-02-17 18:00 | 0 | 0 | 0 | 0 | -12.175 | 102.1691 | 104.5921 | -14.5921 | 99.1078 | 104.9889 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-02-17 19:00 | 0 | 0 | 0 | 0 | -12.1605 | 117.1696 | 107.8118 | -17.8118 | 114.0089 | 119.2369 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-02-17 20:00 | 0 | 0 | 0 | 0 | -12.1459 | 132.17 | 110.6703 | -20.6703 | 129.2478 | 133.5619 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.7 | -4.7 | 1.1188 | 0
2015-02-17 21:00 | 0 | 0 | 0 | 0 | -12.1314 | 147.1704 | 112.955 | -22.955 | 144.8571 | 147.8967 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.7 | -5.7 | 1.1228 | 0
2015-02-17 22:00 | 0 | 0 | 0 | 0 | -12.1168 | 162.1709 | 114.4817 | -24.4817 | 160.7961 | 162.0838 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-02-17 23:00 | 0 | 0 | 0 | 0 | -12.1022 | 177.1713 | 115.1185 | -25.1185 | 176.9451 | 174.4184 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.1 | -4.1 | 1.1164 | 0
2015-02-18 | 0 | 0 | 0 | 0 | -12.0876 | -167.8282 | 114.8077 | -24.8077 | -166.872 | 167.2524 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.8 | -2.8 | 1.1112 | 0
2015-02-18 01:00 | 0 | 0 | 0 | 0 | -12.073 | -152.8277 | 113.5758 | -23.5758 | -150.841 | 153.2693 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-02-18 02:00 | 0 | 0 | 0 | 0 | -12.0585 | -137.8273 | 111.5293 | -21.5293 | -135.106 | 138.9545 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.1048 | 0
2015-02-18 03:00 | 0 | 0 | 0 | 0 | -12.0439 | -122.8268 | 108.8352 | -18.8352 | -119.7367 | 124.6097 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-02-18 04:00 | 0 | 0 | 0 | 0 | -12.0293 | -107.8263 | 105.6979 | -15.6979 | -104.7249 | 110.3159 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-02-18 05:00 | 0 | 0 | 0 | 0 | -12.0146 | -92.8259 | 102.3377 | -12.3377 | -90.002 | 96.1347 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-02-18 06:00 | 0 | 0 | 0 | 0 | -12 | -77.8254 | 98.9769 | -8.9769 | -75.4674 | 82.1469 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-02-18 07:00 | 1.01 | 0.83 | 0.18 | 0 | -11.9854 | -62.8249 | 95.8291 | -5.8291 | -61.0148 | 68.4871 | 0 | 0.6225 | 0.8 | 1 | 0.202 | 0.8245 | -1 | -0.97423 | 1.1039 | 0.00074633
2015-02-18 08:00 | 2.02 | 1.66 | 0.36 | 0 | -11.9708 | -47.8244 | 93.0925 | -3.0925 | -46.5547 | 55.4106 | 0 | 1.245 | 0.8 | 1 | 0.404 | 1.649 | -1.5 | -1.4485 | 1.1058 | 0.0014952
2015-02-18 09:00 | 3.03 | 2.49 | 0.54 | 0 | -11.9561 | -32.8239 | 90.9412 | -0.94116 | -32.0305 | 43.4583 | 0 | 1.8675 | 0.8 | 1 | 0.606 | 2.4735 | -1.7 | -1.6227 | 1.1065 | 0.0022443
2015-02-18 10:00 | 4.6867 | 3.99 | 0.69667 | 0 | -11.9415 | -17.8234 | 89.515 | 0.48502 | -17.4258 | 33.8517 | 0 | 2.9925 | 0.8 | 1 | 0.93733 | 3.9298 | -1.6 | -1.4772 | 1.1059 | 0.0035638
2015-02-18 11:00 | 6.3433 | 5.49 | 0.85333 | 0 | -11.9269 | -2.8229 | 88.9089 | 1.0911 | -2.7624 | 29.0279 | 0 | 4.1175 | 0.8 | 1 | 1.2687 | 5.3862 | -1.9 | -1.7317 | 1.1069 | 0.0048889
2015-02-18 12:00 | 8 | 6.99 | 1.01 | 0 | -11.9122 | 12.1777 | 89.1634 | 0.83658 | 11.9128 | 31.2862 | 0 | 5.2425 | 0.8 | 1 | 1.6 | 6.8425 | -2.8 | -2.5862 | 1.1103 | 0.00623
2015-02-18 13:00 | 5.3333 | 4.66 | 0.67333 | 0 | -11.8976 | 27.1782 | 90.2603 | -0.26029 | 26.5483 | 39.4273 | 0 | 3.495 | 0.8 | 1 | 1.0667 | 4.5617 | -2.9 | -2.7574 | 1.111 | 0.0041559
2015-02-18 14:00 | 2.6667 | 2.33 | 0.33667 | 0 | -11.8829 | 42.1787 | 92.1243 | -2.1243 | 41.1101 | 50.6896 | 0 | 1.7475 | 0.8 | 1 | 0.53333 | 2.2808 | -3.2 | -3.1287 | 1.1125 | 0.0020807
2015-02-18 15:00 | 0 | 0 | 0 | 0 | -11.8682 | 57.1793 | 94.6313 | -4.6313 | 55.5986 | 63.4279 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-02-18 16:00 | 0 | 0 | 0 | 0 | -11.8536 | 72.1798 | 97.6185 | -7.6185 | 70.0546 | 76.9073 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.7 | -5.7 | 1.1228 | 0
2015-02-18 17:00 | 0 | 0 | 0 | 0 | -11.8389 | 87.1803 | 100.8955 | -10.8955 | 84.5554 | 90.7918 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6 | -6 | 1.124 | 0
2015-02-18 18:00 | 0 | 0 | 0 | 0 | -11.8242 | 102.1809 | 104.2531 | -14.2531 | 99.2019 | 104.9116 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.5 | -6.5 | 1.126 | 0
2015-02-18 19:00 | 0 | 0 | 0 | 0 | -11.8095 | 117.1815 | 107.4711 | -17.4711 | 114.0983 | 119.1699 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.7 | -6.7 | 1.1268 | 0
2015-02-18 20:00 | 0 | 0 | 0 | 0 | -11.7948 | 132.182 | 110.327 | -20.327 | 129.327 | 133.4996 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.3 | -7.3 | 1.1292 | 0
2015-02-18 21:00 | 0 | 0 | 0 | 0 | -11.7801 | 147.1826 | 112.6084 | -22.6084 | 144.9204 | 147.8297 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.6 | -7.6 | 1.1304 | 0
2015-02-18 22:00 | 0 | 0 | 0 | 0 | -11.7654 | 162.1832 | 114.1322 | -24.1322 | 160.8384 | 161.9846 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.1 | -8.1 | 1.1324 | 0
2015-02-18 23:00 | 0 | 0 | 0 | 0 | -11.7507 | 177.1837 | 114.7672 | -24.7672 | 176.9632 | 174.1141 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.4 | -8.4 | 1.1336 | 0
2015-02-19 | 0 | 0 | 0 | 0 | -11.736 | -167.8157 | 114.4559 | -24.4559 | -166.8787 | 167.0947 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.4 | -8.4 | 1.1336 | 0
2015-02-19 01:00 | 0 | 0 | 0 | 0 | -11.7213 | -152.8151 | 113.2249 | -23.2249 | -150.8706 | 153.1714 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.8 | -8.8 | 1.1352 | 0
2015-02-19 02:00 | 0 | 0 | 0 | 0 | -11.7066 | -137.8145 | 111.1801 | -21.1801 | -135.1542 | 138.8675 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.2 | -9.2 | 1.1368 | 0
2015-02-19 03:00 | 0 | 0 | 0 | 0 | -11.6918 | -122.8139 | 108.4878 | -18.4878 | -119.798 | 124.5209 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.7 | -9.7 | 1.1388 | 0
2015-02-19 04:00 | 0 | 0 | 0 | 0 | -11.6771 | -107.8133 | 105.3517 | -15.3517 | -104.7934 | 110.2189 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.8 | -9.8 | 1.1392 | 0
2015-02-19 05:00 | 0 | 0 | 0 | 0 | -11.6624 | -92.8127 | 101.992 | -11.992 | -90.0722 | 96.0246 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.1 | -10.1 | 1.1404 | 0
2015-02-19 06:00 | 0 | 0 | 0 | 0 | -11.6476 | -77.8121 | 98.6304 | -8.6304 | -75.5341 | 82.0183 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.8 | -9.8 | 1.1392 | 0
2015-02-19 07:00 | 1.4033 | 1.2433 | 0.16 | 0 | -11.6329 | -62.8115 | 95.4812 | -5.4812 | -61.0733 | 68.3328 | 0 | 0.9325 | 0.8 | 1 | 0.28067 | 1.2132 | -10.1 | -10.0621 | 1.1402 | 0.0011343
2015-02-19 08:00 | 2.8067 | 2.4867 | 0.32 | 0 | -11.6181 | -47.8108 | 92.7426 | -2.7426 | -46.6007 | 55.2204 | 0 | 1.865 | 0.8 | 1 | 0.56133 | 2.4263 | -10.1 | -10.0242 | 1.1401 | 0.0022683
2015-02-19 09:00 | 4.21 | 3.73 | 0.48 | 0 | -11.6034 | -32.8102 | 90.5894 | -0.58937 | -32.0604 | 43.217 | 0 | 2.7975 | 0.8 | 1 | 0.842 | 3.6395 | -10.4 | -10.2863 | 1.1411 | 0.0034056
2015-02-19 10:00 | 6.24 | 5.5667 | 0.67333 | 0 | -11.5886 | -17.8096 | 89.162 | 0.83804 | -17.4367 | 33.5447 | 0 | 4.175 | 0.8 | 1 | 1.248 | 5.423 | -10.5 | -10.3305 | 1.1413 | 0.0050753
2015-02-19 11:00 | 8.27 | 7.4033 | 0.86667 | 0 | -11.5738 | -2.8089 | 88.5557 | 1.4443 | -2.7526 | 28.6752 | 0 | 5.5525 | 0.8 | 1 | 1.654 | 7.2065 | -10.9 | -10.6748 | 1.1427 | 0.0067526
2015-02-19 12:00 | 10.3 | 9.24 | 1.06 | 0 | -11.559 | 12.1917 | 88.8113 | 1.1887 | 11.9434 | 30.9665 | 0 | 6.93 | 0.8 | 1 | 2.06 | 8.99 | -11.1 | -10.8191 | 1.1433 | 0.008428
2015-02-19 13:00 | 6.87 | 6.1633 | 0.70667 | 0 | -11.5443 | 27.1924 | 89.9103 | 0.089716 | 26.5985 | 39.1811 | 0 | 4.6225 | 0.8 | 1 | 1.374 | 5.9965 | -11.5 | -11.3126 | 1.1453 | 0.0056313
2015-02-19 14:00 | 3.44 | 3.0867 | 0.35333 | 0 | -11.5295 | 42.193 | 91.7771 | -1.7771 | 41.1776 | 50.5047 | 0 | 2.315 | 0.8 | 1 | 0.688 | 3.003 | -11.2 | -11.1062 | 1.1444 | 0.0028181
2015-02-19 15:00 | 0.01 | 0.01 | 0 | 0 | -11.5147 | 57.1937 | 94.2868 | -4.2868 | 55.68 | 63.286 | 0 | 0.0075 | 0.8 | 1 | 0.002 | 0.0095 | -11.4 | -11.3997 | 1.1456 | 8.9242e-06
2015-02-19 16:00 | 0.0066667 | 0.0066667 | 0 | 0 | -11.4999 | 72.1944 | 97.2762 | -7.2762 | 70.1459 | 76.7953 | 0 | 0.005 | 0.8 | 1 | 0.0013333 | 0.0063333 | -11.4 | -11.3998 | 1.1456 | 5.9495e-06
2015-02-19 17:00 | 0.0033333 | 0.0033333 | 0 | 0 | -11.4851 | 87.195 | 100.5543 | -10.5543 | 84.6522 | 90.701 | 0 | 0.0025 | 0.8 | 1 | 0.00066667 | 0.0031667 | -11.2 | -11.1999 | 1.1448 | 2.9727e-06
2015-02-19 18:00 | 0 | 0 | 0 | 0 | -11.4703 | 102.1957 | 103.9117 | -13.9117 | 99.2993 | 104.8359 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.6 | -11.6 | 1.1464 | 0
2015-02-19 19:00 | 0 | 0 | 0 | 0 | -11.4554 | 117.1964 | 107.128 | -17.128 | 114.1912 | 119.104 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.7 | -11.7 | 1.1468 | 0
2015-02-19 20:00 | 0 | 0 | 0 | 0 | -11.4406 | 132.1971 | 109.981 | -19.981 | 129.4096 | 133.4377 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.7 | -11.7 | 1.1468 | 0
2015-02-19 21:00 | 0 | 0 | 0 | 0 | -11.4258 | 147.1978 | 112.2592 | -22.2592 | 144.987 | 147.7616 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.8 | -11.8 | 1.1472 | 0
2015-02-19 22:00 | 0 | 0 | 0 | 0 | -11.411 | 162.1985 | 113.7799 | -23.7799 | 160.8841 | 161.881 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.7 | -12.7 | 1.1508 | 0
2015-02-19 23:00 | 0 | 0 | 0 | 0 | -11.3961 | 177.1992 | 114.4128 | -24.4128 | 176.9846 | 173.8034 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.5 | -12.5 | 1.15 | 0
2015-02-20 | 0 | 0 | 0 | 0 | -11.3813 | -167.8001 | 114.1009 | -24.1009 | -166.8824 | 166.9254 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.1 | -13.1 | 1.1524 | 0
2015-02-20 01:00 | 0 | 0 | 0 | 0 | -11.3664 | -152.7994 | 112.8706 | -22.8706 | -150.8972 | 153.0657 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.9 | -13.9 | 1.1556 | 0
2015-02-20 02:00 | 0 | 0 | 0 | 0 | -11.3516 | -137.7987 | 110.8273 | -20.8273 | -135.1995 | 138.7746 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.3 | -14.3 | 1.1572 | 0
2015-02-20 03:00 | 0 | 0 | 0 | 0 | -11.3367 | -122.798 | 108.1367 | -18.1367 | -119.8566 | 124.427 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.9 | -14.9 | 1.1596 | 0
2015-02-20 04:00 | 0 | 0 | 0 | 0 | -11.3219 | -107.7972 | 105.0019 | -15.0019 | -104.8594 | 110.1175 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.1 | -14.1 | 1.1564 | 0
2015-02-20 05:00 | 0 | 0 | 0 | 0 | -11.307 | -92.7965 | 101.6425 | -11.6425 | -90.14 | 95.9105 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.5 | -13.5 | 1.154 | 0
2015-02-20 06:00 | 0 | 0 | 0 | 0 | -11.2921 | -77.7958 | 98.2803 | -8.2803 | -75.5984 | 81.8861 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.5 | -13.5 | 1.154 | 0
2015-02-20 07:00 | 1.8433 | 1.75 | 0.093333 | 0 | -11.2773 | -62.795 | 95.1296 | -5.1296 | -61.1294 | 68.1753 | 0 | 1.3125 | 0.8 | 1 | 0.36867 | 1.6812 | -13.6 | -13.5475 | 1.1542 | 0.0015911
2015-02-20 08:00 | 3.6867 | 3.5 | 0.18667 | 0 | -11.2624 | -47.7943 | 92.3892 | -2.3892 | -46.6443 | 55.0271 | 0 | 2.625 | 0.8 | 1 | 0.73733 | 3.3623 | -13.7 | -13.5949 | 1.1544 | 0.0031828
2015-02-20 09:00 | 5.53 | 5.25 | 0.28 | 0 | -11.2475 | -32.7935 | 90.2342 | -0.23418 | -32.0876 | 42.9727 | 0 | 3.9375 | 0.8 | 1 | 1.106 | 5.0435 | -13.7 | -13.5424 | 1.1542 | 0.0047733
2015-02-20 10:00 | 7.9567 | 7.3667 | 0.59 | 0 | -11.2326 | -17.7927 | 88.8057 | 1.1943 | -17.4448 | 33.2344 | 0 | 5.525 | 0.8 | 1 | 1.5913 | 7.1163 | -13.7 | -13.4776 | 1.1539 | 0.0067335
2015-02-20 11:00 | 10.3833 | 9.4833 | 0.9 | 0 | -11.2177 | -2.792 | 88.1994 | 1.8006 | -2.74 | 28.3192 | 0 | 7.1125 | 0.8 | 1 | 2.0767 | 9.1892 | -13.6 | -13.3128 | 1.1533 | 0.0086899
2015-02-20 12:00 | 12.81 | 11.6 | 1.21 | 0 | -11.2028 | 12.2088 | 88.4563 | 1.5437 | 11.9771 | 30.6458 | 0 | 8.7 | 0.8 | 1 | 2.562 | 11.262 | -14.6 | -14.2481 | 1.157 | 0.010685
2015-02-20 13:00 | 8.5533 | 7.7467 | 0.80667 | 0 | -11.1879 | 27.2096 | 89.5576 | 0.44243 | 26.652 | 38.9362 | 0 | 5.81 | 0.8 | 1 | 1.7107 | 7.5207 | -15 | -14.765 | 1.1591 | 0.0071479
2015-02-20 14:00 | 4.2967 | 3.8933 | 0.40333 | 0 | -11.173 | 42.2103 | 91.4273 | -1.4273 | 41.2484 | 50.322 | 0 | 2.92 | 0.8 | 1 | 0.85933 | 3.7793 | -15.3 | -15.1819 | 1.1607 | 0.0035972
2015-02-20 15:00 | 0.04 | 0.04 | 0 | 0 | -11.1581 | 57.2111 | 93.94 | -3.94 | 55.7647 | 63.1464 | 0 | 0.03 | 0.8 | 1 | 0.008 | 0.038 | -15.3 | -15.2988 | 1.1612 | 3.6183e-05
2015-02-20 16:00 | 0.026667 | 0.026667 | 0 | 0 | -11.1431 | 72.2119 | 96.9317 | -6.9317 | 70.2406 | 76.6856 | 0 | 0.02 | 0.8 | 1 | 0.0053333 | 0.025333 | -15.2 | -15.1992 | 1.1608 | 2.4114e-05
2015-02-20 17:00 | 0.013333 | 0.013333 | 0 | 0 | -11.1282 | 87.2127 | 100.211 | -10.211 | 84.7524 | 90.6122 | 0 | 0.01 | 0.8 | 1 | 0.0026667 | 0.012667 | -15.8 | -15.7996 | 1.1632 | 1.2082e-05
2015-02-20 18:00 | 0 | 0 | 0 | 0 | -11.1133 | 102.2135 | 103.568 | -13.568 | 99.4003 | 104.7618 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.8 | -16.8 | 1.1672 | 0
2015-02-20 19:00 | 0 | 0 | 0 | 0 | -11.0983 | 117.2143 | 106.7825 | -16.7825 | 114.2875 | 119.0392 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.6 | -16.6 | 1.1664 | 0
2015-02-20 20:00 | 0 | 0 | 0 | 0 | -11.0834 | 132.2151 | 109.6327 | -19.6327 | 129.4956 | 133.3759 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.4 | -17.4 | 1.1696 | 0
2015-02-20 21:00 | 0 | 0 | 0 | 0 | -11.0685 | 147.216 | 111.9073 | -21.9073 | 145.057 | 147.6923 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17 | -17 | 1.168 | 0
2015-02-20 22:00 | 0 | 0 | 0 | 0 | -11.0535 | 162.2168 | 113.4248 | -23.4248 | 160.933 | 161.7732 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.7 | -17.7 | 1.1708 | 0
2015-02-20 23:00 | 0 | 0 | 0 | 0 | -11.0385 | 177.2176 | 114.0555 | -24.0555 | 177.0092 | 173.4867 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17 | -17 | 1.168 | 0
2015-02-21 | 0 | 0 | 0 | 0 | -11.0236 | -167.7816 | 113.7427 | -23.7427 | -166.8829 | 166.7449 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.8 | -15.8 | 1.1632 | 0
2015-02-21 01:00 | 0 | 0 | 0 | 0 | -11.0086 | -152.7807 | 112.5129 | -22.5129 | -150.9208 | 152.9525 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.1 | -15.1 | 1.1604 | 0
2015-02-21 02:00 | 0 | 0 | 0 | 0 | -10.9936 | -137.7799 | 110.4711 | -20.4711 | -135.242 | 138.6758 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.7 | -15.7 | 1.1628 | 0
2015-02-21 03:00 | 0 | 0 | 0 | 0 | -10.9787 | -122.779 | 107.7821 | -17.7821 | -119.9124 | 124.3282 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.8 | -16.8 | 1.1672 | 0
2015-02-21 04:00 | 0 | 0 | 0 | 0 | -10.9637 | -107.7782 | 104.6485 | -14.6485 | -104.9228 | 110.0117 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.9 | -16.9 | 1.1676 | 0
2015-02-21 05:00 | 0 | 0 | 0 | 0 | -10.9487 | -92.7773 | 101.2895 | -11.2895 | -90.2053 | 95.7925 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.8 | -15.8 | 1.1632 | 0
2015-02-21 06:00 | 0 | 0 | 0 | 0 | -10.9337 | -77.7764 | 97.9267 | -7.9267 | -75.6604 | 81.7504 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.9 | -16.9 | 1.1676 | 0
2015-02-21 07:00 | 2.38 | 2.1567 | 0.22333 | 0 | -10.9187 | -62.7756 | 94.7745 | -4.7745 | -61.183 | 68.0147 | 0 | 1.6175 | 0.8 | 1 | 0.476 | 2.0935 | -17.3 | -17.2346 | 1.1689 | 0.0020067
2015-02-21 08:00 | 4.76 | 4.3133 | 0.44667 | 0 | -10.9037 | -47.7747 | 92.0323 | -2.0323 | -46.6853 | 54.8308 | 0 | 3.235 | 0.8 | 1 | 0.952 | 4.187 | -16.7 | -16.5692 | 1.1663 | 0.0040042
2015-02-21 09:00 | 7.14 | 6.47 | 0.67 | 0 | -10.8887 | -32.7738 | 89.8757 | 0.12428 | -32.1122 | 42.7254 | 0 | 4.8525 | 0.8 | 1 | 1.428 | 6.2805 | -16.9 | -16.7037 | 1.1668 | 0.0060091
2015-02-21 10:00 | 10.0267 | 8.5667 | 1.46 | 0 | -10.8737 | -17.7729 | 88.4463 | 1.5537 | -17.4501 | 32.9208 | 0 | 6.425 | 0.8 | 1 | 2.0053 | 8.4303 | -16.1 | -15.8366 | 1.1633 | 0.0080421
2015-02-21 11:00 | 12.9133 | 10.6633 | 2.25 | 0 | -10.8587 | -2.772 | 87.8402 | 2.1598 | -2.7243 | 27.96 | 0 | 7.9975 | 0.8 | 1 | 2.5827 | 10.5802 | -17.1 | -16.7694 | 1.1671 | 0.010125
2015-02-21 12:00 | 15.8 | 12.76 | 3.04 | 0 | -10.8437 | 12.2288 | 88.0985 | 1.9015 | 12.0139 | 30.3243 | 0 | 9.57 | 0.8 | 1 | 3.16 | 12.73 | -16.4 | -16.0022 | 1.164 | 0.012151
2015-02-21 13:00 | 10.57 | 8.5433 | 2.0267 | 0 | -10.8286 | 27.2297 | 89.2023 | 0.79774 | 26.7088 | 38.6928 | 0 | 6.4075 | 0.8 | 1 | 2.114 | 8.5215 | -16.8 | -16.5337 | 1.1661 | 0.0081485
2015-02-21 14:00 | 5.34 | 4.3267 | 1.0133 | 0 | -10.8136 | 42.2307 | 91.0751 | -1.0751 | 41.3226 | 50.1416 | 0 | 3.245 | 0.8 | 1 | 1.068 | 4.313 | -17 | -16.8652 | 1.1675 | 0.0041289
2015-02-21 15:00 | 0.11 | 0.11 | 0 | 0 | -10.7986 | 57.2316 | 93.5909 | -3.5909 | 55.8529 | 63.0093 | 0 | 0.0825 | 0.8 | 1 | 0.022 | 0.1045 | -16.6 | -16.5967 | 1.1664 | 9.9948e-05
2015-02-21 16:00 | 0.073333 | 0.073333 | 0 | 0 | -10.7835 | 72.2325 | 96.5849 | -6.5849 | 70.3388 | 76.578 | 0 | 0.055 | 0.8 | 1 | 0.014667 | 0.069667 | -16.6 | -16.5978 | 1.1664 | 6.6632e-05
2015-02-21 17:00 | 0.036667 | 0.036667 | 0 | 0 | -10.7685 | 87.2334 | 99.8654 | -9.8654 | 84.8561 | 90.5254 | 0 | 0.0275 | 0.8 | 1 | 0.0073333 | 0.034833 | -15.5 | -15.4989 | 1.162 | 3.319e-05
2015-02-21 18:00 | 0 | 0 | 0 | 0 | -10.7534 | 102.2343 | 103.2221 | -13.2221 | 99.5045 | 104.6892 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.8 | -15.8 | 1.1632 | 0
2015-02-21 19:00 | 0 | 0 | 0 | 0 | -10.7384 | 117.2353 | 106.4348 | -16.4348 | 114.3871 | 118.9753 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.6 | -16.6 | 1.1664 | 0
2015-02-21 20:00 | 0 | 0 | 0 | 0 | -10.7233 | 132.2362 | 109.2819 | -19.2819 | 129.5848 | 133.3144 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.4 | -17.4 | 1.1696 | 0
2015-02-21 21:00 | 0 | 0 | 0 | 0 | -10.7082 | 147.2371 | 111.5529 | -21.5529 | 145.1301 | 147.6218 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.8 | -17.8 | 1.1712 | 0
2015-02-21 22:00 | 0 | 0 | 0 | 0 | -10.6932 | 162.2381 | 113.0671 | -23.0671 | 160.985 | 161.6608 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.6 | -16.6 | 1.1664 | 0
2015-02-21 23:00 | 0 | 0 | 0 | 0 | -10.6781 | 177.239 | 113.6953 | -23.6953 | 177.0369 | 173.1644 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.4 | -16.4 | 1.1656 | 0
2015-02-22 | 0 | 0 | 0 | 0 | -10.663 | -167.76 | 113.3815 | -23.3815 | -166.8803 | 166.5534 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.2 | -17.2 | 1.1688 | 0
2015-02-22 01:00 | 0 | 0 | 0 | 0 | -10.6479 | -152.7591 | 112.1521 | -22.1521 | -150.9414 | 152.8316 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.3 | -17.3 | 1.1692 | 0
2015-02-22 02:00 | 0 | 0 | 0 | 0 | -10.6328 | -137.7581 | 110.1115 | -20.1115 | -135.2816 | 138.5711 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.6 | -17.6 | 1.1704 | 0
2015-02-22 03:00 | 0 | 0 | 0 | 0 | -10.6178 | -122.7571 | 107.4242 | -17.4242 | -119.9657 | 124.2244 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18 | -18 | 1.172 | 0
2015-02-22 04:00 | 0 | 0 | 0 | 0 | -10.6027 | -107.7561 | 104.2917 | -14.2917 | -104.9837 | 109.9016 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.1 | -18.1 | 1.1724 | 0
2015-02-22 05:00 | 0 | 0 | 0 | 0 | -10.5876 | -92.7552 | 100.933 | -10.933 | -90.2682 | 95.6707 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.3 | -19.3 | 1.1772 | 0
2015-02-22 06:00 | 0 | 0 | 0 | 0 | -10.5724 | -77.7542 | 97.5696 | -7.5696 | -75.72 | 81.6113 | 0 | 0 | 0.8 | 1 | 0 | 0 | -19.7 | -19.7 | 1.1788 | 0
2015-02-22 07:00 | 3.05 | 2.4167 | 0.63333 | 0 | -10.5573 | -62.7532 | 94.4161 | -4.4161 | -61.2344 | 67.8509 | 0 | 1.8125 | 0.8 | 1 | 0.61 | 2.4225 | -18.8 | -18.7243 | 1.1749 | 0.0023339
2015-02-22 08:00 | 6.1 | 4.8333 | 1.2667 | 0 | -10.5422 | -47.7522 | 91.6722 | -1.6722 | -46.7239 | 54.6317 | 0 | 3.625 | 0.8 | 1 | 1.22 | 4.845 | -18.4 | -18.2486 | 1.173 | 0.0046602
2015-02-22 09:00 | 9.15 | 7.25 | 1.9 | 0 | -10.5271 | -32.7512 | 89.5141 | 0.48591 | -32.1343 | 42.4754 | 0 | 5.4375 | 0.8 | 1 | 1.83 | 7.2675 | -18.6 | -18.3729 | 1.1735 | 0.0069932
2015-02-22 10:00 | 12.44 | 9.7233 | 2.7167 | 0 | -10.512 | -17.7502 | 88.0839 | 1.9161 | -17.4527 | 32.6041 | 0 | 7.2925 | 0.8 | 1 | 2.488 | 9.7805 | -18.6 | -18.2944 | 1.1732 | 0.0094089
2015-02-22 11:00 | 15.73 | 12.1967 | 3.5333 | 0 | -10.4968 | -2.7492 | 87.4781 | 2.5219 | -2.7057 | 27.5977 | 0 | 9.1475 | 0.8 | 1 | 3.146 | 12.2935 | -19.5 | -19.1158 | 1.1765 | 0.01186
2015-02-22 12:00 | 19.02 | 14.67 | 4.35 | 0 | -10.4817 | 12.2518 | 87.738 | 2.262 | 12.0538 | 30.0023 | 0 | 11.0025 | 0.8 | 1 | 3.804 | 14.8065 | -19.2 | -18.7373 | 1.1749 | 0.014265
2015-02-22 13:00 | 12.8033 | 9.8767 | 2.9267 | 0 | -10.4666 | 27.2529 | 88.8445 | 1.1555 | 26.7688 | 38.451 | 0 | 7.4075 | 0.8 | 1 | 2.5607 | 9.9682 | -19.4 | -19.0885 | 1.1764 | 0.0096154
2015-02-22 14:00 | 6.5867 | 5.0833 | 1.5033 | 0 | -10.4514 | 42.2539 | 90.7206 | -0.72056 | 41.4001 | 49.9636 | 0 | 3.8125 | 0.8 | 1 | 1.3173 | 5.1298 | -19.4 | -19.2397 | 1.177 | 0.0049508
2015-02-22 15:00 | 0.37 | 0.29 | 0.08 | 0 | -10.4363 | 57.2549 | 93.2395 | -3.2395 | 55.9445 | 62.8745 | 0 | 0.2175 | 0.8 | 1 | 0.074 | 0.2915 | -18.5 | -18.4909 | 1.174 | 0.00028061
2015-02-22 16:00 | 0.24667 | 0.19333 | 0.053333 | 0 | -10.4211 | 72.256 | 96.2361 | -6.2361 | 70.4403 | 76.4727 | 0 | 0.145 | 0.8 | 1 | 0.049333 | 0.19433 | -18.2 | -18.1939 | 1.1728 | 0.00018689
2015-02-22 17:00 | 0.12333 | 0.096667 | 0.026667 | 0 | -10.4059 | 87.257 | 99.5178 | -9.5178 | 84.963 | 90.4405 | 0 | 0.0725 | 0.8 | 1 | 0.024667 | 0.097167 | -17.3 | -17.297 | 1.1692 | 9.3157e-05
2015-02-22 18:00 | 0 | 0 | 0 | 0 | -10.3908 | 102.2581 | 102.8741 | -12.8741 | 99.6121 | 104.6181 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.9 | -17.9 | 1.1716 | 0
2015-02-22 19:00 | 0 | 0 | 0 | 0 | -10.3756 | 117.2591 | 106.085 | -16.085 | 114.4899 | 118.9125 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.8 | -17.8 | 1.1712 | 0
2015-02-22 20:00 | 0 | 0 | 0 | 0 | -10.3604 | 132.2602 | 108.9289 | -18.9289 | 129.6772 | 133.2529 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18 | -18 | 1.172 | 0
2015-02-22 21:00 | 0 | 0 | 0 | 0 | -10.3453 | 147.2612 | 111.1962 | -21.1962 | 145.2064 | 147.5499 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.4 | -16.4 | 1.1656 | 0
2015-02-22 22:00 | 0 | 0 | 0 | 0 | -10.3301 | 162.2623 | 112.7068 | -22.7068 | 161.0402 | 161.5439 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.6 | -15.6 | 1.1624 | 0
2015-02-22 23:00 | 0 | 0 | 0 | 0 | -10.3149 | 177.2634 | 113.3324 | -23.3324 | 177.0676 | 172.837 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.6 | -15.6 | 1.1624 | 0
2015-02-23 | 0 | 0 | 0 | 0 | -10.2997 | -167.7356 | 113.0174 | -23.0174 | -166.8748 | 166.3512 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.5 | -15.5 | 1.162 | 0
2015-02-23 01:00 | 0 | 0 | 0 | 0 | -10.2845 | -152.7345 | 111.7883 | -21.7883 | -150.9592 | 152.7033 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.1 | -15.1 | 1.1604 | 0
2015-02-23 02:00 | 0 | 0 | 0 | 0 | -10.2693 | -137.7334 | 109.7488 | -19.7488 | -135.3185 | 138.4605 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15 | -15 | 1.16 | 0
2015-02-23 03:00 | 0 | 0 | 0 | 0 | -10.2541 | -122.7323 | 107.0629 | -17.0629 | -120.0162 | 124.1158 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.3 | -15.3 | 1.1612 | 0
2015-02-23 04:00 | 0 | 0 | 0 | 0 | -10.2389 | -107.7312 | 103.9315 | -13.9315 | -105.0421 | 109.7872 | 0 | 0 | 0.8 | 1 | 0 | 0 | -14.8 | -14.8 | 1.1592 | 0
2015-02-23 05:00 | 0 | 0 | 0 | 0 | -10.2237 | -92.7301 | 100.5731 | -10.5731 | -90.3287 | 95.5451 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.4 | -15.4 | 1.1616 | 0
2015-02-23 06:00 | 0 | 0 | 0 | 0 | -10.2085 | -77.729 | 97.2092 | -7.2092 | -75.7772 | 81.4688 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.9 | -16.9 | 1.1676 | 0
2015-02-23 07:00 | 3.49 | 3.1933 | 0.29667 | 0 | -10.1932 | -62.7279 | 94.0545 | -4.0545 | -61.2833 | 67.6841 | 0 | 2.395 | 0.8 | 1 | 0.698 | 3.093 | -16.2 | -16.1033 | 1.1644 | 0.0029533
2015-02-23 08:00 | 6.98 | 6.3867 | 0.59333 | 0 | -10.178 | -47.7268 | 91.309 | -1.309 | -46.7601 | 54.4299 | 0 | 4.79 | 0.8 | 1 | 1.396 | 6.186 | -16.1 | -15.9067 | 1.1636 | 0.0059025
2015-02-23 09:00 | 10.47 | 9.58 | 0.89 | 0 | -10.1628 | -32.7256 | 89.1494 | 0.85056 | -32.1538 | 42.2227 | 0 | 7.185 | 0.8 | 1 | 2.094 | 9.279 | -16.9 | -16.61 | 1.1664 | 0.0088752
2015-02-23 10:00 | 13.85 | 13.1033 | 0.74667 | 0 | -10.1475 | -17.7245 | 87.7186 | 2.2814 | -17.4526 | 32.2844 | 0 | 9.8275 | 0.8 | 1 | 2.77 | 12.5975 | -15.6 | -15.2063 | 1.1608 | 0.011991
2015-02-23 11:00 | 17.23 | 16.6267 | 0.60333 | 0 | -10.1323 | -2.7234 | 87.1134 | 2.8866 | -2.6843 | 27.2324 | 0 | 12.47 | 0.8 | 1 | 3.446 | 15.916 | -15.3 | -14.8026 | 1.1592 | 0.015129
2015-02-23 12:00 | 20.61 | 20.15 | 0.46 | 0 | -10.1171 | 12.2777 | 87.375 | 2.625 | 12.0968 | 29.6798 | 0 | 15.1125 | 0.8 | 1 | 4.122 | 19.2345 | -14.6 | -13.9989 | 1.156 | 0.018233
2015-02-23 13:00 | 13.96 | 13.6433 | 0.31667 | 0 | -10.1018 | 27.2789 | 88.4843 | 1.5157 | 26.8319 | 38.2109 | 0 | 10.2325 | 0.8 | 1 | 2.792 | 13.0245 | -15 | -14.593 | 1.1584 | 0.012372
2015-02-23 14:00 | 7.31 | 7.1367 | 0.17333 | 0 | -10.0866 | 42.28 | 90.3638 | -0.36382 | 41.4809 | 49.788 | 0 | 5.3525 | 0.8 | 1 | 1.462 | 6.8145 | -13.9 | -13.687 | 1.1547 | 0.0064526
2015-02-23 15:00 | 0.66 | 0.63 | 0.03 | 0 | -10.0713 | 57.2812 | 92.8861 | -2.8861 | 56.0393 | 62.7423 | 0 | 0.4725 | 0.8 | 1 | 0.132 | 0.6045 | -14.3 | -14.2811 | 1.1571 | 0.00057358
2015-02-23 16:00 | 0.44 | 0.42 | 0.02 | 0 | -10.056 | 72.2823 | 95.8852 | -5.8852 | 70.5451 | 76.3698 | 0 | 0.315 | 0.8 | 1 | 0.088 | 0.403 | -12.5 | -12.4874 | 1.1499 | 0.00038001
2015-02-23 17:00 | 0.22 | 0.21 | 0.01 | 0 | -10.0408 | 87.2835 | 99.1682 | -9.1682 | 85.0733 | 90.3576 | 0 | 0.1575 | 0.8 | 1 | 0.044 | 0.2015 | -12.6 | -12.5937 | 1.1504 | 0.00019008
2015-02-23 18:00 | 0 | 0 | 0 | 0 | -10.0255 | 102.2847 | 102.5242 | -12.5242 | 99.7228 | 104.5486 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.3 | -12.3 | 1.1492 | 0
2015-02-23 19:00 | 0 | 0 | 0 | 0 | -10.0102 | 117.2858 | 105.7331 | -15.7331 | 114.5958 | 118.8505 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.9 | -11.9 | 1.1476 | 0
2015-02-23 20:00 | 0 | 0 | 0 | 0 | -9.9949 | 132.287 | 108.5738 | -18.5738 | 129.7727 | 133.1916 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.4 | -12.4 | 1.1496 | 0
2015-02-23 21:00 | 0 | 0 | 0 | 0 | -9.9796 | 147.2882 | 110.8372 | -20.8372 | 145.2857 | 147.4766 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12 | -12 | 1.148 | 0
2015-02-23 22:00 | 0 | 0 | 0 | 0 | -9.9644 | 162.2894 | 112.344 | -22.344 | 161.0984 | 161.4224 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12 | -12 | 1.148 | 0
2015-02-23 23:00 | 0 | 0 | 0 | 0 | -9.9491 | 177.2906 | 112.9669 | -22.9669 | 177.1014 | 172.5047 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.7 | -11.7 | 1.1468 | 0
2015-02-24 | 0 | 0 | 0 | 0 | -9.9338 | -167.7082 | 112.6506 | -22.6506 | -166.8663 | 166.1387 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.4 | -11.4 | 1.1456 | 0
2015-02-24 01:00 | 0 | 0 | 0 | 0 | -9.9185 | -152.707 | 111.4215 | -21.4215 | -150.9741 | 152.5675 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.4 | -11.4 | 1.1456 | 0
2015-02-24 02:00 | 0 | 0 | 0 | 0 | -9.9032 | -137.7058 | 109.3831 | -19.3831 | -135.3526 | 138.344 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.2 | -11.2 | 1.1448 | 0
2015-02-24 03:00 | 0 | 0 | 0 | 0 | -9.8878 | -122.7046 | 106.6985 | -16.6985 | -120.0642 | 124.0022 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12 | -12 | 1.148 | 0
2015-02-24 04:00 | 0 | 0 | 0 | 0 | -9.8725 | -107.7034 | 103.5682 | -13.5682 | -105.0981 | 109.6687 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.9 | -12.9 | 1.1516 | 0
2015-02-24 05:00 | 0 | 0 | 0 | 0 | -9.8572 | -92.7022 | 100.2101 | -10.2101 | -90.3869 | 95.4158 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13 | -13 | 1.152 | 0
2015-02-24 06:00 | 0 | 0 | 0 | 0 | -9.8419 | -77.701 | 96.8456 | -6.8456 | -75.832 | 81.323 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.1 | -13.1 | 1.1524 | 0
2015-02-24 07:00 | 3.14 | 3.14 | 0 | 0 | -9.8266 | -62.6997 | 93.6897 | -3.6897 | -61.3299 | 67.5144 | 0 | 2.355 | 0.8 | 1 | 0.628 | 2.983 | -13 | -12.9068 | 1.1516 | 0.0028169
2015-02-24 08:00 | 6.28 | 6.28 | 0 | 0 | -9.8112 | -47.6985 | 90.9427 | -0.94267 | -46.7938 | 54.2255 | 0 | 4.71 | 0.8 | 1 | 1.256 | 5.966 | -12.8 | -12.6136 | 1.1505 | 0.0056282
2015-02-24 09:00 | 9.42 | 9.42 | 0 | 0 | -9.7959 | -32.6973 | 88.7819 | 1.2181 | -32.1708 | 41.9675 | 0 | 7.065 | 0.8 | 1 | 1.884 | 8.949 | -12.8 | -12.5203 | 1.1501 | 0.0084395
2015-02-24 10:00 | 12.1433 | 12.1433 | 0 | 0 | -9.7805 | -17.696 | 87.3505 | 2.6495 | -17.4498 | 31.9618 | 0 | 9.1075 | 0.8 | 1 | 2.4287 | 11.5362 | -12.3 | -11.9395 | 1.1478 | 0.010857
2015-02-24 11:00 | 14.8667 | 14.8667 | 0 | 0 | -9.7652 | -2.6948 | 86.746 | 3.254 | -2.66 | 26.8643 | 0 | 11.15 | 0.8 | 1 | 2.9733 | 14.1233 | -13.1 | -12.6586 | 1.1506 | 0.013326
2015-02-24 12:00 | 17.59 | 17.59 | 0 | 0 | -9.7498 | 12.3065 | 87.0096 | 2.9904 | 12.1428 | 29.3571 | 0 | 13.1925 | 0.8 | 1 | 3.518 | 16.7105 | -13.6 | -13.0778 | 1.1523 | 0.01579
2015-02-24 13:00 | 12.0033 | 12.0033 | 0 | 0 | -9.7345 | 27.3077 | 88.1219 | 1.8781 | 26.8982 | 37.9728 | 0 | 9.0025 | 0.8 | 1 | 2.4007 | 11.4032 | -13.3 | -12.9437 | 1.1518 | 0.01077
2015-02-24 14:00 | 6.4167 | 6.4167 | 0 | 0 | -9.7191 | 42.309 | 90.005 | -0.0049939 | 41.5649 | 49.615 | 0 | 4.8125 | 0.8 | 1 | 1.2833 | 6.0958 | -13.7 | -13.5095 | 1.154 | 0.0057686
2015-02-24 15:00 | 0.83 | 0.83 | 0 | 0 | -9.7038 | 57.3103 | 92.5307 | -2.5307 | 56.1374 | 62.6126 | 0 | 0.6225 | 0.8 | 1 | 0.166 | 0.7885 | -12.7 | -12.6754 | 1.1507 | 0.00074401
2015-02-24 16:00 | 0.55333 | 0.55333 | 0 | 0 | -9.6884 | 72.3116 | 95.5325 | -5.5325 | 70.6531 | 76.2691 | 0 | 0.415 | 0.8 | 1 | 0.11067 | 0.52567 | -12.1 | -12.0836 | 1.1483 | 0.00049499
2015-02-24 17:00 | 0.27667 | 0.27667 | 0 | 0 | -9.673 | 87.3128 | 98.8167 | -8.8167 | 85.1867 | 90.2766 | 0 | 0.2075 | 0.8 | 1 | 0.055333 | 0.26283 | -11.3 | -11.2918 | 1.1452 | 0.00024681
2015-02-24 18:00 | 0 | 0 | 0 | 0 | -9.6577 | 102.3141 | 102.1724 | -12.1724 | 99.8367 | 104.4806 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.3 | -11.3 | 1.1452 | 0
2015-02-24 19:00 | 0 | 0 | 0 | 0 | -9.6423 | 117.3154 | 105.3792 | -15.3792 | 114.7048 | 118.7895 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.7 | -10.7 | 1.1428 | 0
2015-02-24 20:00 | 0 | 0 | 0 | 0 | -9.6269 | 132.3167 | 108.2166 | -18.2166 | 129.8712 | 133.1302 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.8 | -10.8 | 1.1432 | 0
2015-02-24 21:00 | 0 | 0 | 0 | 0 | -9.6115 | 147.318 | 110.476 | -20.476 | 145.3681 | 147.4017 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.6 | -10.6 | 1.1424 | 0
2015-02-24 22:00 | 0 | 0 | 0 | 0 | -9.5961 | 162.3193 | 111.979 | -21.979 | 161.1596 | 161.2962 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.9 | -10.9 | 1.1436 | 0
2015-02-24 23:00 | 0 | 0 | 0 | 0 | -9.5807 | 177.3206 | 112.599 | -22.599 | 177.1381 | 172.1679 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.3 | -11.3 | 1.1452 | 0
2015-02-25 | 0 | 0 | 0 | 0 | -9.5653 | -167.6781 | 112.2811 | -22.2811 | -166.8549 | 165.9163 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11 | -11 | 1.144 | 0
2015-02-25 01:00 | 0 | 0 | 0 | 0 | -9.5499 | -152.6768 | 111.0519 | -21.0519 | -150.9861 | 152.4243 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11 | -11 | 1.144 | 0
2015-02-25 02:00 | 0 | 0 | 0 | 0 | -9.5345 | -137.6754 | 109.0144 | -19.0144 | -135.3841 | 138.2219 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.9 | -9.9 | 1.1396 | 0
2015-02-25 03:00 | 0 | 0 | 0 | 0 | -9.5191 | -122.6741 | 106.3311 | -16.3311 | -120.1096 | 123.8839 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.7 | -9.7 | 1.1388 | 0
2015-02-25 04:00 | 0 | 0 | 0 | 0 | -9.5037 | -107.6728 | 103.2017 | -13.2017 | -105.1515 | 109.546 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.8 | -9.8 | 1.1392 | 0
2015-02-25 05:00 | 0 | 0 | 0 | 0 | -9.4883 | -92.6715 | 99.844 | -9.844 | -90.4426 | 95.283 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.3 | -9.3 | 1.1372 | 0
2015-02-25 06:00 | 0 | 0 | 0 | 0 | -9.4728 | -77.6701 | 96.479 | -6.479 | -75.8846 | 81.174 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.6 | -8.6 | 1.1344 | 0
2015-02-25 07:00 | 4.8367 | 4.5933 | 0.24333 | 0 | -9.4574 | -62.6688 | 93.3219 | -3.3219 | -61.3742 | 67.3419 | 0 | 3.445 | 0.8 | 1 | 0.96733 | 4.4123 | -8.1 | -7.9621 | 1.1318 | 0.0040952
2015-02-25 08:00 | 9.6733 | 9.1867 | 0.48667 | 0 | -9.442 | -47.6674 | 90.5735 | -0.57347 | -46.8252 | 54.0185 | 0 | 6.89 | 0.8 | 1 | 1.9347 | 8.8247 | -8.9 | -8.6242 | 1.1345 | 0.0082095
2015-02-25 09:00 | 14.51 | 13.78 | 0.73 | 0 | -9.4265 | -32.6661 | 88.4115 | 1.5885 | -32.1852 | 41.71 | 0 | 10.335 | 0.8 | 1 | 2.902 | 13.237 | -8.1 | -7.6863 | 1.1307 | 0.012273
2015-02-25 10:00 | 16.7067 | 16.1367 | 0.57 | 10.8185 | -9.4111 | -17.6647 | 86.9798 | 3.0202 | -17.4443 | 31.6366 | 9.2107 | 12.1025 | 0.8 | 1 | 3.3413 | 24.6546 | -8 | -7.2295 | 1.1289 | 0.022823
2015-02-25 11:00 | 18.9033 | 18.4933 | 0.41 | 6.4866 | -9.3956 | -2.6633 | 86.3761 | 3.6239 | -2.6329 | 26.4935 | 5.8054 | 13.87 | 0.8 | 1 | 3.7807 | 23.4561 | -7.1 | -6.367 | 1.1255 | 0.021647
2015-02-25 12:00 | 21.1 | 20.85 | 0.25 | 4.2679 | -9.3802 | 12.338 | 86.6418 | 3.3582 | 12.1918 | 29.0344 | 3.7315 | 15.6375 | 0.8 | 1 | 4.22 | 23.589 | -7.4 | -6.6628 | 1.1267 | 0.021793
2015-02-25 13:00 | 14.63 | 14.4067 | 0.22333 | 0 | -9.3647 | 27.3394 | 87.7574 | 2.2426 | 26.9676 | 37.7368 | 0 | 10.805 | 0.8 | 1 | 2.926 | 13.731 | -7.1 | -6.6709 | 1.1267 | 0.012686
2015-02-25 14:00 | 8.16 | 7.9633 | 0.19667 | 0 | -9.3493 | 42.3408 | 89.6442 | 0.35582 | 41.652 | 49.4446 | 0 | 5.9725 | 0.8 | 1 | 1.632 | 7.6045 | -6.5 | -6.2624 | 1.125 | 0.0070155
2015-02-25 15:00 | 1.69 | 1.52 | 0.17 | 0 | -9.3338 | 57.3422 | 92.1735 | -2.1735 | 56.2386 | 62.4856 | 0 | 1.14 | 0.8 | 1 | 0.338 | 1.478 | -6.4 | -6.3538 | 1.1254 | 0.001364
2015-02-25 16:00 | 1.1267 | 1.0133 | 0.11333 | 0 | -9.3183 | 72.3436 | 95.178 | -5.178 | 70.7642 | 76.1708 | 0 | 0.76 | 0.8 | 1 | 0.22533 | 0.98533 | -6.3 | -6.2692 | 1.1251 | 0.00090903
2015-02-25 17:00 | 0.56333 | 0.50667 | 0.056667 | 0 | -9.3029 | 87.3449 | 98.4635 | -8.4635 | 85.3032 | 90.1976 | 0 | 0.38 | 0.8 | 1 | 0.11267 | 0.49267 | -6.2 | -6.1846 | 1.1247 | 0.00045438
2015-02-25 18:00 | 0 | 0 | 0 | 0 | -9.2874 | 102.3463 | 101.8188 | -11.8188 | 99.9536 | 104.4141 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.2 | -6.2 | 1.1248 | 0
2015-02-25 19:00 | 0 | 0 | 0 | 0 | -9.2719 | 117.3477 | 105.0236 | -15.0236 | 114.8168 | 118.7293 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.3 | -6.3 | 1.1252 | 0
2015-02-25 20:00 | 0 | 0 | 0 | 0 | -9.2564 | 132.3492 | 107.8575 | -17.8575 | 129.9727 | 133.0687 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.3 | -6.3 | 1.1252 | 0
2015-02-25 21:00 | 0 | 0 | 0 | 0 | -9.241 | 147.3506 | 110.1128 | -20.1128 | 145.4533 | 147.3253 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.1 | -6.1 | 1.1244 | 0
2015-02-25 22:00 | 0 | 0 | 0 | 0 | -9.2255 | 162.352 | 111.6117 | -21.6117 | 161.2237 | 161.1654 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.2 | -6.2 | 1.1248 | 0
2015-02-25 23:00 | 0 | 0 | 0 | 0 | -9.21 | 177.3534 | 112.2286 | -22.2286 | 177.1776 | 171.8269 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.6 | -5.6 | 1.1224 | 0
2015-02-26 | 0 | 0 | 0 | 0 | -9.1945 | -167.6452 | 111.9091 | -21.9091 | -166.8408 | 165.6842 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-02-26 01:00 | 0 | 0 | 0 | 0 | -9.179 | -152.6437 | 110.6796 | -20.6796 | -150.9955 | 152.2738 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1148 | 0
2015-02-26 02:00 | 0 | 0 | 0 | 0 | -9.1635 | -137.6423 | 108.6429 | -18.6429 | -135.4129 | 138.094 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1148 | 0
2015-02-26 03:00 | 0 | 0 | 0 | 0 | -9.148 | -122.6409 | 105.9608 | -15.9608 | -120.1525 | 123.7608 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.118 | 0
2015-02-26 04:00 | 0 | 0 | 0 | 0 | -9.1324 | -107.6394 | 102.8324 | -12.8324 | -105.2026 | 109.4193 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1208 | 0
2015-02-26 05:00 | 0 | 0 | 0 | 0 | -9.1169 | -92.638 | 99.4749 | -9.4749 | -90.4961 | 95.1466 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.1 | -6.1 | 1.1244 | 0
2015-02-26 06:00 | 0 | 0 | 0 | 0 | -9.1014 | -77.6365 | 96.1095 | -6.1095 | -75.9349 | 81.022 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.4 | -6.4 | 1.1256 | 0
2015-02-26 07:00 | 6.45 | 4.3533 | 2.0967 | 0 | -9.0859 | -62.6351 | 92.9513 | -2.9513 | -61.4162 | 67.1667 | 0 | 3.265 | 0.8 | 1 | 1.29 | 4.555 | -7.2 | -7.0577 | 1.1282 | 0.0042141
2015-02-26 08:00 | 12.9 | 8.7067 | 4.1933 | 0 | -9.0703 | -47.6336 | 90.2015 | -0.20149 | -46.8542 | 53.8092 | 0 | 6.53 | 0.8 | 1 | 2.58 | 9.11 | -7.7 | -7.4153 | 1.1297 | 0.0084388
2015-02-26 09:00 | 19.35 | 13.06 | 6.29 | 0 | -9.0548 | -32.6321 | 88.0385 | 1.9615 | -32.1972 | 41.4502 | 0 | 9.795 | 0.8 | 1 | 3.87 | 13.665 | -8.6 | -8.173 | 1.1327 | 0.012692
2015-02-26 10:00 | 23.9267 | 15.9667 | 7.96 | 134.4783 | -9.0393 | -17.6307 | 86.6066 | 3.3934 | -17.4362 | 31.3087 | 114.8955 | 11.975 | 0.8 | 1 | 4.7853 | 131.6558 | -7.6 | -3.4858 | 1.1139 | 0.12026
2015-02-26 11:00 | 28.5033 | 18.8733 | 9.63 | 138.1851 | -9.0237 | -2.6292 | 86.0039 | 3.9961 | -2.6029 | 26.1201 | 124.0727 | 14.155 | 0.8 | 1 | 5.7007 | 143.9283 | -8 | -3.5022 | 1.114 | 0.13148
2015-02-26 12:00 | 33.08 | 21.78 | 11.3 | 173.7889 | -9.0082 | 12.3723 | 86.2719 | 3.7281 | 12.2436 | 28.7118 | 152.4211 | 16.335 | 0.8 | 1 | 6.616 | 175.3721 | -8.7 | -3.2196 | 1.1129 | 0.16004
2015-02-26 13:00 | 22.91 | 15.1167 | 7.7933 | 0 | -8.9926 | 27.3738 | 87.3908 | 2.6092 | 27.0401 | 37.503 | 0 | 11.3375 | 0.8 | 1 | 4.582 | 15.9195 | -9.2 | -8.7025 | 1.1348 | 0.014814
2015-02-26 14:00 | 12.74 | 8.4533 | 4.2867 | 0 | -8.9771 | 42.3753 | 89.2815 | 0.71851 | 41.7422 | 49.277 | 0 | 6.34 | 0.8 | 1 | 2.548 | 8.888 | -10.4 | -10.1222 | 1.1405 | 0.0083121
2015-02-26 15:00 | 2.57 | 1.79 | 0.78 | 0 | -8.9615 | 57.3768 | 91.8145 | -1.8145 | 56.343 | 62.3612 | 0 | 1.3425 | 0.8 | 1 | 0.514 | 1.8565 | -9.8 | -9.742 | 1.139 | 0.0017339
2015-02-26 16:00 | 1.7133 | 1.1933 | 0.52 | 0 | -8.946 | 72.3783 | 94.8218 | -4.8218 | 70.8785 | 76.0748 | 0 | 0.895 | 0.8 | 1 | 0.34267 | 1.2377 | -10 | -9.9613 | 1.1398 | 0.0011568
2015-02-26 17:00 | 0.85667 | 0.59667 | 0.26 | 0 | -8.9304 | 87.3798 | 98.1087 | -8.1087 | 85.4227 | 90.1206 | 0 | 0.4475 | 0.8 | 1 | 0.17133 | 0.61883 | -11.5 | -11.4807 | 1.1459 | 0.00058149
2015-02-26 18:00 | 0 | 0 | 0 | 0 | -8.9148 | 102.3813 | 101.4636 | -11.4636 | 100.0735 | 104.349 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.6 | -11.6 | 1.1464 | 0
2015-02-26 19:00 | 0 | 0 | 0 | 0 | -8.8993 | 117.3828 | 104.6662 | -14.6662 | 114.9318 | 118.6699 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12 | -12 | 1.148 | 0
2015-02-26 20:00 | 0 | 0 | 0 | 0 | -8.8837 | 132.3843 | 107.4966 | -17.4966 | 130.077 | 133.0072 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.5 | -12.5 | 1.15 | 0
2015-02-26 21:00 | 0 | 0 | 0 | 0 | -8.8681 | 147.3859 | 109.7476 | -19.7476 | 145.5414 | 147.2472 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.8 | -13.8 | 1.1552 | 0
2015-02-26 22:00 | 0 | 0 | 0 | 0 | -8.8525 | 162.3874 | 111.2423 | -21.2423 | 161.2905 | 161.0297 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.1 | -12.1 | 1.1484 | 0
2015-02-26 23:00 | 0 | 0 | 0 | 0 | -8.8369 | 177.3889 | 111.856 | -21.856 | 177.22 | 171.4819 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.4 | -11.4 | 1.1456 | 0
2015-02-27 | 0 | 0 | 0 | 0 | -8.8214 | -167.6095 | 111.5346 | -21.5346 | -166.8238 | 165.4428 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.3 | -12.3 | 1.1492 | 0
2015-02-27 01:00 | 0 | 0 | 0 | 0 | -8.8058 | -152.608 | 110.3048 | -20.3048 | -151.0021 | 152.1161 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.2 | -12.2 | 1.1488 | 0
2015-02-27 02:00 | 0 | 0 | 0 | 0 | -8.7902 | -137.6065 | 108.2688 | -18.2688 | -135.4391 | 137.9605 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.8 | -12.8 | 1.1512 | 0
2015-02-27 03:00 | 0 | 0 | 0 | 0 | -8.7746 | -122.6049 | 105.5877 | -15.5877 | -120.1929 | 123.6331 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.7 | -13.7 | 1.1548 | 0
2015-02-27 04:00 | 0 | 0 | 0 | 0 | -8.759 | -107.6033 | 102.4602 | -12.4602 | -105.2513 | 109.2886 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.6 | -11.6 | 1.1464 | 0
2015-02-27 05:00 | 0 | 0 | 0 | 0 | -8.7433 | -92.6018 | 99.1031 | -9.1031 | -90.5472 | 95.0067 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.5 | -12.5 | 1.15 | 0
2015-02-27 06:00 | 0 | 0 | 0 | 0 | -8.7277 | -77.6002 | 95.7372 | -5.7372 | -75.983 | 80.867 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.4 | -11.4 | 1.1456 | 0
2015-02-27 07:00 | 5.0267 | 5.0267 | 0 | 0 | -8.7121 | -62.5987 | 92.5779 | -2.5779 | -61.4559 | 66.9889 | 0 | 3.77 | 0.8 | 1 | 1.0053 | 4.7753 | -10.8 | -10.6508 | 1.1426 | 0.0044742
2015-02-27 08:00 | 10.0533 | 10.0533 | 0 | 0 | -8.6965 | -47.5971 | 89.8268 | 0.17315 | -46.8809 | 53.5977 | 0 | 7.54 | 0.8 | 1 | 2.0107 | 9.5507 | -11.1 | -10.8015 | 1.1432 | 0.0089531
2015-02-27 09:00 | 15.08 | 15.08 | 0 | 0 | -8.6809 | -32.5955 | 87.6629 | 2.3371 | -32.2068 | 41.1883 | 0 | 11.31 | 0.8 | 1 | 3.016 | 14.326 | -10.7 | -10.2523 | 1.141 | 0.013404
2015-02-27 10:00 | 18.2367 | 18.2367 | 0 | 0 | -8.6652 | -17.5939 | 86.2309 | 3.7691 | -17.4255 | 30.9784 | 0 | 13.6775 | 0.8 | 1 | 3.6473 | 17.3248 | -11.1 | -10.5586 | 1.1422 | 0.016227
2015-02-27 11:00 | 21.3933 | 21.3933 | 0 | 0 | -8.6496 | -2.5923 | 85.6294 | 4.3706 | -2.5703 | 25.7442 | 0 | 16.045 | 0.8 | 1 | 4.2787 | 20.3237 | -11.1 | -10.4649 | 1.1419 | 0.01903
2015-02-27 12:00 | 24.55 | 24.55 | 0 | 0 | -8.634 | 12.4093 | 85.8999 | 4.1001 | 12.2984 | 28.3895 | 0 | 18.4125 | 0.8 | 1 | 4.91 | 23.3225 | -10.9 | -10.1712 | 1.1407 | 0.021815
2015-02-27 13:00 | 17.14 | 17.14 | 0 | 0 | -8.6183 | 27.4109 | 87.0223 | 2.9777 | 27.1155 | 37.2717 | 0 | 12.855 | 0.8 | 1 | 3.428 | 16.283 | -11 | -10.4912 | 1.142 | 0.015248
2015-02-27 14:00 | 9.73 | 9.73 | 0 | 0 | -8.6027 | 42.4125 | 88.917 | 1.083 | 41.8355 | 49.1123 | 0 | 7.2975 | 0.8 | 1 | 1.946 | 9.2435 | -10.8 | -10.5111 | 1.142 | 0.0086563
2015-02-27 15:00 | 2.32 | 2.32 | 0 | 0 | -8.587 | 57.4141 | 91.4538 | -1.4538 | 56.4504 | 62.2395 | 0 | 1.74 | 0.8 | 1 | 0.464 | 2.204 | -10.8 | -10.7311 | 1.1429 | 0.0020656
2015-02-27 16:00 | 1.5467 | 1.5467 | 0 | 0 | -8.5714 | 72.4157 | 94.464 | -4.464 | 70.9957 | 75.9812 | 0 | 1.16 | 0.8 | 1 | 0.30933 | 1.4693 | -12.2 | -12.1541 | 1.1486 | 0.0013839
2015-02-27 17:00 | 0.77333 | 0.77333 | 0 | 0 | -8.5557 | 87.4173 | 97.7523 | -7.7523 | 85.5452 | 90.0455 | 0 | 0.58 | 0.8 | 1 | 0.15467 | 0.73467 | -12.6 | -12.577 | 1.1503 | 0.00069298
2015-02-27 18:00 | 0 | 0 | 0 | 0 | -8.5401 | 102.4189 | 101.1067 | -11.1067 | 100.1963 | 104.2854 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.5 | -11.5 | 1.146 | 0
2015-02-27 19:00 | 0 | 0 | 0 | 0 | -8.5244 | 117.4205 | 104.3072 | -14.3072 | 115.0495 | 118.6112 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10 | -10 | 1.14 | 0
2015-02-27 20:00 | 0 | 0 | 0 | 0 | -8.5088 | 132.4222 | 107.1339 | -17.1339 | 130.1841 | 132.9455 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.7 | -10.7 | 1.1428 | 0
2015-02-27 21:00 | 0 | 0 | 0 | 0 | -8.4931 | 147.4238 | 109.3805 | -19.3805 | 145.6322 | 147.1674 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.7 | -10.7 | 1.1428 | 0
2015-02-27 22:00 | 0 | 0 | 0 | 0 | -8.4774 | 162.4254 | 110.871 | -20.871 | 161.3601 | 160.8893 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.3 | -10.3 | 1.1412 | 0
2015-02-27 23:00 | 0 | 0 | 0 | 0 | -8.4618 | 177.4271 | 111.4812 | -21.4812 | 177.265 | 171.1332 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.1 | -11.1 | 1.1444 | 0
2015-02-28 | 0 | 0 | 0 | 0 | -8.4461 | -167.5713 | 111.1579 | -21.1579 | -166.8042 | 165.1926 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.7 | -11.7 | 1.1468 | 0
2015-02-28 01:00 | 0 | 0 | 0 | 0 | -8.4304 | -152.5696 | 109.9275 | -19.9275 | -151.0062 | 151.9514 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.2 | -12.2 | 1.1488 | 0
2015-02-28 02:00 | 0 | 0 | 0 | 0 | -8.4147 | -137.568 | 107.8921 | -17.8921 | -135.4628 | 137.8215 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.3 | -11.3 | 1.1452 | 0
2015-02-28 03:00 | 0 | 0 | 0 | 0 | -8.399 | -122.5663 | 105.212 | -15.212 | -120.2308 | 123.5008 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.5 | -12.5 | 1.15 | 0
2015-02-28 04:00 | 0.0033333 | 0.0033333 | 0 | 0 | -8.3833 | -107.5646 | 102.0854 | -12.0854 | -105.2977 | 109.1539 | 0 | 0.0025 | 0.8 | 1 | 0.00066667 | 0.0031667 | -13 | -12.9999 | 1.152 | 2.9914e-06
2015-02-28 05:00 | 0.0066667 | 0.0066667 | 0 | 0 | -8.3676 | -92.563 | 98.7285 | -8.7285 | -90.5961 | 94.8635 | 0 | 0.005 | 0.8 | 1 | 0.0013333 | 0.0063333 | -12.7 | -12.6998 | 1.1508 | 5.9765e-06
2015-02-28 06:00 | 0.01 | 0.01 | 0 | 0 | -8.3519 | -77.5613 | 95.3622 | -5.3622 | -76.0288 | 80.709 | 0 | 0.0075 | 0.8 | 1 | 0.002 | 0.0095 | -12 | -11.9997 | 1.148 | 8.9429e-06
2015-02-28 07:00 | 7.8033 | 7.4033 | 0.4 | 0 | -8.3362 | -62.5596 | 92.2019 | -2.2019 | -61.4935 | 66.8087 | 0 | 5.5525 | 0.8 | 1 | 1.5607 | 7.1132 | -11.6 | -11.3777 | 1.1455 | 0.0066815
2015-02-28 08:00 | 15.5967 | 14.7967 | 0.8 | 0 | -8.3205 | -47.5579 | 89.4497 | 0.55033 | -46.9053 | 53.384 | 0 | 11.0975 | 0.8 | 1 | 3.1193 | 14.2168 | -10.8 | -10.3557 | 1.1414 | 0.013306
2015-02-28 09:00 | 23.39 | 22.19 | 1.2 | 0 | -8.3048 | -32.5562 | 87.2849 | 2.7151 | -32.214 | 40.9244 | 0 | 16.6425 | 0.8 | 1 | 4.678 | 21.3205 | -11.2 | -10.5337 | 1.1421 | 0.019968
2015-02-28 10:00 | 27.82 | 26.11 | 1.71 | 23.6464 | -8.2891 | -17.5545 | 85.853 | 4.147 | -17.4123 | 30.6458 | 20.3438 | 19.5825 | 0.8 | 1 | 5.564 | 45.4903 | -11 | -9.5784 | 1.1383 | 0.042461
2015-02-28 11:00 | 32.25 | 30.03 | 2.22 | 26.8246 | -8.2734 | -2.5529 | 85.2528 | 4.7472 | -2.535 | 25.366 | 24.2384 | 22.5225 | 0.8 | 1 | 6.45 | 53.2109 | -11.1 | -9.4372 | 1.1377 | 0.049643
2015-02-28 12:00 | 36.68 | 33.95 | 2.73 | 34.9966 | -8.2577 | 12.4488 | 85.5259 | 4.4741 | 12.356 | 28.0678 | 30.8807 | 25.4625 | 0.8 | 1 | 7.336 | 63.6792 | -11 | -9.01 | 1.136 | 0.059321
2015-02-28 13:00 | 25.5167 | 23.6433 | 1.8733 | 32.078 | -8.2419 | 27.4506 | 86.6521 | 3.3479 | 27.1938 | 37.0429 | 25.6042 | 17.7325 | 0.8 | 1 | 5.1033 | 48.44 | -10.8 | -9.2862 | 1.1371 | 0.045168
2015-02-28 14:00 | 14.3533 | 13.3367 | 1.0167 | 0 | -8.2262 | 42.4523 | 88.5509 | 1.4491 | 41.9317 | 48.9505 | 0 | 10.0025 | 0.8 | 1 | 2.8707 | 12.8732 | -10.9 | -10.4977 | 1.142 | 0.012055
2015-02-28 15:00 | 3.19 | 3.03 | 0.16 | 0 | -8.2105 | 57.454 | 91.0916 | -1.0916 | 56.5608 | 62.1205 | 0 | 2.2725 | 0.8 | 1 | 0.638 | 2.9105 | -10.7 | -10.609 | 1.1424 | 0.0027265
2015-02-28 16:00 | 2.1267 | 2.02 | 0.10667 | 0 | -8.1947 | 72.4557 | 94.1047 | -4.1047 | 71.1159 | 75.89 | 0 | 1.515 | 0.8 | 1 | 0.42533 | 1.9403 | -10.8 | -10.7394 | 1.143 | 0.0018185
2015-02-28 17:00 | 1.0633 | 1.01 | 0.053333 | 0 | -8.179 | 87.4574 | 97.3944 | -7.3944 | 85.6706 | 89.9723 | 0 | 0.7575 | 0.8 | 1 | 0.21267 | 0.97017 | -10.3 | -10.2697 | 1.1411 | 0.00090777
2015-02-28 18:00 | 0 | 0 | 0 | 0 | -8.1633 | 102.4591 | 100.7484 | -10.7484 | 100.3218 | 104.2231 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.3 | -10.3 | 1.1412 | 0
2015-02-28 19:00 | 0 | 0 | 0 | 0 | -8.1475 | 117.4609 | 103.9466 | -13.9466 | 115.17 | 118.5533 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.3 | -10.3 | 1.1412 | 0
2015-02-28 20:00 | 0 | 0 | 0 | 0 | -8.1318 | 132.4626 | 106.7696 | -16.7696 | 130.2938 | 132.8835 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10 | -10 | 1.14 | 0
2015-02-28 21:00 | 0 | 0 | 0 | 0 | -8.116 | 147.4644 | 109.0117 | -19.0117 | 145.7256 | 147.0857 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10 | -10 | 1.14 | 0
2015-02-28 22:00 | 0 | 0 | 0 | 0 | -8.1003 | 162.4661 | 110.4977 | -20.4977 | 161.4323 | 160.7441 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.8 | -8.8 | 1.1352 | 0
2015-02-28 23:00 | 0 | 0 | 0 | 0 | -8.0845 | 177.4678 | 111.1045 | -21.1045 | 177.3127 | 170.7811 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.4 | -8.4 | 1.1336 | 0
2015-03-01 | 0 | 0 | 0 | 0 | -8.0687 | -167.5304 | 110.779 | -20.779 | -166.782 | 164.9338 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.6 | -8.6 | 1.1344 | 0
2015-03-01 01:00 | 0 | 0 | 0 | 0 | -8.053 | -152.5286 | 109.548 | -19.548 | -151.0076 | 151.7797 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9 | -9 | 1.136 | 0
2015-03-01 02:00 | 0 | 0 | 0 | 0 | -8.0372 | -137.5269 | 107.5129 | -17.5129 | -135.484 | 137.677 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8.4 | -8.4 | 1.1336 | 0
2015-03-01 03:00 | 0 | 0 | 0 | 0 | -8.0214 | -122.5251 | 104.8338 | -14.8338 | -120.2664 | 123.364 | 0 | 0 | 0.8 | 1 | 0 | 0 | -8 | -8 | 1.132 | 0
2015-03-01 04:00 | 0.026667 | 0.026667 | 0 | 0 | -8.0057 | -107.5233 | 101.708 | -11.708 | -105.3417 | 109.0155 | 0 | 0.02 | 0.8 | 1 | 0.0053333 | 0.025333 | -8.6 | -8.5992 | 1.1344 | 2.3565e-05
2015-03-01 05:00 | 0.053333 | 0.053333 | 0 | 0 | -7.9899 | -92.5216 | 98.3514 | -8.3514 | -90.6428 | 94.717 | 0 | 0.04 | 0.8 | 1 | 0.010667 | 0.050667 | -8.3 | -8.2984 | 1.1332 | 4.708e-05
2015-03-01 06:00 | 0.08 | 0.08 | 0 | 0 | -7.9741 | -77.5198 | 94.9846 | -4.9846 | -76.0724 | 80.5483 | 0 | 0.06 | 0.8 | 1 | 0.016 | 0.076 | -8.6 | -8.5976 | 1.1344 | 7.0695e-05
2015-03-01 07:00 | 6.9867 | 6.7667 | 0.22 | 0 | -7.9583 | -62.518 | 91.8234 | -1.8234 | -61.5288 | 66.626 | 0 | 5.075 | 0.8 | 1 | 1.3973 | 6.4723 | -8.7 | -8.4977 | 1.134 | 0.0060184
2015-03-01 08:00 | 13.8933 | 13.4533 | 0.44 | 0 | -7.9425 | -47.5162 | 89.0701 | 0.92991 | -46.9275 | 53.1684 | 0 | 10.09 | 0.8 | 1 | 2.7787 | 12.8687 | -9.2 | -8.7979 | 1.1352 | 0.011979
2015-03-01 09:00 | 20.8 | 20.14 | 0.66 | 12.2227 | -7.9267 | -32.5144 | 86.9046 | 3.0954 | -32.2188 | 40.6588 | 9.2722 | 15.105 | 0.8 | 1 | 4.16 | 28.5372 | -8.6 | -7.7082 | 1.1308 | 0.026462
2015-03-01 10:00 | 24.8633 | 23.4 | 1.4633 | 18.5396 | -7.911 | -17.5126 | 85.4729 | 4.5271 | -17.3966 | 30.311 | 16.0052 | 17.55 | 0.8 | 1 | 4.9727 | 38.5278 | -8.4 | -7.196 | 1.1288 | 0.035661
2015-03-01 11:00 | 28.9267 | 26.66 | 2.2667 | 25.3702 | -7.8952 | -2.5108 | 84.8742 | 5.1258 | -2.497 | 24.9855 | 22.9959 | 19.995 | 0.8 | 1 | 5.7853 | 48.7763 | -8.2 | -6.6757 | 1.1267 | 0.045064
2015-03-01 12:00 | 32.99 | 29.92 | 3.07 | 36.312 | -7.8794 | 12.491 | 85.1501 | 4.8499 | 12.4163 | 27.7467 | 32.1366 | 22.44 | 0.8 | 1 | 6.598 | 61.1746 | -8.4 | -6.4883 | 1.126 | 0.056481
2015-03-01 13:00 | 23.3667 | 21.1333 | 2.2333 | 34.4231 | -7.8635 | 27.4928 | 86.2801 | 3.7199 | 27.275 | 36.8168 | 27.5576 | 15.85 | 0.8 | 1 | 4.6733 | 48.081 | -8.1 | -6.5975 | 1.1264 | 0.044409
2015-03-01 14:00 | 13.7433 | 12.3467 | 1.3967 | 0 | -7.8477 | 42.4946 | 88.1833 | 1.8167 | 42.0309 | 48.7917 | 0 | 9.26 | 0.8 | 1 | 2.7487 | 12.0087 | -7.6 | -7.2247 | 1.1289 | 0.011116
2015-03-01 15:00 | 4.12 | 3.56 | 0.56 | 0 | -7.8319 | 57.4964 | 90.728 | -0.72797 | 56.674 | 62.0043 | 0 | 2.67 | 0.8 | 1 | 0.824 | 3.494 | -7.1 | -6.9908 | 1.128 | 0.0032317
2015-03-01 16:00 | 2.7467 | 2.3733 | 0.37333 | 0 | -7.8161 | 72.4982 | 93.7441 | -3.7441 | 71.239 | 75.8012 | 0 | 1.78 | 0.8 | 1 | 0.54933 | 2.3293 | -7.2 | -7.1272 | 1.1285 | 0.0021555
2015-03-01 17:00 | 1.3733 | 1.1867 | 0.18667 | 0 | -7.8003 | 87.5001 | 97.0352 | -7.0352 | 85.7987 | 89.901 | 0 | 0.89 | 0.8 | 1 | 0.27467 | 1.1647 | -6.3 | -6.2636 | 1.1251 | 0.0010745
2015-03-01 18:00 | 0 | 0 | 0 | 0 | -7.7845 | 102.5019 | 100.3888 | -10.3888 | 100.4501 | 104.1622 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.3 | -6.3 | 1.1252 | 0
2015-03-01 19:00 | 0 | 0 | 0 | 0 | -7.7687 | 117.5037 | 103.5846 | -13.5846 | 115.2931 | 118.496 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.7 | -5.7 | 1.1228 | 0
2015-03-01 20:00 | 0 | 0 | 0 | 0 | -7.7528 | 132.5056 | 106.4038 | -16.4038 | 130.4062 | 132.8212 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.2 | -6.2 | 1.1248 | 0
2015-03-01 21:00 | 0 | 0 | 0 | 0 | -7.737 | 147.5074 | 108.6413 | -18.6413 | 145.8216 | 147.0021 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.7 | -5.7 | 1.1228 | 0
2015-03-01 22:00 | 0 | 0 | 0 | 0 | -7.7212 | 162.5093 | 110.1227 | -20.1227 | 161.507 | 160.594 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.5 | -6.5 | 1.126 | 0
2015-03-01 23:00 | 0 | 0 | 0 | 0 | -7.7053 | 177.5111 | 110.7257 | -20.7257 | 177.3628 | 170.4256 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.5 | -5.5 | 1.122 | 0
2015-03-02 | 0 | 0 | 0 | 0 | -7.6895 | -167.487 | 110.398 | -20.398 | -166.7573 | 164.667 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.4 | -6.4 | 1.1256 | 0
2015-03-02 01:00 | 0 | 0 | 0 | 0 | -7.6736 | -152.4851 | 109.1662 | -19.1662 | -151.0066 | 151.6012 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6 | -6 | 1.124 | 0
2015-03-02 02:00 | 0 | 0 | 0 | 0 | -7.6578 | -137.4833 | 107.1315 | -17.1315 | -135.5027 | 137.5271 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.6 | -4.6 | 1.1184 | 0
2015-03-02 03:00 | 0 | 0 | 0 | 0 | -7.642 | -122.4814 | 104.4532 | -14.4532 | -120.2996 | 123.2228 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.118 | 0
2015-03-02 04:00 | 0.053333 | 0.053333 | 0 | 0 | -7.6261 | -107.4795 | 101.3281 | -11.3281 | -105.3836 | 108.8733 | 0 | 0.04 | 0.8 | 1 | 0.010667 | 0.050667 | -5 | -4.9984 | 1.12 | 4.6532e-05
2015-03-02 05:00 | 0.10667 | 0.10667 | 0 | 0 | -7.6102 | -92.4777 | 97.9718 | -7.9718 | -90.6873 | 94.5673 | 0 | 0.08 | 0.8 | 1 | 0.021333 | 0.10133 | -4.1 | -4.0968 | 1.1164 | 9.2764e-05
2015-03-02 06:00 | 0.16 | 0.16 | 0 | 0 | -7.5944 | -77.4758 | 94.6046 | -4.6046 | -76.1139 | 80.3849 | 0 | 0.12 | 0.8 | 1 | 0.032 | 0.152 | -4.5 | -4.4953 | 1.118 | 0.00013935
2015-03-02 07:00 | 7.83 | 7.83 | 0 | 0 | -7.5785 | -62.4739 | 91.4425 | -1.4425 | -61.562 | 66.4412 | 0 | 5.8725 | 0.8 | 1 | 1.566 | 7.4385 | -3.9 | -3.6675 | 1.1147 | 0.006799
2015-03-02 08:00 | 15.5 | 15.5 | 0 | 0 | -7.5627 | -47.472 | 88.6882 | 1.3118 | -46.9475 | 52.9509 | 0 | 11.625 | 0.8 | 1 | 3.1 | 14.725 | -4.1 | -3.6398 | 1.1146 | 0.013458
2015-03-02 09:00 | 23.17 | 23.17 | 0 | 0 | -7.5468 | -32.4701 | 86.5222 | 3.4778 | -32.2213 | 40.3915 | 0 | 17.3775 | 0.8 | 1 | 4.634 | 22.0115 | -3.4 | -2.7121 | 1.1108 | 0.02005
2015-03-02 10:00 | 26.6933 | 26.6933 | 0 | 0 | -7.5309 | -17.4682 | 85.0908 | 4.9092 | -17.3785 | 29.9742 | 0 | 20.02 | 0.8 | 1 | 5.3387 | 25.3587 | -3.6 | -2.8075 | 1.1112 | 0.023107
2015-03-02 11:00 | 30.2167 | 30.2167 | 0 | 0 | -7.515 | -2.4663 | 84.4936 | 5.5064 | -2.4564 | 24.6029 | 0 | 22.6625 | 0.8 | 1 | 6.0433 | 28.7058 | -3.5 | -2.6029 | 1.1104 | 0.026138
2015-03-02 12:00 | 33.74 | 33.74 | 0 | 0 | -7.4992 | 12.5356 | 84.7726 | 5.2274 | 12.4794 | 27.4265 | 0 | 25.305 | 0.8 | 1 | 6.748 | 32.053 | -2.9 | -1.8983 | 1.1076 | 0.029111
2015-03-02 13:00 | 24.1033 | 24.1033 | 0 | 0 | -7.4833 | 27.5375 | 85.9066 | 4.0934 | 27.359 | 36.5935 | 0 | 18.0775 | 0.8 | 1 | 4.8207 | 22.8982 | -2.2 | -1.4844 | 1.1059 | 0.020766
2015-03-02 14:00 | 14.4667 | 14.4667 | 0 | 0 | -7.4674 | 42.5394 | 87.8142 | 2.1858 | 42.1328 | 48.636 | 0 | 10.85 | 0.8 | 1 | 2.8933 | 13.7433 | -2.5 | -2.0705 | 1.1083 | 0.01249
2015-03-02 15:00 | 4.83 | 4.83 | 0 | 0 | -7.4515 | 57.5414 | 90.363 | -0.36298 | 56.7901 | 61.891 | 0 | 3.6225 | 0.8 | 1 | 0.966 | 4.5885 | -2.6 | -2.4566 | 1.1098 | 0.0041758
2015-03-02 16:00 | 3.22 | 3.22 | 0 | 0 | -7.4356 | 72.5433 | 93.3822 | -3.3822 | 71.3648 | 75.7147 | 0 | 2.415 | 0.8 | 1 | 0.644 | 3.059 | -2.5 | -2.4044 | 1.1096 | 0.0027833
2015-03-02 17:00 | 1.61 | 1.61 | 0 | 0 | -7.4197 | 87.5452 | 96.6747 | -6.6747 | 85.9296 | 89.8316 | 0 | 1.2075 | 0.8 | 1 | 0.322 | 1.5295 | -2.8 | -2.7522 | 1.111 | 0.0013934
2015-03-02 18:00 | 0 | 0 | 0 | 0 | -7.4038 | 102.5471 | 100.0278 | -10.0278 | 100.5811 | 104.1026 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-03-02 19:00 | 0 | 0 | 0 | 0 | -7.3879 | 117.5491 | 103.2213 | -13.2213 | 115.4188 | 118.4394 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-03-02 20:00 | 0 | 0 | 0 | 0 | -7.372 | 132.551 | 106.0366 | -16.0366 | 130.521 | 132.7585 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.2 | -2.2 | 1.1088 | 0
2015-03-02 21:00 | 0 | 0 | 0 | 0 | -7.3561 | 147.553 | 108.2693 | -18.2693 | 145.9201 | 146.9166 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.1 | -2.1 | 1.1084 | 0
2015-03-02 22:00 | 0 | 0 | 0 | 0 | -7.3402 | 162.5549 | 109.7461 | -19.7461 | 161.5842 | 160.4391 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-03-02 23:00 | 0 | 0 | 0 | 0 | -7.3243 | 177.5569 | 110.3452 | -20.3452 | 177.4155 | 170.067 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-03-03 | 0 | 0 | 0 | 0 | -7.3084 | -167.4412 | 110.015 | -20.015 | -166.7301 | 164.3923 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.8 | -0.8 | 1.1032 | 0
2015-03-03 01:00 | 0 | 0 | 0 | 0 | -7.2925 | -152.4392 | 108.7823 | -18.7823 | -151.0032 | 151.416 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-03-03 02:00 | 0 | 0 | 0 | 0 | -7.2766 | -137.4372 | 106.7479 | -16.7479 | -135.5191 | 137.372 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-03-03 03:00 | 0 | 0 | 0 | 0 | -7.2607 | -122.4353 | 104.0704 | -14.0704 | -120.3306 | 123.0772 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-03-03 04:00 | 0.16 | 0.16 | 0 | 0 | -7.2447 | -107.4333 | 100.946 | -10.946 | -105.4232 | 108.7275 | 0 | 0.12 | 0.8 | 1 | 0.032 | 0.152 | 0.3 | 0.30475 | 1.0988 | 0.00013695
2015-03-03 05:00 | 0.32 | 0.32 | 0 | 0 | -7.2288 | -92.4313 | 97.5899 | -7.5899 | -90.7297 | 94.4146 | 0 | 0.24 | 0.8 | 1 | 0.064 | 0.304 | 0.7 | 0.7095 | 1.0972 | 0.0002735
2015-03-03 06:00 | 0.48 | 0.48 | 0 | 0 | -7.2129 | -77.4293 | 94.2224 | -4.2224 | -76.1534 | 80.2189 | 0 | 0.36 | 0.8 | 1 | 0.096 | 0.456 | 0.5 | 0.51425 | 1.0979 | 0.00041054
2015-03-03 07:00 | 8.82 | 8.6033 | 0.21667 | 0 | -7.1969 | -62.4273 | 91.0594 | -1.0594 | -61.5931 | 66.2542 | 0 | 6.4525 | 0.8 | 1 | 1.764 | 8.2165 | 0.6 | 0.85677 | 1.0966 | 0.0073882
2015-03-03 08:00 | 17.16 | 16.7267 | 0.43333 | 0 | -7.181 | -47.4253 | 88.3042 | 1.6958 | -46.9653 | 52.7316 | 0 | 12.545 | 0.8 | 1 | 3.432 | 15.977 | 0.1 | 0.59928 | 1.0976 | 0.01438
2015-03-03 09:00 | 25.5 | 24.85 | 0.65 | 9.6496 | -7.1651 | -32.4234 | 86.1376 | 3.8624 | -32.2216 | 40.1226 | 7.3788 | 18.6375 | 0.8 | 1 | 5.1 | 31.1163 | -0.3 | 0.67238 | 1.0973 | 0.027998
2015-03-03 10:00 | 30.1967 | 26.2533 | 3.9433 | 42.7443 | -7.1491 | -17.4214 | 84.7067 | 5.2933 | -17.358 | 29.6356 | 37.1528 | 19.69 | 0.8 | 1 | 6.0393 | 62.8821 | -0.6 | 1.3651 | 1.0945 | 0.056438
2015-03-03 11:00 | 34.8933 | 27.6567 | 7.2367 | 70.5357 | -7.1332 | -2.4194 | 84.1113 | 5.8887 | -2.4134 | 24.2183 | 64.3278 | 20.7425 | 0.8 | 1 | 6.9787 | 92.049 | 0.6 | 3.4765 | 1.0861 | 0.081979
2015-03-03 12:00 | 39.59 | 29.06 | 10.53 | 107.7816 | -7.1172 | 12.5827 | 84.3934 | 5.6066 | 12.5451 | 27.1074 | 95.9423 | 21.795 | 0.8 | 1 | 7.918 | 125.6553 | 0.7 | 4.6267 | 1.0815 | 0.11143
2015-03-03 13:00 | 28.15 | 20.88 | 7.27 | 93.3122 | -7.1013 | 27.5847 | 85.5315 | 4.4685 | 27.4457 | 36.3732 | 75.1323 | 15.66 | 0.8 | 1 | 5.63 | 96.4223 | -0.2 | 2.8132 | 1.0887 | 0.086083
2015-03-03 14:00 | 16.71 | 12.7 | 4.01 | 0 | -7.0853 | 42.5867 | 87.4437 | 2.5563 | 42.2376 | 48.4834 | 0 | 9.525 | 0.8 | 1 | 3.342 | 12.867 | -0.6 | -0.19791 | 1.1008 | 0.011614
2015-03-03 15:00 | 5.27 | 4.52 | 0.75 | 0 | -7.0694 | 57.5887 | 89.9968 | 0.0032448 | 56.909 | 61.7804 | 0 | 3.39 | 0.8 | 1 | 1.054 | 4.444 | -1.2 | -1.0611 | 1.1042 | 0.004024
2015-03-03 16:00 | 3.5133 | 3.0133 | 0.5 | 0 | -7.0534 | 72.5907 | 93.019 | -3.019 | 71.4934 | 75.6305 | 0 | 2.26 | 0.8 | 1 | 0.70267 | 2.9627 | -1.4 | -1.3074 | 1.1052 | 0.002685
2015-03-03 17:00 | 1.7567 | 1.5067 | 0.25 | 0 | -7.0374 | 87.5928 | 96.3131 | -6.3131 | 86.0631 | 89.764 | 0 | 1.13 | 0.8 | 1 | 0.35133 | 1.4813 | -1.8 | -1.7537 | 1.107 | 0.0013447
2015-03-03 18:00 | 0 | 0 | 0 | 0 | -7.0215 | 102.5948 | 99.6657 | -9.6657 | 100.7145 | 104.0443 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.1 | -2.1 | 1.1084 | 0
2015-03-03 19:00 | 0 | 0 | 0 | 0 | -7.0055 | 117.5968 | 102.8567 | -12.8567 | 115.5469 | 118.3833 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.4 | -2.4 | 1.1096 | 0
2015-03-03 20:00 | 0 | 0 | 0 | 0 | -6.9895 | 132.5989 | 105.668 | -15.668 | 130.6383 | 132.6954 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.2 | -2.2 | 1.1088 | 0
2015-03-03 21:00 | 0 | 0 | 0 | 0 | -6.9736 | 147.6009 | 107.8959 | -17.8959 | 146.0209 | 146.8291 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-03-03 22:00 | 0 | 0 | 0 | 0 | -6.9576 | 162.603 | 109.3678 | -19.3678 | 161.6638 | 160.2794 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.2 | -2.2 | 1.1088 | 0
2015-03-03 23:00 | 0 | 0 | 0 | 0 | -6.9416 | 177.605 | 109.963 | -19.963 | 177.4705 | 169.7056 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.2 | -2.2 | 1.1088 | 0
2015-03-04 | 0 | 0 | 0 | 0 | -6.9256 | -167.3929 | 109.6303 | -19.6303 | -166.7005 | 164.1103 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-03-04 01:00 | 0 | 0 | 0 | 0 | -6.9096 | -152.3909 | 108.3965 | -18.3965 | -150.9974 | 151.2244 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-03-04 02:00 | 0 | 0 | 0 | 0 | -6.8937 | -137.3888 | 106.3622 | -16.3622 | -135.5332 | 137.2117 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.11 | 0
2015-03-04 03:00 | 0 | 0 | 0 | 0 | -6.8777 | -122.3867 | 103.6854 | -13.6854 | -120.3593 | 122.9274 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-03-04 04:00 | 0.41667 | 0.25 | 0.16667 | 0 | -6.8617 | -107.3847 | 100.5617 | -10.5617 | -105.4607 | 108.5781 | 0 | 0.1875 | 0.8 | 1 | 0.083333 | 0.27083 | -2.6 | -2.5915 | 1.1104 | 0.00024659
2015-03-04 05:00 | 0.83333 | 0.5 | 0.33333 | 0 | -6.8457 | -92.3826 | 97.2058 | -7.2058 | -90.77 | 94.2588 | 0 | 0.375 | 0.8 | 1 | 0.16667 | 0.54167 | -2.9 | -2.8831 | 1.1115 | 0.00049371
2015-03-04 06:00 | 1.25 | 0.75 | 0.5 | 0 | -6.8297 | -77.3805 | 93.8379 | -3.8379 | -76.1908 | 80.0505 | 0 | 0.5625 | 0.8 | 1 | 0.25 | 0.8125 | -2.6 | -2.5746 | 1.1103 | 0.00073974
2015-03-04 07:00 | 16.75 | 8.7633 | 7.9867 | 0 | -6.8137 | -62.3784 | 90.6742 | -0.67419 | -61.6221 | 66.0652 | 0 | 6.5725 | 0.8 | 1 | 3.35 | 9.9225 | -2 | -1.6899 | 1.1068 | 0.0090051
2015-03-04 08:00 | 32.25 | 16.7767 | 15.4733 | 0 | -6.7977 | -47.3763 | 87.9181 | 2.0819 | -46.981 | 52.5108 | 0 | 12.5825 | 0.8 | 1 | 6.45 | 19.0325 | -2.2 | -1.6052 | 1.1064 | 0.017268
2015-03-04 09:00 | 47.75 | 24.79 | 22.96 | 309.9002 | -6.7817 | -32.3742 | 85.7512 | 4.2488 | -32.2196 | 39.8525 | 237.9095 | 18.5925 | 0.8 | 1 | 9.55 | 266.052 | -2.3 | 6.0141 | 1.0759 | 0.23473
2015-03-04 10:00 | 53.8733 | 27.5233 | 26.35 | 266.2741 | -6.7657 | -17.3722 | 84.3208 | 5.6792 | -17.3351 | 29.2952 | 232.2204 | 20.6425 | 0.8 | 1 | 10.7747 | 263.6376 | -2.1 | 6.1387 | 1.0754 | 0.23249
2015-03-04 11:00 | 59.9967 | 30.2567 | 29.74 | 272.1957 | -6.7497 | -2.3701 | 83.7274 | 6.2726 | -2.3678 | 23.8318 | 248.9871 | 22.6925 | 0.8 | 1 | 11.9993 | 283.679 | -1.9 | 6.965 | 1.0721 | 0.2494
2015-03-04 12:00 | 66.12 | 32.99 | 33.13 | 317.6174 | -6.7336 | 12.6321 | 84.0127 | 5.9873 | 12.6134 | 26.7895 | 283.5269 | 24.7425 | 0.8 | 1 | 13.224 | 321.4934 | -1.2 | 8.8467 | 1.0646 | 0.28066
2015-03-04 13:00 | 46.9267 | 23.9433 | 22.9833 | 272.1273 | -6.7176 | 27.6342 | 85.1551 | 4.8449 | 27.5351 | 36.156 | 219.7194 | 17.9575 | 0.8 | 1 | 9.3853 | 247.0623 | -0.4 | 7.3207 | 1.0707 | 0.21692
2015-03-04 14:00 | 27.7333 | 14.8967 | 12.8367 | 0 | -6.7016 | 42.6363 | 87.072 | 2.928 | 42.345 | 48.3341 | 0 | 11.1725 | 0.8 | 1 | 5.5467 | 16.7192 | -0.3 | 0.22247 | 1.0991 | 0.015068
2015-03-04 15:00 | 8.54 | 5.85 | 2.69 | 0 | -6.6856 | 57.6384 | 89.6294 | 0.37061 | 57.0305 | 61.6726 | 0 | 4.3875 | 0.8 | 1 | 1.708 | 6.0955 | -0.6 | -0.40952 | 1.1016 | 0.0055063
2015-03-04 16:00 | 5.6933 | 3.9 | 1.7933 | 0 | -6.6696 | 72.6405 | 92.6549 | -2.6549 | 71.6245 | 75.5488 | 0 | 2.925 | 0.8 | 1 | 1.1387 | 4.0637 | -0.9 | -0.77301 | 1.1031 | 0.0036757
2015-03-04 17:00 | 2.8467 | 1.95 | 0.89667 | 0 | -6.6535 | 87.6426 | 95.9504 | -5.9504 | 86.1991 | 89.6983 | 0 | 1.4625 | 0.8 | 1 | 0.56933 | 2.0318 | -0.1 | -0.036505 | 1.1001 | 0.001833
2015-03-04 18:00 | 0 | 0 | 0 | 0 | -6.6375 | 102.6448 | 99.3024 | -9.3024 | 100.8504 | 103.9872 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-03-04 19:00 | 0 | 0 | 0 | 0 | -6.6215 | 117.6469 | 102.491 | -12.491 | 115.6774 | 118.3277 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-03-04 20:00 | 0 | 0 | 0 | 0 | -6.6054 | 132.649 | 105.2982 | -15.2982 | 130.7578 | 132.6317 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.1048 | 0
2015-03-04 21:00 | 0 | 0 | 0 | 0 | -6.5894 | 147.6512 | 107.5211 | -17.5211 | 146.124 | 146.7394 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-03-04 22:00 | 0 | 0 | 0 | 0 | -6.5734 | 162.6533 | 108.9881 | -18.9881 | 161.7456 | 160.1148 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-03-04 23:00 | 0 | 0 | 0 | 0 | -6.5573 | 177.6555 | 109.5792 | -19.5792 | 177.5278 | 169.3414 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.4 | -1.4 | 1.1056 | 0
2015-03-05 | 0 | 0 | 0 | 0 | -6.5413 | -167.3424 | 109.2438 | -19.2438 | -166.6687 | 163.8213 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-03-05 01:00 | 0 | 0 | 0 | 0 | -6.5252 | -152.3402 | 108.0089 | -18.0089 | -150.9893 | 151.0264 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5026 | -1.5026 | 1.106 | 0
2015-03-05 02:00 | 0 | 0 | 0 | 0 | -6.5092 | -137.3381 | 105.9746 | -15.9746 | -135.5451 | 137.0463 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5052 | -1.5052 | 1.106 | 0
2015-03-05 03:00 | 0 | 0 | 0 | 0 | -6.4931 | -122.3359 | 103.2984 | -13.2984 | -120.3859 | 122.7735 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5077 | -1.5077 | 1.106 | 0
2015-03-05 04:00 | 0.55 | 0.37667 | 0.17333 | 0 | -6.4771 | -107.3337 | 100.1753 | -10.1753 | -105.496 | 108.4253 | 0 | 0.2825 | 0.8 | 1 | 0.11 | 0.3925 | -1.5103 | -1.498 | 1.106 | 0.00035596
2015-03-05 05:00 | 1.1 | 0.75333 | 0.34667 | 0 | -6.461 | -92.3316 | 96.8196 | -6.8196 | -90.8082 | 94.1002 | 0 | 0.565 | 0.8 | 1 | 0.22 | 0.785 | -1.5129 | -1.4883 | 1.106 | 0.0007119
2015-03-05 06:00 | 1.65 | 1.13 | 0.52 | 0 | -6.4449 | -77.3294 | 93.4515 | -3.4515 | -76.2261 | 79.8796 | 0 | 0.8475 | 0.8 | 1 | 0.33 | 1.1775 | -1.5155 | -1.4787 | 1.1059 | 0.0010678
2015-03-05 07:00 | 16.11 | 10.17 | 5.94 | 0 | -6.4289 | -62.3272 | 90.287 | -0.28697 | -61.6492 | 65.8743 | 0 | 7.6275 | 0.8 | 1 | 3.222 | 10.8495 | -1.518 | -1.179 | 1.1047 | 0.0098282
2015-03-05 08:00 | 30.57 | 19.21 | 11.36 | 0 | -6.4128 | -47.325 | 87.5301 | 2.4699 | -46.9947 | 52.2885 | 0 | 14.4075 | 0.8 | 1 | 6.114 | 20.5215 | -1.5206 | -0.8793 | 1.1035 | 0.01857
2015-03-05 09:00 | 45.03 | 28.25 | 16.78 | 207.5579 | -6.3967 | -32.3229 | 85.3629 | 4.6371 | -32.2155 | 39.5811 | 159.9698 | 21.1875 | 0.8 | 1 | 9.006 | 190.1633 | -1.5232 | 4.4194 | 1.0823 | 0.16877
2015-03-05 10:00 | 48.4633 | 30.5533 | 17.91 | 169.4624 | -6.3807 | -17.3207 | 83.9332 | 6.0668 | -17.31 | 28.9532 | 148.2822 | 22.915 | 0.8 | 1 | 9.6927 | 180.8898 | -1.5258 | 4.1271 | 1.0835 | 0.16071
2015-03-05 11:00 | 51.8967 | 32.8567 | 19.04 | 164.2152 | -6.3646 | -2.3185 | 83.3418 | 6.6582 | -2.3198 | 23.4436 | 150.6596 | 24.6425 | 0.8 | 1 | 10.3793 | 185.6814 | -1.5283 | 4.2742 | 1.0829 | 0.16488
2015-03-05 12:00 | 55.33 | 35.16 | 20.17 | 181.8132 | -6.3485 | 12.6837 | 83.6306 | 6.3694 | 12.6843 | 26.4731 | 162.749 | 26.37 | 0.8 | 1 | 11.066 | 200.185 | -1.5309 | 4.7249 | 1.0811 | 0.17746
2015-03-05 13:00 | 41.1 | 26.0533 | 15.0467 | 165.3047 | -6.3324 | 27.6859 | 84.7775 | 5.2225 | 27.6271 | 35.942 | 133.8327 | 19.54 | 0.8 | 1 | 8.22 | 161.5927 | -1.5335 | 3.5163 | 1.0859 | 0.14389
2015-03-05 14:00 | 26.87 | 16.9467 | 9.9233 | 172.3461 | -6.3164 | 42.6881 | 86.6992 | 3.3008 | 42.455 | 48.188 | 114.9012 | 12.71 | 0.8 | 1 | 5.374 | 132.9852 | -1.5361 | 2.6197 | 1.0895 | 0.11881
2015-03-05 15:00 | 12.64 | 7.84 | 4.8 | 0 | -6.3003 | 57.6903 | 89.261 | 0.73903 | 57.1546 | 61.5677 | 0 | 5.88 | 0.8 | 1 | 2.528 | 8.408 | -1.5386 | -1.2759 | 1.1051 | 0.0076192
2015-03-05 16:00 | 8.4267 | 5.2267 | 3.2 | 0 | -6.2842 | 72.6926 | 92.2897 | -2.2897 | 71.7582 | 75.4693 | 0 | 3.92 | 0.8 | 1 | 1.6853 | 5.6053 | -1.5412 | -1.366 | 1.1055 | 0.0050811
2015-03-05 17:00 | 4.2133 | 2.6133 | 1.6 | 0 | -6.2681 | 87.6948 | 95.5867 | -5.5867 | 86.3376 | 89.6344 | 0 | 1.96 | 0.8 | 1 | 0.84267 | 2.8027 | -1.5438 | -1.4562 | 1.1058 | 0.0025414
2015-03-05 18:00 | 0 | 0 | 0 | 0 | -6.252 | 102.697 | 98.9382 | -8.9382 | 100.9887 | 103.9312 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5464 | -1.5464 | 1.1062 | 0
2015-03-05 19:00 | 0 | 0 | 0 | 0 | -6.2359 | 117.6992 | 102.1242 | -12.1242 | 115.8102 | 118.2725 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5489 | -1.5489 | 1.1062 | 0
2015-03-05 20:00 | 0 | 0 | 0 | 0 | -6.2198 | 132.7014 | 104.9273 | -14.9273 | 130.8796 | 132.5675 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5515 | -1.5515 | 1.1062 | 0
2015-03-05 21:00 | 0 | 0 | 0 | 0 | -6.2037 | 147.7037 | 107.1451 | -17.1451 | 146.2292 | 146.6475 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5541 | -1.5541 | 1.1062 | 0
2015-03-05 22:00 | 0 | 0 | 0 | 0 | -6.1876 | 162.7059 | 108.6071 | -18.6071 | 161.8295 | 159.9455 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5567 | -1.5567 | 1.1062 | 0
2015-03-05 23:00 | 0 | 0 | 0 | 0 | -6.1715 | 177.7081 | 109.194 | -19.194 | 177.5872 | 168.9746 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5592 | -1.5592 | 1.1062 | 0
2015-03-06 | 0 | 0 | 0 | 0 | -6.1554 | -167.2896 | 108.8557 | -18.8557 | -166.6346 | 163.5257 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5618 | -1.5618 | 1.1062 | 0
2015-03-06 01:00 | 0 | 0 | 0 | 0 | -6.1393 | -152.2874 | 107.6195 | -17.6195 | -150.9791 | 150.8222 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5644 | -1.5644 | 1.1063 | 0
2015-03-06 02:00 | 0 | 0 | 0 | 0 | -6.1232 | -137.2851 | 105.5851 | -15.5851 | -135.5548 | 136.876 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.567 | -1.567 | 1.1063 | 0
2015-03-06 03:00 | 0 | 0 | 0 | 0 | -6.1071 | -122.2829 | 102.9095 | -12.9095 | -120.4104 | 122.6155 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5695 | -1.5695 | 1.1063 | 0
2015-03-06 04:00 | 0.51333 | 0.51333 | 0 | 0 | -6.091 | -107.2806 | 99.787 | -9.787 | -105.5294 | 108.2692 | 0 | 0.385 | 0.8 | 1 | 0.10267 | 0.48767 | -1.5721 | -1.5569 | 1.1062 | 0.00044237
2015-03-06 05:00 | 1.0267 | 1.0267 | 0 | 0 | -6.0748 | -92.2783 | 96.4316 | -6.4316 | -90.8445 | 93.9389 | 0 | 0.77 | 0.8 | 1 | 0.20533 | 0.97533 | -1.5747 | -1.5442 | 1.1062 | 0.00088469
2015-03-06 06:00 | 1.54 | 1.54 | 0 | 0 | -6.0587 | -77.2761 | 93.0631 | -3.0631 | -76.2596 | 79.7065 | 0 | 1.155 | 0.8 | 1 | 0.308 | 1.463 | -1.5773 | -1.5315 | 1.1061 | 0.001327
2015-03-06 07:00 | 12.4533 | 11.7667 | 0.68667 | 0 | -6.0426 | -62.2738 | 89.8979 | 0.10212 | -61.6743 | 65.6817 | 0 | 8.825 | 0.8 | 1 | 2.4907 | 11.3157 | -1.5798 | -1.2262 | 1.1049 | 0.010252
2015-03-06 08:00 | 23.3667 | 21.9933 | 1.3733 | 0 | -6.0265 | -47.2715 | 87.1403 | 2.8597 | -47.0063 | 52.0649 | 0 | 16.495 | 0.8 | 1 | 4.6733 | 21.1683 | -1.5824 | -0.92089 | 1.1037 | 0.019158
2015-03-06 09:00 | 34.28 | 32.22 | 2.06 | 23.5087 | -6.0104 | -32.2693 | 84.9729 | 5.0271 | -32.2093 | 39.3087 | 18.1897 | 24.165 | 0.8 | 1 | 6.856 | 49.2107 | -1.585 | -0.047144 | 1.1002 | 0.044396
2015-03-06 10:00 | 36.1667 | 32.2633 | 3.9033 | 34.7152 | -5.9942 | -17.267 | 83.5441 | 6.4559 | -17.2826 | 28.6098 | 30.4765 | 24.1975 | 0.8 | 1 | 7.2333 | 61.9073 | -1.5876 | 0.34705 | 1.0986 | 0.05577
2015-03-06 11:00 | 38.0533 | 32.3067 | 5.7467 | 46.8538 | -5.9781 | -2.2647 | 82.9549 | 7.0451 | -2.2695 | 23.0537 | 43.112 | 24.23 | 0.8 | 1 | 7.6107 | 74.9526 | -1.5901 | 0.75214 | 1.097 | 0.067422
2015-03-06 12:00 | 39.94 | 32.35 | 7.59 | 64.5487 | -5.962 | 12.7376 | 83.2472 | 6.7528 | 12.7575 | 26.1583 | 57.9376 | 24.2625 | 0.8 | 1 | 7.988 | 90.1881 | -1.5927 | 1.2257 | 1.0951 | 0.080987
2015-03-06 13:00 | 29.8433 | 24.1 | 5.7433 | 58.8422 | -5.9458 | 27.7399 | 84.3987 | 5.6013 | 27.7216 | 35.7314 | 47.766 | 18.075 | 0.8 | 1 | 5.9687 | 71.8096 | -1.5953 | 0.64877 | 1.0974 | 0.064619
2015-03-06 14:00 | 19.7467 | 15.85 | 3.8967 | 60.799 | -5.9297 | 42.7422 | 86.3253 | 3.6747 | 42.5676 | 48.0452 | 40.6468 | 11.8875 | 0.8 | 1 | 3.9493 | 56.4837 | -1.5979 | 0.16726 | 1.0993 | 0.050917
2015-03-06 15:00 | 9.65 | 7.6 | 2.05 | 0 | -5.9135 | 57.7445 | 88.8916 | 1.1084 | 57.2812 | 61.4657 | 0 | 5.7 | 0.8 | 1 | 1.93 | 7.63 | -1.6004 | -1.362 | 1.1054 | 0.0069163
2015-03-06 16:00 | 6.4333 | 5.0667 | 1.3667 | 0 | -5.8974 | 72.7468 | 91.9236 | -1.9236 | 71.8943 | 75.3922 | 0 | 3.8 | 0.8 | 1 | 1.2867 | 5.0867 | -1.603 | -1.444 | 1.1058 | 0.0046123
2015-03-06 17:00 | 3.2167 | 2.5333 | 0.68333 | 0 | -5.8813 | 87.7491 | 95.2221 | -5.2221 | 86.4784 | 89.5722 | 0 | 1.9 | 0.8 | 1 | 0.64333 | 2.5433 | -1.6056 | -1.5261 | 1.1061 | 0.0023068
2015-03-06 18:00 | 0 | 0 | 0 | 0 | -5.8651 | 102.7514 | 98.5731 | -8.5731 | 101.1292 | 103.8764 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6082 | -1.6082 | 1.1064 | 0
2015-03-06 19:00 | 0 | 0 | 0 | 0 | -5.849 | 117.7537 | 101.7564 | -11.7564 | 115.9451 | 118.2177 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6107 | -1.6107 | 1.1064 | 0
2015-03-06 20:00 | 0 | 0 | 0 | 0 | -5.8328 | 132.756 | 104.5553 | -14.5553 | 131.0034 | 132.5026 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6133 | -1.6133 | 1.1065 | 0
2015-03-06 21:00 | 0 | 0 | 0 | 0 | -5.8167 | 147.7584 | 106.768 | -16.768 | 146.3366 | 146.5535 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6159 | -1.6159 | 1.1065 | 0
2015-03-06 22:00 | 0 | 0 | 0 | 0 | -5.8005 | 162.7607 | 108.2248 | -18.2248 | 161.9156 | 159.7714 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6185 | -1.6185 | 1.1065 | 0
2015-03-06 23:00 | 0 | 0 | 0 | 0 | -5.7843 | 177.763 | 108.8073 | -18.8073 | 177.6488 | 168.6054 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.621 | -1.621 | 1.1065 | 0
2015-03-07 | 0 | 0 | 0 | 0 | -5.7682 | -167.2347 | 108.4662 | -18.4662 | -166.5985 | 163.2237 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6236 | -1.6236 | 1.1065 | 0
2015-03-07 01:00 | 0 | 0 | 0 | 0 | -5.752 | -152.2323 | 107.2286 | -17.2286 | -150.9667 | 150.612 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6262 | -1.6262 | 1.1065 | 0
2015-03-07 02:00 | 0 | 0 | 0 | 0 | -5.7359 | -137.23 | 105.194 | -15.194 | -135.5625 | 136.7009 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6288 | -1.6288 | 1.1065 | 0
2015-03-07 03:00 | 0 | 0 | 0 | 0 | -5.7197 | -122.2276 | 102.5189 | -12.5189 | -120.4328 | 122.4536 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6313 | -1.6313 | 1.1065 | 0
2015-03-07 04:00 | 1.0333 | 0.71 | 0.32333 | 0 | -5.7035 | -107.2253 | 99.3969 | -9.3969 | -105.5608 | 108.1098 | 0 | 0.5325 | 0.8 | 1 | 0.20667 | 0.73917 | -1.6339 | -1.6108 | 1.1064 | 0.00067063
2015-03-07 05:00 | 2.0667 | 1.42 | 0.64667 | 0 | -5.6874 | -92.223 | 96.0417 | -6.0417 | -90.8789 | 93.7749 | 0 | 1.065 | 0.8 | 1 | 0.41333 | 1.4783 | -1.6365 | -1.5903 | 1.1064 | 0.0013412
2015-03-07 06:00 | 3.1 | 2.13 | 0.97 | 0 | -5.6712 | -77.2206 | 92.6729 | -2.6729 | -76.2912 | 79.5313 | 0 | 1.5975 | 0.8 | 1 | 0.62 | 2.2175 | -1.6391 | -1.5698 | 1.1063 | 0.0020116
2015-03-07 07:00 | 14.17 | 13.5233 | 0.64667 | 0 | -5.655 | -62.2182 | 89.507 | 0.49296 | -61.6975 | 65.4874 | 0 | 10.1425 | 0.8 | 1 | 2.834 | 12.9765 | -1.6416 | -1.2361 | 1.1049 | 0.011757
2015-03-07 08:00 | 25.24 | 24.9167 | 0.32333 | 5.7012 | -5.6388 | -47.2159 | 86.7488 | 3.2512 | -47.016 | 51.8402 | 3.5225 | 18.6875 | 0.8 | 1 | 5.048 | 27.258 | -1.6442 | -0.79239 | 1.1032 | 0.024658
2015-03-07 09:00 | 36.31 | 36.31 | 0 | 0 | -5.6226 | -32.2135 | 84.5813 | 5.4187 | -32.2011 | 39.0353 | 0 | 27.2325 | 0.8 | 1 | 7.262 | 34.4945 | -1.6468 | -0.56883 | 1.1023 | 0.031178
2015-03-07 10:00 | 39.97 | 39.97 | 0 | 0 | -5.6065 | -17.2112 | 83.1535 | 6.8465 | -17.2531 | 28.2652 | 0 | 29.9775 | 0.8 | 1 | 7.994 | 37.9715 | -1.6494 | -0.46275 | 1.1019 | 0.034308
2015-03-07 11:00 | 43.63 | 43.63 | 0 | 0 | -5.5903 | -2.2088 | 82.5666 | 7.4334 | -2.2169 | 22.6624 | 0 | 32.7225 | 0.8 | 1 | 8.726 | 41.4485 | -1.6519 | -0.35667 | 1.1014 | 0.037435
2015-03-07 12:00 | 47.29 | 47.29 | 0 | 0 | -5.5741 | 12.7936 | 82.8626 | 7.1374 | 12.8332 | 25.8454 | 0 | 35.4675 | 0.8 | 1 | 9.458 | 44.9255 | -1.6545 | -0.25058 | 1.101 | 0.04056
2015-03-07 13:00 | 35.02 | 35.02 | 0 | 0 | -5.5579 | 27.796 | 84.0188 | 5.9812 | 27.8185 | 35.5242 | 0 | 26.265 | 0.8 | 1 | 7.004 | 33.269 | -1.6571 | -0.61743 | 1.1025 | 0.030076
2015-03-07 14:00 | 22.75 | 22.75 | 0 | 0 | -5.5417 | 42.7984 | 85.9505 | 4.0495 | 42.6827 | 47.9058 | 0 | 17.0625 | 0.8 | 1 | 4.55 | 21.6125 | -1.6597 | -0.98427 | 1.1039 | 0.019564
2015-03-07 15:00 | 10.48 | 10.48 | 0 | 0 | -5.5255 | 57.8007 | 88.5214 | 1.4786 | 57.4102 | 61.3665 | 0 | 7.86 | 0.8 | 1 | 2.096 | 9.956 | -1.6622 | -1.3511 | 1.1054 | 0.0090244
2015-03-07 16:00 | 6.9867 | 6.9867 | 0 | 0 | -5.5093 | 72.8031 | 91.5567 | -1.5567 | 72.0327 | 75.3174 | 0 | 5.24 | 0.8 | 1 | 1.3973 | 6.6373 | -1.6648 | -1.4574 | 1.1058 | 0.0060186
2015-03-07 17:00 | 3.4933 | 3.4933 | 0 | 0 | -5.4931 | 87.8055 | 94.8567 | -4.8567 | 86.6214 | 89.5117 | 0 | 2.62 | 0.8 | 1 | 0.69867 | 3.3187 | -1.6674 | -1.5637 | 1.1063 | 0.0030105
2015-03-07 18:00 | 0 | 0 | 0 | 0 | -5.4769 | 102.8079 | 98.2071 | -8.2071 | 101.2718 | 103.8227 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.67 | -1.67 | 1.1067 | 0
2015-03-07 19:00 | 0 | 0 | 0 | 0 | -5.4607 | 117.8103 | 101.3878 | -11.3878 | 116.0821 | 118.1632 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6725 | -1.6725 | 1.1067 | 0
2015-03-07 20:00 | 0 | 0 | 0 | 0 | -5.4445 | 132.8127 | 104.1824 | -14.1824 | 131.1293 | 132.437 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6751 | -1.6751 | 1.1067 | 0
2015-03-07 21:00 | 0 | 0 | 0 | 0 | -5.4283 | 147.8151 | 106.3898 | -16.3898 | 146.4459 | 146.4571 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6777 | -1.6777 | 1.1067 | 0
2015-03-07 22:00 | 0 | 0 | 0 | 0 | -5.4121 | 162.8175 | 107.8413 | -17.8413 | 162.0036 | 159.5925 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6803 | -1.6803 | 1.1067 | 0
2015-03-07 23:00 | 0 | 0 | 0 | 0 | -5.3959 | 177.8199 | 108.4194 | -18.4194 | 177.7124 | 168.234 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6828 | -1.6828 | 1.1067 | 0
2015-03-08 | 0 | 0 | 0 | 0 | -5.3797 | -167.1776 | 108.0753 | -18.0753 | -166.5603 | 162.9158 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6854 | -1.6854 | 1.1067 | 0
2015-03-08 01:00 | 0 | 0 | 0 | 0 | -5.3635 | -152.1752 | 106.8362 | -16.8362 | -150.9523 | 150.3959 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.688 | -1.688 | 1.1068 | 0
2015-03-08 02:00 | 0 | 0 | 0 | 0 | -5.3473 | -137.1728 | 104.8013 | -14.8013 | -135.5681 | 136.5211 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6906 | -1.6906 | 1.1068 | 0
2015-03-08 03:00 | 0 | 0 | 0 | 0 | -5.3311 | -122.1704 | 102.1266 | -12.1266 | -120.4533 | 122.2879 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.6931 | -1.6931 | 1.1068 | 0
2015-03-08 04:00 | 0.91 | 0.74 | 0.17 | 0 | -5.3148 | -107.1679 | 99.0051 | -9.0051 | -105.5903 | 107.9473 | 0 | 0.555 | 0.8 | 1 | 0.182 | 0.737 | -1.6957 | -1.6727 | 1.1067 | 0.00066882
2015-03-08 05:00 | 1.82 | 1.48 | 0.34 | 0 | -5.2986 | -92.1655 | 95.6501 | -5.6501 | -90.9114 | 93.6083 | 0 | 1.11 | 0.8 | 1 | 0.364 | 1.474 | -1.6983 | -1.6522 | 1.1066 | 0.0013375
2015-03-08 06:00 | 2.73 | 2.22 | 0.51 | 0 | -5.2824 | -77.1631 | 92.281 | -2.281 | -76.3209 | 79.3541 | 0 | 1.665 | 0.8 | 1 | 0.546 | 2.211 | -1.7009 | -1.6318 | 1.1065 | 0.0020062
2015-03-08 07:00 | 23.61 | 12.4533 | 11.1567 | 0 | -5.2662 | -62.1606 | 89.1146 | 0.88541 | -61.7188 | 65.2917 | 0 | 9.34 | 0.8 | 1 | 4.722 | 14.062 | -1.7034 | -1.264 | 1.1051 | 0.012742
2015-03-08 08:00 | 44.49 | 22.6867 | 21.8033 | 343.0354 | -5.25 | -47.1582 | 86.3558 | 3.6442 | -47.0238 | 51.6144 | 213.0081 | 17.015 | 0.8 | 1 | 8.898 | 238.9211 | -1.706 | 5.7603 | 1.077 | 0.21099
2015-03-08 09:00 | 65.37 | 32.92 | 32.45 | 320.4632 | -5.2337 | -32.1557 | 84.1883 | 5.8117 | -32.1909 | 38.7613 | 249.8847 | 24.69 | 0.8 | 1 | 13.074 | 287.6487 | -1.7086 | 7.2804 | 1.0709 | 0.25259
2015-03-08 10:00 | 65.9333 | 35.1467 | 30.7867 | 244.3389 | -5.2175 | -17.1533 | 82.7615 | 7.2385 | -17.2215 | 27.9195 | 215.8995 | 26.36 | 0.8 | 1 | 13.1867 | 255.4461 | -1.7112 | 6.2715 | 1.0749 | 0.22516
2015-03-08 11:00 | 66.4967 | 37.3733 | 29.1233 | 213.966 | -5.2013 | -2.1508 | 82.1771 | 7.8229 | -2.1621 | 22.2696 | 198.0065 | 28.03 | 0.8 | 1 | 13.2993 | 239.3358 | -1.7137 | 5.7655 | 1.0769 | 0.21135
2015-03-08 12:00 | 67.06 | 39.6 | 27.46 | 209.739 | -5.185 | 12.8516 | 82.477 | 7.523 | 12.9112 | 25.5344 | 189.2531 | 29.7 | 0.8 | 1 | 13.412 | 232.3651 | -1.7163 | 5.5451 | 1.0778 | 0.20537
2015-03-08 13:00 | 50.5133 | 30.1 | 20.4133 | 184.2203 | -5.1688 | 27.8541 | 83.638 | 6.362 | 27.9178 | 35.3206 | 150.3107 | 22.575 | 0.8 | 1 | 10.1027 | 182.9884 | -1.7189 | 3.9995 | 1.084 | 0.16266
2015-03-08 14:00 | 33.9667 | 20.6 | 13.3667 | 173.2431 | -5.1526 | 42.8566 | 85.5749 | 4.4251 | 42.8001 | 47.7697 | 116.4387 | 15.45 | 0.8 | 1 | 6.7933 | 138.682 | -1.7215 | 2.6124 | 1.0896 | 0.1239
2015-03-08 15:00 | 17.42 | 11.1 | 6.32 | 0 | -5.1363 | 57.859 | 88.1504 | 1.8496 | 57.5416 | 61.2701 | 0 | 8.325 | 0.8 | 1 | 3.484 | 11.809 | -1.724 | -1.355 | 1.1054 | 0.010704
2015-03-08 16:00 | 11.6133 | 7.4 | 4.2133 | 0 | -5.1201 | 72.8615 | 91.1892 | -1.1892 | 72.1734 | 75.2448 | 0 | 5.55 | 0.8 | 1 | 2.3227 | 7.8727 | -1.7266 | -1.4806 | 1.1059 | 0.0071394
2015-03-08 17:00 | 5.8067 | 3.7 | 2.1067 | 0 | -5.1038 | 87.864 | 94.4907 | -4.4907 | 86.7666 | 89.4529 | 0 | 2.775 | 0.8 | 1 | 1.1613 | 3.9363 | -1.7292 | -1.6062 | 1.1064 | 0.0035713
2015-03-08 18:00 | 0 | 0 | 0 | 0 | -5.0876 | 102.8664 | 97.8404 | -7.8404 | 101.4165 | 103.77 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7318 | -1.7318 | 1.1069 | 0
2015-03-08 19:00 | 0 | 0 | 0 | 0 | -5.0713 | 117.8689 | 101.0184 | -11.0184 | 116.2211 | 118.1089 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7343 | -1.7343 | 1.1069 | 0
2015-03-08 20:00 | 0 | 0 | 0 | 0 | -5.0551 | 132.8714 | 103.8086 | -13.8086 | 131.257 | 132.3707 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7369 | -1.7369 | 1.1069 | 0
2015-03-08 21:00 | 0 | 0 | 0 | 0 | -5.0388 | 147.8739 | 106.0107 | -16.0107 | 146.557 | 146.3584 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7395 | -1.7395 | 1.107 | 0
2015-03-08 22:00 | 0 | 0 | 0 | 0 | -5.0226 | 162.8764 | 107.4568 | -17.4568 | 162.0935 | 159.4089 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7421 | -1.7421 | 1.107 | 0
2015-03-08 23:00 | 0 | 0 | 0 | 0 | -5.0063 | 177.8789 | 108.0304 | -18.0304 | 177.7778 | 167.8605 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7446 | -1.7446 | 1.107 | 0
2015-03-09 | 0 | 0 | 0 | 0 | -4.9901 | -167.1186 | 107.6831 | -17.6831 | -166.5202 | 162.6024 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7472 | -1.7472 | 1.107 | 0
2015-03-09 01:00 | 0 | 0 | 0 | 0 | -4.9738 | -152.1161 | 106.4424 | -16.4424 | -150.936 | 150.1743 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7498 | -1.7498 | 1.107 | 0
2015-03-09 02:00 | 0 | 0 | 0 | 0 | -4.9576 | -137.1136 | 104.4072 | -14.4072 | -135.5718 | 136.3367 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7524 | -1.7524 | 1.107 | 0
2015-03-09 03:00 | 0 | 0 | 0 | 0 | -4.9413 | -122.1111 | 101.7328 | -11.7328 | -120.4718 | 122.1185 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7549 | -1.7549 | 1.107 | 0
2015-03-09 04:00 | 1.0933 | 1.0667 | 0.026667 | 0 | -4.925 | -107.1086 | 98.6118 | -8.6118 | -105.6179 | 107.7818 | 0 | 0.8 | 0.8 | 1 | 0.21867 | 1.0187 | -1.7575 | -1.7257 | 1.1069 | 0.0009246
2015-03-09 05:00 | 2.1867 | 2.1333 | 0.053333 | 0 | -4.9088 | -92.1061 | 95.2569 | -5.2569 | -90.9422 | 93.4393 | 0 | 1.6 | 0.8 | 1 | 0.43733 | 2.0373 | -1.7601 | -1.6964 | 1.1068 | 0.001849
2015-03-09 06:00 | 3.28 | 3.2 | 0.08 | 0 | -4.8925 | -77.1036 | 91.8876 | -1.8876 | -76.3489 | 79.175 | 0 | 2.4 | 0.8 | 1 | 0.656 | 3.056 | -1.7627 | -1.6672 | 1.1067 | 0.0027732
2015-03-09 07:00 | 15.9767 | 15.3933 | 0.58333 | 0 | -4.8762 | -62.101 | 88.7206 | 1.2794 | -61.7384 | 65.0945 | 0 | 11.545 | 0.8 | 1 | 3.1953 | 14.7403 | -1.7652 | -1.3046 | 1.1052 | 0.013359
2015-03-09 08:00 | 28.6733 | 27.5867 | 1.0867 | 15.4293 | -4.86 | -47.0985 | 85.9614 | 4.0386 | -47.0298 | 51.3877 | 9.6286 | 20.69 | 0.8 | 1 | 5.7347 | 36.0532 | -1.7678 | -0.64115 | 1.1026 | 0.032596
2015-03-09 09:00 | 41.37 | 39.78 | 1.59 | 14.7079 | -4.8437 | -32.096 | 83.7939 | 6.2061 | -32.1788 | 38.4867 | 11.5127 | 29.835 | 0.8 | 1 | 8.274 | 49.6217 | -1.7704 | -0.21971 | 1.1009 | 0.044795
2015-03-09 10:00 | 42.6633 | 39.19 | 3.4733 | 26.1537 | -4.8274 | -17.0934 | 82.3683 | 7.6317 | -17.1879 | 27.5728 | 23.1832 | 29.3925 | 0.8 | 1 | 8.5327 | 61.1084 | -1.773 | 0.13668 | 1.0995 | 0.055092
2015-03-09 11:00 | 43.9567 | 38.6 | 5.3567 | 37.4952 | -4.8111 | -2.0909 | 81.7865 | 8.2135 | -2.1051 | 21.8756 | 34.7954 | 28.95 | 0.8 | 1 | 8.7913 | 72.5367 | -1.7755 | 0.49123 | 1.098 | 0.065311
2015-03-09 12:00 | 45.25 | 38.01 | 7.24 | 52.6119 | -4.7949 | 12.9116 | 82.0903 | 7.9097 | 12.9914 | 25.2257 | 47.5946 | 28.5075 | 0.8 | 1 | 9.05 | 85.1521 | -1.7781 | 0.88289 | 1.0965 | 0.076561
2015-03-09 13:00 | 34.04 | 28.6733 | 5.3667 | 45.7022 | -4.7786 | 27.9142 | 83.2564 | 6.7436 | 28.0194 | 35.1208 | 37.3817 | 21.505 | 0.8 | 1 | 6.808 | 65.6947 | -1.7807 | 0.27227 | 1.0989 | 0.059198
2015-03-09 14:00 | 22.83 | 19.3367 | 3.4933 | 41.7348 | -4.7623 | 42.9167 | 85.1985 | 4.8015 | 42.9198 | 47.6371 | 28.1219 | 14.5025 | 0.8 | 1 | 4.566 | 47.1904 | -1.7833 | -0.30856 | 1.1012 | 0.042613
2015-03-09 15:00 | 11.62 | 10 | 1.62 | 0 | -4.746 | 57.9193 | 87.7788 | 2.2212 | 57.6752 | 61.1767 | 0 | 7.5 | 0.8 | 1 | 2.324 | 9.824 | -1.7858 | -1.4788 | 1.1059 | 0.0089089
2015-03-09 16:00 | 7.7467 | 6.6667 | 1.08 | 0 | -4.7297 | 72.9218 | 90.8209 | -0.82095 | 72.3162 | 75.1745 | 0 | 5 | 0.8 | 1 | 1.5493 | 6.5493 | -1.7884 | -1.5837 | 1.1063 | 0.0059415
2015-03-09 17:00 | 3.8733 | 3.3333 | 0.54 | 0 | -4.7134 | 87.9244 | 94.124 | -4.124 | 86.9139 | 89.3957 | 0 | 2.5 | 0.8 | 1 | 0.77467 | 3.2747 | -1.791 | -1.6887 | 1.1068 | 0.0029719
2015-03-09 18:00 | 0 | 0 | 0 | 0 | -4.6972 | 102.9269 | 97.4731 | -7.4731 | 101.5632 | 103.7183 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7936 | -1.7936 | 1.1072 | 0
2015-03-09 19:00 | 0 | 0 | 0 | 0 | -4.6809 | 117.9295 | 100.6483 | -10.6483 | 116.3619 | 118.0549 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7961 | -1.7961 | 1.1072 | 0
2015-03-09 20:00 | 0 | 0 | 0 | 0 | -4.6646 | 132.932 | 103.434 | -13.434 | 131.3866 | 132.3035 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7987 | -1.7987 | 1.1072 | 0
2015-03-09 21:00 | 0 | 0 | 0 | 0 | -4.6483 | 147.9346 | 105.6307 | -15.6307 | 146.67 | 146.2573 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8013 | -1.8013 | 1.1072 | 0
2015-03-09 22:00 | 0 | 0 | 0 | 0 | -4.632 | 162.9372 | 107.0714 | -17.0714 | 162.1852 | 159.2206 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8039 | -1.8039 | 1.1072 | 0
2015-03-09 23:00 | 0 | 0 | 0 | 0 | -4.6157 | 177.9398 | 107.6403 | -17.6403 | 177.8451 | 167.485 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8064 | -1.8064 | 1.1072 | 0
2015-03-10 | 0 | 0 | 0 | 0 | -4.5994 | -167.0577 | 107.2897 | -17.2897 | -166.4783 | 162.2837 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.809 | -1.809 | 1.1072 | 0
2015-03-10 01:00 | 0 | 0 | 0 | 0 | -4.5831 | -152.0551 | 106.0473 | -16.0473 | -150.9178 | 149.9472 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8116 | -1.8116 | 1.1072 | 0
2015-03-10 02:00 | 0 | 0 | 0 | 0 | -4.5668 | -137.0525 | 104.0117 | -14.0117 | -135.5736 | 136.1479 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8142 | -1.8142 | 1.1073 | 0
2015-03-10 03:00 | 0 | 0 | 0 | 0 | -4.5505 | -122.0499 | 101.3376 | -11.3376 | -120.4886 | 121.9455 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8167 | -1.8167 | 1.1073 | 0
2015-03-10 04:00 | 1.87 | 1.34 | 0.53 | 0 | -4.5342 | -107.0473 | 98.2171 | -8.2171 | -105.6438 | 107.6134 | 0 | 1.005 | 0.8 | 1 | 0.374 | 1.379 | -1.8193 | -1.7762 | 1.1071 | 0.0012519
2015-03-10 05:00 | 3.74 | 2.68 | 1.06 | 0 | -4.5179 | -92.0447 | 94.8624 | -4.8624 | -90.9712 | 93.268 | 0 | 2.01 | 0.8 | 1 | 0.748 | 2.758 | -1.8219 | -1.7357 | 1.1069 | 0.0025034
2015-03-10 06:00 | 5.61 | 4.02 | 1.59 | 0 | -4.5016 | -77.0421 | 91.4928 | -1.4928 | -76.3751 | 78.9941 | 0 | 3.015 | 0.8 | 1 | 1.122 | 4.137 | -1.8245 | -1.6952 | 1.1068 | 0.0037546
2015-03-10 07:00 | 19.5233 | 15.0767 | 4.4467 | 0 | -4.4853 | -62.0395 | 88.3253 | 1.6747 | -61.7563 | 64.8961 | 0 | 11.3075 | 0.8 | 1 | 3.9047 | 15.2122 | -1.827 | -1.3517 | 1.1054 | 0.013789
2015-03-10 08:00 | 33.4367 | 26.1333 | 7.3033 | 94.4591 | -4.469 | -47.0369 | 85.5656 | 4.4344 | -47.0341 | 51.1603 | 59.2394 | 19.6 | 0.8 | 1 | 6.6873 | 85.5267 | -1.8296 | 0.8431 | 1.0966 | 0.076909
2015-03-10 09:00 | 47.35 | 37.19 | 10.16 | 88.3738 | -4.4526 | -32.0343 | 83.3983 | 6.6017 | -32.1648 | 38.2117 | 69.438 | 27.8925 | 0.8 | 1 | 9.47 | 106.8005 | -1.8322 | 1.5053 | 1.094 | 0.095807
2015-03-10 10:00 | 47.5967 | 39.48 | 8.1167 | 58.1329 | -4.4363 | -17.0317 | 81.974 | 8.026 | -17.1523 | 27.2254 | 51.6926 | 29.61 | 0.8 | 1 | 9.5193 | 90.8219 | -1.8348 | 1.0034 | 1.096 | 0.081622
2015-03-10 11:00 | 47.8433 | 41.77 | 6.0733 | 40.5906 | -4.42 | -2.0291 | 81.3949 | 8.6051 | -2.0461 | 21.4804 | 37.7713 | 31.3275 | 0.8 | 1 | 9.5687 | 78.6675 | -1.8373 | 0.62102 | 1.0975 | 0.070798
2015-03-10 12:00 | 48.09 | 44.06 | 4.03 | 27.9266 | -4.4037 | 12.9735 | 81.7028 | 8.2972 | 13.0738 | 24.9194 | 25.3266 | 33.045 | 0.8 | 1 | 9.618 | 67.9896 | -1.8399 | 0.28476 | 1.0989 | 0.061263
2015-03-10 13:00 | 39.3267 | 34.3567 | 4.97 | 40.0638 | -4.3874 | 27.9761 | 82.874 | 7.126 | 28.1232 | 34.9247 | 32.8485 | 25.7675 | 0.8 | 1 | 7.8653 | 66.4813 | -1.8425 | 0.23505 | 1.0991 | 0.059915
2015-03-10 14:00 | 30.5633 | 24.6533 | 5.91 | 65.4787 | -4.3711 | 42.9787 | 84.8215 | 5.1785 | 43.0416 | 47.508 | 44.23 | 18.49 | 0.8 | 1 | 6.1127 | 68.8327 | -1.8451 | 0.30596 | 1.0988 | 0.062018
2015-03-10 15:00 | 21.8 | 14.95 | 6.85 | 0 | -4.3547 | 57.9814 | 87.4066 | 2.5934 | 57.8109 | 61.086 | 0 | 11.2125 | 0.8 | 1 | 4.36 | 15.5725 | -1.8476 | -1.361 | 1.1054 | 0.014116
2015-03-10 16:00 | 14.5333 | 9.9667 | 4.5667 | 0 | -4.3384 | 72.984 | 90.4522 | -0.45221 | 72.4611 | 75.1064 | 0 | 7.475 | 0.8 | 1 | 2.9067 | 10.3817 | -1.8502 | -1.5258 | 1.1061 | 0.0094162
2015-03-10 17:00 | 7.2667 | 4.9833 | 2.2833 | 0 | -4.3221 | 87.9866 | 93.7568 | -3.7568 | 87.0631 | 89.3402 | 0 | 3.7375 | 0.8 | 1 | 1.4533 | 5.1908 | -1.8528 | -1.6906 | 1.1068 | 0.0047109
2015-03-10 18:00 | 0 | 0 | 0 | 0 | -4.3058 | 102.9892 | 97.1052 | -7.1052 | 101.7117 | 103.6675 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8554 | -1.8554 | 1.1074 | 0
2015-03-10 19:00 | 0 | 0 | 0 | 0 | -4.2894 | 117.9919 | 100.2776 | -10.2776 | 116.5045 | 118.001 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8579 | -1.8579 | 1.1074 | 0
2015-03-10 20:00 | 0 | 0 | 0 | 0 | -4.2731 | 132.9945 | 103.0588 | -13.0588 | 131.5178 | 132.2354 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8605 | -1.8605 | 1.1074 | 0
2015-03-10 21:00 | 0 | 0 | 0 | 0 | -4.2568 | 147.9972 | 105.25 | -15.25 | 146.7846 | 146.1537 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8631 | -1.8631 | 1.1075 | 0
2015-03-10 22:00 | 0 | 0 | 0 | 0 | -4.2405 | 162.9998 | 106.6851 | -16.6851 | 162.2785 | 159.0278 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8657 | -1.8657 | 1.1075 | 0
2015-03-10 23:00 | 0 | 0 | 0 | 0 | -4.2241 | 178.0025 | 107.2493 | -17.2493 | 177.914 | 167.1078 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8682 | -1.8682 | 1.1075 | 0
2015-03-11 | 0 | 0 | 0 | 0 | -4.2078 | -166.9949 | 106.8954 | -16.8954 | -166.4346 | 161.96 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8708 | -1.8708 | 1.1075 | 0
2015-03-11 01:00 | 0 | 0 | 0 | 0 | -4.1915 | -151.9922 | 105.6512 | -15.6512 | -150.8978 | 149.7148 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8734 | -1.8734 | 1.1075 | 0
2015-03-11 02:00 | 0 | 0 | 0 | 0 | -4.1751 | -136.9896 | 103.615 | -13.615 | -135.5737 | 135.9549 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.876 | -1.876 | 1.1075 | 0
2015-03-11 03:00 | 0 | 0 | 0 | 0 | -4.1588 | -121.9869 | 100.9411 | -10.9411 | -120.5036 | 121.7691 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.8785 | -1.8785 | 1.1075 | 0
2015-03-11 04:00 | 1.3033 | 1.2433 | 0.06 | 0 | -4.1424 | -106.9843 | 97.821 | -7.821 | -105.668 | 107.4423 | 0 | 0.9325 | 0.8 | 1 | 0.26067 | 1.1932 | -1.8811 | -1.8438 | 1.1074 | 0.0010835
2015-03-11 05:00 | 2.6067 | 2.4867 | 0.12 | 0 | -4.1261 | -91.9816 | 94.4665 | -4.4665 | -90.9985 | 93.0946 | 0 | 1.865 | 0.8 | 1 | 0.52133 | 2.3863 | -1.8837 | -1.8091 | 1.1072 | 0.0021666
2015-03-11 06:00 | 3.91 | 3.73 | 0.18 | 0 | -4.1098 | -76.9789 | 91.0967 | -1.0967 | -76.3998 | 78.8116 | 0 | 2.7975 | 0.8 | 1 | 0.782 | 3.5795 | -1.8863 | -1.7744 | 1.1071 | 0.0032495
2015-03-11 07:00 | 28.91 | 16.43 | 12.48 | 0 | -4.0934 | -61.9763 | 87.9287 | 2.0713 | -61.7725 | 64.6966 | 0 | 12.3225 | 0.8 | 1 | 5.782 | 18.1045 | -1.8888 | -1.3231 | 1.1053 | 0.016409
2015-03-11 08:00 | 53.91 | 29.13 | 24.78 | 294.2193 | -4.0771 | -46.9736 | 85.1687 | 4.8313 | -47.0366 | 50.9323 | 185.4281 | 21.8475 | 0.8 | 1 | 10.782 | 218.0576 | -1.8914 | 4.9229 | 1.0803 | 0.19317
2015-03-11 09:00 | 78.91 | 41.83 | 37.08 | 304.3308 | -4.0607 | -31.9709 | 83.0016 | 6.9984 | -32.1491 | 37.9365 | 240.0234 | 31.3725 | 0.8 | 1 | 15.782 | 287.1779 | -1.894 | 7.0803 | 1.0717 | 0.25237
2015-03-11 10:00 | 87.2167 | 43.7633 | 43.4533 | 296.7086 | -4.0444 | -16.9682 | 81.5787 | 8.4213 | -17.1148 | 26.8773 | 264.6572 | 32.8225 | 0.8 | 1 | 17.4433 | 314.923 | -1.8966 | 7.9448 | 1.0682 | 0.27585
2015-03-11 11:00 | 95.5233 | 45.6967 | 49.8267 | 318.5976 | -4.028 | -1.9655 | 81.0024 | 8.9976 | -1.9851 | 21.0843 | 297.2682 | 34.2725 | 0.8 | 1 | 19.1047 | 350.6454 | -1.8991 | 9.0585 | 1.0638 | 0.30586
2015-03-11 12:00 | 103.83 | 47.63 | 56.2 | 372.1626 | -4.0117 | 13.0372 | 81.3146 | 8.6854 | 13.1582 | 24.6157 | 338.3413 | 35.7225 | 0.8 | 1 | 20.766 | 394.8298 | -1.9017 | 10.4367 | 1.0583 | 0.34262
2015-03-11 13:00 | 74.9367 | 37.47 | 37.4667 | 286.6987 | -3.9953 | 28.0398 | 82.4909 | 7.5091 | 28.2292 | 34.7325 | 235.6149 | 28.1025 | 0.8 | 1 | 14.9873 | 278.7048 | -1.9043 | 6.8052 | 1.0728 | 0.24517
2015-03-11 14:00 | 46.0433 | 27.31 | 18.7333 | 193.4877 | -3.979 | 43.0425 | 84.444 | 5.556 | 43.1656 | 47.3823 | 131.0111 | 20.4825 | 0.8 | 1 | 9.2087 | 160.7022 | -1.9069 | 3.1151 | 1.0875 | 0.14331
2015-03-11 15:00 | 17.15 | 17.15 | 0 | 0 | -3.9626 | 58.0452 | 87.0339 | 2.9661 | 57.9487 | 60.9982 | 0 | 12.8625 | 0.8 | 1 | 3.43 | 16.2925 | -1.9094 | -1.4003 | 1.1056 | 0.014771
2015-03-11 16:00 | 11.4333 | 11.4333 | 0 | 0 | -3.9462 | 73.0479 | 90.083 | -0.083022 | 72.608 | 75.0405 | 0 | 8.575 | 0.8 | 1 | 2.2867 | 10.8617 | -1.912 | -1.5726 | 1.1063 | 0.0098532
2015-03-11 17:00 | 5.7167 | 5.7167 | 0 | 0 | -3.9299 | 88.0506 | 93.3891 | -3.3891 | 87.2141 | 89.2861 | 0 | 4.2875 | 0.8 | 1 | 1.1433 | 5.4308 | -1.9146 | -1.7449 | 1.107 | 0.0049297
2015-03-11 18:00 | 0 | 0 | 0 | 0 | -3.9135 | 103.0533 | 96.7368 | -6.7368 | 101.8619 | 103.6176 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9172 | -1.9172 | 1.1077 | 0
2015-03-11 19:00 | 0 | 0 | 0 | 0 | -3.8972 | 118.056 | 99.9064 | -9.9064 | 116.6487 | 117.9471 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9197 | -1.9197 | 1.1077 | 0
2015-03-11 20:00 | 0 | 0 | 0 | 0 | -3.8808 | 133.0588 | 102.683 | -12.683 | 131.6507 | 132.1663 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9223 | -1.9223 | 1.1077 | 0
2015-03-11 21:00 | 0 | 0 | 0 | 0 | -3.8644 | 148.0615 | 104.8686 | -14.8686 | 146.9007 | 146.0476 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9249 | -1.9249 | 1.1077 | 0
2015-03-11 22:00 | 0 | 0 | 0 | 0 | -3.8481 | 163.0642 | 106.298 | -16.298 | 162.3734 | 158.8304 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9275 | -1.9275 | 1.1077 | 0
2015-03-11 23:00 | 0 | 0 | 0 | 0 | -3.8317 | 178.0669 | 106.8574 | -16.8574 | 177.9846 | 166.7288 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.93 | -1.93 | 1.1077 | 0
2015-03-12 | 0 | 0 | 0 | 0 | -3.8154 | -166.9304 | 106.5001 | -16.5001 | -166.3892 | 161.6318 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9326 | -1.9326 | 1.1077 | 0
2015-03-12 01:00 | 0 | 0 | 0 | 0 | -3.799 | -151.9276 | 105.254 | -15.254 | -150.8762 | 149.4775 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9352 | -1.9352 | 1.1077 | 0
2015-03-12 02:00 | 0 | 0 | 0 | 0 | -3.7826 | -136.9249 | 103.2173 | -13.2173 | -135.5721 | 135.7577 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9378 | -1.9378 | 1.1078 | 0
2015-03-12 03:00 | 0 | 0 | 0 | 0 | -3.7662 | -121.9222 | 100.5435 | -10.5435 | -120.5169 | 121.5894 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9403 | -1.9403 | 1.1078 | 0
2015-03-12 04:00 | 2.0167 | 2.0167 | 0 | 0 | -3.7499 | -106.9195 | 97.4238 | -7.4238 | -105.6905 | 107.2684 | 0 | 1.5125 | 0.8 | 1 | 0.40333 | 1.9158 | -1.9429 | -1.883 | 1.1075 | 0.0017399
2015-03-12 05:00 | 4.0333 | 4.0333 | 0 | 0 | -3.7335 | -91.9167 | 94.0694 | -4.0694 | -91.0243 | 92.919 | 0 | 3.025 | 0.8 | 1 | 0.80667 | 3.8317 | -1.9455 | -1.8258 | 1.1073 | 0.0034791
2015-03-12 06:00 | 6.05 | 6.05 | 0 | 0 | -3.7171 | -76.914 | 90.6995 | -0.69946 | -76.4228 | 78.6276 | 0 | 4.5375 | 0.8 | 1 | 1.21 | 5.7475 | -1.9481 | -1.7685 | 1.1071 | 0.0052176
2015-03-12 07:00 | 20.7867 | 20.7867 | 0 | 0 | -3.7008 | -61.9112 | 87.531 | 2.469 | -61.7872 | 64.4962 | 0 | 15.59 | 0.8 | 1 | 4.1573 | 19.7473 | -1.9506 | -1.3335 | 1.1053 | 0.017898
2015-03-12 08:00 | 35.5233 | 35.5233 | 0 | 0 | -3.6844 | -46.9085 | 84.7706 | 5.2294 | -47.0375 | 50.7039 | 0 | 26.6425 | 0.8 | 1 | 7.1047 | 33.7472 | -1.9532 | -0.89862 | 1.1036 | 0.030539
2015-03-12 09:00 | 50.26 | 50.26 | 0 | 0 | -3.668 | -31.9057 | 82.6039 | 7.3961 | -32.1316 | 37.6612 | 0 | 37.695 | 0.8 | 1 | 10.052 | 47.747 | -1.9558 | -0.4637 | 1.1019 | 0.04314
2015-03-12 10:00 | 53.9833 | 53.9833 | 0 | 0 | -3.6516 | -16.903 | 81.1825 | 8.8175 | -17.0755 | 26.5288 | 0 | 40.4875 | 0.8 | 1 | 10.7967 | 51.2842 | -1.9584 | -0.35574 | 1.1014 | 0.046318
2015-03-12 11:00 | 57.7067 | 57.7067 | 0 | 0 | -3.6352 | -1.9002 | 80.6091 | 9.3909 | -1.9222 | 20.6872 | 0 | 43.28 | 0.8 | 1 | 11.5413 | 54.8213 | -1.9609 | -0.24778 | 1.101 | 0.049493
2015-03-12 12:00 | 61.43 | 61.43 | 0 | 0 | -3.6189 | 13.1025 | 80.9257 | 9.0743 | 13.2446 | 24.3148 | 0 | 46.0725 | 0.8 | 1 | 12.286 | 58.3585 | -1.9635 | -0.13982 | 1.1006 | 0.052666
2015-03-12 13:00 | 46.33 | 45.8567 | 0.47333 | 3.447 | -3.6025 | 28.1053 | 82.1073 | 7.8927 | 28.3371 | 34.5443 | 2.8392 | 34.3925 | 0.8 | 1 | 9.266 | 46.4977 | -1.9661 | -0.51304 | 1.1021 | 0.042019
2015-03-12 14:00 | 31.23 | 30.2833 | 0.94667 | 9.1568 | -3.5861 | 43.108 | 84.0659 | 5.9341 | 43.2917 | 47.2602 | 6.2145 | 22.7125 | 0.8 | 1 | 6.246 | 35.173 | -1.9687 | -0.86951 | 1.1035 | 0.031826
2015-03-12 15:00 | 16.13 | 14.71 | 1.42 | 24.3793 | -3.5697 | 58.1108 | 86.6608 | 3.3392 | 58.0884 | 60.9131 | 11.8516 | 11.0325 | 0.8 | 1 | 3.226 | 26.1101 | -1.9712 | -1.1553 | 1.1046 | 0.02365
2015-03-12 16:00 | 10.7533 | 9.8067 | 0.94667 | 0 | -3.5533 | 73.1136 | 89.7135 | 0.28652 | 72.7567 | 74.9767 | 0 | 7.355 | 0.8 | 1 | 2.1507 | 9.5057 | -1.9738 | -1.6768 | 1.1067 | 0.0086264
2015-03-12 17:00 | 5.3767 | 4.9033 | 0.47333 | 0 | -3.5369 | 88.1163 | 93.0211 | -3.0211 | 87.367 | 89.2335 | 0 | 3.6775 | 0.8 | 1 | 1.0753 | 4.7528 | -1.9764 | -1.8279 | 1.1073 | 0.0043156
2015-03-12 18:00 | 0 | 0 | 0 | 0 | -3.5205 | 103.1191 | 96.3681 | -6.3681 | 102.0138 | 103.5684 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.979 | -1.979 | 1.1079 | 0
2015-03-12 19:00 | 0 | 0 | 0 | 0 | -3.5042 | 118.1219 | 99.5347 | -9.5347 | 116.7945 | 117.8933 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9815 | -1.9815 | 1.1079 | 0
2015-03-12 20:00 | 0 | 0 | 0 | 0 | -3.4878 | 133.1247 | 102.3067 | -12.3067 | 131.785 | 132.0961 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9841 | -1.9841 | 1.1079 | 0
2015-03-12 21:00 | 0 | 0 | 0 | 0 | -3.4714 | 148.1274 | 104.4866 | -14.4866 | 147.0183 | 145.9389 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9867 | -1.9867 | 1.1079 | 0
2015-03-12 22:00 | 0 | 0 | 0 | 0 | -3.455 | 163.1302 | 105.9103 | -15.9103 | 162.4698 | 158.6285 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9893 | -1.9893 | 1.108 | 0
2015-03-12 23:00 | 0 | 0 | 0 | 0 | -3.4386 | 178.133 | 106.4648 | -16.4648 | 178.0567 | 166.3483 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9918 | -1.9918 | 1.108 | 0
2015-03-13 | 0 | 0 | 0 | 0 | -3.4222 | -166.8642 | 106.1039 | -16.1039 | -166.3423 | 161.2992 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9944 | -1.9944 | 1.108 | 0
2015-03-13 01:00 | 0 | 0 | 0 | 0 | -3.4058 | -151.8614 | 104.8559 | -14.8559 | -150.8529 | 149.2352 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.997 | -1.997 | 1.108 | 0
2015-03-13 02:00 | 0 | 0 | 0 | 0 | -3.3894 | -136.8586 | 102.8185 | -12.8185 | -135.5688 | 135.5565 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.9996 | -1.9996 | 1.108 | 0
2015-03-13 03:00 | 0 | 0 | 0 | 0 | -3.373 | -121.8558 | 100.1449 | -10.1449 | -120.5287 | 121.4065 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.0021 | -2.0021 | 1.108 | 0
2015-03-13 04:00 | 2.0067 | 1.83 | 0.17667 | 0 | -3.3566 | -106.853 | 97.0255 | -7.0255 | -105.7115 | 107.0921 | 0 | 1.3725 | 0.8 | 1 | 0.40133 | 1.7738 | -2.0047 | -1.9493 | 1.1078 | 0.0016113
2015-03-13 05:00 | 4.0133 | 3.66 | 0.35333 | 0 | -3.3402 | -91.8502 | 93.6713 | -3.6713 | -91.0485 | 92.7416 | 0 | 2.745 | 0.8 | 1 | 0.80267 | 3.5477 | -2.0073 | -1.8964 | 1.1076 | 0.0032221
2015-03-13 06:00 | 6.02 | 5.49 | 0.53 | 0 | -3.3238 | -76.8474 | 90.3011 | -0.30115 | -76.4444 | 78.4422 | 0 | 4.1175 | 0.8 | 1 | 1.204 | 5.3215 | -2.0099 | -1.8436 | 1.1074 | 0.0048322
2015-03-13 07:00 | 21.2933 | 20.94 | 0.35333 | 0 | -3.3074 | -61.8446 | 87.1323 | 2.8677 | -61.8003 | 64.2949 | 0 | 15.705 | 0.8 | 1 | 4.2587 | 19.9637 | -2.0124 | -1.3886 | 1.1056 | 0.018098
2015-03-13 08:00 | 36.5667 | 36.39 | 0.17667 | 1.8013 | -3.291 | -46.8418 | 84.3717 | 5.6283 | -47.0369 | 50.4752 | 1.1464 | 27.2925 | 0.8 | 1 | 7.3133 | 35.7522 | -2.015 | -0.89776 | 1.1036 | 0.032354
2015-03-13 09:00 | 51.84 | 51.84 | 0 | 0 | -3.2746 | -31.839 | 82.2054 | 7.7946 | -32.1125 | 37.3861 | 0 | 38.88 | 0.8 | 1 | 10.368 | 49.248 | -2.0176 | -0.4786 | 1.1019 | 0.044499
2015-03-13 10:00 | 55.5967 | 55.5967 | 0 | 0 | -3.2582 | -16.8362 | 80.7855 | 9.2145 | -17.0345 | 26.1801 | 0 | 41.6975 | 0.8 | 1 | 11.1193 | 52.8168 | -2.0202 | -0.36965 | 1.1015 | 0.047705
2015-03-13 11:00 | 59.3533 | 59.3533 | 0 | 0 | -3.2418 | -1.8333 | 80.2152 | 9.7848 | -1.8574 | 20.2894 | 0 | 44.515 | 0.8 | 1 | 11.8707 | 56.3857 | -2.0227 | -0.26069 | 1.101 | 0.050908
2015-03-13 12:00 | 63.11 | 63.11 | 0 | 0 | -3.2254 | 13.1695 | 80.5362 | 9.4638 | 13.333 | 24.0168 | 0 | 47.3325 | 0.8 | 1 | 12.622 | 59.9545 | -2.0253 | -0.15174 | 1.1006 | 0.054109
2015-03-13 13:00 | 48.9033 | 48.8733 | 0.03 | 0.2084 | -3.209 | 28.1723 | 81.7233 | 8.2767 | 28.447 | 34.3602 | 0.17204 | 36.655 | 0.8 | 1 | 9.7807 | 46.6077 | -2.0279 | -0.57141 | 1.1023 | 0.042128
2015-03-13 14:00 | 34.6967 | 34.6367 | 0.06 | 0.5457 | -3.1926 | 43.1751 | 83.6876 | 6.3124 | 43.4196 | 47.1415 | 0.37118 | 25.9775 | 0.8 | 1 | 6.9393 | 33.288 | -2.0305 | -0.99022 | 1.104 | 0.030134
2015-03-13 15:00 | 20.49 | 20.4 | 0.09 | 1.39 | -3.1762 | 58.178 | 86.2875 | 3.7125 | 58.23 | 60.8309 | 0.67745 | 15.3 | 0.8 | 1 | 4.098 | 20.0754 | -2.033 | -1.4057 | 1.1056 | 0.018201
2015-03-13 16:00 | 13.66 | 13.6 | 0.06 | 0 | -3.1597 | 73.1808 | 89.3437 | 0.65634 | 72.9072 | 74.9149 | 0 | 10.2 | 0.8 | 1 | 2.732 | 12.932 | -2.0356 | -1.6315 | 1.1065 | 0.011734
2015-03-13 17:00 | 6.83 | 6.8 | 0.03 | 0 | -3.1433 | 88.1836 | 92.6528 | -2.6528 | 87.5214 | 89.1824 | 0 | 5.1 | 0.8 | 1 | 1.366 | 6.466 | -2.0382 | -1.8361 | 1.1073 | 0.0058713
2015-03-13 18:00 | 0 | 0 | 0 | 0 | -3.1269 | 103.1865 | 95.999 | -5.999 | 102.1673 | 103.52 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.0408 | -2.0408 | 1.1082 | 0
2015-03-13 19:00 | 0 | 0 | 0 | 0 | -3.1105 | 118.1893 | 99.1627 | -9.1627 | 116.9417 | 117.8394 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.0433 | -2.0433 | 1.1082 | 0
2015-03-13 20:00 | 0 | 0 | 0 | 0 | -3.0941 | 133.1922 | 101.9299 | -11.9299 | 131.9207 | 132.0249 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.0459 | -2.0459 | 1.1082 | 0
2015-03-13 21:00 | 0 | 0 | 0 | 0 | -3.0777 | 148.195 | 104.1042 | -14.1042 | 147.1373 | 145.8277 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.0485 | -2.0485 | 1.1082 | 0
2015-03-13 22:00 | 0 | 0 | 0 | 0 | -3.0613 | 163.1978 | 105.5221 | -15.5221 | 162.5675 | 158.4222 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.0511 | -2.0511 | 1.1082 | 0
2015-03-13 23:00 | 0 | 0 | 0 | 0 | -3.0448 | 178.2007 | 106.0716 | -16.0716 | 178.1301 | 165.9665 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.0536 | -2.0536 | 1.1082 | 0
2015-03-14 | 0 | 0 | 0 | 0 | -3.0284 | -166.7965 | 105.7071 | -15.7071 | -166.294 | 160.9627 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.0562 | -2.0562 | 1.1082 | 0
2015-03-14 01:00 | 0 | 0 | 0 | 0 | -3.012 | -151.7936 | 104.4571 | -14.4571 | -150.8281 | 148.9884 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.0588 | -2.0588 | 1.1082 | 0
2015-03-14 02:00 | 0 | 0 | 0 | 0 | -2.9956 | -136.7907 | 102.419 | -12.419 | -135.5641 | 135.3515 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.0614 | -2.0614 | 1.1082 | 0
2015-03-14 03:00 | 0 | 0 | 0 | 0 | -2.9792 | -121.7879 | 99.7454 | -9.7454 | -120.5389 | 121.2205 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.0639 | -2.0639 | 1.1083 | 0
2015-03-14 04:00 | 4.39 | 3.0267 | 1.3633 | 0 | -2.9627 | -106.785 | 96.6263 | -6.6263 | -105.731 | 106.9134 | 0 | 2.27 | 0.8 | 1 | 0.878 | 3.148 | -2.0665 | -1.9681 | 1.1079 | 0.0028598
2015-03-14 05:00 | 8.78 | 6.0533 | 2.7267 | 0 | -2.9463 | -91.7821 | 93.2722 | -3.2722 | -91.0713 | 92.5623 | 0 | 4.54 | 0.8 | 1 | 1.756 | 6.296 | -2.0691 | -1.8723 | 1.1075 | 0.0057177
2015-03-14 06:00 | 13.17 | 9.08 | 4.09 | 0 | -2.9299 | -76.7793 | 89.9019 | 0.098086 | -76.4645 | 78.2556 | 0 | 6.81 | 0.8 | 1 | 2.634 | 9.444 | -2.0717 | -1.7765 | 1.1071 | 0.0085735
2015-03-14 07:00 | 31.43 | 28.68 | 2.75 | 48.2505 | -2.9135 | -61.7764 | 86.7327 | 3.2673 | -61.812 | 64.0929 | 21.0812 | 21.51 | 0.8 | 1 | 6.286 | 48.8772 | -2.0742 | -0.54683 | 1.1022 | 0.044175
2015-03-14 08:00 | 49.69 | 48.28 | 1.41 | 13.4264 | -2.897 | -46.7735 | 83.9719 | 6.0281 | -47.0348 | 50.2464 | 8.586 | 36.21 | 0.8 | 1 | 9.938 | 54.734 | -2.0768 | -0.36639 | 1.1015 | 0.049436
2015-03-14 09:00 | 67.95 | 67.88 | 0.07 | 0.49115 | -2.8806 | -31.7707 | 81.8061 | 8.1939 | -32.0919 | 37.1112 | 0.39167 | 50.91 | 0.8 | 1 | 13.59 | 64.8917 | -2.0794 | -0.051534 | 1.1002 | 0.058543
2015-03-14 10:00 | 72.44 | 72.3933 | 0.046667 | 0.27948 | -2.8642 | -16.7678 | 80.3878 | 9.6122 | -16.9919 | 25.8312 | 0.25155 | 54.295 | 0.8 | 1 | 14.488 | 69.0346 | -2.082 | 0.075356 | 1.0997 | 0.062252
2015-03-14 11:00 | 76.93 | 76.9067 | 0.023333 | 0.13203 | -2.8478 | -1.7649 | 79.8206 | 10.1794 | -1.7909 | 19.8909 | 0.12415 | 57.68 | 0.8 | 1 | 15.386 | 73.1902 | -2.0845 | 0.20264 | 1.0992 | 0.065969
2015-03-14 12:00 | 81.42 | 81.42 | 0 | 0 | -2.8313 | 13.238 | 80.1463 | 9.8537 | 13.4232 | 23.7221 | 0 | 61.065 | 0.8 | 1 | 16.284 | 77.349 | -2.0871 | 0.33003 | 1.0987 | 0.069685
2015-03-14 13:00 | 63.52 | 63.52 | 0 | 0 | -2.8149 | 28.2409 | 81.3389 | 8.6611 | 28.5588 | 34.1803 | 0 | 47.64 | 0.8 | 1 | 12.704 | 60.344 | -2.0897 | -0.20395 | 1.1008 | 0.054471
2015-03-14 14:00 | 45.62 | 45.62 | 0 | 0 | -2.7985 | 43.2438 | 83.3089 | 6.6911 | 43.5494 | 47.0264 | 0 | 34.215 | 0.8 | 1 | 9.124 | 43.339 | -2.0923 | -0.73793 | 1.103 | 0.039197
2015-03-14 15:00 | 27.72 | 27.72 | 0 | 0 | -2.782 | 58.2466 | 85.9139 | 4.0861 | 58.3734 | 60.7513 | 0 | 20.79 | 0.8 | 1 | 5.544 | 26.334 | -2.0948 | -1.2719 | 1.1051 | 0.023863
2015-03-14 16:00 | 18.48 | 18.48 | 0 | 0 | -2.7656 | 73.2495 | 88.9737 | 1.0263 | 73.0594 | 74.8552 | 0 | 13.86 | 0.8 | 1 | 3.696 | 17.556 | -2.0974 | -1.5488 | 1.1062 | 0.015925
2015-03-14 17:00 | 9.24 | 9.24 | 0 | 0 | -2.7492 | 88.2524 | 92.2843 | -2.2843 | 87.6774 | 89.1326 | 0 | 6.93 | 0.8 | 1 | 1.848 | 8.778 | -2.1 | -1.8257 | 1.1073 | 0.0079703
2015-03-14 18:00 | 0 | 0 | 0 | 0 | -2.7327 | 103.2553 | 95.6297 | -5.6297 | 102.3221 | 103.4723 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-03-14 19:00 | 0 | 0 | 0 | 0 | -2.7163 | 118.2582 | 98.7904 | -8.7904 | 117.0902 | 117.7853 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.7 | 0.7 | 1.0972 | 0
2015-03-14 20:00 | 0 | 0 | 0 | 0 | -2.6999 | 133.2611 | 101.5529 | -11.5529 | 132.0576 | 131.9525 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-03-14 21:00 | 0 | 0 | 0 | 0 | -2.6834 | 148.264 | 103.7214 | -13.7214 | 147.2575 | 145.7138 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.3 | 1.3 | 1.0948 | 0
2015-03-14 22:00 | 0 | 0 | 0 | 0 | -2.667 | 163.2669 | 105.1334 | -15.1334 | 162.6665 | 158.2115 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.7 | 1.7 | 1.0932 | 0
2015-03-14 23:00 | 0 | 0 | 0 | 0 | -2.6506 | 178.2699 | 105.6778 | -15.6778 | 178.2049 | 165.5833 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-03-15 | 0 | 0 | 0 | 0 | -2.6341 | -166.7272 | 105.3097 | -15.3097 | -166.2443 | 160.6225 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-03-15 01:00 | 0 | 0 | 0 | 0 | -2.6177 | -151.7243 | 104.0576 | -14.0576 | -150.802 | 148.7371 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.8 | 0.8 | 1.0968 | 0
2015-03-15 02:00 | 0 | 0 | 0 | 0 | -2.6013 | -136.7214 | 102.0187 | -12.0187 | -135.5579 | 135.1429 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-03-15 03:00 | 0 | 0 | 0 | 0 | -2.5848 | -121.7185 | 99.3451 | -9.3451 | -120.5477 | 121.0317 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-03-15 04:00 | 2.4767 | 2.4767 | 0 | 0 | -2.5684 | -106.7156 | 96.2263 | -6.2263 | -105.7491 | 106.7324 | 0 | 1.8575 | 0.8 | 1 | 0.49533 | 2.3528 | 0.5 | 0.57353 | 1.0977 | 0.0021178
2015-03-15 05:00 | 4.9533 | 4.9533 | 0 | 0 | -2.5519 | -91.7126 | 92.8724 | -2.8724 | -91.0927 | 92.3814 | 0 | 3.715 | 0.8 | 1 | 0.99067 | 4.7057 | 0.4 | 0.54705 | 1.0978 | 0.0042361
2015-03-15 06:00 | 7.43 | 7.43 | 0 | 0 | -2.5355 | -76.7097 | 89.5019 | 0.49812 | -76.4833 | 78.0678 | 0 | 5.5725 | 0.8 | 1 | 1.486 | 7.0585 | 0.8 | 1.0206 | 1.0959 | 0.0063431
2015-03-15 07:00 | 12.6567 | 12.2667 | 0.39 | 6.0967 | -2.5191 | -61.7068 | 86.3323 | 3.6677 | -61.8224 | 63.8904 | 2.6831 | 9.2 | 0.8 | 1 | 2.5313 | 14.4144 | 0.3 | 0.75045 | 1.097 | 0.012966
2015-03-15 08:00 | 17.8833 | 17.1033 | 0.78 | 6.9664 | -2.5026 | -46.7038 | 83.5714 | 6.4286 | -47.0313 | 50.0175 | 4.4763 | 12.8275 | 0.8 | 1 | 3.5767 | 20.8805 | 0.3 | 0.95251 | 1.0962 | 0.018769
2015-03-15 09:00 | 23.11 | 21.94 | 1.17 | 7.8298 | -2.4862 | -31.7009 | 81.4061 | 8.5939 | -32.0698 | 36.8368 | 6.2665 | 16.455 | 0.8 | 1 | 4.622 | 27.3435 | 0.5 | 1.3545 | 1.0946 | 0.024542
2015-03-15 10:00 | 31.62 | 30.84 | 0.78 | 4.4872 | -2.4697 | -16.698 | 79.9896 | 10.0104 | -16.9476 | 25.4825 | 4.0507 | 23.13 | 0.8 | 1 | 6.324 | 33.5047 | 0 | 1.047 | 1.0958 | 0.030106
2015-03-15 11:00 | 40.13 | 39.74 | 0.39 | 2.1252 | -2.4533 | -1.695 | 79.4257 | 10.5743 | -1.7228 | 19.4919 | 2.0034 | 29.805 | 0.8 | 1 | 8.026 | 39.8344 | 0.4 | 1.6448 | 1.0934 | 0.035716
2015-03-15 12:00 | 48.64 | 48.64 | 0 | 0 | -2.4368 | 13.3079 | 79.756 | 10.244 | 13.5151 | 23.4307 | 0 | 36.48 | 0.8 | 1 | 9.728 | 46.208 | 0.6 | 2.044 | 1.0918 | 0.04137
2015-03-15 13:00 | 38.06 | 38.06 | 0 | 0 | -2.4204 | 28.3108 | 80.9543 | 9.0457 | 28.6723 | 34.0045 | 0 | 28.545 | 0.8 | 1 | 7.612 | 36.157 | 0.5 | 1.6299 | 1.0935 | 0.03242
2015-03-15 14:00 | 27.48 | 27.48 | 0 | 0 | -2.4039 | 43.3138 | 82.9301 | 7.0699 | 43.6809 | 46.9147 | 0 | 20.61 | 0.8 | 1 | 5.496 | 26.106 | 0.4 | 1.2158 | 1.0951 | 0.023444
2015-03-15 15:00 | 16.9 | 16.9 | 0 | 0 | -2.3875 | 58.3167 | 85.5402 | 4.4598 | 58.5184 | 60.6745 | 0 | 12.675 | 0.8 | 1 | 3.38 | 16.055 | 0.2 | 0.70172 | 1.0972 | 0.014445
2015-03-15 16:00 | 11.2667 | 11.2667 | 0 | 0 | -2.371 | 73.3197 | 88.6035 | 1.3965 | 73.2131 | 74.7975 | 0 | 8.45 | 0.8 | 1 | 2.2533 | 10.7033 | 1.2 | 1.5345 | 1.0939 | 0.0096005
2015-03-15 17:00 | 5.6333 | 5.6333 | 0 | 0 | -2.3546 | 88.3226 | 91.9158 | -1.9158 | 87.8349 | 89.0841 | 0 | 4.225 | 0.8 | 1 | 1.1267 | 5.3517 | 0.9 | 1.0672 | 1.0957 | 0.0048085
2015-03-15 18:00 | 0 | 0 | 0 | 0 | -2.3381 | 103.3256 | 95.2603 | -5.2603 | 102.4783 | 103.4251 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-03-15 19:00 | 0 | 0 | 0 | 0 | -2.3217 | 118.3286 | 98.418 | -8.418 | 117.24 | 117.7311 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-03-15 20:00 | 0 | 0 | 0 | 0 | -2.3052 | 133.3315 | 101.1756 | -11.1756 | 132.1957 | 131.8788 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-03-15 21:00 | 0 | 0 | 0 | 0 | -2.2888 | 148.3345 | 103.3382 | -13.3382 | 147.3788 | 145.5972 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-03-15 22:00 | 0 | 0 | 0 | 0 | -2.2723 | 163.3374 | 104.7444 | -14.7444 | 162.7666 | 157.9967 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-03-15 23:00 | 0 | 0 | 0 | 0 | -2.2559 | 178.3404 | 105.2836 | -15.2836 | 178.2809 | 165.199 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-03-16 | 0 | 0 | 0 | 0 | -2.2394 | -166.6566 | 104.9118 | -14.9118 | -166.1933 | 160.2789 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-03-16 01:00 | 0 | 0 | 0 | 0 | -2.223 | -151.6537 | 103.6575 | -13.6575 | -150.7745 | 148.4817 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-03-16 02:00 | 0 | 0 | 0 | 0 | -2.2065 | -136.6507 | 101.6177 | -11.6177 | -135.5504 | 134.9307 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-03-16 03:00 | 0 | 0 | 0 | 0 | -2.1901 | -121.6477 | 98.9442 | -8.9442 | -120.5552 | 120.84 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.4 | -1.4 | 1.1056 | 0
2015-03-16 04:00 | 3.9633 | 3.1867 | 0.77667 | 0 | -2.1736 | -106.6447 | 95.8256 | -5.8256 | -105.7659 | 106.5493 | 0 | 2.39 | 0.8 | 1 | 0.79267 | 3.1827 | -2 | -1.9005 | 1.1076 | 0.0028906
2015-03-16 05:00 | 7.9267 | 6.3733 | 1.5533 | 0 | -2.1572 | -91.6418 | 92.4718 | -2.4718 | -91.1129 | 92.1989 | 0 | 4.78 | 0.8 | 1 | 1.5853 | 6.3653 | -2.5 | -2.3011 | 1.1092 | 0.0057896
2015-03-16 06:00 | 11.89 | 9.56 | 2.33 | 0 | -2.1407 | -76.6388 | 89.1012 | 0.89883 | -76.5008 | 77.879 | 0 | 7.17 | 0.8 | 1 | 2.378 | 9.548 | -4.2 | -3.9016 | 1.1156 | 0.0087345
2015-03-16 07:00 | 27.1867 | 23.54 | 3.6467 | 51.3961 | -2.1243 | -61.6358 | 85.9313 | 4.0687 | -61.8314 | 63.6874 | 22.7822 | 17.655 | 0.8 | 1 | 5.4373 | 45.8746 | -4.2406 | -2.807 | 1.1112 | 0.041801
2015-03-16 08:00 | 42.4833 | 37.52 | 4.9633 | 41.7369 | -2.1078 | -46.6328 | 83.1703 | 6.8297 | -47.0264 | 49.7888 | 26.9456 | 28.14 | 0.8 | 1 | 8.4967 | 63.5823 | -4.2812 | -2.2943 | 1.1092 | 0.05783
2015-03-16 09:00 | 57.78 | 51.5 | 6.28 | 40.1695 | -2.0913 | -31.6298 | 81.0056 | 8.9944 | -32.0463 | 36.563 | 32.2643 | 38.625 | 0.8 | 1 | 11.556 | 82.4453 | -4.3219 | -1.7455 | 1.107 | 0.074838
2015-03-16 10:00 | 54.6867 | 50.5 | 4.1867 | 23.1725 | -2.0749 | -16.6268 | 79.591 | 10.409 | -16.9019 | 25.134 | 20.9785 | 37.875 | 0.8 | 1 | 10.9373 | 69.7908 | -4.3625 | -2.1815 | 1.1087 | 0.063451
2015-03-16 11:00 | 51.5933 | 49.5 | 2.0933 | 11.0008 | -2.0584 | -1.6238 | 79.0304 | 10.9696 | -1.653 | 19.0925 | 10.3957 | 37.125 | 0.8 | 1 | 10.3187 | 57.8394 | -4.4031 | -2.5956 | 1.1104 | 0.052664
2015-03-16 12:00 | 48.5 | 48.5 | 0 | 0 | -2.042 | 13.3792 | 79.3654 | 10.6346 | 13.6086 | 23.1429 | 0 | 36.375 | 0.8 | 1 | 9.7 | 46.075 | -4.4438 | -3.0039 | 1.112 | 0.042014
2015-03-16 13:00 | 39.7733 | 39.7733 | 0 | 0 | -2.0255 | 28.3822 | 80.5695 | 9.4305 | 28.7874 | 33.8331 | 0 | 29.83 | 0.8 | 1 | 7.9547 | 37.7847 | -4.4844 | -3.3036 | 1.1132 | 0.034491
2015-03-16 14:00 | 31.0467 | 31.0467 | 0 | 0 | -2.0091 | 43.3852 | 82.5512 | 7.4488 | 43.814 | 46.8066 | 0 | 23.285 | 0.8 | 1 | 6.2093 | 29.4943 | -4.525 | -3.6033 | 1.1144 | 0.026952
2015-03-16 15:00 | 22.32 | 22.32 | 0 | 0 | -1.9926 | 58.3882 | 85.1664 | 4.8336 | 58.665 | 60.6004 | 0 | 16.74 | 0.8 | 1 | 4.464 | 21.204 | -4.5656 | -3.903 | 1.1156 | 0.019397
2015-03-16 16:00 | 14.89 | 14.89 | 0 | 0 | -1.9761 | 73.3912 | 88.2334 | 1.7666 | 73.3682 | 74.7418 | 0 | 11.1675 | 0.8 | 1 | 2.978 | 14.1455 | -4.6063 | -4.1642 | 1.1167 | 0.012952
2015-03-16 17:00 | 7.46 | 7.46 | 0 | 0 | -1.9597 | 88.3942 | 91.5471 | -1.5471 | 87.9937 | 89.0369 | 0 | 5.595 | 0.8 | 1 | 1.492 | 7.087 | -4.6469 | -4.4254 | 1.1177 | 0.0064953
2015-03-16 18:00 | 0.03 | 0.03 | 0 | 0 | -1.9432 | 103.3972 | 94.8909 | -4.8909 | 102.6357 | 103.3785 | 0 | 0.0225 | 0.8 | 1 | 0.006 | 0.0285 | -4.6875 | -4.6866 | 1.1187 | 2.6145e-05
2015-03-16 19:00 | 0.02 | 0.02 | 0 | 0 | -1.9268 | 118.4002 | 98.0454 | -8.0454 | 117.3909 | 117.6765 | 0 | 0.015 | 0.8 | 1 | 0.004 | 0.019 | -4.7281 | -4.7275 | 1.1189 | 1.7433e-05
2015-03-16 20:00 | 0.01 | 0.01 | 0 | 0 | -1.9103 | 133.4032 | 100.7981 | -10.7981 | 132.3348 | 131.8039 | 0 | 0.0075 | 0.8 | 1 | 0.002 | 0.0095 | -4.7687 | -4.7685 | 1.1191 | 8.7176e-06
2015-03-16 21:00 | 0 | 0 | 0 | 0 | -1.8938 | 148.4062 | 102.9549 | -12.9549 | 147.5011 | 145.478 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.8094 | -4.8094 | 1.1192 | 0
2015-03-16 22:00 | 0 | 0 | 0 | 0 | -1.8774 | 163.4092 | 104.355 | -14.355 | 162.8678 | 157.7777 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.85 | -4.85 | 1.1194 | 0
2015-03-16 23:00 | 0 | 0 | 0 | 0 | -1.8609 | 178.4122 | 104.8891 | -14.8891 | 178.3579 | 164.8138 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.8906 | -4.8906 | 1.1196 | 0
2015-03-17 | 0 | 0 | 0 | 0 | -1.8444 | -166.5847 | 104.5135 | -14.5135 | -166.1412 | 159.9321 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9313 | -4.9313 | 1.1197 | 0
2015-03-17 01:00 | 0 | 0 | 0 | 0 | -1.828 | -151.5817 | 103.257 | -13.257 | -150.7458 | 148.2222 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9719 | -4.9719 | 1.1199 | 0
2015-03-17 02:00 | 0 | 0 | 0 | 0 | -1.8115 | -136.5787 | 101.2163 | -11.2163 | -135.5416 | 134.7152 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.0125 | -5.0125 | 1.12 | 0
2015-03-17 03:00 | 0 | 0 | 0 | 0 | -1.7951 | -121.5757 | 98.5427 | -8.5427 | -120.5614 | 120.6457 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.0531 | -5.0531 | 1.1202 | 0
2015-03-17 04:00 | 6.39 | 6.3733 | 0.016667 | 0 | -1.7786 | -106.5726 | 95.4243 | -5.4243 | -105.7814 | 106.3642 | 0 | 4.78 | 0.8 | 1 | 1.278 | 6.058 | -5.0938 | -4.9044 | 1.1196 | 0.0055618
2015-03-17 05:00 | 12.78 | 12.7467 | 0.033333 | 0 | -1.7621 | -91.5696 | 92.0707 | -2.0707 | -91.1317 | 92.0149 | 0 | 9.56 | 0.8 | 1 | 2.556 | 12.116 | -5.1344 | -4.7558 | 1.119 | 0.011118
2015-03-17 06:00 | 19.17 | 19.12 | 0.05 | 0 | -1.7457 | -76.5666 | 88.6999 | 1.3001 | -76.5171 | 77.6894 | 0 | 14.34 | 0.8 | 1 | 3.834 | 18.174 | -5.175 | -4.6071 | 1.1184 | 0.016668
2015-03-17 07:00 | 59.61 | 30.9567 | 28.6533 | 367.6293 | -1.7292 | -61.5635 | 85.5298 | 4.4702 | -61.8393 | 63.4842 | 164.1261 | 23.2175 | 0.8 | 1 | 11.922 | 199.2656 | -5.2156 | 1.0114 | 1.096 | 0.17908
2015-03-17 08:00 | 100.05 | 42.7933 | 57.2567 | 454.8665 | -1.7127 | -46.5605 | 82.7687 | 7.2313 | -47.0203 | 49.5605 | 295.0468 | 32.095 | 0.8 | 1 | 20.01 | 347.1518 | -5.2562 | 5.5922 | 1.0776 | 0.30676
2015-03-17 09:00 | 140.49 | 54.63 | 85.86 | 525.9592 | -1.6963 | -31.5575 | 80.6047 | 9.3953 | -32.0215 | 36.29 | 423.9399 | 40.9725 | 0.8 | 1 | 28.098 | 493.0104 | -5.2969 | 10.1097 | 1.0596 | 0.42835
2015-03-17 10:00 | 143.57 | 58.4467 | 85.1233 | 453.9463 | -1.6798 | -16.5544 | 79.192 | 10.808 | -16.8548 | 24.786 | 412.1288 | 43.835 | 0.8 | 1 | 28.714 | 484.6778 | -5.3375 | 9.8087 | 1.0608 | 0.42159
2015-03-17 11:00 | 146.65 | 62.2633 | 84.3867 | 428.2252 | -1.6633 | -1.5514 | 78.6348 | 11.3652 | -1.5818 | 18.6928 | 405.6366 | 46.6975 | 0.8 | 1 | 29.33 | 481.6641 | -5.3781 | 9.6739 | 1.0613 | 0.41918
2015-03-17 12:00 | 149.73 | 66.08 | 83.65 | 437.4047 | -1.6469 | 13.4517 | 78.9747 | 11.0253 | 13.7037 | 22.8589 | 403.0529 | 49.56 | 0.8 | 1 | 29.946 | 482.5589 | -5.4188 | 9.6612 | 1.0614 | 0.41998
2015-03-17 13:00 | 115.38 | 58.8633 | 56.5167 | 331.5253 | -1.6304 | 28.4547 | 80.1846 | 9.8154 | 28.9042 | 33.666 | 275.9231 | 44.1475 | 0.8 | 1 | 23.076 | 343.1466 | -5.4594 | 5.264 | 1.0789 | 0.30359
2015-03-17 14:00 | 81.03 | 51.6467 | 29.3833 | 215.7442 | -1.6139 | 43.4578 | 82.1723 | 7.8277 | 43.9487 | 46.702 | 147.9559 | 38.735 | 0.8 | 1 | 16.206 | 202.8969 | -5.5 | 0.84053 | 1.0966 | 0.18245
2015-03-17 15:00 | 46.68 | 44.43 | 2.25 | 24.7909 | -1.5975 | 58.4608 | 84.7927 | 5.2073 | 58.813 | 60.5289 | 12.1967 | 33.3225 | 0.8 | 1 | 9.336 | 54.8552 | -5.7 | -3.9858 | 1.1159 | 0.050197
2015-03-17 16:00 | 31.1567 | 29.65 | 1.5067 | 0 | -1.581 | 73.4639 | 87.8633 | 2.1367 | 73.5247 | 74.6879 | 0 | 22.2375 | 0.8 | 1 | 6.2313 | 28.4688 | -5.4 | -4.5103 | 1.118 | 0.0261
2015-03-17 17:00 | 15.6333 | 14.87 | 0.76333 | 0 | -1.5645 | 88.4669 | 91.1785 | -1.1785 | 88.1536 | 88.9908 | 0 | 11.1525 | 0.8 | 1 | 3.1267 | 14.2792 | -6.1 | -5.6538 | 1.1226 | 0.013145
2015-03-17 18:00 | 0.11 | 0.09 | 0.02 | 0 | -1.5481 | 103.47 | 94.5214 | -4.5214 | 102.7941 | 103.3324 | 0 | 0.0675 | 0.8 | 1 | 0.022 | 0.0895 | -5.1 | -5.0972 | 1.1204 | 8.2225e-05
2015-03-17 19:00 | 0.073333 | 0.06 | 0.013333 | 0 | -1.5316 | 118.473 | 97.6728 | -7.6728 | 117.5427 | 117.6217 | 0 | 0.045 | 0.8 | 1 | 0.014667 | 0.059667 | -4.6 | -4.5981 | 1.1184 | 5.4719e-05
2015-03-17 20:00 | 0.036667 | 0.03 | 0.0066667 | 0 | -1.5151 | 133.4761 | 100.4206 | -10.4206 | 132.4749 | 131.7276 | 0 | 0.0225 | 0.8 | 1 | 0.0073333 | 0.029833 | -4.8 | -4.7991 | 1.1192 | 2.7379e-05
2015-03-17 21:00 | 0 | 0 | 0 | 0 | -1.4987 | 148.4791 | 102.5714 | -12.5714 | 147.6244 | 145.356 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-03-17 22:00 | 0 | 0 | 0 | 0 | -1.4822 | 163.4822 | 103.9656 | -13.9656 | 162.9698 | 157.5546 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1208 | 0
2015-03-17 23:00 | 0 | 0 | 0 | 0 | -1.4657 | 178.4853 | 104.4944 | -14.4944 | 178.436 | 164.4276 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.3 | -5.3 | 1.1212 | 0
2015-03-18 | 0 | 0 | 0 | 0 | -1.4492 | -166.5117 | 104.1149 | -14.1149 | -166.088 | 159.5825 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.7 | -5.7 | 1.1228 | 0
2015-03-18 01:00 | 0 | 0 | 0 | 0 | -1.4328 | -151.5086 | 102.8561 | -12.8561 | -150.716 | 147.959 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.8 | -5.8 | 1.1232 | 0
2015-03-18 02:00 | 0 | 0 | 0 | 0 | -1.4163 | -136.5055 | 100.8145 | -10.8145 | -135.5316 | 134.4966 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.2 | -6.2 | 1.1248 | 0
2015-03-18 03:00 | 0 | 0 | 0 | 0 | -1.3998 | -121.5024 | 98.1408 | -8.1408 | -120.5664 | 120.449 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.6 | -7.6 | 1.1304 | 0
2015-03-18 04:00 | 4.7633 | 4.57 | 0.19333 | 0 | -1.3834 | -106.4994 | 95.0227 | -5.0227 | -105.7957 | 106.1772 | 0 | 3.4275 | 0.8 | 1 | 0.95267 | 4.3802 | -6.8 | -6.6631 | 1.1267 | 0.0040466
2015-03-18 05:00 | 9.5267 | 9.14 | 0.38667 | 0 | -1.3669 | -91.4963 | 91.6691 | -1.6691 | -91.1495 | 91.8297 | 0 | 6.855 | 0.8 | 1 | 1.9053 | 8.7603 | -7 | -6.7262 | 1.1269 | 0.0080951
2015-03-18 06:00 | 14.29 | 13.71 | 0.58 | 0 | -1.3504 | -76.4932 | 88.2982 | 1.7018 | -76.5322 | 77.4991 | 0 | 10.2825 | 0.8 | 1 | 2.858 | 13.1405 | -7.1 | -6.6894 | 1.1268 | 0.012141
2015-03-18 07:00 | 28.7267 | 28.32 | 0.40667 | 4.7881 | -1.334 | -61.4901 | 85.1278 | 4.8722 | -61.846 | 63.2808 | 2.1528 | 21.24 | 0.8 | 1 | 5.7453 | 29.1382 | -7.5 | -6.5894 | 1.1264 | 0.026912
2015-03-18 08:00 | 43.1633 | 42.93 | 0.23333 | 1.7566 | -1.3175 | -46.487 | 82.3667 | 7.6333 | -47.0131 | 49.3326 | 1.1447 | 32.1975 | 0.8 | 1 | 8.6327 | 41.9749 | -7.7 | -6.3883 | 1.1256 | 0.038741
2015-03-18 09:00 | 57.6 | 57.54 | 0.06 | 0.35263 | -1.301 | -31.484 | 80.2035 | 9.7965 | -31.9954 | 36.018 | 0.28522 | 43.155 | 0.8 | 1 | 11.52 | 54.9602 | -8.2 | -6.4825 | 1.1259 | 0.050743
2015-03-18 10:00 | 56.76 | 56.69 | 0.07 | 0.36016 | -1.2845 | -16.4809 | 78.7928 | 11.2072 | -16.8063 | 24.4386 | 0.32789 | 42.5175 | 0.8 | 1 | 11.352 | 54.1974 | -8.3 | -6.6063 | 1.1264 | 0.05006
2015-03-18 11:00 | 55.92 | 55.84 | 0.08 | 0.39249 | -1.2681 | -1.4778 | 78.2391 | 11.7609 | -1.5091 | 18.2929 | 0.37265 | 41.88 | 0.8 | 1 | 11.184 | 53.4367 | -8.4 | -6.7301 | 1.1269 | 0.049379
2015-03-18 12:00 | 55.08 | 54.99 | 0.09 | 0.4547 | -1.2516 | 13.5253 | 78.584 | 11.416 | 13.8003 | 22.5788 | 0.41985 | 41.2425 | 0.8 | 1 | 11.016 | 52.6784 | -8.3 | -6.6538 | 1.1266 | 0.048666
2015-03-18 13:00 | 45.8533 | 45.78 | 0.073333 | 0.4141 | -1.2351 | 28.5284 | 79.7997 | 10.2003 | 29.0224 | 33.5032 | 0.3453 | 34.335 | 0.8 | 1 | 9.1707 | 43.851 | -8.7 | -7.3297 | 1.1293 | 0.040608
2015-03-18 14:00 | 36.6267 | 36.57 | 0.056667 | 0.39699 | -1.2187 | 43.5315 | 81.7934 | 8.2066 | 44.0847 | 46.6008 | 0.27276 | 27.4275 | 0.8 | 1 | 7.3253 | 35.0256 | -8.9 | -7.8055 | 1.1312 | 0.03249
2015-03-18 15:00 | 27.4 | 27.36 | 0.04 | 0.41131 | -1.2022 | 58.5346 | 84.4191 | 5.5809 | 58.9624 | 60.4599 | 0.20279 | 20.52 | 0.8 | 1 | 5.48 | 26.2028 | -9.2 | -8.3812 | 1.1335 | 0.024355
2015-03-18 16:00 | 18.33 | 18.3033 | 0.026667 | 0 | -1.1857 | 73.5377 | 87.4934 | 2.5066 | 73.6824 | 74.6358 | 0 | 13.7275 | 0.8 | 1 | 3.666 | 17.3935 | -9.4 | -8.8565 | 1.1354 | 0.016194
2015-03-18 17:00 | 9.26 | 9.2467 | 0.013333 | 0 | -1.1692 | 88.5408 | 90.8101 | -0.8101 | 88.3147 | 88.9459 | 0 | 6.935 | 0.8 | 1 | 1.852 | 8.787 | -9.6 | -9.3254 | 1.1373 | 0.0081946
2015-03-18 18:00 | 0.19 | 0.19 | 0 | 0 | -1.1528 | 103.5439 | 94.152 | -4.152 | 102.9536 | 103.2866 | 0 | 0.1425 | 0.8 | 1 | 0.038 | 0.1805 | -9.8 | -9.7944 | 1.1392 | 0.00016861
2015-03-18 19:00 | 0.12667 | 0.12667 | 0 | 0 | -1.1363 | 118.547 | 97.3003 | -7.3003 | 117.6955 | 117.5664 | 0 | 0.095 | 0.8 | 1 | 0.025333 | 0.12033 | -9.7 | -9.6962 | 1.1388 | 0.00011237
2015-03-18 20:00 | 0.063333 | 0.063333 | 0 | 0 | -1.1198 | 133.5501 | 100.0431 | -10.0431 | 132.6158 | 131.6499 | 0 | 0.0475 | 0.8 | 1 | 0.012667 | 0.060167 | -9.7 | -9.6981 | 1.1388 | 5.6184e-05
2015-03-18 21:00 | 0 | 0 | 0 | 0 | -1.1034 | 148.5532 | 102.188 | -12.188 | 147.7484 | 145.2312 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.8 | -9.8 | 1.1392 | 0
2015-03-18 22:00 | 0 | 0 | 0 | 0 | -1.0869 | 163.5563 | 103.576 | -13.576 | 163.0728 | 157.3276 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.7 | -9.7 | 1.1388 | 0
2015-03-18 23:00 | 0 | 0 | 0 | 0 | -1.0704 | 178.5594 | 104.0995 | -14.0995 | 178.5149 | 164.0406 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.2 | -10.2 | 1.1408 | 0
2015-03-19 | 0 | 0 | 0 | 0 | -1.0539 | -166.4375 | 103.7162 | -13.7162 | -166.0338 | 159.2303 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.3 | -10.3 | 1.1412 | 0
2015-03-19 01:00 | 0 | 0 | 0 | 0 | -1.0375 | -151.4344 | 102.455 | -12.455 | -150.6851 | 147.6922 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.8 | -10.8 | 1.1432 | 0
2015-03-19 02:00 | 0 | 0 | 0 | 0 | -1.021 | -136.4312 | 100.4124 | -10.4124 | -135.5206 | 134.2749 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.8 | -11.8 | 1.1472 | 0
2015-03-19 03:00 | 0 | 0 | 0 | 0 | -1.0045 | -121.4281 | 97.7386 | -7.7386 | -120.5704 | 120.2499 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12 | -12 | 1.148 | 0
2015-03-19 04:00 | 5.4967 | 5.1667 | 0.33 | 0 | -0.98806 | -106.425 | 94.6206 | -4.6206 | -105.809 | 105.9885 | 0 | 3.875 | 0.8 | 1 | 1.0993 | 4.9743 | -12.3 | -12.1446 | 1.1486 | 0.004685
2015-03-19 05:00 | 10.9933 | 10.3333 | 0.66 | 0 | -0.97159 | -91.4219 | 91.2672 | -1.2672 | -91.1662 | 91.6434 | 0 | 7.75 | 0.8 | 1 | 2.1987 | 9.9487 | -12.7 | -12.3891 | 1.1496 | 0.009378
2015-03-19 06:00 | 16.49 | 15.5 | 0.99 | 0 | -0.95512 | -76.4188 | 87.8962 | 2.1038 | -76.5464 | 77.3082 | 0 | 11.625 | 0.8 | 1 | 3.298 | 14.923 | -12.9 | -12.4337 | 1.1497 | 0.014069
2015-03-19 07:00 | 39.7733 | 34.1867 | 5.5867 | 60.774 | -0.93865 | -61.4156 | 84.7256 | 5.2744 | -61.8517 | 63.0775 | 27.5176 | 25.64 | 0.8 | 1 | 7.9547 | 61.1123 | -13.1 | -11.1902 | 1.1448 | 0.057366
2015-03-19 08:00 | 63.0567 | 52.8733 | 10.1833 | 72.8495 | -0.92218 | -46.4125 | 81.9645 | 8.0355 | -47.0047 | 49.1053 | 47.6924 | 39.655 | 0.8 | 1 | 12.6113 | 99.9587 | -13.2 | -10.0763 | 1.1403 | 0.093466
2015-03-19 09:00 | 86.34 | 71.56 | 14.78 | 83.4802 | -0.90571 | -31.4094 | 79.8021 | 10.1979 | -31.9682 | 35.7471 | 67.7528 | 53.67 | 0.8 | 1 | 17.268 | 138.6908 | -13.5 | -9.1659 | 1.1367 | 0.12927
2015-03-19 10:00 | 90.2067 | 75.1733 | 15.0333 | 74.7222 | -0.88924 | -16.4063 | 78.3935 | 11.6065 | -16.7567 | 24.0921 | 68.2132 | 56.38 | 0.8 | 1 | 18.0413 | 142.6345 | -13.8 | -9.3427 | 1.1374 | 0.13303
2015-03-19 11:00 | 94.0733 | 78.7867 | 15.2867 | 72.5916 | -0.87276 | -1.4031 | 77.8434 | 12.1566 | -1.4352 | 17.893 | 69.0805 | 59.09 | 0.8 | 1 | 18.8147 | 146.9852 | -13.5 | -8.9067 | 1.1356 | 0.13687
2015-03-19 12:00 | 97.94 | 82.4 | 15.54 | 75.9492 | -0.85629 | 13.6 | 78.1933 | 11.8067 | 13.8982 | 22.3028 | 70.2675 | 61.8 | 0.8 | 1 | 19.588 | 151.6555 | -13.7 | -8.9608 | 1.1358 | 0.14125
2015-03-19 13:00 | 78.7567 | 66.3667 | 12.39 | 67.4491 | -0.83982 | 28.6031 | 79.415 | 10.585 | 29.142 | 33.345 | 56.3453 | 49.775 | 0.8 | 1 | 15.7513 | 121.8717 | -13.6 | -9.7915 | 1.1392 | 0.11384
2015-03-19 14:00 | 59.5733 | 50.3333 | 9.24 | 61.897 | -0.82335 | 43.6063 | 81.4148 | 8.5852 | 44.2222 | 46.5031 | 42.6046 | 37.75 | 0.8 | 1 | 11.9147 | 92.2693 | -13.9 | -11.0166 | 1.1441 | 0.086561
2015-03-19 15:00 | 40.39 | 34.3 | 6.09 | 58.7077 | -0.80688 | 58.6094 | 84.0458 | 5.9542 | 59.113 | 60.3936 | 29.0039 | 25.725 | 0.8 | 1 | 8.078 | 62.8069 | -13.9 | -11.9373 | 1.1477 | 0.059111
2015-03-19 16:00 | 27.0767 | 23 | 4.0767 | 0 | -0.79041 | 73.6125 | 87.1237 | 2.8763 | 73.8413 | 74.5855 | 0 | 17.25 | 0.8 | 1 | 5.4153 | 22.6653 | -14.7 | -13.9917 | 1.156 | 0.021484
2015-03-19 17:00 | 13.7633 | 11.7 | 2.0633 | 0 | -0.77394 | 88.6157 | 90.4419 | -0.44185 | 88.4768 | 88.902 | 0 | 8.775 | 0.8 | 1 | 2.7527 | 11.5277 | -15.5 | -15.1398 | 1.1606 | 0.01097
2015-03-19 18:00 | 0.45 | 0.4 | 0.05 | 0 | -0.75747 | 103.6188 | 93.7829 | -3.7829 | 103.114 | 103.2412 | 0 | 0.3 | 0.8 | 1 | 0.09 | 0.39 | -16.1 | -16.0878 | 1.1644 | 0.00037236
2015-03-19 19:00 | 0.3 | 0.26667 | 0.033333 | 0 | -0.741 | 118.622 | 96.9279 | -6.9279 | 117.849 | 117.5107 | 0 | 0.2 | 0.8 | 1 | 0.06 | 0.26 | -17.2 | -17.1919 | 1.1688 | 0.00024918
2015-03-19 20:00 | 0.15 | 0.13333 | 0.016667 | 0 | -0.72453 | 133.6251 | 99.6657 | -9.6657 | 132.7574 | 131.5708 | 0 | 0.1 | 0.8 | 1 | 0.03 | 0.13 | -15.7 | -15.6959 | 1.1628 | 0.00012395
2015-03-19 21:00 | 0 | 0 | 0 | 0 | -0.70806 | 148.6283 | 101.8045 | -11.8045 | 147.8731 | 145.1037 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.5 | -16.5 | 1.166 | 0
2015-03-19 22:00 | 0 | 0 | 0 | 0 | -0.69159 | 163.6314 | 103.1865 | -13.1865 | 163.1764 | 157.0967 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.6 | -16.6 | 1.1664 | 0
2015-03-19 23:00 | 0 | 0 | 0 | 0 | -0.67512 | 178.6346 | 103.7047 | -13.7047 | 178.5946 | 163.6531 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.6 | -17.6 | 1.1704 | 0
2015-03-20 | 0 | 0 | 0 | 0 | -0.65865 | -166.3623 | 103.3173 | -13.3173 | -165.9788 | 158.8757 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.9 | -16.9 | 1.1676 | 0
2015-03-20 01:00 | 0 | 0 | 0 | 0 | -0.64218 | -151.3591 | 102.0538 | -12.0538 | -150.6533 | 147.4221 | 0 | 0 | 0.8 | 1 | 0 | 0 | -16.5 | -16.5 | 1.166 | 0
2015-03-20 02:00 | 0 | 0 | 0 | 0 | -0.62571 | -136.356 | 100.0102 | -10.0102 | -135.5085 | 134.0504 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.8 | -15.8 | 1.1632 | 0
2015-03-20 03:00 | 0 | 0 | 0 | 0 | -0.60924 | -121.3528 | 97.3362 | -7.3362 | -120.5733 | 120.0486 | 0 | 0 | 0.8 | 1 | 0 | 0 | -15.6 | -15.6 | 1.1624 | 0
2015-03-20 04:00 | 7.6067 | 6.4667 | 1.14 | 0 | -0.59277 | -106.3497 | 94.2184 | -4.2184 | -105.8213 | 105.7983 | 0 | 4.85 | 0.8 | 1 | 1.5213 | 6.3713 | -15.7 | -15.5009 | 1.162 | 0.0060709
2015-03-20 05:00 | 15.2133 | 12.9333 | 2.28 | 0 | -0.57631 | -91.3465 | 90.8651 | -0.8651 | -91.1819 | 91.4561 | 0 | 9.7 | 0.8 | 1 | 3.0427 | 12.7427 | -16 | -15.6018 | 1.1624 | 0.012146
2015-03-20 06:00 | 22.82 | 19.4 | 3.42 | 0 | -0.55984 | -76.3434 | 87.494 | 2.506 | -76.5595 | 77.1168 | 0 | 14.55 | 0.8 | 1 | 4.564 | 19.114 | -16.3 | -15.7027 | 1.1628 | 0.018225
2015-03-20 07:00 | 50.07 | 38.67 | 11.4 | 115.2491 | -0.54337 | -61.3402 | 84.3232 | 5.6768 | -61.8563 | 62.8742 | 52.5472 | 29.0025 | 0.8 | 1 | 10.014 | 91.5637 | -15.9 | -13.0386 | 1.1522 | 0.086506
2015-03-20 08:00 | 77.32 | 57.94 | 19.38 | 132.0746 | -0.5269 | -46.337 | 81.5622 | 8.4378 | -46.9954 | 48.8789 | 86.8593 | 43.455 | 0.8 | 1 | 15.464 | 145.7783 | -15.5 | -10.9444 | 1.1438 | 0.13673
2015-03-20 09:00 | 104.57 | 77.21 | 27.36 | 148.7444 | -0.51043 | -31.3339 | 79.4007 | 10.5993 | -31.9399 | 35.4776 | 121.1289 | 57.9075 | 0.8 | 1 | 20.914 | 199.9504 | -15.5 | -9.2516 | 1.137 | 0.18642
2015-03-20 10:00 | 112.0133 | 80.1533 | 31.86 | 153.1641 | -0.49397 | -16.3307 | 77.9941 | 12.0059 | -16.7058 | 23.7466 | 140.1966 | 60.115 | 0.8 | 1 | 22.4027 | 222.7143 | -15.9 | -8.9402 | 1.1358 | 0.20742
2015-03-20 11:00 | 119.4567 | 83.0967 | 36.36 | 167.3029 | -0.4775 | -1.3275 | 77.4477 | 12.5523 | -1.36 | 17.4932 | 159.5656 | 62.3225 | 0.8 | 1 | 23.8913 | 245.7794 | -15.3 | -7.6194 | 1.1305 | 0.22784
2015-03-20 12:00 | 126.9 | 86.04 | 40.86 | 193.3944 | -0.46103 | 13.6756 | 77.8027 | 12.1973 | 13.9974 | 22.0311 | 179.2727 | 64.53 | 0.8 | 1 | 25.38 | 269.1827 | -15.4 | -6.988 | 1.128 | 0.24897
2015-03-20 13:00 | 102.6567 | 70.5367 | 32.12 | 168.7976 | -0.44457 | 28.6788 | 79.0305 | 10.9695 | 29.2628 | 33.1912 | 141.258 | 52.9025 | 0.8 | 1 | 20.5313 | 214.6919 | -16.2 | -9.4909 | 1.138 | 0.20034
2015-03-20 14:00 | 78.4133 | 55.0333 | 23.38 | 150.0572 | -0.4281 | 43.682 | 81.0364 | 8.9636 | 44.3608 | 46.4088 | 103.4656 | 41.275 | 0.8 | 1 | 15.6827 | 160.4233 | -15.8 | -10.7868 | 1.1431 | 0.15038
2015-03-20 15:00 | 54.17 | 39.53 | 14.64 | 132.8391 | -0.41163 | 58.6852 | 83.6727 | 6.3273 | 59.2648 | 60.3296 | 65.7566 | 29.6475 | 0.8 | 1 | 10.834 | 106.2381 | -15.9 | -12.5801 | 1.1503 | 0.10021
2015-03-20 16:00 | 36.4033 | 26.58 | 9.8233 | 173.4999 | -0.39517 | 73.6883 | 86.7543 | 3.2457 | 74.0012 | 74.5369 | 46.2583 | 19.935 | 0.8 | 1 | 7.2807 | 73.474 | -17 | -14.7039 | 1.1588 | 0.069817
2015-03-20 17:00 | 18.6367 | 13.63 | 5.0067 | 0 | -0.3787 | 88.6915 | 90.0739 | -0.073889 | 88.6398 | 88.859 | 0 | 10.2225 | 0.8 | 1 | 3.7273 | 13.9498 | -17.1 | -16.6641 | 1.1667 | 0.013345
2015-03-20 18:00 | 0.87 | 0.68 | 0.19 | 0 | -0.36224 | 103.6947 | 93.4139 | -3.4139 | 103.2751 | 103.1961 | 0 | 0.51 | 0.8 | 1 | 0.174 | 0.684 | -17.1 | -17.0786 | 1.1683 | 0.00065528
2015-03-20 19:00 | 0.58 | 0.45333 | 0.12667 | 0 | -0.34577 | 118.6979 | 96.5557 | -6.5557 | 118.0032 | 117.4544 | 0 | 0.34 | 0.8 | 1 | 0.116 | 0.456 | -17.6 | -17.5858 | 1.1703 | 0.00043761
2015-03-20 20:00 | 0.29 | 0.22667 | 0.063333 | 0 | -0.32931 | 133.7011 | 99.2885 | -9.2885 | 132.8996 | 131.4901 | 0 | 0.17 | 0.8 | 1 | 0.058 | 0.228 | -18 | -17.9929 | 1.172 | 0.00021911
2015-03-20 21:00 | 0 | 0 | 0 | 0 | -0.31284 | 148.7042 | 101.4213 | -11.4213 | 147.9984 | 144.9734 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.1 | -17.1 | 1.1684 | 0
2015-03-20 22:00 | 0 | 0 | 0 | 0 | -0.29638 | 163.7074 | 102.797 | -12.797 | 163.2806 | 156.8621 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.3 | -17.3 | 1.1692 | 0
2015-03-20 23:00 | 0 | 0 | 0 | 0 | -0.27992 | 178.7106 | 103.3099 | -13.3099 | 178.675 | 163.265 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18 | -18 | 1.172 | 0
2015-03-21 | 0 | 0 | 0 | 0 | -0.26345 | -166.2862 | 102.9186 | -12.9186 | -165.923 | 158.5191 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.1 | -18.1 | 1.1724 | 0
2015-03-21 01:00 | 0 | 0 | 0 | 0 | -0.24699 | -151.283 | 101.6526 | -11.6526 | -150.6206 | 147.1488 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18.4 | -18.4 | 1.1736 | 0
2015-03-21 02:00 | 0 | 0 | 0 | 0 | -0.23053 | -136.2798 | 99.608 | -9.608 | -135.4956 | 133.8232 | 0 | 0 | 0.8 | 1 | 0 | 0 | -18 | -18 | 1.172 | 0
2015-03-21 03:00 | 0 | 0 | 0 | 0 | -0.21407 | -121.2766 | 96.9337 | -6.9337 | -120.5753 | 119.8453 | 0 | 0 | 0.8 | 1 | 0 | 0 | -17.6 | -17.6 | 1.1704 | 0
2015-03-21 04:00 | 9.26 | 5.5667 | 3.6933 | 0 | -0.1976 | -106.2734 | 93.8161 | -3.8161 | -105.8327 | 105.6066 | 0 | 4.175 | 0.8 | 1 | 1.852 | 6.027 | -17.1 | -16.9117 | 1.1676 | 0.0057707
2015-03-21 05:00 | 18.52 | 11.1333 | 7.3867 | 0 | -0.18114 | -91.2703 | 90.4629 | -0.46292 | -91.1967 | 91.2678 | 0 | 8.35 | 0.8 | 1 | 3.704 | 12.054 | -15.8 | -15.4233 | 1.1617 | 0.011483
2015-03-21 06:00 | 27.78 | 16.7 | 11.08 | 0 | -0.16468 | -76.2671 | 87.0917 | 2.9083 | -76.5718 | 76.9251 | 0 | 12.525 | 0.8 | 1 | 5.556 | 18.081 | -16.2 | -15.635 | 1.1625 | 0.017236
2015-03-21 07:00 | 61.9267 | 26.3433 | 35.5833 | 335.9991 | -0.14822 | -61.2639 | 83.9208 | 6.0792 | -61.8601 | 62.6713 | 154.2552 | 19.7575 | 0.8 | 1 | 12.3853 | 186.3981 | -14.8 | -8.9751 | 1.1359 | 0.17362
2015-03-21 08:00 | 96.0733 | 35.9867 | 60.0867 | 390.9922 | -0.13176 | -46.2607 | 81.1599 | 8.8401 | -46.9851 | 48.6533 | 258.2946 | 26.99 | 0.8 | 1 | 19.2147 | 304.4993 | -14.4 | -4.8844 | 1.1195 | 0.27954
2015-03-21 09:00 | 130.22 | 45.63 | 84.59 | 443.2933 | -0.1153 | -31.2575 | 78.9993 | 11.0007 | -31.9107 | 35.2096 | 362.1919 | 34.2225 | 0.8 | 1 | 26.044 | 422.4584 | -14.7 | -1.4982 | 1.106 | 0.38313
2015-03-21 10:00 | 136.7033 | 50.1667 | 86.5367 | 402.8283 | -0.098842 | -16.2543 | 77.5949 | 12.4051 | -16.654 | 23.4023 | 369.6911 | 37.625 | 0.8 | 1 | 27.3407 | 434.6567 | -14.1 | -0.51698 | 1.1021 | 0.3928
2015-03-21 11:00 | 143.1867 | 54.7033 | 88.4833 | 394.9036 | -0.082383 | -1.2511 | 77.0522 | 12.9478 | -1.2837 | 17.0935 | 377.4592 | 41.0275 | 0.8 | 1 | 28.6373 | 447.1241 | -13.8 | 0.17263 | 1.0993 | 0.40305
2015-03-21 12:00 | 149.67 | 59.24 | 90.43 | 414.9461 | -0.065924 | 13.7521 | 77.4124 | 12.5876 | 14.0977 | 21.764 | 385.3684 | 44.43 | 0.8 | 1 | 29.934 | 459.7324 | -13.2 | 1.1666 | 1.0953 | 0.41292
2015-03-21 13:00 | 120.1 | 51.1033 | 68.9967 | 350.4748 | -0.049466 | 28.7553 | 78.6462 | 11.3538 | 29.3848 | 33.0419 | 293.7931 | 38.3275 | 0.8 | 1 | 24.02 | 356.1406 | -13.4 | -2.2706 | 1.1091 | 0.32389
2015-03-21 14:00 | 90.53 | 42.9667 | 47.5633 | 293.0194 | -0.033008 | 43.7586 | 80.6583 | 9.3417 | 44.5006 | 46.318 | 202.3756 | 32.225 | 0.8 | 1 | 18.106 | 252.7066 | -13.6 | -5.7029 | 1.1228 | 0.23267
2015-03-21 15:00 | 60.96 | 34.83 | 26.13 | 223.9619 | -0.016551 | 58.7618 | 83.2999 | 6.7001 | 59.4175 | 60.2682 | 111.0719 | 26.1225 | 0.8 | 1 | 12.192 | 149.3864 | -13.9 | -9.2317 | 1.1369 | 0.13927
2015-03-21 16:00 | 40.9967 | 23.52 | 17.4767 | 277.195 | -9.4198e-05 | 73.765 | 86.3852 | 3.6148 | 74.1619 | 74.4899 | 74.1244 | 17.64 | 0.8 | 1 | 8.1993 | 99.9638 | -13.3 | -10.1761 | 1.1407 | 0.093504
2015-03-21 17:00 | 21.0333 | 12.21 | 8.8233 | 0 | 0.016362 | 88.7682 | 89.7063 | 0.29372 | 88.8036 | 88.817 | 0 | 9.1575 | 0.8 | 1 | 4.2067 | 13.3642 | -11.8 | -11.3824 | 1.1455 | 0.012553
2015-03-21 18:00 | 1.07 | 0.9 | 0.17 | 0 | 0.032818 | 103.7714 | 93.0453 | -3.0453 | 103.4368 | 103.1511 | 0 | 0.675 | 0.8 | 1 | 0.214 | 0.889 | -11.9 | -11.8722 | 1.1475 | 0.0008365
2015-03-21 19:00 | 0.71333 | 0.6 | 0.11333 | 0 | 0.049273 | 118.7746 | 96.1838 | -6.1838 | 118.158 | 117.3976 | 0 | 0.45 | 0.8 | 1 | 0.14267 | 0.59267 | -11.1 | -11.0815 | 1.1443 | 0.00055613
2015-03-21 20:00 | 0.35667 | 0.3 | 0.056667 | 0 | 0.065728 | 133.7778 | 98.9116 | -8.9116 | 133.0423 | 131.4079 | 0 | 0.225 | 0.8 | 1 | 0.071333 | 0.29633 | -10.6 | -10.5907 | 1.1424 | 0.00027759
2015-03-21 21:00 | 0 | 0 | 0 | 0 | 0.082183 | 148.781 | 101.0382 | -11.0382 | 148.1242 | 144.8404 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.4 | -10.4 | 1.1416 | 0
2015-03-21 22:00 | 0 | 0 | 0 | 0 | 0.098637 | 163.7842 | 102.4078 | -12.4078 | 163.3854 | 156.6238 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.1 | -10.1 | 1.1404 | 0
2015-03-21 23:00 | 0 | 0 | 0 | 0 | 0.11509 | 178.7875 | 102.9153 | -12.9153 | 178.756 | 162.8765 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.1 | -10.1 | 1.1404 | 0
2015-03-22 | 0 | 0 | 0 | 0 | 0.13154 | -166.2093 | 102.52 | -12.52 | -165.8665 | 158.1606 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.1 | -10.1 | 1.1404 | 0
2015-03-22 01:00 | 0 | 0 | 0 | 0 | 0.148 | -151.2061 | 101.2516 | -11.2516 | -150.5872 | 146.8726 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10 | -10 | 1.14 | 0
2015-03-22 02:00 | 0 | 0 | 0 | 0 | 0.16445 | -136.2029 | 99.2058 | -9.2058 | -135.4819 | 133.5936 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.05 | -10.05 | 1.1402 | 0
2015-03-22 03:00 | 0 | 0 | 0 | 0 | 0.1809 | -121.1997 | 96.5313 | -6.5313 | -120.5765 | 119.6401 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.1 | -10.1 | 1.1404 | 0
2015-03-22 04:00 | 3.98 | 3.98 | 0 | 0 | 0.19735 | -106.1964 | 93.4139 | -3.4139 | -105.8432 | 105.4135 | 0 | 2.985 | 0.8 | 1 | 0.796 | 3.781 | -10.2 | -10.0818 | 1.1403 | 0.0035355
2015-03-22 05:00 | 7.96 | 7.96 | 0 | 0 | 0.2138 | -91.1932 | 90.0608 | -0.060777 | -91.2107 | 91.0789 | 0 | 5.97 | 0.8 | 1 | 1.592 | 7.562 | -9.8 | -9.5637 | 1.1383 | 0.0070581
2015-03-22 06:00 | 11.94 | 11.94 | 0 | 0 | 0.23025 | -76.19 | 86.6895 | 3.3105 | -76.5832 | 76.7333 | 0 | 8.955 | 0.8 | 1 | 2.388 | 11.343 | -9.9 | -9.5455 | 1.1382 | 0.010587
2015-03-22 07:00 | 19.9867 | 19.1667 | 0.82 | 7.2641 | 0.2467 | -61.1868 | 83.5184 | 6.4816 | -61.8631 | 62.4688 | 3.3577 | 14.375 | 0.8 | 1 | 3.9973 | 21.73 | -10 | -9.3209 | 1.1373 | 0.020265
2015-03-22 08:00 | 28.0333 | 26.3933 | 1.64 | 10.2111 | 0.26315 | -46.1835 | 80.7577 | 9.2423 | -46.974 | 48.4289 | 6.7755 | 19.795 | 0.8 | 1 | 5.6067 | 32.1772 | -9.95 | -8.9445 | 1.1358 | 0.029968
2015-03-22 09:00 | 36.08 | 33.62 | 2.46 | 12.4436 | 0.27959 | -31.1803 | 78.598 | 11.402 | -31.8806 | 34.9433 | 10.2003 | 25.215 | 0.8 | 1 | 7.216 | 42.6313 | -9.9 | -8.5678 | 1.1343 | 0.039651
2015-03-22 10:00 | 49.9233 | 45.3033 | 4.62 | 20.8465 | 0.29604 | -16.1771 | 77.1958 | 12.8042 | -16.6011 | 23.0595 | 19.1809 | 33.9775 | 0.8 | 1 | 9.9847 | 63.143 | -9.6 | -7.6268 | 1.1305 | 0.058535
2015-03-22 11:00 | 63.7667 | 56.9867 | 6.78 | 29.3785 | 0.31249 | -1.1738 | 76.657 | 13.343 | -1.2064 | 16.6943 | 28.1403 | 42.74 | 0.8 | 1 | 12.7533 | 83.6336 | -9.7 | -7.0864 | 1.1283 | 0.077381
2015-03-22 12:00 | 77.61 | 68.67 | 8.94 | 39.8094 | 0.32893 | 13.8294 | 77.0224 | 12.9776 | 14.1992 | 21.5015 | 37.039 | 51.5025 | 0.8 | 1 | 15.522 | 104.0635 | -9.85 | -6.598 | 1.1264 | 0.096117
2015-03-22 13:00 | 62.4233 | 55.8133 | 6.61 | 32.4927 | 0.34538 | 28.8326 | 78.2624 | 11.7376 | 29.5079 | 32.8972 | 27.2824 | 41.86 | 0.8 | 1 | 12.4847 | 81.6271 | -10 | -7.4492 | 1.1298 | 0.075622
2015-03-22 14:00 | 47.2367 | 42.9567 | 4.28 | 25.3523 | 0.36183 | 43.8359 | 80.2807 | 9.7193 | 44.6413 | 46.2304 | 17.5377 | 32.2175 | 0.8 | 1 | 9.4473 | 59.2025 | -10.3 | -8.4499 | 1.1338 | 0.055042
2015-03-22 15:00 | 32.05 | 30.1 | 1.95 | 15.8379 | 0.37827 | 58.8391 | 82.9277 | 7.0723 | 59.5712 | 60.209 | 7.8689 | 22.575 | 0.8 | 1 | 6.41 | 36.8539 | -10.3 | -9.1483 | 1.1366 | 0.034348
2015-03-22 16:00 | 21.63 | 20.3267 | 1.3033 | 18.7618 | 0.39471 | 73.8423 | 86.0166 | 3.9834 | 74.3235 | 74.4444 | 5.0314 | 15.245 | 0.8 | 1 | 4.326 | 24.6024 | -10.5 | -9.7312 | 1.1389 | 0.022977
2015-03-22 17:00 | 11.21 | 10.5533 | 0.65667 | 0 | 0.41116 | 88.8456 | 89.3391 | 0.66089 | 88.968 | 88.7759 | 0 | 7.915 | 0.8 | 1 | 2.242 | 10.157 | -10.7 | -10.3826 | 1.1415 | 0.0095075
2015-03-22 18:00 | 0.79 | 0.78 | 0.01 | 0 | 0.4276 | 103.8488 | 92.6771 | -2.6771 | 103.5992 | 103.1063 | 0 | 0.585 | 0.8 | 1 | 0.158 | 0.743 | -11.1 | -11.0768 | 1.1443 | 0.00069718
2015-03-22 19:00 | 0.52667 | 0.52 | 0.0066667 | 0 | 0.44404 | 118.8521 | 95.8123 | -5.8123 | 118.3132 | 117.3401 | 0 | 0.39 | 0.8 | 1 | 0.10533 | 0.49533 | -11 | -10.9845 | 1.1439 | 0.00046464
2015-03-22 20:00 | 0.26333 | 0.26 | 0.0033333 | 0 | 0.46048 | 133.8553 | 98.535 | -8.535 | 133.1854 | 131.324 | 0 | 0.195 | 0.8 | 1 | 0.052667 | 0.24767 | -10.9 | -10.8923 | 1.1436 | 0.00023224
2015-03-22 21:00 | 0 | 0 | 0 | 0 | 0.47692 | 148.8585 | 100.6555 | -10.6555 | 148.2504 | 144.7045 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11 | -11 | 1.144 | 0
2015-03-22 22:00 | 0 | 0 | 0 | 0 | 0.49336 | 163.8618 | 102.0189 | -12.0189 | 163.4905 | 156.382 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.3 | -11.3 | 1.1452 | 0
2015-03-22 23:00 | 0 | 0 | 0 | 0 | 0.5098 | 178.865 | 102.5209 | -12.5209 | 178.8374 | 162.4878 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.6 | -11.6 | 1.1464 | 0
2015-03-23 | 0 | 0 | 0 | 0 | 0.52624 | -166.1317 | 102.1216 | -12.1216 | -165.8095 | 157.8004 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.9 | -11.9 | 1.1476 | 0
2015-03-23 01:00 | 0 | 0 | 0 | 0 | 0.54268 | -151.1285 | 100.8507 | -10.8507 | -150.5532 | 146.5938 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.6 | -12.6 | 1.1504 | 0
2015-03-23 02:00 | 0 | 0 | 0 | 0 | 0.55911 | -136.1252 | 98.8038 | -8.8038 | -135.4675 | 133.3616 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.6 | -12.6 | 1.1504 | 0
2015-03-23 03:00 | 0 | 0 | 0 | 0 | 0.57555 | -121.122 | 96.1291 | -6.1291 | -120.5769 | 119.4332 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.9 | -12.9 | 1.1516 | 0
2015-03-23 04:00 | 9.3 | 8.9267 | 0.37333 | 0 | 0.59199 | -106.1187 | 93.0118 | -3.0118 | -105.853 | 105.2194 | 0 | 6.695 | 0.8 | 1 | 1.86 | 8.555 | -13.1 | -12.8327 | 1.1513 | 0.0080767
2015-03-23 05:00 | 18.6 | 17.8533 | 0.74667 | 0 | 0.60842 | -91.1155 | 89.6588 | 0.34121 | -91.2239 | 90.8893 | 0 | 13.39 | 0.8 | 1 | 3.72 | 17.11 | -13.65 | -13.1153 | 1.1525 | 0.016169
2015-03-23 06:00 | 27.9 | 26.78 | 1.12 | 17.2972 | 0.62485 | -76.1122 | 86.2875 | 3.7125 | -76.5939 | 76.5414 | 4.0258 | 20.085 | 0.8 | 1 | 5.58 | 29.6908 | -14.2 | -13.2722 | 1.1531 | 0.028074
2015-03-23 07:00 | 57.46 | 48.6333 | 8.8267 | 73.6445 | 0.64129 | -61.109 | 83.1163 | 6.8837 | -61.8654 | 62.2669 | 34.2707 | 36.475 | 0.8 | 1 | 11.492 | 82.2377 | -14.5 | -11.9301 | 1.1477 | 0.077396
2015-03-23 08:00 | 87.02 | 70.4867 | 16.5333 | 98.6879 | 0.65772 | -46.1057 | 80.3557 | 9.6443 | -46.9621 | 48.2057 | 65.7714 | 52.865 | 0.8 | 1 | 17.404 | 136.0404 | -14.5 | -10.2487 | 1.141 | 0.12728
2015-03-23 09:00 | 116.58 | 92.34 | 24.24 | 118.5052 | 0.67415 | -31.1025 | 78.197 | 11.803 | -31.8496 | 34.6789 | 97.4531 | 69.255 | 0.8 | 1 | 23.316 | 190.0241 | -14.1 | -8.1617 | 1.1326 | 0.17649
2015-03-23 10:00 | 124.02 | 92.7867 | 31.2333 | 136.7483 | 0.69058 | -16.0992 | 76.7971 | 13.2029 | -16.5475 | 22.7183 | 126.1387 | 69.59 | 0.8 | 1 | 24.804 | 220.5327 | -14.4 | -7.5084 | 1.13 | 0.20435
2015-03-23 11:00 | 131.46 | 93.2333 | 38.2267 | 160.9673 | 0.70701 | -1.0959 | 76.2621 | 13.7379 | -1.1281 | 16.2954 | 154.5008 | 69.925 | 0.8 | 1 | 26.292 | 250.7178 | -14.7 | -6.8651 | 1.1275 | 0.23179
2015-03-23 12:00 | 138.9 | 93.68 | 45.22 | 195.5963 | 0.72344 | 13.9073 | 76.6328 | 13.3672 | 14.3015 | 21.2438 | 182.3049 | 70.26 | 0.8 | 1 | 27.78 | 280.3449 | -14.7 | -5.9392 | 1.1238 | 0.25833
2015-03-23 13:00 | 114.5733 | 77.6133 | 36.96 | 176.0197 | 0.73987 | 28.9106 | 77.879 | 12.121 | 29.6319 | 32.757 | 148.0277 | 58.21 | 0.8 | 1 | 22.9147 | 229.1524 | -14.6 | -7.439 | 1.1298 | 0.21229
2015-03-23 14:00 | 90.2467 | 61.5467 | 28.7 | 163.7149 | 0.7563 | 43.9138 | 79.9036 | 10.0964 | 44.783 | 46.1462 | 113.425 | 46.16 | 0.8 | 1 | 18.0493 | 177.6344 | -14.6 | -9.0489 | 1.1362 | 0.1655
2015-03-23 15:00 | 65.92 | 45.48 | 20.44 | 157.767 | 0.77273 | 58.9171 | 82.5559 | 7.4441 | 59.7257 | 60.1522 | 78.5202 | 34.11 | 0.8 | 1 | 13.184 | 125.8142 | -14.4 | -10.4683 | 1.1419 | 0.1178
2015-03-23 16:00 | 44.6467 | 30.9133 | 13.7333 | 181.0003 | 0.78915 | 73.9204 | 85.6485 | 4.3515 | 74.4858 | 74.4005 | 48.6732 | 23.185 | 0.8 | 1 | 8.9293 | 80.7875 | -14 | -11.4754 | 1.1459 | 0.075911
2015-03-23 17:00 | 23.3733 | 16.3467 | 7.0267 | 0 | 0.80558 | 88.9236 | 88.9724 | 1.0276 | 89.133 | 88.7355 | 0 | 12.26 | 0.8 | 1 | 4.6747 | 16.9347 | -13.9 | -13.3708 | 1.1535 | 0.016018
2015-03-23 18:00 | 2.1 | 1.78 | 0.32 | 0 | 0.82201 | 103.9269 | 92.3094 | -2.3094 | 103.7619 | 103.0615 | 0 | 1.335 | 0.8 | 1 | 0.42 | 1.755 | -14.3 | -14.2452 | 1.157 | 0.001665
2015-03-23 19:00 | 1.4 | 1.1867 | 0.21333 | 0 | 0.83843 | 118.9301 | 95.4413 | -5.4413 | 118.4687 | 117.2819 | 0 | 0.89 | 0.8 | 1 | 0.28 | 1.17 | -13.7 | -13.6634 | 1.1547 | 0.0011078
2015-03-23 20:00 | 0.7 | 0.59333 | 0.10667 | 0 | 0.85485 | 133.9334 | 98.1588 | -8.1588 | 133.3287 | 131.2385 | 0 | 0.445 | 0.8 | 1 | 0.14 | 0.585 | -13.5 | -13.4817 | 1.1539 | 0.00055354
2015-03-23 21:00 | 0 | 0 | 0 | 0 | 0.87128 | 148.9367 | 100.2732 | -10.2732 | 148.3768 | 144.5658 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.7 | -13.7 | 1.1548 | 0
2015-03-23 22:00 | 0 | 0 | 0 | 0 | 0.8877 | 163.9399 | 101.6304 | -11.6304 | 163.5959 | 156.1369 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.4 | -13.4 | 1.1536 | 0
2015-03-23 23:00 | 0 | 0 | 0 | 0 | 0.90412 | 178.9432 | 102.127 | -12.127 | 178.9192 | 162.0989 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.2 | -13.2 | 1.1528 | 0
2015-03-24 | 0 | 0 | 0 | 0 | 0.92054 | -166.0535 | 101.7236 | -11.7236 | -165.7521 | 157.4389 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.5 | -13.5 | 1.154 | 0
2015-03-24 01:00 | 0 | 0 | 0 | 0 | 0.93696 | -151.0502 | 100.4502 | -10.4502 | -150.5186 | 146.3124 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.2 | -13.2 | 1.1528 | 0
2015-03-24 02:00 | 0 | 0 | 0 | 0 | 0.95337 | -136.047 | 98.4021 | -8.4021 | -135.4524 | 133.1275 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.4 | -13.4 | 1.1536 | 0
2015-03-24 03:00 | 0 | 0 | 0 | 0 | 0.96979 | -121.0437 | 95.7272 | -5.7272 | -120.5767 | 119.2247 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.2 | -13.2 | 1.1528 | 0
2015-03-24 04:00 | 10.0367 | 6.52 | 3.5167 | 0 | 0.98621 | -106.0404 | 92.61 | -2.61 | -105.8621 | 105.0242 | 0 | 4.89 | 0.8 | 1 | 2.0073 | 6.8973 | -15.2 | -14.9845 | 1.1599 | 0.0065604
2015-03-24 05:00 | 20.0733 | 13.04 | 7.0333 | 0 | 1.0026 | -91.0372 | 89.2571 | 0.74292 | -91.2365 | 90.6993 | 0 | 9.78 | 0.8 | 1 | 4.0147 | 13.7947 | -13.3 | -12.8689 | 1.1515 | 0.013025
2015-03-24 06:00 | 30.11 | 19.56 | 10.55 | 147.0461 | 1.019 | -76.0339 | 85.8857 | 4.1143 | -76.604 | 76.3496 | 34.7024 | 14.67 | 0.8 | 1 | 6.022 | 55.3944 | -14.5 | -12.7689 | 1.1511 | 0.052286
2015-03-24 07:00 | 66.25 | 33.7367 | 32.5133 | 256.3828 | 1.0355 | -61.0306 | 82.7144 | 7.2856 | -61.867 | 62.0657 | 120.1048 | 25.3025 | 0.8 | 1 | 13.25 | 158.6573 | -14.1 | -9.142 | 1.1366 | 0.14787
2015-03-24 08:00 | 102.39 | 47.9133 | 54.4767 | 312.297 | 1.0519 | -46.0273 | 79.954 | 10.046 | -46.9496 | 47.9839 | 209.0328 | 35.935 | 0.8 | 1 | 20.478 | 265.4458 | -13 | -4.7048 | 1.1188 | 0.24353
2015-03-24 09:00 | 138.53 | 62.09 | 76.44 | 361.6103 | 1.0683 | -31.0241 | 77.7963 | 12.2037 | -31.818 | 34.4166 | 298.3105 | 46.5675 | 0.8 | 1 | 27.706 | 372.584 | -13 | -1.3568 | 1.1054 | 0.33773
2015-03-24 10:00 | 147.75 | 67.3867 | 80.3633 | 341.7348 | 1.0847 | -16.0208 | 76.3988 | 13.6012 | -16.493 | 22.3789 | 315.9974 | 50.54 | 0.8 | 1 | 29.55 | 396.0874 | -12.9 | -0.52227 | 1.1021 | 0.35795
2015-03-24 11:00 | 156.97 | 72.6833 | 84.2867 | 345.2076 | 1.1011 | -1.0175 | 75.8677 | 14.1323 | -1.0491 | 15.8971 | 332.0051 | 54.5125 | 0.8 | 1 | 31.394 | 417.9116 | -11.8 | 1.2597 | 1.095 | 0.37523
2015-03-24 12:00 | 166.19 | 77.98 | 88.21 | 370.9553 | 1.1175 | 13.9858 | 76.2438 | 13.7562 | 14.4048 | 20.9912 | 346.337 | 58.485 | 0.8 | 1 | 33.238 | 438.06 | -11.3 | 2.3894 | 1.0904 | 0.3917
2015-03-24 13:00 | 145.0167 | 64.9567 | 80.06 | 369.7852 | 1.1339 | 28.9891 | 77.4962 | 12.5038 | 29.7568 | 32.6214 | 311.452 | 48.7175 | 0.8 | 1 | 29.0033 | 389.1728 | -11.5 | 0.66165 | 1.0974 | 0.35019
2015-03-24 14:00 | 123.8433 | 51.9333 | 71.91 | 395.6085 | 1.1503 | 43.9923 | 79.5271 | 10.4729 | 44.9255 | 46.0652 | 274.4885 | 38.95 | 0.8 | 1 | 24.7687 | 338.2072 | -11.8 | -1.231 | 1.1049 | 0.30643
2015-03-24 15:00 | 102.67 | 38.91 | 63.76 | 468.8985 | 1.1667 | 58.9956 | 82.1848 | 7.8152 | 59.8809 | 60.0977 | 233.7568 | 29.1825 | 0.8 | 1 | 20.534 | 283.4733 | -11.8 | -2.9415 | 1.1118 | 0.25843
2015-03-24 16:00 | 69.5067 | 26.8067 | 42.7 | 519.034 | 1.1831 | 73.9989 | 85.281 | 4.719 | 74.6486 | 74.3579 | 139.9455 | 20.105 | 0.8 | 1 | 13.9013 | 173.9519 | -12.6 | -7.164 | 1.1287 | 0.16099
2015-03-24 17:00 | 36.3433 | 14.7033 | 21.64 | 0 | 1.1995 | 89.0022 | 88.6063 | 1.3937 | 89.2984 | 88.6958 | 0 | 11.0275 | 0.8 | 1 | 7.2687 | 18.2962 | -13.7 | -13.1282 | 1.1525 | 0.017291
2015-03-24 18:00 | 3.18 | 2.6 | 0.58 | 0 | 1.2159 | 104.0055 | 91.9423 | -1.9423 | 103.925 | 103.0168 | 0 | 1.95 | 0.8 | 1 | 0.636 | 2.586 | -13 | -12.9192 | 1.1517 | 0.0024422
2015-03-24 19:00 | 2.12 | 1.7333 | 0.38667 | 0 | 1.2323 | 119.0088 | 95.0707 | -5.0707 | 118.6245 | 117.2229 | 0 | 1.3 | 0.8 | 1 | 0.424 | 1.724 | -14.4 | -14.3461 | 1.1574 | 0.0016362
2015-03-24 20:00 | 1.06 | 0.86667 | 0.19333 | 0 | 1.2487 | 134.012 | 97.7831 | -7.7831 | 133.4722 | 131.1514 | 0 | 0.65 | 0.8 | 1 | 0.212 | 0.862 | -13.4 | -13.3731 | 1.1535 | 0.00081533
2015-03-24 21:00 | 0 | 0 | 0 | 0 | 1.2651 | 149.0153 | 99.8913 | -9.8913 | 148.5033 | 144.4243 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13 | -13 | 1.152 | 0
2015-03-24 22:00 | 0 | 0 | 0 | 0 | 1.2815 | 164.0186 | 101.2423 | -11.2423 | 163.7015 | 155.8884 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.3 | -13.3 | 1.1532 | 0
2015-03-24 23:00 | 0 | 0 | 0 | 0 | 1.2979 | 179.0219 | 101.7335 | -11.7335 | 179.0013 | 161.7099 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.6 | -13.6 | 1.1544 | 0
2015-03-25 | 0 | 0 | 0 | 0 | 1.3143 | -165.9748 | 101.326 | -11.326 | -165.6942 | 157.0762 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.35 | -13.35 | 1.1534 | 0
2015-03-25 01:00 | 0 | 0 | 0 | 0 | 1.3307 | -150.9715 | 100.0501 | -10.0501 | -150.4836 | 146.0288 | 0 | 0 | 0.8 | 1 | 0 | 0 | -13.1 | -13.1 | 1.1524 | 0
2015-03-25 02:00 | 0 | 0 | 0 | 0 | 1.3471 | -135.9682 | 98.0009 | -8.0009 | -135.4368 | 132.8914 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.85 | -12.85 | 1.1514 | 0
2015-03-25 03:00 | 0 | 0 | 0 | 0 | 1.3635 | -120.9649 | 95.3257 | -5.3257 | -120.5759 | 119.0148 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.6 | -12.6 | 1.1504 | 0
2015-03-25 04:00 | 8.85 | 7.2733 | 1.5767 | 0 | 1.3799 | -105.9616 | 92.2085 | -2.2085 | -105.8706 | 104.8282 | 0 | 5.455 | 0.8 | 1 | 1.77 | 7.225 | -13.3 | -13.0742 | 1.1523 | 0.0068268
2015-03-25 05:00 | 17.7 | 14.5467 | 3.1533 | 0 | 1.3963 | -90.9583 | 88.8558 | 1.1442 | -91.2485 | 90.5089 | 0 | 10.91 | 0.8 | 1 | 3.54 | 14.45 | -12.6 | -12.1484 | 1.1486 | 0.01361
2015-03-25 06:00 | 26.55 | 21.82 | 4.73 | 60.0777 | 1.4127 | -75.9551 | 85.4844 | 4.5156 | -76.6135 | 76.1581 | 14.3732 | 16.365 | 0.8 | 1 | 5.31 | 36.0482 | -12.5 | -11.3735 | 1.1455 | 0.03386
2015-03-25 07:00 | 60.58 | 33 | 27.58 | 206.1864 | 1.4291 | -60.9518 | 82.3129 | 7.6871 | -61.8681 | 61.8653 | 97.2263 | 24.75 | 0.8 | 1 | 12.116 | 134.0923 | -12.1 | -7.9096 | 1.1316 | 0.12443
2015-03-25 08:00 | 94.61 | 44.18 | 50.43 | 278.1122 | 1.4455 | -45.9485 | 79.5528 | 10.4472 | -46.9365 | 47.7636 | 186.9446 | 33.135 | 0.8 | 1 | 18.922 | 239.0016 | -12.4 | -4.9312 | 1.1197 | 0.21945
2015-03-25 09:00 | 128.64 | 55.36 | 73.28 | 335.8247 | 1.4619 | -30.9452 | 77.3961 | 12.6039 | -31.7857 | 34.1565 | 277.8975 | 41.52 | 0.8 | 1 | 25.728 | 345.1455 | -11.8 | -1.0142 | 1.1041 | 0.31247
2015-03-25 10:00 | 138.8867 | 62.18 | 76.7067 | 317.0936 | 1.4783 | -15.9419 | 76.001 | 13.999 | -16.4378 | 22.0416 | 293.9177 | 46.635 | 0.8 | 1 | 27.7773 | 368.33 | -11.7 | -0.18969 | 1.1008 | 0.33246
2015-03-25 11:00 | 149.1333 | 69 | 80.1333 | 319.4824 | 1.4946 | -0.93858 | 75.4738 | 14.5262 | -0.96925 | 15.4996 | 307.8636 | 51.75 | 0.8 | 1 | 29.8267 | 389.4403 | -11.1 | 1.07 | 1.0957 | 0.34991
2015-03-25 12:00 | 159.38 | 75.82 | 83.56 | 341.9388 | 1.511 | 14.0647 | 75.8553 | 14.1447 | 14.5088 | 20.7438 | 319.7722 | 56.865 | 0.8 | 1 | 31.876 | 408.5132 | -10.7 | 2.066 | 1.0917 | 0.36571
2015-03-25 13:00 | 123.6267 | 67.53 | 56.0967 | 251.5423 | 1.5274 | 29.068 | 77.1141 | 12.8859 | 29.8824 | 32.4904 | 212.1714 | 50.6475 | 0.8 | 1 | 24.7253 | 287.5442 | -10.9 | -1.9142 | 1.1077 | 0.26117
2015-03-25 14:00 | 87.8733 | 59.24 | 28.6333 | 152.1294 | 1.5438 | 44.0713 | 79.1513 | 10.8487 | 45.0687 | 45.9875 | 105.7018 | 44.43 | 0.8 | 1 | 17.5747 | 167.7065 | -10.7 | -5.4592 | 1.1218 | 0.15427
2015-03-25 15:00 | 52.12 | 50.95 | 1.17 | 8.2174 | 1.5602 | 59.0746 | 81.8144 | 8.1856 | 60.0367 | 60.0453 | 4.1031 | 38.2125 | 0.8 | 1 | 10.424 | 52.7396 | -9.8 | -8.1519 | 1.1326 | 0.048981
2015-03-25 16:00 | 35.63 | 34.8467 | 0.78333 | 8.8366 | 1.5765 | 74.0779 | 84.9142 | 5.0858 | 74.8119 | 74.3168 | 2.3887 | 26.135 | 0.8 | 1 | 7.126 | 35.6497 | -10.3 | -9.1859 | 1.1367 | 0.03323
2015-03-25 17:00 | 19.14 | 18.7433 | 0.39667 | 0 | 1.5929 | 89.0812 | 88.2409 | 1.7591 | 89.4642 | 88.6567 | 0 | 14.0575 | 0.8 | 1 | 3.828 | 17.8855 | -10.2 | -9.6411 | 1.1386 | 0.016698
2015-03-25 18:00 | 2.65 | 2.64 | 0.01 | 0 | 1.6093 | 104.0845 | 91.5757 | -1.5757 | 104.0882 | 102.9719 | 0 | 1.98 | 0.8 | 1 | 0.53 | 2.51 | -9.7 | -9.6216 | 1.1385 | 0.0023432
2015-03-25 19:00 | 1.7667 | 1.76 | 0.0066667 | 0 | 1.6257 | 119.0878 | 94.7008 | -4.7008 | 118.7803 | 117.163 | 0 | 1.32 | 0.8 | 1 | 0.35333 | 1.6733 | -7.9 | -7.8477 | 1.1314 | 0.0015524
2015-03-25 20:00 | 0.88333 | 0.88 | 0.0033333 | 0 | 1.6421 | 134.0911 | 97.408 | -7.408 | 133.6157 | 131.0624 | 0 | 0.66 | 0.8 | 1 | 0.17667 | 0.83667 | -5.4 | -5.3739 | 1.1215 | 0.00076942
2015-03-25 21:00 | 0 | 0 | 0 | 0 | 1.6584 | 149.0944 | 99.5101 | -9.5101 | 148.6299 | 144.28 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2 | -4.2 | 1.1168 | 0
2015-03-25 22:00 | 0 | 0 | 0 | 0 | 1.6748 | 164.0977 | 100.8548 | -10.8548 | 163.8072 | 155.6368 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-03-25 23:00 | 0 | 0 | 0 | 0 | 1.6912 | 179.101 | 101.3405 | -11.3405 | 179.0835 | 161.3211 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.5 | -2.5 | 1.11 | 0
2015-03-26 | 0 | 0 | 0 | 0 | 1.7075 | -165.8957 | 100.929 | -10.929 | -165.6361 | 156.7126 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-03-26 01:00 | 0.023333 | 0.023333 | 0 | 0 | 1.7239 | -150.8924 | 99.6506 | -9.6506 | -150.4481 | 145.7431 | 0 | 0.0175 | 0.8 | 1 | 0.0046667 | 0.022167 | -2.6 | -2.5993 | 1.1104 | 2.0183e-05
2015-03-26 02:00 | 0.046667 | 0.046667 | 0 | 0 | 1.7403 | -135.8891 | 97.6002 | -7.6002 | -135.4208 | 132.6536 | 0 | 0.035 | 0.8 | 1 | 0.0093333 | 0.044333 | -2.2 | -2.1986 | 1.1088 | 4.0308e-05
2015-03-26 03:00 | 0.07 | 0.07 | 0 | 0 | 1.7567 | -120.8858 | 94.9246 | -4.9246 | -120.5746 | 118.8036 | 0 | 0.0525 | 0.8 | 1 | 0.014 | 0.0665 | -1.9 | -1.8979 | 1.1076 | 6.0397e-05
2015-03-26 04:00 | 6.85 | 6.85 | 0 | 0 | 1.773 | -105.8825 | 91.8076 | -1.8076 | -105.8787 | 104.6314 | 0 | 5.1375 | 0.8 | 1 | 1.37 | 6.5075 | -0.3 | -0.096641 | 1.1004 | 0.0058718
2015-03-26 05:00 | 13.63 | 13.63 | 0 | 0 | 1.7894 | -90.8792 | 88.455 | 1.545 | -91.2601 | 90.3184 | 0 | 10.2225 | 0.8 | 1 | 2.726 | 12.9485 | -0.8 | -0.39536 | 1.1016 | 0.011696
2015-03-26 06:00 | 20.41 | 20.41 | 0 | 0 | 1.8057 | -75.8758 | 85.0835 | 4.9165 | -76.6226 | 75.9669 | 0 | 15.3075 | 0.8 | 1 | 4.082 | 19.3895 | -0.4 | 0.20592 | 1.0992 | 0.017476
2015-03-26 07:00 | 30.2233 | 29.2767 | 0.94667 | 6.7286 | 1.8221 | -60.8725 | 81.912 | 8.088 | -61.8687 | 61.666 | 3.1935 | 21.9575 | 0.8 | 1 | 6.0447 | 31.1956 | 0.3 | 1.2749 | 1.0949 | 0.028008
2015-03-26 08:00 | 40.0367 | 38.1433 | 1.8933 | 10.0601 | 1.8385 | -45.8692 | 79.1521 | 10.8479 | -46.9229 | 47.545 | 6.7907 | 28.6075 | 0.8 | 1 | 8.0073 | 43.4055 | 1 | 2.3564 | 1.0906 | 0.038816
2015-03-26 09:00 | 49.85 | 47.01 | 2.84 | 12.6217 | 1.8548 | -30.8659 | 76.9965 | 13.0035 | -31.7529 | 33.8988 | 10.4763 | 35.2575 | 0.8 | 1 | 9.97 | 55.7038 | 0.9 | 2.6407 | 1.0894 | 0.049762
2015-03-26 10:00 | 54.0267 | 52.1133 | 1.9133 | 7.6956 | 1.8712 | -15.8626 | 75.6038 | 14.3962 | -16.3821 | 21.7066 | 7.1499 | 39.085 | 0.8 | 1 | 10.8053 | 57.0403 | 1.1 | 2.8825 | 1.0885 | 0.050911
2015-03-26 11:00 | 58.2033 | 57.2167 | 0.98667 | 3.8323 | 1.8875 | -0.85931 | 75.0806 | 14.9194 | -0.8888 | 15.1028 | 3.6999 | 42.9125 | 0.8 | 1 | 11.6407 | 58.2531 | 1 | 2.8204 | 1.0887 | 0.052005
2015-03-26 12:00 | 62.38 | 62.32 | 0.06 | 0.23911 | 1.9039 | 14.144 | 75.4676 | 14.5324 | 14.6135 | 20.5017 | 0.22397 | 46.74 | 0.8 | 1 | 12.476 | 59.44 | 0.6 | 2.4575 | 1.0902 | 0.053136
2015-03-26 13:00 | 54.6233 | 54.5733 | 0.05 | 0.21787 | 1.9203 | 29.1473 | 76.7326 | 13.2674 | 30.0087 | 32.3639 | 0.18403 | 40.93 | 0.8 | 1 | 10.9247 | 52.0387 | 0.9 | 2.5262 | 1.0899 | 0.046508
2015-03-26 14:00 | 46.8667 | 46.8267 | 0.04 | 0.20551 | 1.9366 | 44.1506 | 78.7762 | 11.2238 | 45.2124 | 45.9129 | 0.14298 | 35.12 | 0.8 | 1 | 9.3733 | 44.6363 | 1.2 | 2.5949 | 1.0896 | 0.039882
2015-03-26 15:00 | 39.11 | 39.08 | 0.03 | 0.20166 | 1.953 | 59.1539 | 81.4447 | 8.5553 | 60.193 | 59.995 | 0.10085 | 29.31 | 0.8 | 1 | 7.822 | 37.2328 | 1.1 | 2.2635 | 1.0909 | 0.033308
2015-03-26 16:00 | 26.9467 | 26.8767 | 0.07 | 0.73678 | 1.9693 | 74.1572 | 84.5482 | 5.4518 | 74.9755 | 74.2768 | 0.19966 | 20.1575 | 0.8 | 1 | 5.3893 | 25.7465 | 1 | 1.8046 | 1.0928 | 0.023071
2015-03-26 17:00 | 14.7833 | 14.6733 | 0.11 | 0 | 1.9857 | 89.1606 | 87.8762 | 2.1238 | 89.6302 | 88.6181 | 0 | 11.005 | 0.8 | 1 | 2.9567 | 13.9617 | 0.7 | 1.1363 | 1.0955 | 0.012541
2015-03-26 18:00 | 2.62 | 2.47 | 0.15 | 0 | 2.002 | 104.1639 | 91.2099 | -1.2099 | 104.2516 | 102.9269 | 0 | 1.8525 | 0.8 | 1 | 0.524 | 2.3765 | 0.7 | 0.77427 | 1.0969 | 0.0021376
2015-03-26 19:00 | 1.7467 | 1.6467 | 0.1 | 0 | 2.0184 | 119.1672 | 94.3315 | -4.3315 | 118.9362 | 117.1023 | 0 | 1.235 | 0.8 | 1 | 0.34933 | 1.5843 | 0.8 | 0.84951 | 1.0966 | 0.0014247
2015-03-26 20:00 | 0.87333 | 0.82333 | 0.05 | 0 | 2.0347 | 134.1705 | 97.0336 | -7.0336 | 133.7592 | 130.9717 | 0 | 0.6175 | 0.8 | 1 | 0.17467 | 0.79217 | 0.7 | 0.72476 | 1.0971 | 0.00071265
2015-03-26 21:00 | 0 | 0 | 0 | 0 | 2.051 | 149.1738 | 99.1295 | -9.1295 | 148.7564 | 144.133 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-03-26 22:00 | 0 | 0 | 0 | 0 | 2.0674 | 164.1771 | 100.468 | -10.468 | 163.9129 | 155.3822 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.8 | 0.8 | 1.0968 | 0
2015-03-26 23:00 | 0 | 0 | 0 | 0 | 2.0837 | 179.1804 | 100.9483 | -10.9483 | 179.1658 | 160.9325 | 0 | 0 | 0.8 | 1 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-03-27 | 0 | 0 | 0 | 0 | 2.1001 | -165.8162 | 100.5326 | -10.5326 | -165.5778 | 156.3482 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-03-27 01:00 | 0.093333 | 0.07 | 0.023333 | 0 | 2.1164 | -150.8129 | 99.2517 | -9.2517 | -150.4125 | 145.4556 | 0 | 0.0525 | 0.8 | 1 | 0.018667 | 0.071167 | 0.3 | 0.30222 | 1.0988 | 6.4122e-05
2015-03-27 02:00 | 0.18667 | 0.14 | 0.046667 | 0 | 2.1327 | -135.8096 | 97.2001 | -7.2001 | -135.4044 | 132.4141 | 0 | 0.105 | 0.8 | 1 | 0.037333 | 0.14233 | 0 | 0.0044479 | 1.1 | 0.00012838
2015-03-27 03:00 | 0.28 | 0.21 | 0.07 | 0 | 2.1491 | -120.8063 | 94.5243 | -4.5243 | -120.573 | 118.5913 | 0 | 0.1575 | 0.8 | 1 | 0.056 | 0.2135 | 0.3 | 0.30667 | 1.0988 | 0.00019236
2015-03-27 04:00 | 14.19 | 12.22 | 1.97 | 0 | 2.1654 | -105.803 | 91.4073 | -1.4073 | -105.8863 | 104.434 | 0 | 9.165 | 0.8 | 1 | 2.838 | 12.003 | 1.1 | 1.4751 | 1.0941 | 0.010769
2015-03-27 05:00 | 28.1 | 24.23 | 3.87 | 0 | 2.1817 | -90.7997 | 88.0548 | 1.9452 | -91.2712 | 90.1278 | 0 | 18.1725 | 0.8 | 1 | 5.62 | 23.7925 | 0.6 | 1.3435 | 1.0946 | 0.021356
2015-03-27 06:00 | 42.01 | 36.24 | 5.77 | 62.2703 | 2.1981 | -75.7964 | 84.6833 | 5.3167 | -76.6312 | 75.7763 | 15.3004 | 27.18 | 0.8 | 1 | 8.402 | 50.8824 | 0.6 | 2.1901 | 1.0912 | 0.04553
2015-03-27 07:00 | 63.84 | 52.8567 | 10.9833 | 74.4095 | 2.2144 | -60.793 | 81.5118 | 8.4882 | -61.8689 | 61.4677 | 35.542 | 39.6425 | 0.8 | 1 | 12.768 | 87.9525 | 0.8 | 3.5485 | 1.0858 | 0.078309
2015-03-27 08:00 | 85.67 | 69.4733 | 16.1967 | 83.0368 | 2.2307 | -45.7897 | 78.7521 | 11.2479 | -46.9089 | 47.3283 | 56.2821 | 52.105 | 0.8 | 1 | 17.134 | 125.5211 | 1.2 | 5.1225 | 1.0795 | 0.11111
2015-03-27 09:00 | 107.5 | 86.09 | 21.41 | 92.369 | 2.2471 | -30.7864 | 76.5977 | 13.4023 | -31.7197 | 33.6436 | 76.8971 | 64.5675 | 0.8 | 1 | 21.5 | 162.9646 | 0.9 | 5.9926 | 1.076 | 0.14379
2015-03-27 10:00 | 85.6033 | 71.33 | 14.2733 | 55.9032 | 2.2634 | -15.7831 | 75.2073 | 14.7927 | -16.3259 | 21.3741 | 52.0583 | 53.4975 | 0.8 | 1 | 17.1207 | 122.6764 | 1.1 | 4.9336 | 1.0803 | 0.10867
2015-03-27 11:00 | 63.7067 | 56.57 | 7.1367 | 27.0255 | 2.2797 | -0.77977 | 74.6882 | 15.3118 | -0.80783 | 14.7069 | 26.14 | 42.4275 | 0.8 | 1 | 12.7413 | 81.3089 | 1.6 | 4.1409 | 1.0834 | 0.072236
2015-03-27 12:00 | 41.81 | 41.81 | 0 | 0 | 2.296 | 14.2236 | 75.0806 | 14.9194 | 14.7187 | 20.2651 | 0 | 31.3575 | 0.8 | 1 | 8.362 | 39.7195 | 0.4 | 1.6412 | 1.0934 | 0.035613
2015-03-27 13:00 | 37.8067 | 37.2467 | 0.56 | 2.3733 | 2.3124 | 29.2269 | 76.352 | 13.648 | 30.1355 | 32.2419 | 2.0074 | 27.935 | 0.8 | 1 | 7.5613 | 37.5037 | 0.2 | 1.372 | 1.0945 | 0.03366
2015-03-27 14:00 | 33.8033 | 32.6833 | 1.12 | 5.5709 | 2.3287 | 44.2302 | 78.4019 | 11.5981 | 45.3566 | 45.8414 | 3.8809 | 24.5125 | 0.8 | 1 | 6.7607 | 35.1541 | 0.4 | 1.4986 | 1.094 | 0.031536
2015-03-27 15:00 | 29.8 | 28.12 | 1.68 | 10.8298 | 2.345 | 59.2335 | 81.0758 | 8.9242 | 60.3496 | 59.9467 | 5.4236 | 21.09 | 0.8 | 1 | 5.96 | 32.4736 | -0.3 | 0.7148 | 1.0971 | 0.029215
2015-03-27 16:00 | 21.0067 | 19.5767 | 1.43 | 14.1092 | 2.3613 | 74.2368 | 84.183 | 5.817 | 75.1394 | 74.2381 | 3.8326 | 14.6825 | 0.8 | 1 | 4.2013 | 22.7165 | -0.6 | 0.10989 | 1.0996 | 0.020482
2015-03-27 17:00 | 12.2133 | 11.0333 | 1.18 | 0 | 2.3776 | 89.2401 | 87.5123 | 2.4877 | 89.7962 | 88.5801 | 0 | 8.275 | 0.8 | 1 | 2.4427 | 10.7177 | -0.2 | 0.13493 | 1.0995 | 0.0096626
2015-03-27 18:00 | 3.42 | 2.49 | 0.93 | 0 | 2.3939 | 104.2435 | 90.8448 | -0.84484 | 104.4149 | 102.8817 | 0 | 1.8675 | 0.8 | 1 | 0.684 | 2.5515 | -0.7 | -0.62027 | 1.1025 | 0.0023066
2015-03-27 19:00 | 2.28 | 1.66 | 0.62 | 0 | 2.4103 | 119.2468 | 93.9631 | -3.9631 | 119.0919 | 117.0406 | 0 | 1.245 | 0.8 | 1 | 0.456 | 1.701 | -0.6 | -0.54684 | 1.1022 | 0.0015374
2015-03-27 20:00 | 1.14 | 0.83 | 0.31 | 0 | 2.4266 | 134.2501 | 96.6599 | -6.6599 | 133.9025 | 130.8792 | 0 | 0.6225 | 0.8 | 1 | 0.228 | 0.8505 | -0.7 | -0.67342 | 1.1027 | 0.00076903
2015-03-27 21:00 | 0 | 0 | 0 | 0 | 2.4429 | 149.2534 | 98.7496 | -8.7496 | 148.8827 | 143.9832 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-03-27 22:00 | 0 | 0 | 0 | 0 | 2.4592 | 164.2568 | 100.0819 | -10.0819 | 164.0184 | 155.1247 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.8 | -0.8 | 1.1032 | 0
2015-03-27 23:00 | 0 | 0 | 0 | 0 | 2.4755 | 179.2601 | 100.5567 | -10.5567 | 179.248 | 160.5441 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-03-28 | 0 | 0 | 0 | 0 | 2.4918 | -165.7366 | 100.137 | -10.137 | -165.5195 | 155.9832 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.1048 | 0
2015-03-28 01:00 | 0.22333 | 0.13 | 0.093333 | 0 | 2.5081 | -150.7333 | 98.8536 | -8.8536 | -150.3766 | 145.1664 | 0 | 0.0975 | 0.8 | 1 | 0.044667 | 0.14217 | -1.4 | -1.3956 | 1.1056 | 0.00012889
2015-03-28 02:00 | 0.44667 | 0.26 | 0.18667 | 0 | 2.5244 | -135.73 | 96.8007 | -6.8007 | -135.3878 | 132.1732 | 0 | 0.195 | 0.8 | 1 | 0.089333 | 0.28433 | -1.4 | -1.3911 | 1.1056 | 0.00025777
2015-03-28 03:00 | 0.67 | 0.39 | 0.28 | 0 | 2.5407 | -120.7266 | 94.1246 | -4.1246 | -120.571 | 118.3781 | 0 | 0.2925 | 0.8 | 1 | 0.134 | 0.4265 | -1.5 | -1.4867 | 1.1059 | 0.00038678
2015-03-28 04:00 | 21.8067 | 10.5933 | 11.2133 | 0 | 2.557 | -105.7233 | 91.0078 | -1.0078 | -105.8936 | 104.2362 | 0 | 7.945 | 0.8 | 1 | 4.3613 | 12.3063 | -1.5 | -1.1154 | 1.1045 | 0.011145
2015-03-28 05:00 | 42.9433 | 20.7967 | 22.1467 | 0 | 2.5733 | -90.72 | 87.6554 | 2.3446 | -91.282 | 89.9373 | 0 | 15.5975 | 0.8 | 1 | 8.5887 | 24.1862 | -1.9 | -1.1442 | 1.1046 | 0.021907
2015-03-28 06:00 | 64.08 | 31 | 33.08 | 332.1287 | 2.5896 | -75.7167 | 84.2839 | 5.7161 | -76.6396 | 75.5863 | 82.6742 | 23.25 | 0.8 | 1 | 12.816 | 118.7402 | -1.7 | 2.0106 | 1.092 | 0.10632
2015-03-28 07:00 | 99.45 | 43.67 | 55.78 | 361.0379 | 2.6059 | -60.7134 | 81.1123 | 8.8877 | -61.8688 | 61.2707 | 173.5405 | 32.7525 | 0.8 | 1 | 19.89 | 226.183 | -1.4 | 5.6682 | 1.0773 | 0.19981
2015-03-28 08:00 | 134.82 | 56.34 | 78.48 | 388.7396 | 2.6222 | -45.71 | 78.3529 | 11.6471 | -46.8947 | 47.1135 | 264.5559 | 42.255 | 0.8 | 1 | 26.964 | 333.7749 | -0.6 | 9.8305 | 1.0607 | 0.2903
2015-03-28 09:00 | 170.19 | 69.01 | 101.18 | 424.162 | 2.6385 | -30.7067 | 76.1996 | 13.8004 | -31.6861 | 33.3913 | 354.1461 | 51.7575 | 0.8 | 1 | 34.038 | 439.9416 | -1 | 12.7482 | 1.049 | 0.37843
2015-03-28 10:00 | 190.6533 | 69.6867 | 120.9667 | 461.7186 | 2.6548 | -15.7034 | 74.8117 | 15.1883 | -16.2693 | 21.0443 | 430.9233 | 52.265 | 0.8 | 1 | 38.1307 | 521.319 | -1.1 | 15.1912 | 1.0392 | 0.44425
2015-03-28 11:00 | 211.1167 | 70.3633 | 140.7533 | 520.0426 | 2.6711 | -0.70006 | 74.2966 | 15.7034 | -0.72641 | 14.3122 | 503.9022 | 52.7725 | 0.8 | 1 | 42.2233 | 598.898 | -1.6 | 17.1156 | 1.0315 | 0.50658
2015-03-28 12:00 | 231.58 | 71.04 | 160.54 | 608.1872 | 2.6873 | 14.3033 | 74.6946 | 15.3054 | 14.8244 | 20.0342 | 571.3848 | 53.28 | 0.8 | 1 | 46.316 | 670.9808 | -1.9 | 19.0681 | 1.0237 | 0.56326
2015-03-28 13:00 | 194.5 | 62.5267 | 131.9733 | 544.4667 | 2.7036 | 29.3066 | 75.9724 | 14.0276 | 30.2628 | 32.1245 | 461.106 | 46.895 | 0.8 | 1 | 38.9 | 546.901 | -2.8 | 14.2907 | 1.0428 | 0.46767
2015-03-28 14:00 | 157.42 | 54.0133 | 103.4067 | 498.5291 | 2.7199 | 44.3099 | 78.0286 | 11.9714 | 45.5012 | 45.773 | 347.7256 | 40.51 | 0.8 | 1 | 31.484 | 419.7196 | -2.3 | 10.8162 | 1.0567 | 0.3637
2015-03-28 15:00 | 120.34 | 45.5 | 74.84 | 463.497 | 2.7362 | 59.3132 | 80.7079 | 9.2921 | 60.5065 | 59.9004 | 232.4463 | 34.125 | 0.8 | 1 | 24.068 | 290.6393 | -4.4 | 4.6825 | 1.0813 | 0.25769
2015-03-28 16:00 | 82.9733 | 31.9433 | 51.03 | 473.9207 | 2.7525 | 74.3166 | 83.8186 | 6.1814 | 75.3034 | 74.2005 | 129.0351 | 23.9575 | 0.8 | 1 | 16.5947 | 169.5872 | -6.9 | -1.6004 | 1.1064 | 0.15386
2015-03-28 17:00 | 45.6067 | 18.3867 | 27.22 | 0 | 2.7687 | 89.3199 | 87.1493 | 2.8507 | 89.9623 | 88.5425 | 0 | 13.79 | 0.8 | 1 | 9.1213 | 22.9113 | -6.5 | -5.784 | 1.1231 | 0.021101
2015-03-28 18:00 | 8.24 | 4.83 | 3.41 | 0 | 2.785 | 104.3232 | 90.4806 | -0.48062 | 104.5781 | 102.8362 | 0 | 3.6225 | 0.8 | 1 | 1.648 | 5.2705 | -8.1 | -7.9353 | 1.1317 | 0.0048912
2015-03-28 19:00 | 5.4933 | 3.22 | 2.2733 | 0 | 2.8013 | 119.3265 | 93.5954 | -3.5954 | 119.2474 | 116.9779 | 0 | 2.415 | 0.8 | 1 | 1.0987 | 3.5137 | -7.6 | -7.4902 | 1.13 | 0.0032557
2015-03-28 20:00 | 2.7467 | 1.61 | 1.1367 | 0 | 2.8176 | 134.3299 | 96.287 | -6.287 | 134.0456 | 130.7849 | 0 | 1.2075 | 0.8 | 1 | 0.54933 | 1.7568 | -8.2 | -8.1451 | 1.1326 | 0.0016316
2015-03-28 21:00 | 0 | 0 | 0 | 0 | 2.8338 | 149.3332 | 98.3706 | -8.3706 | 149.0088 | 143.8307 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.6 | -9.6 | 1.1384 | 0
2015-03-28 22:00 | 0 | 0 | 0 | 0 | 2.8501 | 164.3365 | 99.6967 | -9.6967 | 164.1237 | 154.8645 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.4 | -10.4 | 1.1416 | 0
2015-03-28 23:00 | 0 | 0 | 0 | 0 | 2.8664 | 179.3398 | 100.1661 | -10.1661 | 179.3301 | 160.1562 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.9 | -9.9 | 1.1396 | 0
2015-03-29 | 0 | 0 | 0 | 0 | 2.8826 | -165.6569 | 99.7423 | -9.7423 | -165.4612 | 155.6179 | 0 | 0 | 0.8 | 1 | 0 | 0 | -12.2 | -12.2 | 1.1488 | 0
2015-03-29 01:00 | 0.25 | 0.19333 | 0.056667 | 0 | 2.8989 | -150.6535 | 98.4563 | -8.4563 | -150.3407 | 144.8758 | 0 | 0.145 | 0.8 | 1 | 0.05 | 0.195 | -10.3 | -10.2939 | 1.1412 | 0.00018247
2015-03-29 02:00 | 0.5 | 0.38667 | 0.11333 | 0 | 2.9152 | -135.6502 | 96.4023 | -6.4023 | -135.371 | 131.931 | 0 | 0.29 | 0.8 | 1 | 0.1 | 0.39 | -9 | -8.9878 | 1.136 | 0.00036328
2015-03-29 03:00 | 0.75 | 0.58 | 0.17 | 0 | 2.9314 | -120.6469 | 93.7259 | -3.7259 | -120.5688 | 118.164 | 0 | 0.435 | 0.8 | 1 | 0.15 | 0.585 | -9.5 | -9.4817 | 1.1379 | 0.00054586
2015-03-29 04:00 | 12.89 | 12.3067 | 0.58333 | 0 | 2.9477 | -105.6436 | 90.6091 | -0.60914 | -105.9007 | 104.0381 | 0 | 9.23 | 0.8 | 1 | 2.578 | 11.808 | -5.3 | -4.931 | 1.1197 | 0.010842
2015-03-29 05:00 | 25.03 | 24.0333 | 0.99667 | 0 | 2.964 | -90.6402 | 87.2568 | 2.7432 | -91.2926 | 89.747 | 0 | 18.025 | 0.8 | 1 | 5.006 | 23.031 | -4.6 | -3.8803 | 1.1155 | 0.021067
2015-03-29 06:00 | 37.17 | 35.76 | 1.41 | 13.237 | 2.9802 | -75.6369 | 83.8853 | 6.1147 | -76.6477 | 75.397 | 3.3373 | 26.82 | 0.8 | 1 | 7.434 | 37.5913 | -5 | -3.8253 | 1.1153 | 0.034379
2015-03-29 07:00 | 58.9267 | 48.86 | 10.0667 | 62.383 | 2.9965 | -60.6336 | 80.7136 | 9.2864 | -61.8685 | 61.0752 | 30.1722 | 36.645 | 0.8 | 1 | 11.7853 | 78.6026 | -5.2 | -2.7437 | 1.111 | 0.071607
2015-03-29 08:00 | 80.6833 | 61.96 | 18.7233 | 89.7196 | 3.0127 | -45.6303 | 77.9546 | 12.0454 | -46.8801 | 46.9009 | 61.302 | 46.47 | 0.8 | 1 | 16.1367 | 123.9087 | -4.6 | -0.72785 | 1.1029 | 0.11206
2015-03-29 09:00 | 102.44 | 75.06 | 27.38 | 111.6333 | 3.029 | -30.6269 | 75.8024 | 14.1976 | -31.6523 | 33.1419 | 93.4727 | 56.295 | 0.8 | 1 | 20.488 | 170.2557 | -4.5778 | 0.74271 | 1.097 | 0.15316
2015-03-29 10:00 | 107.3167 | 81.7633 | 25.5533 | 95.1232 | 3.0452 | -15.6236 | 74.417 | 15.583 | -16.2124 | 20.7175 | 88.9721 | 61.3225 | 0.8 | 1 | 21.4633 | 171.758 | -4.5556 | 0.81188 | 1.0968 | 0.15447
2015-03-29 11:00 | 112.1933 | 88.4667 | 23.7267 | 85.5896 | 3.0615 | -0.62029 | 73.906 | 16.094 | -0.64467 | 13.9185 | 83.0766 | 66.35 | 0.8 | 1 | 22.4387 | 171.8653 | -4.5333 | 0.83746 | 1.0967 | 0.15455
2015-03-29 12:00 | 117.07 | 95.17 | 21.9 | 80.9787 | 3.0777 | 14.383 | 74.3095 | 15.6905 | 14.9304 | 19.8091 | 76.1869 | 71.3775 | 0.8 | 1 | 23.414 | 170.9784 | -4.5111 | 0.83196 | 1.0967 | 0.15376
2015-03-29 13:00 | 98.7667 | 84.03 | 14.7367 | 59.2316 | 3.094 | 29.3864 | 75.5936 | 14.4064 | 30.3903 | 32.0116 | 50.2249 | 63.0225 | 0.8 | 1 | 19.7533 | 133.0008 | -4.4889 | -0.33261 | 1.1013 | 0.12011
2015-03-29 14:00 | 80.4633 | 72.89 | 7.5733 | 35.4265 | 3.1102 | 44.3897 | 77.6563 | 12.3437 | 45.646 | 45.7075 | 24.7391 | 54.6675 | 0.8 | 1 | 16.0927 | 95.4992 | -4.4667 | -1.4823 | 1.1059 | 0.086605
2015-03-29 15:00 | 62.16 | 61.75 | 0.41 | 2.4436 | 3.1264 | 59.393 | 80.3409 | 9.6591 | 60.6635 | 59.8559 | 1.2271 | 46.3125 | 0.8 | 1 | 12.432 | 59.9716 | -4.4444 | -2.5703 | 1.1103 | 0.0546
2015-03-29 16:00 | 43.3533 | 43.0067 | 0.34667 | 3.0415 | 3.1427 | 74.3963 | 83.4553 | 6.5447 | 75.4674 | 74.164 | 0.82998 | 32.255 | 0.8 | 1 | 8.6707 | 41.7556 | -4.4222 | -3.1174 | 1.1125 | 0.038091
2015-03-29 17:00 | 24.5467 | 24.2633 | 0.28333 | 5.0554 | 3.1589 | 89.3997 | 86.7872 | 3.2128 | 90.1282 | 88.5051 | 0.13188 | 18.1975 | 0.8 | 1 | 4.9093 | 23.2387 | -4.4 | -3.6738 | 1.1147 | 0.021241
2015-03-29 18:00 | 5.74 | 5.52 | 0.22 | 0 | 3.1751 | 104.403 | 90.1173 | -0.11733 | 104.7411 | 102.7904 | 0 | 4.14 | 0.8 | 1 | 1.148 | 5.288 | -4.3778 | -4.2125 | 1.1169 | 0.0048428
2015-03-29 19:00 | 3.8267 | 3.68 | 0.14667 | 0 | 3.1914 | 119.4063 | 93.2286 | -3.2286 | 119.4026 | 116.9141 | 0 | 2.76 | 0.8 | 1 | 0.76533 | 3.5253 | -4.3556 | -4.2454 | 1.117 | 0.0032289
2015-03-29 20:00 | 1.9133 | 1.84 | 0.073333 | 0 | 3.2076 | 134.4096 | 95.915 | -5.915 | 134.1882 | 130.6886 | 0 | 1.38 | 0.8 | 1 | 0.38267 | 1.7627 | -4.3333 | -4.2782 | 1.1171 | 0.0016147
2015-03-29 21:00 | 0 | 0 | 0 | 0 | 3.2238 | 149.4129 | 97.9925 | -7.9925 | 149.1345 | 143.6754 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.3111 | -4.3111 | 1.1172 | 0
2015-03-29 22:00 | 0 | 0 | 0 | 0 | 3.2401 | 164.4163 | 99.3124 | -9.3124 | 164.2287 | 154.6016 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2889 | -4.2889 | 1.1172 | 0
2015-03-29 23:00 | 0 | 0 | 0 | 0 | 3.2563 | 179.4196 | 99.7764 | -9.7764 | 179.412 | 159.7689 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2667 | -4.2667 | 1.1171 | 0
2015-03-30 | 0 | 0 | 0 | 0 | 3.2725 | -165.5771 | 99.3485 | -9.3485 | -165.403 | 155.2525 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2444 | -4.2444 | 1.117 | 0
2015-03-30 01:00 | 0.06 | 0.06 | 0 | 0 | 3.2887 | -150.5738 | 98.06 | -8.06 | -150.3047 | 144.584 | 0 | 0.045 | 0.8 | 1 | 0.012 | 0.057 | -4.2222 | -4.2204 | 1.1169 | 5.2203e-05
2015-03-30 02:00 | 0.12 | 0.12 | 0 | 0 | 3.305 | -135.5704 | 96.0048 | -6.0048 | -135.3541 | 131.6877 | 0 | 0.09 | 0.8 | 1 | 0.024 | 0.114 | -4.2 | -4.1964 | 1.1168 | 0.0001044
2015-03-30 03:00 | 0.18 | 0.18 | 0 | 0 | 3.3212 | -120.5671 | 93.3281 | -3.3281 | -120.5664 | 117.9493 | 0 | 0.135 | 0.8 | 1 | 0.036 | 0.171 | -4.1778 | -4.1724 | 1.1167 | 0.00015658
2015-03-30 04:00 | 3.6733 | 3.6733 | 0 | 0 | 3.3374 | -105.5638 | 90.2114 | -0.21145 | -105.9076 | 103.8399 | 0 | 2.755 | 0.8 | 1 | 0.73467 | 3.4897 | -4.1556 | -4.0465 | 1.1162 | 0.003194
2015-03-30 05:00 | 7.1667 | 7.1667 | 0 | 0 | 3.3536 | -90.5605 | 86.8593 | 3.1407 | -91.303 | 89.5571 | 0 | 5.375 | 0.8 | 1 | 1.4333 | 6.8083 | -4.1333 | -3.9206 | 1.1157 | 0.0062287
2015-03-30 06:00 | 10.66 | 10.66 | 0 | 0 | 3.3698 | -75.5572 | 83.4877 | 6.5123 | -76.6557 | 75.2087 | 0 | 7.995 | 0.8 | 1 | 2.132 | 10.127 | -4.1111 | -3.7946 | 1.1152 | 0.0092606
2015-03-30 07:00 | 14.51 | 14.51 | 0 | 0 | 3.386 | -60.5538 | 80.316 | 9.684 | -61.868 | 60.8811 | 0 | 10.8825 | 0.8 | 1 | 2.902 | 13.7845 | -4.0889 | -3.6581 | 1.1146 | 0.012599
2015-03-30 08:00 | 18.36 | 18.36 | 0 | 0 | 3.4022 | -45.5505 | 77.5573 | 12.4427 | -46.8655 | 46.6906 | 0 | 13.77 | 0.8 | 1 | 3.672 | 17.442 | -4.0667 | -3.5216 | 1.1141 | 0.015934
2015-03-30 09:00 | 22.21 | 22.21 | 0 | 0 | 3.4184 | -30.5472 | 75.4062 | 14.5938 | -31.6183 | 32.8957 | 0 | 16.6575 | 0.8 | 1 | 4.442 | 21.0995 | -4.0444 | -3.3851 | 1.1135 | 0.019266
2015-03-30 10:00 | 16.6333 | 16.6333 | 0 | 0 | 3.4347 | -15.5439 | 74.0233 | 15.9767 | -16.1553 | 20.3938 | 0 | 12.475 | 0.8 | 1 | 3.3267 | 15.8017 | -4.0222 | -3.5284 | 1.1141 | 0.014436
2015-03-30 11:00 | 11.0567 | 11.0567 | 0 | 0 | 3.4509 | -0.54055 | 73.5164 | 16.4836 | -0.5627 | 13.5262 | 0 | 8.2925 | 0.8 | 1 | 2.2113 | 10.5038 | -4 | -3.6718 | 1.1147 | 0.009601
2015-03-30 12:00 | 5.48 | 5.48 | 0 | 0 | 3.4671 | 14.4628 | 73.9254 | 16.0746 | 15.0367 | 19.5899 | 0 | 4.11 | 0.8 | 1 | 1.096 | 5.206 | -3.5 | -3.3373 | 1.1133 | 0.0047528
2015-03-30 13:00 | 20.0633 | 20.04 | 0.023333 | 0.09144 | 3.4833 | 29.4661 | 75.216 | 14.784 | 30.5181 | 31.9031 | 0.077628 | 15.03 | 0.8 | 1 | 4.0127 | 19.1203 | -3.1 | -2.5025 | 1.11 | 0.017403
2015-03-30 14:00 | 34.6467 | 34.6 | 0.046667 | 0.21202 | 3.4995 | 44.4694 | 77.285 | 12.715 | 45.7909 | 45.6449 | 0.14823 | 25.95 | 0.8 | 1 | 6.9293 | 33.0276 | -3.5 | -2.4679 | 1.1099 | 0.030058
2015-03-30 15:00 | 49.23 | 49.16 | 0.07 | 0.40212 | 3.5156 | 59.4727 | 79.975 | 10.025 | 60.8205 | 59.8133 | 0.20219 | 36.87 | 0.8 | 1 | 9.846 | 46.9182 | -3.5 | -2.0338 | 1.1081 | 0.042633
2015-03-30 16:00 | 34.4467 | 34.4 | 0.046667 | 0.38805 | 3.5318 | 74.476 | 83.0929 | 6.9071 | 75.6314 | 74.1284 | 0.10612 | 25.8 | 0.8 | 1 | 6.8893 | 32.7955 | -3.3 | -2.2751 | 1.1091 | 0.029826
2015-03-30 17:00 | 19.6633 | 19.64 | 0.023333 | 0.37431 | 3.548 | 89.4794 | 86.4261 | 3.5739 | 90.294 | 88.4681 | 0.010007 | 14.73 | 0.8 | 1 | 3.9327 | 18.6727 | -2.9 | -2.3165 | 1.1093 | 0.016985
2015-03-30 18:00 | 4.88 | 4.88 | 0 | 0 | 3.5642 | 104.4827 | 89.755 | 0.24498 | 104.9037 | 102.7442 | 0 | 3.66 | 0.8 | 1 | 0.976 | 4.636 | -3.1 | -2.9551 | 1.1118 | 0.0042266
2015-03-30 19:00 | 3.2533 | 3.2533 | 0 | 0 | 3.5804 | 119.486 | 92.8628 | -2.8628 | 119.5573 | 116.8493 | 0 | 2.44 | 0.8 | 1 | 0.65067 | 3.0907 | -2.7 | -2.6034 | 1.1104 | 0.0028142
2015-03-30 20:00 | 1.6267 | 1.6267 | 0 | 0 | 3.5966 | 134.4893 | 95.5441 | -5.5441 | 134.3304 | 130.5905 | 0 | 1.22 | 0.8 | 1 | 0.32533 | 1.5453 | -2.6 | -2.5517 | 1.1102 | 0.0014068
2015-03-30 21:00 | 0 | 0 | 0 | 0 | 3.6128 | 149.4926 | 97.6154 | -7.6154 | 149.2596 | 143.5175 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-03-30 22:00 | 0 | 0 | 0 | 0 | 3.629 | 164.496 | 98.9291 | -8.9291 | 164.3332 | 154.3363 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.2 | -5.2 | 1.1208 | 0
2015-03-30 23:00 | 0 | 0 | 0 | 0 | 3.6451 | 179.4993 | 99.3877 | -9.3877 | 179.4935 | 159.3823 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-03-31 | 0 | 0 | 0 | 0 | 3.6613 | -165.4974 | 98.9558 | -8.9558 | -165.3451 | 154.8871 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-03-31 01:00 | 0.036667 | 0.036667 | 0 | 0 | 3.6775 | -150.4941 | 97.6648 | -7.6648 | -150.2689 | 144.2912 | 0 | 0.0275 | 0.8 | 1 | 0.0073333 | 0.034833 | -4.5 | -4.4989 | 1.118 | 3.1934e-05
2015-03-31 02:00 | 0.073333 | 0.073333 | 0 | 0 | 3.6937 | -135.4908 | 95.6084 | -5.6084 | -135.3372 | 131.4436 | 0 | 0.055 | 0.8 | 1 | 0.014667 | 0.069667 | -4.0333 | -4.0312 | 1.1161 | 6.376e-05
2015-03-31 03:00 | 0.11 | 0.11 | 0 | 0 | 3.7098 | -120.4875 | 92.9314 | -2.9314 | -120.5641 | 117.7341 | 0 | 0.0825 | 0.8 | 1 | 0.022 | 0.1045 | -3.5667 | -3.5634 | 1.1143 | 9.548e-05
2015-03-31 04:00 | 1.77 | 1.7667 | 0.0033333 | 0 | 3.726 | -105.4841 | 89.8148 | 0.18515 | -105.9144 | 103.6416 | 0 | 1.325 | 0.8 | 1 | 0.354 | 1.679 | -3.1 | -3.0475 | 1.1122 | 0.0015312
2015-03-31 05:00 | 3.43 | 3.4233 | 0.0066667 | 0.10806 | 3.7422 | -90.4808 | 86.4628 | 3.5372 | -91.3134 | 89.3677 | 0.0011925 | 2.5675 | 0.8 | 1 | 0.686 | 3.2547 | -3.5 | -3.3983 | 1.1136 | 0.002972
2015-03-31 06:00 | 5.09 | 5.08 | 0.01 | 0.083133 | 3.7583 | -75.4775 | 83.0912 | 6.9088 | -76.6636 | 75.0214 | 0.021486 | 3.81 | 0.8 | 1 | 1.018 | 4.8495 | -4.1 | -3.9485 | 1.1158 | 0.004437
2015-03-31 07:00 | 11.6333 | 7.9667 | 3.6667 | 20.9486 | 3.7745 | -60.4742 | 79.9195 | 10.0805 | -61.8675 | 60.6888 | 10.2555 | 5.975 | 0.8 | 1 | 2.3267 | 18.5571 | -4.25 | -3.6701 | 1.1147 | 0.016962
2015-03-31 08:00 | 18.1767 | 10.8533 | 7.3233 | 32.9566 | 3.7907 | -45.4709 | 77.161 | 12.839 | -46.8508 | 46.4827 | 22.693 | 8.14 | 0.8 | 1 | 3.6353 | 34.4684 | -4.4 | -3.3229 | 1.1133 | 0.031466
2015-03-31 09:00 | 24.72 | 13.74 | 10.98 | 42.4543 | 3.8068 | -30.4676 | 75.0112 | 14.9888 | -31.5843 | 32.6527 | 35.7447 | 10.305 | 0.8 | 1 | 4.944 | 50.9937 | -5.3 | -3.7064 | 1.1148 | 0.046616
2015-03-31 10:00 | 46.6567 | 23.8067 | 22.85 | 81.0783 | 3.823 | -15.4643 | 73.6308 | 16.3692 | -16.0981 | 20.0736 | 76.153 | 17.855 | 0.8 | 1 | 9.3313 | 103.3394 | -5.35 | -2.1206 | 1.1085 | 0.093931
2015-03-31 11:00 | 68.5933 | 33.8733 | 34.72 | 119.6272 | 3.8391 | -0.46094 | 73.128 | 16.872 | -0.4806 | 13.1353 | 116.4973 | 25.405 | 0.8 | 1 | 13.7187 | 155.6209 | -5.4 | -0.53685 | 1.1021 | 0.14064
2015-03-31 12:00 | 90.53 | 43.94 | 46.59 | 164.4527 | 3.8553 | 14.5424 | 73.5425 | 16.4575 | 15.1431 | 19.3768 | 155.1376 | 32.955 | 0.8 | 1 | 18.106 | 206.1986 | -5.7 | 0.74371 | 1.097 | 0.18549
2015-03-31 13:00 | 97.68 | 43.9633 | 53.7167 | 205.3994 | 3.8714 | 29.5457 | 74.8395 | 15.1605 | 30.646 | 31.7991 | 174.5692 | 32.9725 | 0.8 | 1 | 19.536 | 227.0777 | -5.8 | 1.2962 | 1.0948 | 0.20386
2015-03-31 14:00 | 104.83 | 43.9867 | 60.8433 | 268.7448 | 3.8876 | 44.549 | 76.9149 | 13.0851 | 45.9359 | 45.5851 | 188.0807 | 32.99 | 0.8 | 1 | 20.966 | 242.0367 | -6.5 | 1.0636 | 1.0957 | 0.21747
2015-03-31 15:00 | 111.98 | 44.01 | 67.97 | 376.8934 | 3.9037 | 59.5523 | 79.6103 | 10.3897 | 60.9775 | 59.7723 | 189.7422 | 33.0075 | 0.8 | 1 | 22.396 | 245.1457 | -6.3 | 1.3608 | 1.0946 | 0.22003
2015-03-31 16:00 | 76.24 | 30.8267 | 45.4133 | 358.9538 | 3.9199 | 74.5556 | 82.7317 | 7.2683 | 75.7951 | 74.0937 | 98.3766 | 23.12 | 0.8 | 1 | 15.248 | 136.7446 | -6.3 | -2.0267 | 1.1081 | 0.12425
2015-03-31 17:00 | 40.5 | 17.6433 | 22.8567 | 333.1582 | 3.936 | 89.5589 | 86.0661 | 3.9339 | 90.4593 | 88.4312 | 9.1207 | 13.2325 | 0.8 | 1 | 8.1 | 30.4532 | -6.4 | -5.4483 | 1.1218 | 0.028013
2015-03-31 18:00 | 4.76 | 4.46 | 0.3 | 0 | 3.9522 | 104.5622 | 89.3938 | 0.60622 | 105.0659 | 102.6975 | 0 | 3.345 | 0.8 | 1 | 0.952 | 4.297 | -6.9 | -6.7657 | 1.1271 | 0.0039713
2015-03-31 19:00 | 3.1733 | 2.9733 | 0.2 | 0 | 3.9683 | 119.5655 | 92.4981 | -2.4981 | 119.7115 | 116.7832 | 0 | 2.23 | 0.8 | 1 | 0.63467 | 2.8647 | -7.1 | -7.0105 | 1.128 | 0.0026498
2015-03-31 20:00 | 1.5867 | 1.4867 | 0.1 | 0 | 3.9844 | 134.5689 | 95.1741 | -5.1741 | 134.472 | 130.4905 | 0 | 1.115 | 0.8 | 1 | 0.31733 | 1.4323 | -6.4 | -6.3552 | 1.1254 | 0.0013218
2015-03-31 21:00 | 0 | 0 | 0 | 0 | 4.0006 | 149.5722 | 97.2393 | -7.2393 | 149.3842 | 143.3569 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.5 | -6.5 | 1.126 | 0
2015-03-31 22:00 | 0 | 0 | 0 | 0 | 4.0167 | 164.5755 | 98.5469 | -8.5469 | 164.4372 | 154.0686 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.4 | -6.4 | 1.1256 | 0
2015-03-31 23:00 | 0 | 0 | 0 | 0 | 4.0328 | 179.5788 | 99.0002 | -9.0002 | 179.5746 | 158.9964 | 0 | 0 | 0.8 | 1 | 0 | 0 | -6.4 | -6.4 | 1.1256 | 0
2015-04-01 | 0 | 0 | 0 | 0 | 4.0489 | -165.4179 | 98.5643 | -8.5643 | -165.2874 | 154.5219 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.6 | -4.6 | 1.1184 | 0
2015-04-01 01:00 | 0.14667 | 0.14667 | 0 | 0 | 4.0651 | -150.4146 | 97.2708 | -7.2708 | -150.2333 | 143.9975 | 0 | 0.11 | 0.8 | 1 | 0.029333 | 0.13933 | -4.4 | -4.3956 | 1.1176 | 0.00012769
2015-04-01 02:00 | 0.29333 | 0.29333 | 0 | 0 | 4.0812 | -135.4113 | 95.2132 | -5.2132 | -135.3204 | 131.1986 | 0 | 0.22 | 0.8 | 1 | 0.058667 | 0.27867 | -6.4 | -6.3913 | 1.1256 | 0.0002572
2015-04-01 03:00 | 0.44 | 0.44 | 0 | 0 | 4.0973 | -120.408 | 92.5359 | -2.5359 | -120.5617 | 117.5186 | 0 | 0.33 | 0.8 | 1 | 0.088 | 0.418 | -4.7 | -4.6869 | 1.1187 | 0.00038346
2015-04-01 04:00 | 6.31 | 6.0267 | 0.28333 | 0 | 4.1134 | -105.4047 | 89.4195 | 0.58055 | -105.9213 | 103.4435 | 0 | 4.52 | 0.8 | 1 | 1.262 | 5.782 | -5.3 | -5.1193 | 1.1205 | 0.0053125
2015-04-01 05:00 | 12.18 | 11.6133 | 0.56667 | 8.2627 | 4.1295 | -90.4014 | 86.0675 | 3.9325 | -91.3237 | 89.1789 | 0.11841 | 8.71 | 0.8 | 1 | 2.436 | 11.2644 | -5.9 | -5.548 | 1.1222 | 0.010365
2015-04-01 06:00 | 18.05 | 17.2 | 0.85 | 6.6858 | 4.1457 | -75.3981 | 82.696 | 7.304 | -76.6716 | 74.8353 | 1.749 | 12.9 | 0.8 | 1 | 3.61 | 18.259 | -5.5 | -4.9294 | 1.1197 | 0.016765
2015-04-01 07:00 | 29.2367 | 21.5633 | 7.6733 | 42.2029 | 4.1618 | -60.3948 | 79.5242 | 10.4758 | -61.8671 | 60.4982 | 20.7828 | 16.1725 | 0.8 | 1 | 5.8473 | 42.8027 | -5.5 | -4.1624 | 1.1166 | 0.039192
2015-04-01 08:00 | 40.4233 | 25.9267 | 14.4967 | 63.3243 | 4.1779 | -45.3915 | 76.7661 | 13.2339 | -46.8361 | 46.2774 | 43.7677 | 19.445 | 0.8 | 1 | 8.0847 | 71.2974 | -5.4 | -3.172 | 1.1127 | 0.065052
2015-04-01 09:00 | 51.61 | 30.29 | 21.32 | 80.3726 | 4.194 | -30.3882 | 74.6173 | 15.3827 | -31.5502 | 32.4132 | 67.8509 | 22.7175 | 0.8 | 1 | 10.322 | 100.8904 | -5 | -1.8472 | 1.1074 | 0.091614
2015-04-01 10:00 | 67.24 | 45.2967 | 21.9433 | 76.0937 | 4.2101 | -15.3849 | 73.2395 | 16.7605 | -16.0409 | 19.757 | 71.6144 | 33.9725 | 0.8 | 1 | 13.448 | 119.0349 | -5.2 | -1.4802 | 1.1059 | 0.10795
2015-04-01 11:00 | 82.87 | 60.3033 | 22.5667 | 76.06 | 4.2262 | -0.38156 | 72.7408 | 17.2592 | -0.39847 | 12.746 | 74.1858 | 45.2275 | 0.8 | 1 | 16.574 | 135.9873 | -5 | -0.7504 | 1.103 | 0.123
2015-04-01 12:00 | 98.5 | 75.31 | 23.19 | 80.0525 | 4.2423 | 14.6217 | 73.1609 | 16.8391 | 15.2495 | 19.1699 | 75.6135 | 56.4825 | 0.8 | 1 | 19.7 | 151.796 | -5.2 | -0.45638 | 1.1018 | 0.13715
2015-04-01 13:00 | 92.4867 | 72.9233 | 19.5633 | 73.0415 | 4.2584 | 29.625 | 74.4643 | 15.5357 | 30.7739 | 31.6994 | 62.145 | 54.6925 | 0.8 | 1 | 18.4973 | 135.3348 | -5.8 | -1.5708 | 1.1063 | 0.12277
2015-04-01 14:00 | 86.4733 | 70.5367 | 15.9367 | 68.4964 | 4.2745 | 44.6283 | 76.546 | 13.454 | 46.0808 | 45.5281 | 47.9858 | 52.9025 | 0.8 | 1 | 17.2947 | 118.1829 | -5.8 | -2.1068 | 1.1084 | 0.10742
2015-04-01 15:00 | 80.46 | 68.15 | 12.31 | 65.977 | 4.2906 | 59.6316 | 79.2467 | 10.7533 | 61.1343 | 59.733 | 33.2544 | 51.1125 | 0.8 | 1 | 16.092 | 100.4589 | -6 | -2.8607 | 1.1114 | 0.091556
2015-04-01 16:00 | 56.88 | 48.3267 | 8.5533 | 64.4335 | 4.3067 | 74.6349 | 82.3717 | 7.6283 | 75.9585 | 74.0598 | 17.6956 | 36.245 | 0.8 | 1 | 11.376 | 65.3166 | -5.8 | -3.7589 | 1.115 | 0.059721
2015-04-01 17:00 | 33.3 | 28.5033 | 4.7967 | 64.0812 | 4.3228 | 89.6382 | 85.7072 | 4.2928 | 90.6243 | 88.3945 | 1.7954 | 21.3775 | 0.8 | 1 | 6.66 | 29.8329 | -5.8 | -4.8677 | 1.1195 | 0.027386
2015-04-01 18:00 | 9.72 | 8.68 | 1.04 | 0 | 4.3388 | 104.6415 | 89.0337 | 0.96633 | 105.2275 | 102.6502 | 0 | 6.51 | 0.8 | 1 | 1.944 | 8.454 | -5.6 | -5.3358 | 1.1213 | 0.0077735
2015-04-01 19:00 | 6.48 | 5.7867 | 0.69333 | 0 | 4.3549 | 119.6448 | 92.1345 | -2.1345 | 119.8651 | 116.716 | 0 | 4.34 | 0.8 | 1 | 1.296 | 5.636 | -5.5 | -5.3239 | 1.1213 | 0.0051821
2015-04-01 20:00 | 3.24 | 2.8933 | 0.34667 | 0 | 4.371 | 134.6481 | 94.8053 | -4.8053 | 134.6128 | 130.3886 | 0 | 2.17 | 0.8 | 1 | 0.648 | 2.818 | -6.3 | -6.2119 | 1.1248 | 0.0025993
2015-04-01 21:00 | 0 | 0 | 0 | 0 | 4.3871 | 149.6514 | 96.8644 | -6.8644 | 149.5081 | 143.1937 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.2 | -7.2 | 1.1288 | 0
2015-04-01 22:00 | 0 | 0 | 0 | 0 | 4.4032 | 164.6547 | 98.1659 | -8.1659 | 164.5405 | 153.7988 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.4 | -7.4 | 1.1296 | 0
2015-04-01 23:00 | 0 | 0 | 0 | 0 | 4.4192 | 179.658 | 98.6139 | -8.6139 | 179.6551 | 158.6114 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.7 | -7.7 | 1.1308 | 0
2015-04-02 | 0 | 0 | 0 | 0 | 4.4353 | -165.3387 | 98.174 | -8.174 | -165.2302 | 154.1571 | 0 | 0 | 0.8 | 1 | 0 | 0 | -7.5 | -7.5 | 1.13 | 0
2015-04-02 01:00 | 0.84333 | 0.76333 | 0.08 | 0 | 4.4514 | -150.3354 | 96.878 | -6.878 | -150.1979 | 143.7032 | 0 | 0.5725 | 0.8 | 1 | 0.16867 | 0.74117 | -7.1 | -7.0768 | 1.1283 | 0.00068574
2015-04-02 02:00 | 1.6867 | 1.5267 | 0.16 | 0 | 4.4675 | -135.3321 | 94.8193 | -4.8193 | -135.3038 | 130.9531 | 0 | 1.145 | 0.8 | 1 | 0.33733 | 1.4823 | -7.3 | -7.2537 | 1.129 | 0.0013723
2015-04-02 03:00 | 2.53 | 2.29 | 0.24 | 0 | 4.4835 | -120.3288 | 92.1417 | -2.1417 | -120.5595 | 117.3028 | 0 | 1.7175 | 0.8 | 1 | 0.506 | 2.2235 | -7.3 | -7.2305 | 1.1289 | 0.0020583
2015-04-02 04:00 | 21.9967 | 17.46 | 4.5367 | 0 | 4.4996 | -105.3255 | 89.0254 | 0.97462 | -105.9282 | 103.2456 | 0 | 13.095 | 0.8 | 1 | 4.3993 | 17.4943 | -7.7 | -7.1533 | 1.1286 | 0.01619
2015-04-02 05:00 | 41.4633 | 32.63 | 8.8333 | 117.0929 | 4.5156 | -90.3222 | 85.6736 | 4.3264 | -91.3342 | 88.9908 | 2.0623 | 24.4725 | 0.8 | 1 | 8.2927 | 34.8275 | -7.9 | -6.8116 | 1.1272 | 0.032192
2015-04-02 06:00 | 60.93 | 47.8 | 13.13 | 98.0206 | 4.5317 | -75.3189 | 82.302 | 7.698 | -76.6796 | 74.6505 | 25.9466 | 35.85 | 0.8 | 1 | 12.186 | 73.9826 | -8.1 | -5.788 | 1.1232 | 0.068137
2015-04-02 07:00 | 97.73 | 64.7967 | 32.9333 | 174.6412 | 4.5478 | -60.3157 | 79.1302 | 10.8698 | -61.8668 | 60.3096 | 86.5021 | 48.5975 | 0.8 | 1 | 19.546 | 154.6456 | -8.1 | -3.2673 | 1.1131 | 0.14115
2015-04-02 08:00 | 134.53 | 81.7933 | 52.7367 | 223.8302 | 4.5638 | -45.3124 | 76.3724 | 13.6276 | -46.8216 | 46.0747 | 155.2753 | 61.345 | 0.8 | 1 | 26.906 | 243.5263 | -7.9 | -0.2898 | 1.1012 | 0.21989
2015-04-02 09:00 | 171.33 | 98.79 | 72.54 | 266.8255 | 4.5799 | -30.3091 | 74.2248 | 15.7752 | -31.5163 | 32.1773 | 225.8422 | 74.0925 | 0.8 | 1 | 34.266 | 334.2007 | -8.5 | 1.9438 | 1.0922 | 0.29932
2015-04-02 10:00 | 186.1067 | 97.86 | 88.2467 | 299.2598 | 4.5959 | -15.3058 | 72.8495 | 17.1505 | -15.9839 | 19.4443 | 282.1917 | 73.395 | 0.8 | 1 | 37.2213 | 392.808 | -8.2 | 4.0752 | 1.0837 | 0.34906
2015-04-02 11:00 | 200.8833 | 96.93 | 103.9533 | 342.9444 | 4.612 | -0.30251 | 72.3549 | 17.6451 | -0.31641 | 12.3583 | 334.9978 | 72.6975 | 0.8 | 1 | 40.1767 | 447.872 | -8.3 | 5.696 | 1.0772 | 0.39561
2015-04-02 12:00 | 215.66 | 96 | 119.66 | 404.2135 | 4.628 | 14.7008 | 72.7806 | 17.2194 | 15.3558 | 18.9693 | 382.2618 | 72 | 0.8 | 1 | 43.132 | 497.3938 | -8.3 | 7.2436 | 1.071 | 0.43683
2015-04-02 13:00 | 193.6133 | 85.7433 | 107.87 | 393.5134 | 4.644 | 29.7041 | 74.0904 | 15.9096 | 30.9016 | 31.6041 | 335.1514 | 64.3075 | 0.8 | 1 | 38.7227 | 438.1815 | -8.2 | 5.4932 | 1.078 | 0.38734
2015-04-02 14:00 | 171.5667 | 75.4867 | 96.08 | 402.1784 | 4.6601 | 44.7073 | 76.1784 | 13.8216 | 46.2255 | 45.4737 | 282.0222 | 56.615 | 0.8 | 1 | 34.3133 | 372.9505 | -8.5 | 3.1547 | 1.0874 | 0.33254
2015-04-02 15:00 | 149.52 | 65.23 | 84.29 | 437.2156 | 4.6761 | 59.7106 | 78.8845 | 11.1155 | 61.2907 | 59.6953 | 220.6184 | 48.9225 | 0.8 | 1 | 29.904 | 299.4449 | -8.7 | 0.65765 | 1.0974 | 0.26945
2015-04-02 16:00 | 104.6133 | 47.37 | 57.2433 | 411.9688 | 4.6921 | 74.7139 | 82.0129 | 7.9871 | 76.1214 | 74.0267 | 113.3696 | 35.5275 | 0.8 | 1 | 20.9227 | 169.8198 | -8.7 | -3.3931 | 1.1136 | 0.15507
2015-04-02 17:00 | 59.7067 | 29.51 | 30.1967 | 372.4504 | 4.7082 | 89.7172 | 85.3496 | 4.6504 | 90.7886 | 88.3578 | 10.6735 | 22.1325 | 0.8 | 1 | 11.9413 | 44.7473 | -8.7 | -7.3016 | 1.1292 | 0.041434
2015-04-02 18:00 | 14.8 | 11.65 | 3.15 | 0 | 4.7242 | 104.7205 | 88.6748 | 1.3252 | 105.3884 | 102.6024 | 0 | 8.7375 | 0.8 | 1 | 2.96 | 11.6975 | -8.5 | -8.1345 | 1.1325 | 0.010863
2015-04-02 19:00 | 9.8667 | 7.7667 | 2.1 | 0 | 4.7402 | 119.7238 | 91.7721 | -1.7721 | 120.0178 | 116.6475 | 0 | 5.825 | 0.8 | 1 | 1.9733 | 7.7983 | -8.9 | -8.6563 | 1.1346 | 0.0072555
2015-04-02 20:00 | 4.9333 | 3.8833 | 1.05 | 0 | 4.7563 | 134.727 | 94.4378 | -4.4378 | 134.7529 | 130.2847 | 0 | 2.9125 | 0.8 | 1 | 0.98667 | 3.8992 | -8.8 | -8.6782 | 1.1347 | 0.003628
2015-04-02 21:00 | 0 | 0 | 0 | 0 | 4.7723 | 149.7303 | 96.4908 | -6.4908 | 149.6312 | 143.028 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9 | -9 | 1.136 | 0
2015-04-02 22:00 | 0 | 0 | 0 | 0 | 4.7883 | 164.7336 | 97.7862 | -7.7862 | 164.6431 | 153.5268 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9 | -9 | 1.136 | 0
2015-04-02 23:00 | 0 | 0 | 0 | 0 | 4.8043 | 179.7369 | 98.2289 | -8.2289 | 179.7351 | 158.2275 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.2 | -9.2 | 1.1368 | 0
2015-04-03 | 0 | 0 | 0 | 0 | 4.8203 | -165.2599 | 97.7851 | -7.7851 | -165.1734 | 153.7929 | 0 | 0 | 0.8 | 1 | 0 | 0 | -9.3 | -9.3 | 1.1372 | 0
2015-04-03 01:00 | 1.1333 | 1.0533 | 0.08 | 0 | 4.8363 | -150.2566 | 96.4867 | -6.4867 | -150.1629 | 143.4084 | 0 | 0.79 | 0.8 | 1 | 0.22667 | 1.0167 | -9.5 | -9.4682 | 1.1379 | 0.00094861
2015-04-03 02:00 | 2.2667 | 2.1067 | 0.16 | 0 | 4.8524 | -135.2533 | 94.4268 | -4.4268 | -135.2875 | 130.7072 | 0 | 1.58 | 0.8 | 1 | 0.45333 | 2.0333 | -9.5 | -9.4365 | 1.1377 | 0.001897
2015-04-03 03:00 | 3.4 | 3.16 | 0.24 | 0 | 4.8684 | -120.25 | 91.7489 | -1.7489 | -120.5574 | 117.0871 | 0 | 2.37 | 0.8 | 1 | 0.68 | 3.05 | -9.5 | -9.4047 | 1.1376 | 0.0028452
2015-04-03 04:00 | 22.0233 | 21.32 | 0.70333 | 0 | 4.8844 | -105.2468 | 88.6327 | 1.3673 | -105.9353 | 103.0482 | 0 | 15.99 | 0.8 | 1 | 4.4047 | 20.3947 | -9.9 | -9.2627 | 1.1371 | 0.019016
2015-04-03 05:00 | 40.6467 | 39.48 | 1.1667 | 14.1813 | 4.9004 | -90.2435 | 85.2811 | 4.7189 | -91.3448 | 88.8037 | 0.29608 | 29.61 | 0.8 | 1 | 8.1293 | 38.0354 | -10.4 | -9.2114 | 1.1368 | 0.035457
2015-04-03 06:00 | 59.27 | 57.64 | 1.63 | 11.5819 | 4.9164 | -75.2402 | 81.9095 | 8.0905 | -76.6879 | 74.4672 | 3.1015 | 43.23 | 0.8 | 1 | 11.854 | 58.1855 | -10.8 | -8.9817 | 1.1359 | 0.054197
2015-04-03 07:00 | 97.0467 | 77.7733 | 19.2733 | 98.6856 | 4.9324 | -60.2369 | 78.7377 | 11.2623 | -61.8666 | 60.123 | 49.1592 | 58.33 | 0.8 | 1 | 19.4093 | 126.8985 | -10.6 | -6.6344 | 1.1265 | 0.11722
2015-04-03 08:00 | 134.8233 | 97.9067 | 36.9167 | 152.3862 | 4.9484 | -45.2337 | 75.9802 | 14.0198 | -46.8073 | 45.875 | 106.0954 | 73.43 | 0.8 | 1 | 26.9647 | 206.49 | -10.8 | -4.3472 | 1.1174 | 0.1892
2015-04-03 09:00 | 172.6 | 118.04 | 54.56 | 195.9596 | 4.9643 | -30.2304 | 73.8338 | 16.1662 | -31.4826 | 31.9453 | 166.2823 | 88.53 | 0.8 | 1 | 34.52 | 289.3323 | -10.8 | -1.7584 | 1.107 | 0.26265
2015-04-03 10:00 | 185.1833 | 116.1567 | 69.0267 | 229.0534 | 4.9803 | -15.2271 | 72.4609 | 17.5391 | -15.9269 | 19.1358 | 216.3968 | 87.1175 | 0.8 | 1 | 37.0367 | 340.551 | -10.8 | -0.15778 | 1.1006 | 0.30735
2015-04-03 11:00 | 197.7667 | 114.2733 | 83.4933 | 269.762 | 4.9963 | -0.22387 | 71.9705 | 18.0295 | -0.23454 | 11.9724 | 263.8941 | 85.705 | 0.8 | 1 | 39.5533 | 389.1524 | -10.9 | 1.261 | 1.095 | 0.34941
2015-04-03 12:00 | 210.35 | 112.39 | 97.96 | 324.0043 | 5.0123 | 14.7794 | 72.4017 | 17.5983 | 15.462 | 18.7751 | 306.7637 | 84.2925 | 0.8 | 1 | 42.07 | 433.1262 | -11 | 2.5352 | 1.0899 | 0.38708
2015-04-03 13:00 | 179.6133 | 100.84 | 78.7733 | 280.9652 | 5.0283 | 29.7827 | 73.7179 | 16.2821 | 31.0291 | 31.513 | 239.5289 | 75.63 | 0.8 | 1 | 35.9227 | 351.0816 | -11 | -0.0287 | 1.1001 | 0.31671
2015-04-03 14:00 | 148.8767 | 89.29 | 59.5867 | 243.1114 | 5.0443 | 44.7859 | 75.8122 | 14.1878 | 46.3699 | 45.4219 | 170.6352 | 66.9675 | 0.8 | 1 | 29.7753 | 267.3781 | -10.9 | -2.5444 | 1.1102 | 0.24341
2015-04-03 15:00 | 118.14 | 77.74 | 40.4 | 203.0505 | 5.0602 | 59.7892 | 78.5235 | 11.4765 | 61.4468 | 59.659 | 102.5699 | 58.305 | 0.8 | 1 | 23.628 | 184.5029 | -11 | -5.2343 | 1.1209 | 0.16959
2015-04-03 16:00 | 84 | 55.6167 | 28.3833 | 195.5767 | 5.0762 | 74.7925 | 81.6554 | 8.3446 | 76.2838 | 73.9942 | 53.9273 | 41.7125 | 0.8 | 1 | 16.8 | 112.4398 | -11.2 | -7.6863 | 1.1307 | 0.10426
2015-04-03 17:00 | 49.86 | 33.4933 | 16.3667 | 187.5348 | 5.0922 | 89.7957 | 84.9933 | 5.0067 | 90.9523 | 88.3211 | 5.4944 | 25.12 | 0.8 | 1 | 9.972 | 40.5864 | -10.9 | -9.6317 | 1.1385 | 0.037891
2015-04-03 18:00 | 15.72 | 11.37 | 4.35 | 0 | 5.1081 | 104.799 | 88.3171 | 1.6829 | 105.5486 | 102.5539 | 0 | 8.5275 | 0.8 | 1 | 3.144 | 11.6715 | -10.8 | -10.4353 | 1.1417 | 0.010927
2015-04-03 19:00 | 10.48 | 7.58 | 2.9 | 0 | 5.1241 | 119.8022 | 91.411 | -1.411 | 120.1697 | 116.5778 | 0 | 5.685 | 0.8 | 1 | 2.096 | 7.781 | -10.7 | -10.4568 | 1.1418 | 0.0072853
2015-04-03 20:00 | 5.24 | 3.79 | 1.45 | 0 | 5.1401 | 134.8055 | 94.0715 | -4.0715 | 134.892 | 130.1788 | 0 | 2.8425 | 0.8 | 1 | 1.048 | 3.8905 | -10.8 | -10.6784 | 1.1427 | 0.0036455
2015-04-03 21:00 | 0 | 0 | 0 | 0 | 5.156 | 149.8087 | 96.1185 | -6.1185 | 149.7534 | 142.8598 | 0 | 0 | 0.8 | 1 | 0 | 0 | -10.7 | -10.7 | 1.1428 | 0
2015-04-03 22:00 | 0 | 0 | 0 | 0 | 5.172 | 164.812 | 97.4078 | -7.4078 | 164.7449 | 153.253 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.2 | -11.2 | 1.1448 | 0
2015-04-03 23:00 | 0 | 0 | 0 | 0 | 5.1879 | 179.8153 | 97.8453 | -7.8453 | 179.8143 | 157.8446 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11 | -11 | 1.144 | 0
2015-04-04 | 0 | 0 | 0 | 0 | 5.2039 | -165.1815 | 97.3977 | -7.3977 | -165.1172 | 153.4294 | 0 | 0 | 0.8 | 1 | 0 | 0 | -11.2 | -11.2 | 1.1448 | 0
2015-04-04 01:00 | 1.5767 | 1.1467 | 0.43 | 0 | 5.2198 | -150.1782 | 96.0968 | -6.0968 | -150.1284 | 143.1134 | 0 | 0.86 | 0.8 | 1 | 0.31533 | 1.1753 | -11.3 | -11.2633 | 1.1451 | 0.0011036
2015-04-04 02:00 | 3.1533 | 2.2933 | 0.86 | 0 | 5.2358 | -135.175 | 94.0358 | -4.0358 | -135.2715 | 130.4611 | 0 | 1.72 | 0.8 | 1 | 0.63067 | 2.3507 | -11.3 | -11.2265 | 1.1449 | 0.0022069
2015-04-04 03:00 | 4.73 | 3.44 | 1.29 | 0 | 5.2517 | -120.1717 | 91.3577 | -1.3577 | -120.5557 | 116.8714 | 0 | 2.58 | 0.8 | 1 | 0.946 | 3.526 | -11.4 | -11.2898 | 1.1452 | 0.003311
2015-04-04 04:00 | 25.4033 | 17.46 | 7.9433 | 0 | 5.2677 | -105.1685 | 88.2416 | 1.7584 | -105.9426 | 102.8513 | 0 | 13.095 | 0.8 | 1 | 5.0807 | 18.1757 | -11.5 | -10.932 | 1.1437 | 0.017046
2015-04-04 05:00 | 46.0767 | 31.48 | 14.5967 | 163.8859 | 5.2836 | -90.1652 | 84.8901 | 5.1099 | -91.3557 | 88.6176 | 3.9538 | 23.61 | 0.8 | 1 | 9.2153 | 36.7792 | -11.2 | -10.0507 | 1.1402 | 0.034387
2015-04-04 06:00 | 66.75 | 45.5 | 21.25 | 144.0787 | 5.2995 | -75.162 | 81.5186 | 8.4814 | -76.6964 | 74.2853 | 39.0233 | 34.125 | 0.8 | 1 | 13.35 | 86.4983 | -10.9 | -8.1969 | 1.1328 | 0.080347
2015-04-04 07:00 | 74.78 | 55.93 | 18.85 | 93.3224 | 5.3155 | -60.1587 | 78.3468 | 11.6532 | -61.8668 | 59.9386 | 46.7478 | 41.9475 | 0.8 | 1 | 14.956 | 103.6513 | -10.7 | -7.4609 | 1.1298 | 0.09603
2015-04-04 08:00 | 82.81 | 66.36 | 16.45 | 66.0996 | 5.3314 | -45.1555 | 75.5895 | 14.4105 | -46.7933 | 45.6781 | 46.183 | 49.77 | 0.8 | 1 | 16.562 | 112.515 | -10.5 | -6.9839 | 1.1279 | 0.10407
2015-04-04 09:00 | 90.84 | 76.79 | 14.05 | 49.3073 | 5.3473 | -30.1522 | 73.4443 | 16.5557 | -31.4493 | 31.7172 | 41.9434 | 57.5925 | 0.8 | 1 | 18.168 | 117.7039 | -10.1 | -6.4218 | 1.1257 | 0.10865
2015-04-04 10:00 | 94.4967 | 81.5033 | 12.9933 | 42.2149 | 5.3633 | -15.149 | 72.0739 | 17.9261 | -15.8703 | 18.8317 | 39.9552 | 61.1275 | 0.8 | 1 | 18.8993 | 119.982 | -9.3 | -5.5506 | 1.1222 | 0.11041
2015-04-04 11:00 | 98.1533 | 86.2167 | 11.9367 | 37.7915 | 5.3792 | -0.14575 | 71.5875 | 18.4125 | -0.15294 | 11.5884 | 37.0212 | 64.6625 | 0.8 | 1 | 19.6307 | 121.3144 | -8.6 | -4.8089 | 1.1192 | 0.11134
2015-04-04 12:00 | 101.81 | 90.93 | 10.88 | 35.2544 | 5.3951 | 14.8575 | 72.0243 | 17.9757 | 15.5679 | 18.5874 | 33.4155 | 68.1975 | 0.8 | 1 | 20.362 | 121.975 | -8.1 | -4.2883 | 1.1172 | 0.11174
2015-04-04 13:00 | 96.33 | 87.0633 | 9.2667 | 32.3357 | 5.411 | 29.8607 | 73.3469 | 16.6531 | 31.1563 | 31.4261 | 27.5925 | 65.2975 | 0.8 | 1 | 19.266 | 112.156 | -7.3 | -3.7951 | 1.1152 | 0.10256
2015-04-04 14:00 | 90.85 | 83.1967 | 7.6533 | 30.459 | 5.4269 | 44.864 | 75.4475 | 14.5525 | 46.5139 | 45.3726 | 21.3972 | 62.3975 | 0.8 | 1 | 18.17 | 101.9647 | -6.9 | -3.7136 | 1.1149 | 0.093214
2015-04-04 15:00 | 85.37 | 79.33 | 6.04 | 29.4476 | 5.4428 | 59.8672 | 78.1641 | 11.8359 | 61.6023 | 59.6241 | 14.8908 | 59.4975 | 0.8 | 1 | 17.074 | 91.4623 | -7 | -4.1418 | 1.1166 | 0.083742
2015-04-04 16:00 | 61.1367 | 56.29 | 4.8467 | 32.0394 | 5.4588 | 74.8705 | 81.2993 | 8.7007 | 76.4456 | 73.9623 | 8.8515 | 42.2175 | 0.8 | 1 | 12.2273 | 63.2963 | -6.6 | -4.622 | 1.1185 | 0.058053
2015-04-04 17:00 | 36.9033 | 33.25 | 3.6533 | 39.0971 | 5.4747 | 89.8737 | 84.6383 | 5.3617 | 91.1152 | 88.2843 | 1.1706 | 24.9375 | 0.8 | 1 | 7.3807 | 33.4887 | -6.2 | -5.1535 | 1.1206 | 0.030773
2015-04-04 18:00 | 12.67 | 10.21 | 2.46 | 0 | 5.4906 | 104.8769 | 87.9609 | 2.0391 | 105.7078 | 102.5048 | 0 | 7.6575 | 0.8 | 1 | 2.534 | 10.1915 | -5.7 | -5.3815 | 1.1215 | 0.0093726
2015-04-04 19:00 | 8.4467 | 6.8067 | 1.64 | 0 | 5.5065 | 119.8802 | 91.0512 | -1.0512 | 120.3207 | 116.5067 | 0 | 5.105 | 0.8 | 1 | 1.6893 | 6.7943 | -5.5 | -5.2877 | 1.1212 | 0.0062463
2015-04-04 20:00 | 4.2233 | 3.4033 | 0.82 | 0 | 5.5224 | 134.8834 | 93.7066 | -3.7066 | 135.0302 | 130.071 | 0 | 2.5525 | 0.8 | 1 | 0.84467 | 3.3972 | -5.3 | -5.1938 | 1.1208 | 0.0031221
2015-04-04 21:00 | 0 | 0 | 0 | 0 | 5.5383 | 149.8866 | 95.7476 | -5.7476 | 149.8746 | 142.6891 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-04-04 22:00 | 0 | 0 | 0 | 0 | 5.5541 | 164.8899 | 97.031 | -7.031 | 164.8458 | 152.9774 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.118 | 0
2015-04-04 23:00 | 0 | 0 | 0 | 0 | 5.57 | 179.8931 | 97.4633 | -7.4633 | 179.8927 | 157.4631 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-04-05 | 0 | 0 | 0 | 0 | 5.5859 | -165.1037 | 97.0118 | -7.0118 | -165.0618 | 153.0669 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-04-05 01:00 | 1.9267 | 1.2767 | 0.65 | 0 | 5.6018 | -150.1005 | 95.7086 | -5.7086 | -150.0944 | 142.8183 | 0 | 0.9575 | 0.8 | 1 | 0.38533 | 1.3428 | -4.3 | -4.258 | 1.117 | 0.00123
2015-04-05 02:00 | 3.8533 | 2.5533 | 1.3 | 0 | 5.6177 | -135.0972 | 93.6465 | -3.6465 | -135.256 | 130.2149 | 0 | 1.915 | 0.8 | 1 | 0.77067 | 2.6857 | -4.6 | -4.5161 | 1.1181 | 0.0024623
2015-04-05 03:00 | 5.78 | 3.83 | 1.95 | 0 | 5.6336 | -120.094 | 90.9681 | -0.96812 | -120.5543 | 116.656 | 0 | 2.8725 | 0.8 | 1 | 1.156 | 4.0285 | -4.5 | -4.3741 | 1.1175 | 0.0036915
2015-04-05 04:00 | 34.2933 | 17.07 | 17.2233 | 0 | 5.6494 | -105.0908 | 87.8522 | 2.1478 | -105.9503 | 102.6551 | 0 | 12.8025 | 0.8 | 1 | 6.8587 | 19.6612 | -4.8 | -4.1856 | 1.1167 | 0.018004
2015-04-05 05:00 | 62.8067 | 30.31 | 32.4967 | 339.1033 | 5.6653 | -90.0876 | 84.5008 | 5.4992 | -91.3668 | 88.4326 | 9.2754 | 22.7325 | 0.8 | 1 | 12.5613 | 44.5692 | -4.5 | -3.1072 | 1.1124 | 0.040656
2015-04-05 06:00 | 91.32 | 43.55 | 47.77 | 309.7822 | 5.6812 | -75.0843 | 81.1293 | 8.8707 | -76.7053 | 74.1052 | 84.8407 | 32.6625 | 0.8 | 1 | 18.264 | 135.7672 | -4.8 | -0.55727 | 1.1022 | 0.12271
2015-04-05 07:00 | 120.4767 | 56.2133 | 64.2633 | 308.0138 | 5.697 | -60.0811 | 77.9575 | 12.0425 | -61.8674 | 59.7565 | 155.1391 | 42.16 | 0.8 | 1 | 24.0953 | 221.3945 | -4.8 | 2.1186 | 1.0915 | 0.19816
2015-04-05 08:00 | 149.6333 | 68.8767 | 80.7567 | 316.1513 | 5.7129 | -45.0779 | 75.2005 | 14.7995 | -46.7796 | 45.4844 | 221.6548 | 51.6575 | 0.8 | 1 | 29.9267 | 303.2389 | -4.4 | 5.0762 | 1.0797 | 0.26847
2015-04-05 09:00 | 178.79 | 81.54 | 97.25 | 333.6991 | 5.7288 | -30.0747 | 73.0564 | 16.9436 | -31.4163 | 31.4932 | 284.546 | 61.155 | 0.8 | 1 | 35.758 | 381.459 | -4.8 | 7.1206 | 1.0715 | 0.33517
2015-04-05 10:00 | 165.91 | 90.4233 | 75.4867 | 240.2633 | 5.7446 | -15.0715 | 71.6885 | 18.3115 | -15.8141 | 18.5322 | 227.8045 | 67.8175 | 0.8 | 1 | 33.182 | 328.804 | -4.6 | 5.6751 | 1.0773 | 0.29046
2015-04-05 11:00 | 153.03 | 99.3067 | 53.7233 | 166.7581 | 5.7605 | -0.068235 | 71.2062 | 18.7938 | -0.071714 | 11.2064 | 163.5786 | 74.48 | 0.8 | 1 | 30.606 | 268.6646 | -4.4 | 3.9958 | 1.084 | 0.23881
2015-04-05 12:00 | 140.15 | 108.19 | 31.96 | 101.5101 | 5.7763 | 14.935 | 71.6485 | 18.3515 | 15.6734 | 18.4063 | 96.3169 | 81.1425 | 0.8 | 1 | 28.03 | 205.4894 | -4.6 | 1.8215 | 1.0927 | 0.18412
2015-04-05 13:00 | 117.97 | 94.21 | 23.76 | 81.1618 | 5.7922 | 29.9382 | 72.9774 | 17.0226 | 31.2831 | 31.3434 | 69.3175 | 70.6575 | 0.8 | 1 | 23.594 | 163.569 | -4.4 | 0.71153 | 1.0972 | 0.14716
2015-04-05 14:00 | 95.79 | 80.23 | 15.56 | 60.4513 | 5.808 | 44.9414 | 75.0843 | 14.9157 | 46.6573 | 45.3257 | 42.5018 | 60.1725 | 0.8 | 1 | 19.158 | 121.8323 | -4.5 | -0.69274 | 1.1028 | 0.11017
2015-04-05 15:00 | 73.61 | 66.25 | 7.36 | 34.845 | 5.8239 | 59.9446 | 77.8061 | 12.1939 | 61.7572 | 59.5906 | 17.6377 | 49.6875 | 0.8 | 1 | 14.722 | 82.0472 | -4.3 | -1.736 | 1.1069 | 0.074474
2015-04-05 16:00 | 52.87 | 47.7733 | 5.0967 | 32.383 | 5.8397 | 74.9478 | 80.9447 | 9.0553 | 76.6065 | 73.9309 | 8.9635 | 35.83 | 0.8 | 1 | 10.574 | 55.3675 | -4.5 | -2.7698 | 1.1111 | 0.050444
2015-04-05 17:00 | 32.13 | 29.2967 | 2.8333 | 28.4517 | 5.8555 | 89.951 | 84.2848 | 5.7152 | 91.2772 | 88.2474 | 0.87017 | 21.9725 | 0.8 | 1 | 6.426 | 29.2687 | -4.5 | -3.5854 | 1.1143 | 0.026745
2015-04-05 18:00 | 11.39 | 10.82 | 0.57 | 0 | 5.8714 | 104.9542 | 87.606 | 2.394 | 105.866 | 102.4548 | 0 | 8.115 | 0.8 | 1 | 2.278 | 10.393 | -4.2 | -3.8752 | 1.1155 | 0.0095066
2015-04-05 19:00 | 7.5933 | 7.2133 | 0.38 | 0 | 5.8872 | 119.9575 | 90.6928 | -0.69284 | 120.4706 | 116.4343 | 0 | 5.41 | 0.8 | 1 | 1.5187 | 6.9287 | -4.4 | -4.1835 | 1.1167 | 0.0063447
2015-04-05 20:00 | 3.7967 | 3.6067 | 0.19 | 0 | 5.903 | 134.9607 | 93.3431 | -3.3431 | 135.1672 | 129.9613 | 0 | 2.705 | 0.8 | 1 | 0.75933 | 3.4643 | -4.4 | -4.2917 | 1.1172 | 0.0031736
2015-04-05 21:00 | 0 | 0 | 0 | 0 | 5.9188 | 149.9639 | 95.3782 | -5.3782 | 149.9948 | 142.516 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.118 | 0
2015-04-05 22:00 | 0 | 0 | 0 | 0 | 5.9347 | 164.9671 | 96.6556 | -6.6556 | 164.9457 | 152.7001 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.5 | -4.5 | 1.118 | 0
2015-04-05 23:00 | 0 | 0 | 0 | 0 | 5.9505 | 179.9703 | 97.0828 | -7.0828 | 179.9702 | 157.0828 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.2 | -4.2 | 1.1168 | 0
2015-04-06 | 0 | 0 | 0 | 0 | 5.9663 | -165.0265 | 96.6275 | -6.6275 | -165.007 | 152.7054 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.3 | -4.3 | 1.1172 | 0
2015-04-06 01:00 | 0.41667 | 0.41667 | 0 | 0 | 5.9821 | -150.0233 | 95.322 | -5.322 | -150.061 | 142.5234 | 0 | 0.3125 | 0.8 | 1 | 0.083333 | 0.39583 | -3.8 | -3.7876 | 1.1152 | 0.00036196
2015-04-06 02:00 | 0.83333 | 0.83333 | 0 | 0 | 5.9979 | -135.0201 | 93.2589 | -3.2589 | -135.2409 | 129.9689 | 0 | 0.625 | 0.8 | 1 | 0.16667 | 0.79167 | -3.8 | -3.7753 | 1.1151 | 0.00072389
2015-04-06 03:00 | 1.25 | 1.25 | 0 | 0 | 6.0137 | -120.0169 | 90.5803 | -0.5803 | -120.5533 | 116.441 | 0 | 0.9375 | 0.8 | 1 | 0.25 | 1.1875 | -3.5 | -3.4629 | 1.1139 | 0.0010846
2015-04-06 04:00 | 7.6333 | 7.52 | 0.11333 | 0 | 6.0295 | -105.0137 | 87.4645 | 2.5355 | -105.9584 | 102.4597 | 0 | 5.64 | 0.8 | 1 | 1.5267 | 7.1667 | -3.5 | -3.276 | 1.1131 | 0.0065413
2015-04-06 05:00 | 14.0167 | 13.79 | 0.22667 | 2.2101 | 6.0453 | -90.0106 | 84.1133 | 5.8867 | -91.3784 | 88.2489 | 0.067534 | 10.3425 | 0.8 | 1 | 2.8033 | 13.2134 | -3.1 | -2.6871 | 1.1107 | 0.012035
2015-04-06 06:00 | 20.4 | 20.06 | 0.34 | 2.1133 | 6.0611 | -75.0074 | 80.7418 | 9.2582 | -76.7145 | 73.9268 | 0.58511 | 15.045 | 0.8 | 1 | 4.08 | 19.7101 | -2.2 | -1.5841 | 1.1063 | 0.017881
2015-04-06 07:00 | 29.72 | 28.6067 | 1.1133 | 5.1723 | 6.0769 | -60.0042 | 77.5699 | 12.4301 | -61.8683 | 59.5768 | 2.6192 | 21.455 | 0.8 | 1 | 5.944 | 30.0182 | -2 | -1.0619 | 1.1042 | 0.027181
2015-04-06 08:00 | 39.04 | 37.1533 | 1.8867 | 7.202 | 6.0927 | -45.001 | 74.8133 | 15.1867 | -46.7665 | 45.2939 | 5.0664 | 27.865 | 0.8 | 1 | 7.808 | 40.7394 | -2.6 | -1.3269 | 1.1053 | 0.036924
2015-04-06 09:00 | 48.36 | 45.7 | 2.66 | 8.9301 | 6.1085 | -29.9978 | 72.6703 | 17.3297 | -31.3837 | 31.2735 | 7.6325 | 34.275 | 0.8 | 1 | 9.672 | 51.5795 | -2.3 | -0.68814 | 1.1028 | 0.046641
2015-04-06 10:00 | 60.3067 | 57.38 | 2.9267 | 9.1306 | 6.1243 | -14.9946 | 71.3048 | 18.6952 | -15.7584 | 18.2377 | 8.672 | 43.035 | 0.8 | 1 | 12.0613 | 63.7683 | -2.5 | -0.50724 | 1.102 | 0.057625
2015-04-06 11:00 | 72.2533 | 69.06 | 3.1933 | 9.7231 | 6.1401 | 0.0085764 | 70.8266 | 19.1734 | 0.009028 | 10.8266 | 9.55 | 51.795 | 0.8 | 1 | 14.4507 | 75.7957 | -2.1 | 0.26861 | 1.0989 | 0.068301
2015-04-06 12:00 | 84.2 | 80.74 | 3.46 | 10.7776 | 6.1559 | 15.0118 | 71.2744 | 18.7256 | 15.7784 | 18.2319 | 10.2365 | 60.555 | 0.8 | 1 | 16.84 | 87.6315 | -1.9 | 0.83849 | 1.0966 | 0.078803
2015-04-06 13:00 | 73.0833 | 67.26 | 5.8233 | 19.4838 | 6.1716 | 30.0149 | 72.6096 | 17.3904 | 31.4093 | 31.2647 | 16.6543 | 50.445 | 0.8 | 1 | 14.6167 | 81.716 | -2 | 0.55363 | 1.0978 | 0.073559
2015-04-06 14:00 | 61.9667 | 53.78 | 8.1867 | 31.0701 | 6.1874 | 45.0181 | 74.7227 | 15.2773 | 46.8001 | 45.2811 | 21.8618 | 40.335 | 0.8 | 1 | 12.3933 | 74.5901 | -1.3 | 1.0309 | 1.0959 | 0.067028
2015-04-06 15:00 | 50.85 | 40.3 | 10.55 | 48.551 | 6.2032 | 60.0213 | 77.4497 | 12.5503 | 61.9113 | 59.5582 | 24.599 | 30.225 | 0.8 | 1 | 10.17 | 64.994 | -1.2 | 0.83106 | 1.0967 | 0.058447
2015-04-06 16:00 | 37.1867 | 29.5967 | 7.59 | 46.4306 | 6.2189 | 75.0245 | 80.5917 | 9.4083 | 76.7667 | 73.8999 | 12.876 | 22.1975 | 0.8 | 1 | 7.4373 | 42.5108 | -1.1 | 0.22846 | 1.0991 | 0.038313
2015-04-06 17:00 | 23.5233 | 18.8933 | 4.63 | 43.805 | 6.2347 | 90.0277 | 83.9328 | 6.0672 | 91.4383 | 88.2102 | 1.3681 | 14.17 | 0.8 | 1 | 4.7047 | 20.2428 | -0.8 | -0.16741 | 1.1007 | 0.01827
2015-04-06 18:00 | 9.86 | 8.19 | 1.67 | 0 | 6.2505 | 105.0308 | 87.2526 | 2.7474 | 106.0232 | 102.4041 | 0 | 6.1425 | 0.8 | 1 | 1.972 | 8.1145 | -0.8 | -0.54642 | 1.1022 | 0.0073338
2015-04-06 19:00 | 6.5733 | 5.46 | 1.1133 | 0 | 6.2662 | 120.034 | 90.336 | -0.33598 | 120.6193 | 116.3605 | 0 | 4.095 | 0.8 | 1 | 1.3147 | 5.4097 | -0.6 | -0.43095 | 1.1017 | 0.0048872
2015-04-06 20:00 | 3.2867 | 2.73 | 0.55667 | 0 | 6.282 | 135.0372 | 92.9812 | -2.9812 | 135.3031 | 129.8495 | 0 | 2.0475 | 0.8 | 1 | 0.65733 | 2.7048 | -0.8 | -0.71547 | 1.1029 | 0.0024461
2015-04-06 21:00 | 0 | 0 | 0 | 0 | 6.2977 | 150.0404 | 95.0103 | -5.0103 | 150.1137 | 142.3406 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-04-06 22:00 | 0 | 0 | 0 | 0 | 6.3135 | 165.0435 | 96.282 | -6.282 | 165.0445 | 152.4214 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-04-06 23:00 | 0 | 0 | 0 | 0 | 6.3292 | 180.0467 | 96.7041 | -6.7041 | -179.9533 | 156.7041 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-04-07 | 0 | 0 | 0 | 0 | 6.345 | -164.9501 | 96.2451 | -6.2451 | -164.9531 | 152.3452 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-04-07 01:00 | 2.72 | 1.89 | 0.83 | 0 | 6.3607 | -149.947 | 94.9373 | -4.9373 | -150.0283 | 142.2288 | 0 | 1.4175 | 0.8 | 1 | 0.544 | 1.9615 | -2.7 | -2.6387 | 1.1106 | 0.0017862
2015-04-07 02:00 | 5.44 | 3.78 | 1.66 | 0 | 6.3764 | -134.9438 | 92.8731 | -2.8731 | -135.2265 | 129.723 | 0 | 2.835 | 0.8 | 1 | 1.088 | 3.923 | -3 | -2.8774 | 1.1115 | 0.0035756
2015-04-07 03:00 | 8.16 | 5.67 | 2.49 | 0 | 6.3922 | -119.9407 | 90.1943 | -0.19433 | -120.5528 | 116.2266 | 0 | 4.2525 | 0.8 | 1 | 1.632 | 5.8845 | -2.9 | -2.7161 | 1.1109 | 0.0053602
2015-04-07 04:00 | 37.55 | 21.0367 | 16.5133 | 0 | 6.4079 | -104.9375 | 87.0787 | 2.9213 | -105.9669 | 102.2652 | 0 | 15.7775 | 0.8 | 1 | 7.51 | 23.2875 | -2.4 | -1.6723 | 1.1067 | 0.021133
2015-04-07 05:00 | 66.94 | 36.4033 | 30.5367 | 279.503 | 6.4236 | -89.9343 | 83.7277 | 6.2723 | -91.3905 | 88.0666 | 9.4297 | 27.3025 | 0.8 | 1 | 13.388 | 50.1202 | -1.8 | -0.23374 | 1.1009 | 0.045247
2015-04-07 06:00 | 96.33 | 51.77 | 44.56 | 265.9944 | 6.4393 | -74.9312 | 80.3562 | 9.6438 | -76.7243 | 73.7504 | 74.4311 | 38.8275 | 0.8 | 1 | 19.266 | 132.5246 | -2.6 | 1.5414 | 1.0938 | 0.11887
2015-04-07 07:00 | 138.92 | 65.4133 | 73.5067 | 331.3862 | 6.4551 | -59.928 | 77.1843 | 12.8157 | -61.8699 | 59.3997 | 168.6909 | 49.06 | 0.8 | 1 | 27.784 | 245.5349 | -2.9 | 4.773 | 1.0809 | 0.21763
2015-04-07 08:00 | 181.51 | 79.0567 | 102.4533 | 381.6471 | 6.4708 | -44.9249 | 74.4279 | 15.5721 | -46.7539 | 45.1067 | 269.3622 | 59.2925 | 0.8 | 1 | 36.302 | 364.9567 | -3 | 8.4049 | 1.0664 | 0.31913
2015-04-07 09:00 | 224.1 | 92.7 | 131.4 | 431.8593 | 6.4865 | -29.9217 | 72.286 | 17.714 | -31.3518 | 31.0582 | 369.9494 | 69.525 | 0.8 | 1 | 44.82 | 484.2944 | -3.4 | 11.7342 | 1.0531 | 0.41819
2015-04-07 10:00 | 227.6167 | 93.33 | 134.2867 | 410.8651 | 6.5022 | -14.9186 | 70.923 | 19.077 | -15.7032 | 17.9483 | 390.8703 | 69.9975 | 0.8 | 1 | 45.5233 | 506.3912 | -3.1 | 12.7247 | 1.0491 | 0.43563
2015-04-07 11:00 | 231.1333 | 93.96 | 137.1733 | 409.9013 | 6.5179 | 0.084596 | 70.4488 | 19.5512 | 0.089192 | 10.4491 | 403.1037 | 70.47 | 0.8 | 1 | 46.2267 | 519.8004 | -2.7 | 13.5438 | 1.0458 | 0.44577
2015-04-07 12:00 | 234.65 | 94.59 | 140.06 | 428.0763 | 6.5336 | 15.0877 | 70.902 | 19.098 | 15.8828 | 18.0641 | 406.9765 | 70.9425 | 0.8 | 1 | 46.93 | 524.849 | -2.4 | 14.0015 | 1.044 | 0.44931
2015-04-07 13:00 | 223.2833 | 76.22 | 147.0633 | 482.2193 | 6.5493 | 30.0909 | 72.2435 | 17.7565 | 31.5349 | 31.19 | 412.5169 | 57.165 | 0.8 | 1 | 44.6567 | 514.3386 | -3 | 13.0731 | 1.0477 | 0.44188
2015-04-07 14:00 | 211.9167 | 57.85 | 154.0667 | 571.5812 | 6.565 | 45.094 | 74.3628 | 15.6372 | 46.9422 | 45.2387 | 402.4816 | 43.3875 | 0.8 | 1 | 42.3833 | 488.2524 | -1.4 | 13.8579 | 1.0446 | 0.41821
2015-04-07 15:00 | 200.55 | 39.48 | 161.07 | 721.1965 | 6.5807 | 60.0972 | 77.0949 | 12.9051 | 62.0646 | 59.527 | 365.7425 | 29.61 | 0.8 | 1 | 40.11 | 435.4625 | -2.6 | 11.0082 | 1.056 | 0.37706
2015-04-07 16:00 | 142.27 | 31.1533 | 111.1167 | 655.4845 | 6.5964 | 75.1003 | 80.2402 | 9.7598 | 76.9258 | 73.8693 | 182.1132 | 23.365 | 0.8 | 1 | 28.454 | 233.9322 | -3.1 | 4.2104 | 1.0832 | 0.20778
2015-04-07 17:00 | 83.99 | 22.8267 | 61.1633 | 547.1963 | 6.6121 | 90.1035 | 83.5823 | 6.4177 | 91.5982 | 88.1728 | 17.4478 | 17.12 | 0.8 | 1 | 16.798 | 51.3658 | -3.5 | -1.8948 | 1.1076 | 0.046651
2015-04-07 18:00 | 25.71 | 14.5 | 11.21 | 207.3447 | 6.6278 | 105.1066 | 86.9008 | 3.0992 | 106.1792 | 102.3525 | 0 | 10.875 | 0.8 | 1 | 5.142 | 16.017 | -4.3 | -3.7995 | 1.1152 | 0.014647
2015-04-07 19:00 | 17.14 | 9.6667 | 7.4733 | 0 | 6.6435 | 120.1097 | 89.9807 | 0.019307 | 120.7667 | 116.2853 | 0 | 7.25 | 0.8 | 1 | 3.428 | 10.678 | -5.3 | -4.9663 | 1.1199 | 0.0098055
2015-04-07 20:00 | 8.57 | 4.8333 | 3.7367 | 0 | 6.6591 | 135.1129 | 92.6208 | -2.6208 | 135.4376 | 129.7359 | 0 | 3.625 | 0.8 | 1 | 1.714 | 5.339 | -4.8 | -4.6332 | 1.1185 | 0.0048969
2015-04-07 21:00 | 0 | 0 | 0 | 0 | 6.6748 | 150.116 | 94.6442 | -4.6442 | 150.2314 | 142.1629 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5.5 | -5.5 | 1.122 | 0
2015-04-07 22:00 | 0 | 0 | 0 | 0 | 6.6905 | 165.1191 | 95.91 | -5.91 | 165.142 | 152.1414 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.9 | -4.9 | 1.1196 | 0
2015-04-07 23:00 | 0 | 0 | 0 | 0 | 6.7061 | 180.1223 | 96.3272 | -6.3272 | -179.8778 | 156.3269 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.3 | -4.3 | 1.1172 | 0
2015-04-08 | 0 | 0 | 0 | 0 | 6.7218 | -164.8746 | 95.8645 | -5.8645 | -164.9001 | 151.9864 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.6 | -4.6 | 1.1184 | 0
2015-04-08 01:00 | 3.0433 | 2.1567 | 0.88667 | 0 | 6.7375 | -149.8715 | 94.5544 | -4.5544 | -149.9964 | 141.9346 | 0 | 1.6175 | 0.8 | 1 | 0.60867 | 2.2262 | -5.1 | -5.0304 | 1.1201 | 0.0020447
2015-04-08 02:00 | 6.0867 | 4.3133 | 1.7733 | 0 | 6.7531 | -134.8683 | 92.4893 | -2.4893 | -135.2127 | 129.4777 | 0 | 3.235 | 0.8 | 1 | 1.2173 | 4.4523 | -4.8 | -4.6609 | 1.1186 | 0.0040841
2015-04-08 03:00 | 9.13 | 6.47 | 2.66 | 0 | 6.7688 | -119.8652 | 89.8103 | 0.18966 | -120.553 | 116.0129 | 0 | 4.8525 | 0.8 | 1 | 1.826 | 6.6785 | -5.8 | -5.5913 | 1.1224 | 0.0061465
2015-04-08 04:00 | 39.3667 | 22.09 | 17.2767 | 299.6713 | 6.7844 | -104.8621 | 86.6949 | 3.3051 | -105.976 | 102.0718 | 0 | 16.5675 | 0.8 | 1 | 7.8733 | 24.4408 | -6.2 | -5.4362 | 1.1217 | 0.022481
2015-04-08 05:00 | 69.6033 | 37.71 | 31.8933 | 275.1649 | 6.8001 | -89.859 | 83.3441 | 6.6559 | -91.4031 | 87.8859 | 10.1509 | 28.2825 | 0.8 | 1 | 13.9207 | 52.3541 | -6.2 | -4.5639 | 1.1183 | 0.048007
2015-04-08 06:00 | 99.84 | 53.33 | 46.51 | 267.1162 | 6.8157 | -74.8558 | 79.9726 | 10.0274 | -76.7346 | 73.576 | 75.5253 | 39.9975 | 0.8 | 1 | 19.968 | 135.4908 | -5.2 | -0.96591 | 1.1039 | 0.12264
2015-04-08 07:00 | 155.7833 | 61.2167 | 94.5667 | 414.149 | 6.8314 | -59.8527 | 76.8007 | 13.1993 | -61.872 | 59.2252 | 211.9057 | 45.9125 | 0.8 | 1 | 31.1567 | 288.9748 | -4.4 | 4.6305 | 1.0815 | 0.25627
2015-04-08 08:00 | 211.7267 | 69.1033 | 142.6233 | 518.8375 | 6.847 | -44.8496 | 74.0445 | 15.9555 | -46.742 | 44.923 | 367.3661 | 51.8275 | 0.8 | 1 | 42.3453 | 461.5389 | -2.3 | 12.1231 | 1.0515 | 0.39796
2015-04-08 09:00 | 267.67 | 76.99 | 190.68 | 613.8782 | 6.8626 | -29.8465 | 71.9037 | 18.0963 | -31.3205 | 30.8475 | 527.0358 | 57.7425 | 0.8 | 1 | 53.534 | 638.3123 | -2.8 | 17.1473 | 1.0314 | 0.53986
2015-04-08 10:00 | 273.0767 | 76.23 | 196.8467 | 590.9565 | 6.8783 | -14.8434 | 70.5431 | 19.4569 | -15.6487 | 17.6643 | 563.0932 | 57.1725 | 0.8 | 1 | 54.6153 | 674.8811 | -2.6 | 18.49 | 1.026 | 0.56781
2015-04-08 11:00 | 278.4833 | 75.47 | 203.0133 | 595.652 | 6.8939 | 0.15973 | 70.0728 | 19.9272 | 0.16868 | 10.074 | 586.4687 | 56.6025 | 0.8 | 1 | 55.6967 | 698.7679 | -2.6 | 19.2365 | 1.0231 | 0.5862
2015-04-08 12:00 | 283.89 | 74.71 | 209.18 | 627.6244 | 6.9095 | 15.1628 | 70.5315 | 19.4685 | 15.9865 | 17.9032 | 597.2332 | 56.0325 | 0.8 | 1 | 56.778 | 710.0437 | -2.6 | 19.5889 | 1.0216 | 0.59484
2015-04-08 13:00 | 249.7967 | 75.88 | 173.9167 | 559.1805 | 6.9251 | 30.166 | 71.8793 | 18.1207 | 31.6596 | 31.1191 | 478.7115 | 56.91 | 0.8 | 1 | 49.9593 | 585.5808 | -2.2 | 16.0994 | 1.0356 | 0.49727
2015-04-08 14:00 | 215.7033 | 77.05 | 138.6533 | 503.1717 | 6.9407 | 45.1691 | 74.0047 | 15.9953 | 47.0835 | 45.1985 | 354.5616 | 57.7875 | 0.8 | 1 | 43.1407 | 455.4897 | -2 | 12.2341 | 1.0511 | 0.39257
2015-04-08 15:00 | 181.61 | 78.22 | 103.39 | 450.8169 | 6.9564 | 60.1722 | 76.7418 | 13.2582 | 62.2169 | 59.4968 | 228.8287 | 58.665 | 0.8 | 1 | 36.322 | 323.8157 | -2.3 | 7.8192 | 1.0687 | 0.28378
2015-04-08 16:00 | 130.9 | 58.52 | 72.38 | 412.3468 | 6.972 | 75.1753 | 79.8904 | 10.1096 | 77.0839 | 73.8389 | 114.772 | 43.89 | 0.8 | 1 | 26.18 | 184.842 | -3.4 | 2.3763 | 1.0905 | 0.16529
2015-04-08 17:00 | 80.19 | 38.82 | 41.37 | 351.1187 | 6.9876 | 90.1784 | 83.2335 | 6.7665 | 91.7569 | 88.135 | 11.4272 | 29.115 | 0.8 | 1 | 16.038 | 56.5802 | -4.1 | -2.3319 | 1.1093 | 0.051468
2015-04-08 18:00 | 29.48 | 19.12 | 10.36 | 172.1896 | 7.0032 | 105.1815 | 86.5506 | 3.4494 | 106.3338 | 102.3 | 0 | 14.34 | 0.8 | 1 | 5.896 | 20.236 | -5.6 | -4.9676 | 1.1199 | 0.018583
2015-04-08 19:00 | 19.6533 | 12.7467 | 6.9067 | 0 | 7.0188 | 120.1846 | 89.6271 | 0.37294 | 120.9127 | 116.2086 | 0 | 9.56 | 0.8 | 1 | 3.9307 | 13.4907 | -6 | -5.5784 | 1.1223 | 0.012415
2015-04-08 20:00 | 9.8267 | 6.3733 | 3.4533 | 0 | 7.0344 | 135.1877 | 92.2622 | -2.2622 | 135.5708 | 129.6203 | 0 | 4.78 | 0.8 | 1 | 1.9653 | 6.7453 | -5.5 | -5.2892 | 1.1212 | 0.0062013
2015-04-08 21:00 | 0 | 0 | 0 | 0 | 7.05 | 150.1908 | 94.2797 | -4.2797 | 150.3477 | 141.983 | 0 | 0 | 0.8 | 1 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-04-08 22:00 | 0 | 0 | 0 | 0 | 7.0656 | 165.1939 | 95.5398 | -5.5398 | 165.2383 | 151.8601 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.1132 | 0
2015-04-08 23:00 | 0 | 0 | 0 | 0 | 7.0811 | 180.1969 | 95.9521 | -5.9521 | -179.8035 | 155.9514 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.8 | -2.8 | 1.1112 | 0
2015-04-09 | 0 | 0 | 0 | 0 | 7.0967 | -164.8 | 95.4858 | -5.4858 | -164.8481 | 151.6291 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-04-09 01:00 | 2.71 | 2.2967 | 0.41333 | 0 | 7.1123 | -149.7969 | 94.1736 | -4.1736 | -149.9654 | 141.6411 | 0 | 1.7225 | 0.8 | 1 | 0.542 | 2.2645 | -2.6 | -2.5292 | 1.1101 | 0.0020614
2015-04-09 02:00 | 5.42 | 4.5933 | 0.82667 | 0 | 7.1279 | -134.7938 | 92.1075 | -2.1075 | -135.1996 | 129.2328 | 0 | 3.445 | 0.8 | 1 | 1.084 | 4.529 | -2.8 | -2.6585 | 1.1106 | 0.0041246
2015-04-09 03:00 | 8.13 | 6.89 | 1.24 | 0 | 7.1435 | -119.7907 | 89.4284 | 0.57157 | -120.5538 | 115.8 | 0 | 5.1675 | 0.8 | 1 | 1.626 | 6.7935 | -2.2 | -1.9877 | 1.108 | 0.006172
2015-04-09 04:00 | 31.14 | 23.9267 | 7.2133 | 112.1798 | 7.159 | -104.7876 | 86.3133 | 3.6867 | -105.9857 | 101.8797 | 0 | 17.945 | 0.8 | 1 | 6.228 | 24.173 | -2.1 | -1.3446 | 1.1054 | 0.021911
2015-04-09 05:00 | 54.15 | 40.9633 | 13.1867 | 107.6311 | 7.1746 | -89.7845 | 82.9626 | 7.0374 | -91.4163 | 87.7067 | 4.3068 | 30.7225 | 0.8 | 1 | 10.83 | 45.8593 | -1.9 | -0.4669 | 1.1019 | 0.041435
2015-04-09 06:00 | 77.16 | 58 | 19.16 | 106.0488 | 7.1902 | -74.7815 | 79.5911 | 10.4089 | -76.7456 | 73.4037 | 30.2903 | 43.5 | 0.8 | 1 | 15.432 | 89.2223 | -2.1 | 0.6882 | 1.0972 | 0.080277
2015-04-09 07:00 | 99.1567 | 73.42 | 25.7367 | 109.6027 | 7.2057 | -59.7784 | 76.4191 | 13.5809 | -61.8748 | 59.0534 | 56.3619 | 55.065 | 0.8 | 1 | 19.8313 | 131.2582 | -2 | 2.1018 | 1.0916 | 0.11749
2015-04-09 08:00 | 121.1533 | 88.84 | 32.3133 | 114.8785 | 7.2213 | -44.7753 | 73.6632 | 16.3368 | -46.7307 | 44.7429 | 81.595 | 66.63 | 0.8 | 1 | 24.2307 | 172.4557 | -1.9 | 3.4892 | 1.086 | 0.15358
2015-04-09 09:00 | 143.15 | 104.26 | 38.89 | 122.7135 | 7.2368 | -29.7722 | 71.5234 | 18.4766 | -31.29 | 30.6416 | 105.5793 | 78.195 | 0.8 | 1 | 28.63 | 212.4043 | -2 | 4.6376 | 1.0814 | 0.18836
2015-04-09 10:00 | 140.59 | 100.3867 | 40.2033 | 118.4855 | 7.2524 | -14.7692 | 70.1651 | 19.8349 | -15.5949 | 17.3861 | 113.0722 | 75.29 | 0.8 | 1 | 28.118 | 216.4802 | -2.1 | 4.665 | 1.0813 | 0.19195
2015-04-09 11:00 | 138.03 | 96.5133 | 41.5167 | 119.6604 | 7.2679 | 0.2339 | 69.6989 | 20.3011 | 0.24739 | 9.7014 | 117.9492 | 72.385 | 0.8 | 1 | 27.606 | 217.9402 | -2.1 | 4.7106 | 1.0812 | 0.19321
2015-04-09 12:00 | 135.47 | 92.64 | 42.83 | 126.2131 | 7.2834 | 15.237 | 70.1629 | 19.8371 | 16.0894 | 17.749 | 120.2055 | 69.48 | 0.8 | 1 | 27.094 | 216.7795 | -2 | 4.7744 | 1.0809 | 0.19214
2015-04-09 13:00 | 122.73 | 80.2167 | 42.5133 | 134.1007 | 7.299 | 30.24 | 71.5169 | 18.4831 | 31.7836 | 31.0521 | 114.8839 | 60.1625 | 0.8 | 1 | 24.546 | 199.5924 | -2.3 | 3.9373 | 1.0843 | 0.17745
2015-04-09 14:00 | 109.99 | 67.7933 | 42.1967 | 149.8828 | 7.3145 | 45.2431 | 73.6484 | 16.3516 | 47.2237 | 45.1602 | 105.6863 | 50.845 | 0.8 | 1 | 21.998 | 178.5293 | -2.4 | 3.179 | 1.0873 | 0.15917
2015-04-09 15:00 | 97.25 | 55.37 | 41.88 | 177.9839 | 7.33 | 60.2462 | 76.3906 | 13.6094 | 62.3682 | 59.4676 | 90.4205 | 41.5275 | 0.8 | 1 | 19.45 | 151.398 | -2.3 | 2.4312 | 1.0903 | 0.13535
2015-04-09 16:00 | 71.7533 | 42.0933 | 29.66 | 163.408 | 7.3456 | 75.2492 | 79.5423 | 10.4577 | 77.2407 | 73.8088 | 45.5653 | 31.57 | 0.8 | 1 | 14.3507 | 91.486 | -2.6 | 0.25894 | 1.099 | 0.082443
2015-04-09 17:00 | 46.2567 | 28.8167 | 17.44 | 140.8305 | 7.3611 | 90.2523 | 82.8864 | 7.1136 | 91.9143 | 88.0968 | 4.6772 | 21.6125 | 0.8 | 1 | 9.2513 | 35.541 | -2.8 | -1.6893 | 1.1068 | 0.032255
2015-04-09 18:00 | 20.76 | 15.54 | 5.22 | 78.8092 | 7.3766 | 105.2553 | 86.2022 | 3.7978 | 106.4871 | 102.2466 | 0 | 11.655 | 0.8 | 1 | 4.152 | 15.807 | -3.1 | -2.606 | 1.1104 | 0.014393
2015-04-09 19:00 | 13.84 | 10.36 | 3.48 | 0 | 7.3921 | 120.2584 | 89.2751 | 0.72486 | 121.0573 | 116.1305 | 0 | 7.77 | 0.8 | 1 | 2.768 | 10.538 | -3.5 | -3.1707 | 1.1127 | 0.0096149
2015-04-09 20:00 | 6.92 | 5.18 | 1.74 | 0 | 7.4076 | 135.2614 | 91.9053 | -1.9053 | 135.7025 | 129.5028 | 0 | 3.885 | 0.8 | 1 | 1.384 | 5.269 | -4.5 | -4.3353 | 1.1173 | 0.0048276
2015-04-09 21:00 | 0 | 0 | 0 | 0 | 7.4231 | 150.2645 | 93.9171 | -3.9171 | 150.4626 | 141.801 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.6 | -4.6 | 1.1184 | 0
2015-04-09 22:00 | 0 | 0 | 0 | 0 | 7.4387 | 165.2675 | 95.1716 | -5.1716 | 165.3333 | 151.5779 | 0 | 0 | 0.8 | 1 | 0 | 0 | -4.3 | -4.3 | 1.1172 | 0
2015-04-09 23:00 | 0 | 0 | 0 | 0 | 7.4542 | 180.2706 | 95.579 | -5.579 | -179.7304 | 155.5777 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.7 | -3.7 | 1.1148 | 0
2015-04-10 | 0 | 0 | 0 | 0 | 7.4697 | -164.7264 | 95.1092 | -5.1092 | -164.7972 | 151.2736 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-04-10 01:00 | 0.65333 | 0.55333 | 0.1 | 0 | 7.4851 | -149.7233 | 93.7949 | -3.7949 | -149.9352 | 141.3485 | 0 | 0.415 | 0.8 | 1 | 0.13067 | 0.54567 | -4 | -3.9829 | 1.1159 | 0.00049932
2015-04-10 02:00 | 1.3067 | 1.1067 | 0.2 | 0 | 7.5006 | -134.7203 | 91.7279 | -1.7279 | -135.1873 | 128.9888 | 0 | 0.83 | 0.8 | 1 | 0.26133 | 1.0913 | -3.9 | -3.8659 | 1.1155 | 0.00099822
2015-04-10 03:00 | 1.96 | 1.66 | 0.3 | 0 | 7.5161 | -119.7172 | 89.0487 | 0.95128 | -120.5553 | 115.5881 | 0 | 1.245 | 0.8 | 1 | 0.392 | 1.637 | -3.7 | -3.6488 | 1.1146 | 0.0014962
2015-04-10 04:00 | 7.7467 | 5.97 | 1.7767 | 25.0554 | 7.5316 | -104.7142 | 85.9338 | 4.0662 | -105.9961 | 101.6889 | 0 | 4.4775 | 0.8 | 1 | 1.5493 | 6.0268 | -3.8 | -3.6117 | 1.1144 | 0.0055076
2015-04-10 05:00 | 13.5333 | 10.28 | 3.2533 | 25.2031 | 7.5471 | -89.7112 | 82.5833 | 7.4167 | -91.4302 | 87.5294 | 1.0864 | 7.71 | 0.8 | 1 | 2.7067 | 11.5031 | -3.7 | -3.3405 | 1.1134 | 0.010502
2015-04-10 06:00 | 19.32 | 14.59 | 4.73 | 25.27 | 7.5626 | -74.7081 | 79.2119 | 10.7881 | -76.7573 | 73.2337 | 7.2896 | 10.9425 | 0.8 | 1 | 3.864 | 22.0961 | -4.4 | -3.7095 | 1.1148 | 0.0202
2015-04-10 07:00 | 23.9467 | 19.2567 | 4.69 | 19.4406 | 7.578 | -59.7051 | 76.0398 | 13.9602 | -61.8784 | 58.8846 | 10.0462 | 14.4425 | 0.8 | 1 | 4.7893 | 29.278 | -4.1 | -3.1851 | 1.1127 | 0.026715
2015-04-10 08:00 | 28.5733 | 23.9233 | 4.65 | 16.1668 | 7.5935 | -44.7021 | 73.2841 | 16.7159 | -46.7203 | 44.5664 | 11.5178 | 17.9425 | 0.8 | 1 | 5.7147 | 35.175 | -3.8 | -2.7008 | 1.1108 | 0.032039
2015-04-10 09:00 | 33.2 | 28.59 | 4.61 | 14.265 | 7.609 | -29.699 | 71.1453 | 18.8547 | -31.2603 | 30.4405 | 12.2986 | 21.4425 | 0.8 | 1 | 6.64 | 40.3811 | -0.8 | 0.46191 | 1.0982 | 0.036363
2015-04-10 10:00 | 64.0033 | 51.0667 | 12.9367 | 37.4463 | 7.6244 | -14.696 | 69.7894 | 20.2106 | -15.542 | 17.1138 | 35.7883 | 38.3 | 0.8 | 1 | 12.8007 | 86.8889 | -0.6 | 2.1153 | 1.0915 | 0.077771
2015-04-10 11:00 | 94.8067 | 73.5433 | 21.2633 | 60.2302 | 7.6399 | 0.30701 | 69.327 | 20.673 | 0.32523 | 9.3316 | 59.4332 | 55.1575 | 0.8 | 1 | 18.9613 | 133.552 | -0.35 | 3.8235 | 1.0847 | 0.11879
2015-04-10 12:00 | 125.61 | 96.02 | 29.59 | 85.6793 | 7.6553 | 15.31 | 69.7964 | 20.2036 | 16.1913 | 17.6016 | 81.6679 | 72.015 | 0.8 | 1 | 25.122 | 178.8049 | -0.1 | 5.4877 | 1.078 | 0.15806
2015-04-10 13:00 | 136.5533 | 99.3767 | 37.1767 | 115.1033 | 7.6708 | 30.3131 | 71.1564 | 18.8436 | 31.9065 | 30.9887 | 98.6745 | 74.5325 | 0.8 | 1 | 27.3107 | 200.5176 | -0.1 | 6.1662 | 1.0753 | 0.17681
2015-04-10 14:00 | 147.4967 | 102.7333 | 44.7633 | 155.7198 | 7.6862 | 45.3161 | 73.294 | 16.706 | 47.3629 | 45.124 | 109.872 | 77.05 | 0.8 | 1 | 29.4993 | 216.4214 | 0 | 6.7632 | 1.0729 | 0.19041
2015-04-10 15:00 | 158.44 | 106.09 | 52.35 | 217.0174 | 7.7017 | 60.3191 | 76.0412 | 13.9588 | 62.5182 | 59.4392 | 110.343 | 79.5675 | 0.8 | 1 | 31.688 | 221.5985 | 0 | 6.925 | 1.0723 | 0.19485
2015-04-10 16:00 | 115.44 | 78.47 | 36.97 | 197.228 | 7.7171 | 75.3221 | 79.1961 | 10.8039 | 77.3963 | 73.7788 | 55.095 | 58.8525 | 0.8 | 1 | 23.088 | 137.0355 | -0.2 | 4.0824 | 1.0837 | 0.12177
2015-04-10 17:00 | 72.44 | 50.85 | 21.59 | 166.3138 | 7.7325 | 90.3251 | 82.5411 | 7.4589 | 92.0704 | 88.0581 | 5.6356 | 38.1375 | 0.8 | 1 | 14.488 | 58.2611 | -0.3 | 1.5207 | 1.0939 | 0.052261
2015-04-10 18:00 | 29.44 | 23.23 | 6.21 | 85.9251 | 7.748 | 105.3281 | 85.8555 | 4.1445 | 106.6388 | 102.1922 | 0 | 17.4225 | 0.8 | 1 | 5.888 | 23.3105 | -0.8 | -0.071547 | 1.1003 | 0.021032
2015-04-10 19:00 | 19.6267 | 15.4867 | 4.14 | 0 | 7.7634 | 120.3311 | 88.925 | 1.075 | 121.2004 | 116.051 | 0 | 11.615 | 0.8 | 1 | 3.9253 | 15.5403 | -0.5 | -0.014365 | 1.1001 | 0.014018
2015-04-10 20:00 | 9.8133 | 7.7433 | 2.07 | 0 | 7.7788 | 135.3341 | 91.5503 | -1.5503 | 135.8326 | 129.3833 | 0 | 5.8075 | 0.8 | 1 | 1.9627 | 7.7702 | -0.7 | -0.45718 | 1.1018 | 0.0070203
2015-04-10 21:00 | 0 | 0 | 0 | 0 | 7.7942 | 150.3371 | 93.5564 | -3.5564 | 150.5759 | 141.617 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-04-10 22:00 | 0 | 0 | 0 | 0 | 7.8097 | 165.3401 | 94.8053 | -4.8053 | 165.4268 | 151.2947 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.5 | -0.5 | 1.102 | 0
2015-04-10 23:00 | 0 | 0 | 0 | 0 | 7.8251 | 180.3431 | 95.208 | -5.208 | -179.6586 | 155.2059 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.8 | -0.8 | 1.1032 | 0
2015-04-11 | 0 | 0 | 0 | 0 | 7.8405 | -164.6539 | 94.7347 | -4.7347 | -164.7475 | 150.9198 | 0 | 0 | 0.8 | 1 | 0 | 0 | -1.2 | -1.2 | 1.1048 | 0
2015-04-11 01:00 | 3.2467 | 2.07 | 1.1767 | 0 | 7.8559 | -149.6509 | 93.4184 | -3.4184 | -149.9061 | 141.0568 | 0 | 1.5525 | 0.8 | 1 | 0.64933 | 2.2018 | -0.9 | -0.83119 | 1.1033 | 0.0019921
2015-04-11 02:00 | 6.4933 | 4.14 | 2.3533 | 0 | 7.8713 | -134.6479 | 91.3505 | -1.3505 | -135.1759 | 128.7456 | 0 | 3.105 | 0.8 | 1 | 1.2987 | 4.4037 | -0.9 | -0.76239 | 1.103 | 0.0039831
2015-04-11 03:00 | 9.74 | 6.21 | 3.53 | 0 | 7.8867 | -119.6449 | 88.6713 | 1.3287 | -120.5576 | 115.3774 | 0 | 4.6575 | 0.8 | 1 | 1.948 | 6.6055 | -2 | -1.7936 | 1.1072 | 0.005997
2015-04-11 04:00 | 28.7767 | 16.4933 | 12.2833 | 158.5472 | 7.9021 | -104.6419 | 85.5566 | 4.4434 | -106.0073 | 101.4995 | 0 | 12.37 | 0.8 | 1 | 5.7553 | 18.1253 | -2.3 | -1.7336 | 1.1069 | 0.016452
2015-04-11 05:00 | 47.8133 | 26.7767 | 21.0367 | 155.1312 | 7.9175 | -89.6389 | 82.2064 | 7.7936 | -91.4449 | 87.3539 | 7.162 | 20.0825 | 0.8 | 1 | 9.5627 | 36.8071 | -2.1 | -0.94978 | 1.1038 | 0.033315
2015-04-11 06:00 | 66.85 | 37.06 | 29.79 | 153.8449 | 7.9328 | -74.6359 | 78.8349 | 11.1651 | -76.7698 | 73.0661 | 44.8102 | 27.795 | 0.8 | 1 | 13.37 | 85.9752 | -2 | 0.68673 | 1.0973 | 0.077356
2015-04-11 07:00 | 81.4633 | 49.04 | 32.4233 | 130.9353 | 7.9482 | -59.6329 | 75.6628 | 14.3372 | -61.8828 | 58.7187 | 67.987 | 36.78 | 0.8 | 1 | 16.2927 | 121.0596 | -2.3 | 1.4831 | 1.0941 | 0.10861
2015-04-11 08:00 | 96.0767 | 61.02 | 35.0567 | 119.2732 | 7.9636 | -44.6299 | 72.9073 | 17.0927 | -46.7107 | 44.3938 | 85.2265 | 45.765 | 0.8 | 1 | 19.2153 | 150.2069 | -2.4 | 2.294 | 1.0908 | 0.13436
2015-04-11 09:00 | 110.69 | 73 | 37.69 | 114.4305 | 7.979 | -29.627 | 70.7694 | 19.2306 | -31.2315 | 30.2443 | 98.8548 | 54.75 | 0.8 | 1 | 22.138 | 175.7428 | -2.4 | 3.092 | 1.0876 | 0.15674
2015-04-11 10:00 | 104.0267 | 72.7433 | 31.2833 | 88.9783 | 7.9943 | -14.624 | 69.4158 | 20.5842 | -15.4901 | 16.8477 | 85.1592 | 54.5575 | 0.8 | 1 | 20.8053 | 160.522 | -2.4 | 2.6163 | 1.0895 | 0.14341
2015-04-11 11:00 | 97.3633 | 72.4867 | 24.8767 | 69.2819 | 8.0097 | 0.37898 | 68.9573 | 21.0427 | 0.4021 | 8.9646 | 68.4356 | 54.365 | 0.8 | 1 | 19.4727 | 142.2733 | -2.4 | 2.046 | 1.0918 | 0.12738
2015-04-11 12:00 | 90.7 | 72.23 | 18.47 | 52.5731 | 8.0251 | 15.382 | 69.4319 | 20.5681 | 16.2923 | 17.4611 | 50.1506 | 54.1725 | 0.8 | 1 | 18.14 | 122.4631 | -2.5 | 1.327 | 1.0947 | 0.10993
2015-04-11 13:00 | 124.5967 | 82.84 | 41.7567 | 126.9591 | 8.0404 | 30.3849 | 70.7981 | 19.2019 | 32.0284 | 30.9289 | 108.9063 | 62.13 | 0.8 | 1 | 24.9193 | 195.9556 | -2.6 | 3.5236 | 1.0859 | 0.17449
2015-04-11 14:00 | 158.4933 | 93.45 | 65.0433 | 221.7289 | 8.0558 | 45.3879 | 72.9416 | 17.0584 | 47.501 | 45.0895 | 156.5408 | 70.0875 | 0.8 | 1 | 31.6987 | 258.327 | -2.5 | 5.5727 | 1.0777 | 0.22829
2015-04-11 15:00 | 192.39 | 104.06 | 88.33 | 357.4582 | 8.0711 | 60.3909 | 75.6937 | 14.3063 | 62.6671 | 59.4117 | 181.8983 | 78.045 | 0.8 | 1 | 38.478 | 298.4213 | -2.6 | 6.7257 | 1.0731 | 0.26259
2015-04-11 16:00 | 140.4467 | 77.8933 | 62.5533 | 323.527 | 8.0865 | 75.3938 | 78.8518 | 11.1482 | 77.5505 | 73.7488 | 90.5385 | 58.42 | 0.8 | 1 | 28.0893 | 177.0479 | -2.7 | 2.8327 | 1.0887 | 0.15805
2015-04-11 17:00 | 88.5033 | 51.7267 | 36.7767 | 270.9027 | 8.1018 | 90.3968 | 82.1977 | 7.8023 | 92.2249 | 88.019 | 9.3647 | 38.795 | 0.8 | 1 | 17.7007 | 65.8604 | -3 | -0.94186 | 1.1038 | 0.05961
2015-04-11 18:00 | 36.56 | 25.56 | 11 | 140.5326 | 8.1172 | 105.3997 | 85.5107 | 4.4893 | 106.789 | 102.1367 | 0 | 19.17 | 0.8 | 1 | 7.312 | 26.482 | -3.2 | -2.3724 | 1.1095 | 0.024093
2015-04-11 19:00 | 24.3733 | 17.04 | 7.3333 | 0 | 8.1325 | 120.4027 | 88.5768 | 1.4232 | 121.3418 | 115.9699 | 0 | 12.78 | 0.8 | 1 | 4.8747 | 17.6547 | -3 | -2.4483 | 1.1098 | 0.016066
2015-04-11 20:00 | 12.1867 | 8.52 | 3.6667 | 0 | 8.1478 | 135.4057 | 91.1971 | -1.1971 | 135.961 | 129.262 | 0 | 6.39 | 0.8 | 1 | 2.4373 | 8.8273 | -2.9 | -2.6241 | 1.1105 | 0.0080382
2015-04-11 21:00 | 0 | 0 | 0 | 0 | 8.1632 | 150.4086 | 93.1977 | -3.1977 | 150.6877 | 141.431 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-04-11 22:00 | 0 | 0 | 0 | 0 | 8.1785 | 165.4116 | 94.4412 | -4.4412 | 165.5187 | 151.0108 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-04-11 23:00 | 0 | 0 | 0 | 0 | 8.1938 | 180.4145 | 94.8392 | -4.8392 | -179.5882 | 154.8362 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.3 | -3.3 | 1.1132 | 0
2015-04-12 | 0 | 0 | 0 | 0 | 8.2091 | -164.5825 | 94.3625 | -4.3625 | -164.699 | 150.5681 | 0 | 0 | 0.8 | 1 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-04-12 01:00 | 5.6433 | 3.11 | 2.5333 | 0 | 8.2244 | -149.5796 | 93.0442 | -3.0442 | -149.8781 | 140.7663 | 0 | 2.3325 | 0.8 | 1 | 1.1287 | 3.4612 | -3.3 | -3.1918 | 1.1128 | 0.0031582
2015-04-12 02:00 | 11.2867 | 6.22 | 5.0667 | 0 | 8.2397 | -134.5767 | 90.9755 | -0.97553 | -135.1655 | 128.5035 | 0 | 4.665 | 0.8 | 1 | 2.2573 | 6.9223 | -3.5 | -3.2837 | 1.1131 | 0.0063185
2015-04-12 03:00 | 16.93 | 9.33 | 7.6 | 0 | 8.255 | -119.5737 | 88.2963 | 1.7037 | -120.5607 | 115.1678 | 0 | 6.9975 | 0.8 | 1 | 3.386 | 10.3835 | -3.3 | -2.9755 | 1.1119 | 0.0094673
2015-04-12 04:00 | 49.8433 | 21.92 | 27.9233 | 332.4467 | 8.2703 | -104.5708 | 85.1819 | 4.8181 | -106.0193 | 101.3118 | 0 | 16.44 | 0.8 | 1 | 9.9687 | 26.4087 | -2.8 | -1.9747 | 1.1079 | 0.023992
2015-04-12 05:00 | 82.7567 | 34.51 | 48.2467 | 339.5768 | 8.2856 | -89.5678 | 81.8318 | 8.1682 | -91.4604 | 87.1804 | 16.7044 | 25.8825 | 0.8 | 1 | 16.5513 | 59.1383 | -2.5 | -0.65193 | 1.1026 | 0.053469
2015-04-12 06:00 | 115.67 | 47.1 | 68.57 | 342.7731 | 8.3009 | -74.5649 | 78.4604 | 11.5396 | -76.7832 | 72.9009 | 100.784 | 35.325 | 0.8 | 1 | 23.134 | 159.243 | -2.4 | 2.5763 | 1.0897 | 0.14229
2015-04-12 07:00 | 98.5967 | 52.8633 | 45.7333 | 180.0826 | 8.3162 | -59.562 | 75.2882 | 14.7118 | -61.8881 | 58.5558 | 93.9433 | 39.6475 | 0.8 | 1 | 19.7193 | 153.3102 | -2.5 | 2.2909 | 1.0908 | 0.13713
2015-04-12 08:00 | 81.5233 | 58.6267 | 22.8967 | 76.2818 | 8.3315 | -44.559 | 72.5328 | 17.4672 | -46.7021 | 44.225 | 54.664 | 43.97 | 0.8 | 1 | 16.3047 | 114.9387 | -2.9 | 0.69183 | 1.0972 | 0.10341
2015-04-12 09:00 | 64.45 | 64.39 | 0.06 | 0.17883 | 8.3468 | -29.5561 | 70.3959 | 19.6041 | -31.2037 | 30.0533 | 0.15479 | 48.2925 | 0.8 | 1 | 12.89 | 61.3373 | -3.3 | -1.3832 | 1.1055 | 0.055605
2015-04-12 10:00 | 75.7933 | 75.7233 | 0.07 | 0.19573 | 8.362 | -14.5532 | 69.0445 | 20.9555 | -15.4392 | 16.5881 | 0.18758 | 56.7925 | 0.8 | 1 | 15.1587 | 72.1387 | -3.5 | -1.2457 | 1.105 | 0.065364
2015-04-12 11:00 | 87.1367 | 87.0567 | 0.08 | 0.21915 | 8.3773 | 0.44973 | 68.5898 | 21.4102 | 0.47791 | 8.6005 | 0.21669 | 65.2925 | 0.8 | 1 | 17.4273 | 82.9365 | -3.7 | -1.1082 | 1.1044 | 0.07511
2015-04-12 12:00 | 98.48 | 98.39 | 0.09 | 0.25194 | 8.3926 | 15.4527 | 69.0696 | 20.9304 | 16.3922 | 17.3274 | 0.2405 | 73.7925 | 0.8 | 1 | 19.696 | 93.729 | -3.7 | -0.77097 | 1.1031 | 0.084781
2015-04-12 13:00 | 83.2533 | 83.1933 | 0.06 | 0.17923 | 8.4078 | 30.4556 | 70.4418 | 19.5582 | 32.1491 | 30.8726 | 0.15384 | 62.395 | 0.8 | 1 | 16.6507 | 79.1995 | -4.3 | -1.825 | 1.1073 | 0.071912
2015-04-12 14:00 | 68.0267 | 67.9967 | 0.03 | 0.10027 | 8.4231 | 45.4585 | 72.5913 | 17.4087 | 47.6378 | 45.0568 | 0.070833 | 50.9975 | 0.8 | 1 | 13.6053 | 64.6737 | -4.3 | -2.2789 | 1.1091 | 0.058819
2015-04-12 15:00 | 52.8 | 52.8 | 0 | 0 | 8.4384 | 60.4614 | 75.3482 | 14.6518 | 62.8145 | 59.3848 | 0 | 39.6 | 0.8 | 1 | 10.56 | 50.16 | -4.1 | -2.5325 | 1.1101 | 0.045661
2015-04-12 16:00 | 40.4133 | 40.4133 | 0 | 0 | 8.4536 | 75.4643 | 78.5094 | 11.4906 | 77.7032 | 73.7189 | 0 | 30.31 | 0.8 | 1 | 8.0827 | 38.3927 | -3.9 | -2.7002 | 1.1108 | 0.03497
2015-04-12 17:00 | 28.0267 | 28.0267 | 0 | 0 | 8.4689 | 90.4672 | 81.8561 | 8.1439 | 92.3778 | 87.9792 | 0 | 21.02 | 0.8 | 1 | 5.6053 | 26.6253 | -3.7 | -2.868 | 1.1115 | 0.024267
2015-04-12 18:00 | 15.64 | 15.64 | 0 | 0 | 8.4841 | 105.4701 | 85.1677 | 4.8323 | 106.9375 | 102.0802 | 0 | 11.73 | 0.8 | 1 | 3.128 | 14.858 | -3.7 | -3.2357 | 1.1129 | 0.01356
2015-04-12 19:00 | 10.4367 | 10.4367 | 0 | 0 | 8.4993 | 120.473 | 88.2305 | 1.7695 | 121.4814 | 115.8873 | 0 | 7.8275 | 0.8 | 1 | 2.0873 | 9.9148 | -3.3 | -2.9902 | 1.112 | 0.0090404
2015-04-12 20:00 | 5.2333 | 5.2333 | 0 | 0 | 8.5146 | 135.4759 | 90.846 | -0.84603 | 136.0877 | 129.1388 | 0 | 3.925 | 0.8 | 1 | 1.0467 | 4.9717 | -3.1 | -2.9446 | 1.1118 | 0.0045325
2015-04-12 21:00 | 0.03 | 0.03 | 0 | 0 | 8.5298 | 150.4788 | 92.8411 | -2.8411 | 150.7977 | 141.2432 | 0 | 0.0225 | 0.8 | 1 | 0.006 | 0.0285 | -3.1 | -3.0991 | 1.1124 | 2.5997e-05
2015-04-12 22:00 | 0.02 | 0.02 | 0 | 0 | 8.545 | 165.4817 | 94.0791 | -4.0791 | 165.6091 | 150.7263 | 0 | 0.015 | 0.8 | 1 | 0.004 | 0.019 | -3 | -2.9994 | 1.112 | 1.7325e-05
2015-04-12 23:00 | 0.01 | 0.01 | 0 | 0 | 8.5602 | 180.4846 | 94.4726 | -4.4726 | -179.5193 | 154.4686 | 0 | 0.0075 | 0.8 | 1 | 0.002 | 0.0095 | -2.3 | -2.2997 | 1.1092 | 8.6407e-06
2015-04-13 | 0 | 0 | 0 | 0 | 8.5755 | -164.5125 | 93.9927 | -3.9927 | -164.6517 | 150.2185 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.2 | -2.2 | 1.1088 | 0
2015-04-13 01:00 | 2.2233 | 2.2233 | 0 | 0 | 8.5907 | -149.5096 | 92.6724 | -2.6724 | -149.8512 | 140.4772 | 0 | 1.6675 | 0.8 | 1 | 0.44467 | 2.1122 | -2.2 | -2.134 | 1.1085 | 0.00192
2015-04-13 02:00 | 4.4467 | 4.4467 | 0 | 0 | 8.6059 | -134.5067 | 90.603 | -0.60301 | -135.1561 | 128.2626 | 0 | 3.335 | 0.8 | 1 | 0.88933 | 4.2243 | -2.1 | -1.968 | 1.1079 | 0.0038376
2015-04-13 03:00 | 6.67 | 6.67 | 0 | 0 | 8.6211 | -119.5038 | 87.9238 | 2.0762 | -120.5648 | 114.9597 | 0 | 5.0025 | 0.8 | 1 | 1.334 | 6.3365 | -1.9 | -1.702 | 1.1068 | 0.0057509
2015-04-13 04:00 | 18.6333 | 18.62 | 0.013333 | 0.14739 | 8.6363 | -104.5009 | 84.8096 | 5.1904 | -106.0321 | 101.1257 | 0 | 13.965 | 0.8 | 1 | 3.7267 | 17.6917 | -1.7 | -1.1471 | 1.1046 | 0.016024
2015-04-13 05:00 | 30.5967 | 30.57 | 0.026667 | 0.17957 | 8.6515 | -89.4981 | 81.4599 | 8.5401 | -91.4768 | 87.009 | 0.00937 | 22.9275 | 0.8 | 1 | 6.1193 | 29.0562 | -1.1 | -0.19199 | 1.1008 | 0.026227
2015-04-13 06:00 | 42.56 | 42.52 | 0.04 | 0.1938 | 8.6667 | -74.4952 | 78.0885 | 11.9115 | -76.7974 | 72.7383 | 0.057507 | 31.89 | 0.8 | 1 | 8.512 | 40.4595 | -0.9 | 0.36436 | 1.0985 | 0.036446
2015-04-13 07:00 | 50.5733 | 50.48 | 0.093333 | 0.35865 | 8.6819 | -59.4923 | 74.9161 | 15.0839 | -61.8943 | 58.3961 | 0.18795 | 37.86 | 0.8 | 1 | 10.1147 | 48.1626 | -0.8 | 0.70508 | 1.0972 | 0.043331
2015-04-13 08:00 | 58.5867 | 58.44 | 0.14667 | 0.47876 | 8.6971 | -44.4894 | 72.1609 | 17.8391 | -46.6946 | 44.0602 | 0.34404 | 43.83 | 0.8 | 1 | 11.7173 | 55.8914 | -0.1 | 1.6466 | 1.0934 | 0.050112
2015-04-13 09:00 | 66.6 | 66.4 | 0.2 | 0.58546 | 8.7122 | -29.4866 | 70.0249 | 19.9751 | -31.177 | 29.8676 | 0.5077 | 49.8 | 0.8 | 1 | 13.32 | 63.6277 | 0 | 1.9884 | 1.092 | 0.056977
2015-04-13 10:00 | 80.4267 | 80.1167 | 0.31 | 0.85247 | 8.7274 | -14.4837 | 68.6756 | 21.3244 | -15.3894 | 16.3353 | 0.81806 | 60.0875 | 0.8 | 1 | 16.0853 | 76.9909 | 0.3 | 2.706 | 1.0892 | 0.068762
2015-04-13 11:00 | 94.2533 | 93.8333 | 0.42 | 1.1322 | 8.7426 | 0.51917 | 68.2246 | 21.7754 | 0.55257 | 8.2396 | 1.1205 | 70.375 | 0.8 | 1 | 18.8507 | 90.3462 | 0.1 | 2.9233 | 1.0883 | 0.080626
2015-04-13 12:00 | 108.08 | 107.55 | 0.53 | 1.4597 | 8.7578 | 15.522 | 68.7097 | 21.2903 | 16.4908 | 17.2005 | 1.3944 | 80.6625 | 0.8 | 1 | 21.616 | 103.6729 | 0.1 | 3.3398 | 1.0866 | 0.092377
2015-04-13 13:00 | 85.6633 | 85.31 | 0.35333 | 1.0374 | 8.7729 | 30.5249 | 70.0878 | 19.9122 | 32.2686 | 30.8197 | 0.89094 | 63.9825 | 0.8 | 1 | 17.1327 | 82.0061 | -0.1 | 2.4627 | 1.0901 | 0.073307
2015-04-13 14:00 | 63.2467 | 63.07 | 0.17667 | 0.57927 | 8.7881 | 45.5278 | 72.2431 | 17.7569 | 47.7732 | 45.0258 | 0.40942 | 47.3025 | 0.8 | 1 | 12.6493 | 60.3613 | -0.7 | 1.1863 | 1.0953 | 0.054211
2015-04-13 15:00 | 40.83 | 40.83 | 0 | 0 | 8.8032 | 60.5306 | 75.0048 | 14.9952 | 62.9604 | 59.3586 | 0 | 30.6225 | 0.8 | 1 | 8.166 | 38.7885 | -0.4 | 0.81214 | 1.0968 | 0.034884
2015-04-13 16:00 | 31.0733 | 31.0467 | 0.026667 | 0.13007 | 8.8184 | 75.5335 | 78.169 | 11.831 | 77.8543 | 73.6889 | 0.036529 | 23.285 | 0.8 | 1 | 6.2147 | 29.5362 | 0 | 0.92301 | 1.0963 | 0.026552
2015-04-13 17:00 | 21.3167 | 21.2633 | 0.053333 | 0.36153 | 8.8335 | 90.5363 | 81.5166 | 8.4834 | 92.529 | 87.9389 | 0.013003 | 15.9475 | 0.8 | 1 | 4.2633 | 20.2238 | 0.6 | 1.232 | 1.0951 | 0.01816
2015-04-13 18:00 | 11.56 | 11.48 | 0.08 | 0.88725 | 8.8487 | 105.5392 | 84.8268 | 5.1732 | 107.0842 | 102.0227 | 0 | 8.61 | 0.8 | 1 | 2.312 | 10.922 | -0.2 | 0.14131 | 1.0994 | 0.0098466
2015-04-13 19:00 | 7.7233 | 7.67 | 0.053333 | 0 | 8.8638 | 120.542 | 87.8862 | 2.1138 | 121.6193 | 115.8033 | 0 | 5.7525 | 0.8 | 1 | 1.5447 | 7.2972 | -0.5 | -0.27196 | 1.1011 | 0.0065886
2015-04-13 20:00 | 3.8867 | 3.86 | 0.026667 | 0 | 8.879 | 135.5449 | 90.497 | -0.497 | 136.2126 | 129.0139 | 0 | 2.895 | 0.8 | 1 | 0.77733 | 3.6723 | -1.1 | -0.98524 | 1.1039 | 0.0033243
2015-04-13 21:00 | 0.05 | 0.05 | 0 | 0 | 8.8941 | 150.5477 | 92.4866 | -2.4866 | 150.906 | 141.0535 | 0 | 0.0375 | 0.8 | 1 | 0.01 | 0.0475 | -1.1 | -1.0985 | 1.1044 | 4.3016e-05
2015-04-13 22:00 | 0.033333 | 0.033333 | 0 | 0 | 8.9092 | 165.5505 | 93.7194 | -3.7194 | 165.6978 | 150.4414 | 0 | 0.025 | 0.8 | 1 | 0.0066667 | 0.031667 | -0.9 | -0.89901 | 1.1036 | 2.8657e-05
2015-04-13 23:00 | 0.016667 | 0.016667 | 0 | 0 | 8.9243 | 180.5534 | 94.1084 | -4.1084 | -179.4519 | 154.1032 | 0 | 0.0125 | 0.8 | 1 | 0.0033333 | 0.015833 | -0.6 | -0.59951 | 1.1024 | 1.4313e-05
2015-04-14 | 0 | 0 | 0 | 0 | 8.9394 | -164.4438 | 93.6252 | -3.6252 | -164.6059 | 149.8712 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-04-14 01:00 | 5.7733 | 4.3467 | 1.4267 | 0 | 8.9546 | -149.441 | 92.3031 | -2.3031 | -149.8255 | 140.1895 | 0 | 3.26 | 0.8 | 1 | 1.1547 | 4.4147 | -0.6 | -0.46204 | 1.1018 | 0.0039887
2015-04-14 02:00 | 11.5467 | 8.6933 | 2.8533 | 0 | 8.9697 | -134.4381 | 90.2331 | -0.23307 | -135.1477 | 128.023 | 0 | 6.52 | 0.8 | 1 | 2.3093 | 8.8293 | -1.3 | -1.0241 | 1.1041 | 0.0079937
2015-04-14 03:00 | 17.32 | 13.04 | 4.28 | 0 | 8.9848 | -119.4353 | 87.5539 | 2.4461 | -120.5699 | 114.7531 | 0 | 9.78 | 0.8 | 1 | 3.464 | 13.244 | -1.2 | -0.78612 | 1.1031 | 0.01198
2015-04-14 04:00 | 53.78 | 30.1367 | 23.6433 | 244.031 | 8.9999 | -104.4325 | 84.4401 | 5.5599 | -106.0459 | 100.9415 | 0 | 22.6025 | 0.8 | 1 | 10.756 | 33.3585 | -1.5 | -0.45755 | 1.1018 | 0.030139
2015-04-14 05:00 | 90.24 | 47.2333 | 43.0067 | 277.6897 | 9.015 | -89.4297 | 81.0906 | 8.9094 | -91.4941 | 86.8398 | 15.3087 | 35.425 | 0.8 | 1 | 18.048 | 68.7817 | -1.5 | 0.64943 | 1.0974 | 0.061895
2015-04-14 06:00 | 126.7 | 64.33 | 62.37 | 293.2251 | 9.0301 | -74.4268 | 77.7192 | 12.2808 | -76.8126 | 72.5783 | 87.7922 | 48.2475 | 0.8 | 1 | 25.34 | 161.3797 | -1.5 | 3.5431 | 1.0858 | 0.14369
2015-04-14 07:00 | 160.9533 | 76.26 | 84.6933 | 317.8549 | 9.0451 | -59.424 | 74.5467 | 15.4533 | -61.9016 | 58.2397 | 167.3083 | 57.195 | 0.8 | 1 | 32.1907 | 256.694 | -1.3 | 6.7217 | 1.0731 | 0.22588
2015-04-14 08:00 | 195.2067 | 88.19 | 107.0167 | 342.4814 | 9.0602 | -44.4212 | 71.7916 | 18.2084 | -46.6881 | 43.8995 | 246.7774 | 66.1425 | 0.8 | 1 | 39.0413 | 351.9613 | -1.3 | 9.6988 | 1.0612 | 0.30627
2015-04-14 09:00 | 229.46 | 100.12 | 129.34 | 372.042 | 9.0753 | -29.4184 | 69.6564 | 20.3436 | -31.1514 | 29.6872 | 323.2087 | 75.09 | 0.8 | 1 | 45.892 | 444.1907 | -1.4 | 12.481 | 1.0501 | 0.38248
2015-04-14 10:00 | 261.8233 | 93.73 | 168.0933 | 454.8021 | 9.0904 | -14.4156 | 68.3093 | 21.6907 | -15.3408 | 16.0894 | 436.9877 | 70.2975 | 0.8 | 1 | 52.3647 | 559.6499 | -1.5 | 15.9891 | 1.036 | 0.47545
2015-04-14 11:00 | 294.1867 | 87.34 | 206.8467 | 548.8983 | 9.1055 | 0.58723 | 67.8619 | 22.1381 | 0.62598 | 7.882 | 543.7127 | 65.505 | 0.8 | 1 | 58.8373 | 668.055 | -0.8 | 20.0767 | 1.0197 | 0.55859
2015-04-14 12:00 | 326.55 | 80.95 | 245.6 | 665.7579 | 9.1205 | 15.59 | 68.352 | 21.648 | 16.5882 | 17.0804 | 636.3938 | 60.7125 | 0.8 | 1 | 65.31 | 762.4163 | 2.2 | 26.0255 | 0.9959 | 0.62262
2015-04-14 13:00 | 288.98 | 74.0567 | 214.9233 | 620.5456 | 9.1356 | 30.5928 | 69.736 | 20.264 | 32.3866 | 30.7701 | 533.1895 | 55.5425 | 0.8 | 1 | 57.796 | 646.528 | -1.1 | 19.104 | 1.0236 | 0.54266
2015-04-14 14:00 | 251.41 | 67.1633 | 184.2467 | 592.9582 | 9.1506 | 45.5956 | 71.8971 | 18.1029 | 47.9071 | 44.9963 | 419.312 | 50.3725 | 0.8 | 1 | 50.282 | 519.9665 | -0.8 | 15.449 | 1.0382 | 0.44266
2015-04-14 15:00 | 213.84 | 60.27 | 153.57 | 580.6358 | 9.1657 | 60.5984 | 74.6636 | 15.3364 | 63.1048 | 59.333 | 296.152 | 45.2025 | 0.8 | 1 | 42.768 | 384.1225 | -0.7 | 11.3038 | 1.0548 | 0.33224
2015-04-14 16:00 | 157.5567 | 47.7167 | 109.84 | 521.0623 | 9.1807 | 75.6012 | 77.8308 | 12.1692 | 78.0037 | 73.6587 | 146.605 | 35.7875 | 0.8 | 1 | 31.5113 | 213.9038 | -1.5 | 5.1845 | 1.0793 | 0.1893
2015-04-14 17:00 | 101.2733 | 35.1633 | 66.11 | 431.1198 | 9.1958 | 90.604 | 81.1792 | 8.8208 | 92.6784 | 87.8979 | 15.8139 | 26.3725 | 0.8 | 1 | 20.2547 | 62.4411 | -1.2 | 0.75128 | 1.097 | 0.056168
2015-04-14 18:00 | 44.99 | 22.61 | 22.38 | 232.993 | 9.2108 | 105.6068 | 84.488 | 5.512 | 107.229 | 101.964 | 0 | 16.9575 | 0.8 | 1 | 8.998 | 25.9555 | -1.3 | -0.48889 | 1.102 | 0.023453
2015-04-14 19:00 | 30.0533 | 15.1233 | 14.93 | 0 | 9.2259 | 120.6096 | 87.544 | 2.456 | 121.7552 | 115.7177 | 0 | 11.3425 | 0.8 | 1 | 6.0107 | 17.3532 | -1 | -0.45771 | 1.1018 | 0.015679
2015-04-14 20:00 | 15.1167 | 7.6367 | 7.48 | 0 | 9.2409 | 135.6124 | 90.1501 | -0.15013 | 136.3356 | 128.8871 | 0 | 5.7275 | 0.8 | 1 | 3.0233 | 8.7508 | -0.5 | -0.22654 | 1.1009 | 0.0078998
2015-04-14 21:00 | 0.18 | 0.15 | 0.03 | 0 | 9.2559 | 150.6152 | 92.1344 | -2.1344 | 151.0124 | 140.8622 | 0 | 0.1125 | 0.8 | 1 | 0.036 | 0.1485 | -0.3 | -0.29536 | 1.1012 | 0.00013409
2015-04-14 22:00 | 0.12 | 0.1 | 0.02 | 0 | 9.2709 | 165.6179 | 93.362 | -3.362 | 165.7848 | 150.1562 | 0 | 0.075 | 0.8 | 1 | 0.024 | 0.099 | -0.6 | -0.59691 | 1.1024 | 8.9492e-05
2015-04-14 23:00 | 0.06 | 0.05 | 0.01 | 0 | 9.286 | 180.6207 | 93.7466 | -3.7466 | -179.3861 | 153.7402 | 0 | 0.0375 | 0.8 | 1 | 0.012 | 0.0495 | -0.4 | -0.39845 | 1.1016 | 4.4714e-05
2015-04-15 | 0 | 0 | 0 | 0 | 9.301 | -164.3765 | 93.2604 | -3.2604 | -164.5614 | 149.5263 | 0 | 0 | 0.8 | 1 | 0 | 0 | -0.8 | -0.8 | 1.1032 | 0
2015-04-15 01:00 | 5.9567 | 5.03 | 0.92667 | 0 | 9.316 | -149.3737 | 91.9365 | -1.9365 | -149.8011 | 139.9035 | 0 | 3.7725 | 0.8 | 1 | 1.1913 | 4.9638 | 0.1 | 0.25512 | 1.099 | 0.0044732
2015-04-15 02:00 | 11.9133 | 10.06 | 1.8533 | 0 | 9.331 | -134.371 | 89.8658 | 0.1342 | -135.1405 | 127.785 | 0 | 7.545 | 0.8 | 1 | 2.3827 | 9.9277 | 0.3 | 0.61024 | 1.0976 | 0.0089349
2015-04-15 03:00 | 17.87 | 15.09 | 2.78 | 0 | 9.346 | -119.3682 | 87.1867 | 2.8133 | -120.576 | 114.5482 | 0 | 11.3175 | 0.8 | 1 | 3.574 | 14.8915 | -0.3 | 0.16536 | 1.0993 | 0.013424
2015-04-15 04:00 | 59.2367 | 31.0067 | 28.23 | 273.3966 | 9.361 | -104.3654 | 84.0733 | 5.9267 | -106.0607 | 100.7592 | 0 | 23.255 | 0.8 | 1 | 11.8473 | 35.1023 | 1.3 | 2.3969 | 1.0904 | 0.031386
2015-04-15 05:00 | 100.6033 | 46.9233 | 53.68 | 333.0227 | 9.376 | -89.3627 | 80.724 | 9.276 | -91.5124 | 86.6729 | 19.3276 | 35.1925 | 0.8 | 1 | 20.1207 | 74.6408 | 1.3 | 3.6325 | 1.0855 | 0.066437
2015-04-15 06:00 | 141.97 | 62.84 | 79.13 | 361.4067 | 9.3909 | -74.3599 | 77.3526 | 12.6474 | -76.8289 | 72.4211 | 109.1517 | 47.13 | 0.8 | 1 | 28.394 | 184.6757 | 1 | 6.7711 | 1.0729 | 0.16248
2015-04-15 07:00 | 189.63 | 72.0033 | 117.6267 | 431.4744 | 9.4059 | -59.3572 | 74.18 | 15.82 | -61.91 | 58.0866 | 228.0933 | 54.0025 | 0.8 | 1 | 37.926 | 320.0218 | 1.8 | 11.8007 | 1.0528 | 0.27627
2015-04-15 08:00 | 237.29 | 81.1667 | 156.1233 | 490.112 | 9.4209 | -44.3544 | 71.425 | 18.575 | -46.6828 | 43.7429 | 354.081 | 60.875 | 0.8 | 1 | 47.458 | 462.414 | 1.1 | 15.5504 | 1.0378 | 0.39351
2015-04-15 09:00 | 284.95 | 90.33 | 194.62 | 550.3517 | 9.4359 | -29.3517 | 69.2906 | 20.7094 | -31.1271 | 29.5122 | 478.9441 | 67.7475 | 0.8 | 1 | 56.99 | 603.6816 | 1.1 | 19.9651 | 1.0201 | 0.50499
2015-04-15 10:00 | 263.72 | 98.1633 | 165.5567 | 440.9099 | 9.4508 | -14.3489 | 67.9455 | 22.0545 | -15.2935 | 15.8508 | 424.1447 | 73.6225 | 0.8 | 1 | 52.744 | 550.5112 | 1.3 | 18.5035 | 1.026 | 0.46315
2015-04-15 11:00 | 242.49 | 105.9967 | 136.4933 | 356.7006 | 9.4658 | 0.65382 | 67.5018 | 22.4982 | 0.69805 | 7.5278 | 353.6264 | 79.4975 | 0.8 | 1 | 48.498 | 481.6219 | 1.3 | 16.3507 | 1.0346 | 0.40859
2015-04-15 12:00 | 221.26 | 113.83 | 107.43 | 286.7418 | 9.4808 | 15.6566 | 67.9968 | 22.0032 | 16.6841 | 16.967 | 274.2608 | 85.3725 | 0.8 | 1 | 44.252 | 403.8853 | 1.7 | 14.3214 | 1.0427 | 0.34533
2015-04-15 13:00 | 175.6567 | 99.5333 | 76.1233 | 216.2227 | 9.4957 | 30.6593 | 69.3866 | 20.6134 | 32.5032 | 30.7236 | 185.8741 | 74.65 | 0.8 | 1 | 35.1313 | 295.6554 | 1.5 | 10.7392 | 1.057 | 0.25627
2015-04-15 14:00 | 130.0533 | 85.2367 | 44.8167 | 141.6364 | 9.5107 | 45.662 | 71.5534 | 18.4466 | 48.0395 | 44.9682 | 100.2076 | 63.9275 | 0.8 | 1 | 26.0107 | 190.1458 | 1.5696 | 7.5116 | 1.07 | 0.16683
2015-04-15 15:00 | 84.45 | 70.94 | 13.51 | 50.0023 | 9.5256 | 60.6648 | 74.3246 | 15.6754 | 63.2475 | 59.3078 | 25.5225 | 53.205 | 0.8 | 1 | 16.89 | 95.6175 | 1.6391 | 4.6272 | 1.0815 | 0.084796
2015-04-15 16:00 | 67.07 | 54.9933 | 12.0767 | 55.7735 | 9.5406 | 75.6675 | 77.4947 | 12.5053 | 78.1513 | 73.6284 | 15.7207 | 41.245 | 0.8 | 1 | 13.414 | 70.3797 | 1.7087 | 3.9081 | 1.0844 | 0.06258
2015-04-15 17:00 | 49.69 | 39.0467 | 10.6433 | 66.8866 | 9.5555 | 90.6702 | 80.8439 | 9.1561 | 92.826 | 87.8561 | 2.5022 | 29.285 | 0.8 | 1 | 9.938 | 41.7252 | 1.7783 | 3.0822 | 1.0877 | 0.037214
2015-04-15 18:00 | 32.31 | 23.1 | 9.21 | 90.3809 | 9.5704 | 105.673 | 84.1513 | 5.8487 | 107.3719 | 101.9041 | 0 | 17.325 | 0.8 | 1 | 6.462 | 23.787 | 1.8478 | 2.5912 | 1.0896 | 0.021254
2015-04-15 19:00 | 21.64 | 15.48 | 6.16 | 0 | 9.5854 | 120.6757 | 87.204 | 2.796 | 121.8891 | 115.6306 | 0 | 11.61 | 0.8 | 1 | 4.328 | 15.938 | 1.9174 | 2.4155 | 1.0903 | 0.01425
2015-04-15 20:00 | 10.97 | 7.86 | 3.11 | 0 | 9.6003 | 135.6784 | 89.8055 | 0.19451 | 136.4566 | 128.7585 | 0 | 5.895 | 0.8 | 1 | 2.194 | 8.089 | 1.987 | 2.2397 | 1.091 | 0.0072369
2015-04-15 21:00 | 0.3 | 0.24 | 0.06 | 0 | 9.6152 | 150.6811 | 91.7845 | -1.7845 | 151.1168 | 140.6693 | 0 | 0.18 | 0.8 | 1 | 0.06 | 0.24 | 2.0565 | 2.064 | 1.0917 | 0.00021486
2015-04-15 22:00 | 0.2 | 0.16 | 0.04 | 0 | 9.6301 | 165.6838 | 93.007 | -3.007 | 165.8699 | 149.8708 | 0 | 0.12 | 0.8 | 1 | 0.04 | 0.16 | 2.1261 | 2.1311 | 1.0915 | 0.0001432
2015-04-15 23:00 | 0.1 | 0.08 | 0.02 | 0 | 9.645 | 180.6866 | 93.3874 | -3.3874 | -179.322 | 153.3797 | 0 | 0.06 | 0.8 | 1 | 0.02 | 0.08 | 2.1957 | 2.1982 | 1.0912 | 7.1583e-05
2015-04-16 | 0 | 0 | 0 | 0 | 9.6599 | -164.3107 | 92.8981 | -2.8981 | -164.5185 | 149.1839 | 0 | 0 | 0.8 | 1 | 0 | 0 | 2.2652 | 2.2652 | 1.0909 | 0
2015-04-16 01:00 | 5.8767 | 4.9967 | 0.88 | 0 | 9.6748 | -149.308 | 91.5726 | -1.5726 | -149.778 | 139.6192 | 0 | 3.7475 | 0.8 | 1 | 1.1753 | 4.9228 | 2.3348 | 2.4886 | 1.09 | 0.0044002
2015-04-16 02:00 | 11.7533 | 9.9933 | 1.76 | 0 | 9.6897 | -134.3053 | 89.5013 | 0.49869 | -135.1345 | 127.5485 | 0 | 7.495 | 0.8 | 1 | 2.3507 | 9.8457 | 2.4043 | 2.712 | 1.0892 | 0.0087932
2015-04-16 03:00 | 17.63 | 14.99 | 2.64 | 47.6258 | 9.7046 | -119.3026 | 86.8223 | 3.1777 | -120.5832 | 114.345 | 0 | 11.2425 | 0.8 | 1 | 3.526 | 14.7685 | 2.4739 | 2.9354 | 1.0883 | 0.013179
2015-04-16 04:00 | 61.2133 | 27.6067 | 33.6067 | 306.7061 | 9.7195 | -104.2999 | 83.7093 | 6.2907 | -106.0765 | 100.579 | 0 | 20.705 | 0.8 | 1 | 12.2427 | 32.9477 | 2.5435 | 3.5731 | 1.0857 | 0.029333
2015-04-16 05:00 | 104.7967 | 40.2233 | 64.5733 | 385.6244 | 9.7344 | -89.2972 | 80.3603 | 9.6397 | -91.5318 | 86.5084 | 23.4856 | 30.1675 | 0.8 | 1 | 20.9593 | 74.6125 | 2.613 | 4.9447 | 1.0802 | 0.06609
2015-04-16 06:00 | 148.38 | 52.84 | 95.54 | 424.3605 | 9.7493 | -74.2945 | 76.989 | 13.011 | -76.8463 | 72.2667 | 129.2543 | 39.63 | 0.8 | 1 | 29.676 | 198.5603 | 2.6826 | 8.8876 | 1.0644 | 0.17331
2015-04-16 07:00 | 178.9667 | 88.3133 | 90.6533 | 325.2492 | 9.7641 | -59.2918 | 73.8162 | 16.1838 | -61.9196 | 57.9369 | 172.6594 | 66.235 | 0.8 | 1 | 35.7933 | 274.6878 | 2.7522 | 11.3362 | 1.0547 | 0.23755
2015-04-16 08:00 | 209.5533 | 123.7867 | 85.7667 | 264.2564 | 9.779 | -44.2892 | 71.0612 | 18.9388 | -46.6787 | 43.5906 | 191.3968 | 92.84 | 0.8 | 1 | 41.9107 | 326.1475 | 2.8217 | 13.0138 | 1.0479 | 0.28026
2015-04-16 09:00 | 240.14 | 159.26 | 80.88 | 224.9488 | 9.7939 | -29.2865 | 68.9275 | 21.0725 | -31.1041 | 29.3428 | 196.0887 | 119.445 | 0.8 | 1 | 48.028 | 363.5617 | 2.8913 | 14.2526 | 1.043 | 0.31094
2015-04-16 10:00 | 252.8333 | 154.88 | 97.9533 | 256.8781 | 9.8087 | -14.2838 | 67.5844 | 22.4156 | -15.2475 | 15.6198 | 247.3915 | 116.16 | 0.8 | 1 | 50.5667 | 414.1182 | 2.9609 | 15.9021 | 1.0364 | 0.35193
2015-04-16 11:00 | 265.5267 | 150.5 | 115.0267 | 296.1449 | 9.8236 | 0.71888 | 67.1442 | 22.8558 | 0.7687 | 7.1772 | 293.8244 | 112.875 | 0.8 | 1 | 53.1053 | 459.8048 | 3.0304 | 17.3993 | 1.0304 | 0.3885
2015-04-16 12:00 | 278.22 | 146.12 | 132.1 | 347.3051 | 9.8384 | 15.7216 | 67.6442 | 22.3558 | 16.7786 | 16.8602 | 332.3763 | 109.59 | 0.8 | 1 | 55.644 | 497.6103 | 3.1 | 18.6503 | 1.0254 | 0.4184
2015-04-16 13:00 | 230.3433 | 141.2133 | 89.13 | 249.1607 | 9.8533 | 30.7242 | 69.0397 | 20.9603 | 32.6183 | 30.6802 | 214.2854 | 105.91 | 0.8 | 1 | 46.0687 | 366.2641 | 3 | 14.4458 | 1.0422 | 0.31302
2015-04-16 14:00 | 182.4667 | 136.3067 | 46.16 | 143.3247 | 9.8681 | 45.7269 | 71.2121 | 18.7879 | 48.1702 | 44.9415 | 101.4492 | 102.23 | 0.8 | 1 | 36.4933 | 240.1726 | 2.9 | 10.4054 | 1.0584 | 0.20844
2015-04-16 15:00 | 134.59 | 131.4 | 3.19 | 11.5646 | 9.8829 | 60.7296 | 73.9879 | 16.0121 | 63.3884 | 59.283 | 5.9072 | 98.55 | 0.8 | 1 | 26.918 | 131.3752 | 2.8 | 6.9055 | 1.0724 | 0.11552
2015-04-16 16:00 | 103.7733 | 99.5267 | 4.2467 | 19.1106 | 9.8978 | 75.7322 | 77.1608 | 12.8392 | 78.297 | 73.5978 | 5.3964 | 74.645 | 0.8 | 1 | 20.7547 | 100.7961 | 2.7 | 5.8499 | 1.0766 | 0.088984
2015-04-16 17:00 | 72.9567 | 67.6533 | 5.3033 | 32.1684 | 9.9126 | 90.7349 | 80.5108 | 9.4892 | 92.9716 | 87.8136 | 1.2272 | 50.74 | 0.8 | 1 | 14.5913 | 66.5586 | 2.7 | 4.78 | 1.0809 | 0.058992
2015-04-16 18:00 | 42.14 | 35.78 | 6.36 | 59.0488 | 9.9274 | 105.7376 | 83.8168 | 6.1832 | 107.5127 | 101.8431 | 0 | 26.835 | 0.8 | 1 | 8.428 | 35.263 | 2 | 3.102 | 1.0876 | 0.031448
2015-04-16 19:00 | 28.2967 | 24.0567 | 4.24 | 77.562 | 9.9422 | 120.7402 | 86.8663 | 3.1337 | 122.021 | 115.542 | 0 | 18.0425 | 0.8 | 1 | 5.6593 | 23.7018 | 1.4 | 2.1407 | 1.0914 | 0.021213
2015-04-16 20:00 | 14.4533 | 12.3333 | 2.12 | 0 | 9.957 | 135.7429 | 89.4632 | 0.53681 | 136.5755 | 128.6283 | 0 | 9.25 | 0.8 | 1 | 2.8907 | 12.1407 | 0.8 | 1.1794 | 1.0953 | 0.010904
2015-04-16 21:00 | 0.61 | 0.61 | 0 | 0 | 9.9719 | 150.7455 | 91.4371 | -1.4371 | 151.2193 | 140.4748 | 0 | 0.4575 | 0.8 | 1 | 0.122 | 0.5795 | 0.8 | 0.81811 | 1.0967 | 0.00052115
2015-04-16 22:00 | 0.40667 | 0.40667 | 0 | 0 | 9.9867 | 165.7482 | 92.6545 | -2.6545 | 165.9532 | 149.5854 | 0 | 0.305 | 0.8 | 1 | 0.081333 | 0.38633 | 0.6 | 0.61207 | 1.0976 | 0.0003477
2015-04-16 23:00 | 0.20333 | 0.20333 | 0 | 0 | 10.0015 | 180.7508 | 93.0308 | -3.0308 | -179.2596 | 153.0217 | 0 | 0.1525 | 0.8 | 1 | 0.040667 | 0.19317 | 0.35 | 0.35604 | 1.0986 | 0.00017401
2015-04-17 | 0 | 0 | 0 | 0 | 10.0162 | -164.2465 | 92.5386 | -2.5386 | -164.4771 | 148.8442 | 0 | 0 | 0.8 | 1 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-04-17 01:00 | 9.4367 | 6.7033 | 2.7333 | 0 | 10.031 | -149.2439 | 91.2115 | -1.2115 | -149.7562 | 139.337 | 0 | 5.0275 | 0.8 | 1 | 1.8873 | 6.9148 | 0 | 0.21609 | 1.0991 | 0.0062323
2015-04-17 02:00 | 18.8733 | 13.4067 | 5.4667 | 0 | 10.0458 | -134.2413 | 89.1397 | 0.86031 | -135.1297 | 127.3138 | 0 | 10.055 | 0.8 | 1 | 3.7747 | 13.8297 | 0 | 0.43218 | 1.0983 | 0.012455
2015-04-17 03:00 | 28.31 | 20.11 | 8.2 | 132.8379 | 10.0606 | -119.2386 | 86.4609 | 3.5391 | -120.5915 | 114.1438 | 0 | 15.0825 | 0.8 | 1 | 5.662 | 20.7445 | -0.4 | 0.24827 | 1.099 | 0.018695
2015-04-17 04:00 | 65.06 | 39.0167 | 26.0433 | 224.8344 | 10.0754 | -104.236 | 83.3483 | 6.6517 | -106.0935 | 100.4009 | 0 | 29.2625 | 0.8 | 1 | 13.012 | 42.2745 | -0.4 | 0.92108 | 1.0963 | 0.038004
2015-04-17 05:00 | 101.81 | 57.9233 | 43.8867 | 252.7238 | 10.0901 | -89.2334 | 79.9996 | 10.0004 | -91.5522 | 86.3464 | 16.1047 | 43.4425 | 0.8 | 1 | 20.362 | 79.9092 | -0.2 | 2.2972 | 1.0908 | 0.071476
2015-04-17 06:00 | 138.56 | 76.83 | 61.73 | 266.9197 | 10.1049 | -74.2307 | 76.6283 | 13.3717 | -76.8648 | 72.1153 | 81.9717 | 57.6225 | 0.8 | 1 | 27.712 | 167.3062 | 0.9 | 6.1283 | 1.0755 | 0.14755
2015-04-17 07:00 | 155.0133 | 103.5467 | 51.4667 | 180.7351 | 10.1197 | -59.2281 | 73.4553 | 16.5447 | -61.9304 | 57.7907 | 96.3342 | 77.66 | 0.8 | 1 | 31.0027 | 204.9969 | 0.8 | 7.2062 | 1.0712 | 0.18006
2015-04-17 08:00 | 171.4667 | 130.2633 | 41.2033 | 124.666 | 10.1344 | -44.2255 | 70.7003 | 19.2997 | -46.6759 | 43.4426 | 90.5154 | 97.6975 | 0.8 | 1 | 34.2933 | 222.5062 | 0.9 | 7.8533 | 1.0686 | 0.19497
2015-04-17 09:00 | 187.92 | 156.98 | 30.94 | 84.6725 | 10.1492 | -29.2229 | 68.5673 | 21.4327 | -31.0824 | 29.179 | 73.9276 | 117.735 | 0.8 | 1 | 37.584 | 229.2466 | 0.6 | 7.764 | 1.0689 | 0.20094
2015-04-17 10:00 | 173.82 | 144.1533 | 29.6667 | 76.6391 | 10.1639 | -14.2203 | 67.2261 | 22.7739 | -15.203 | 15.3964 | 73.8886 | 108.115 | 0.8 | 1 | 34.764 | 216.7676 | 0.5 | 7.274 | 1.0709 | 0.19035
2015-04-17 11:00 | 159.72 | 131.3267 | 28.3933 | 72.0436 | 10.1786 | 0.78234 | 66.7893 | 23.2107 | 0.83784 | 6.8304 | 71.5322 | 98.495 | 0.8 | 1 | 31.944 | 201.9712 | 0.6 | 6.9116 | 1.0724 | 0.1776
2015-04-17 12:00 | 145.62 | 118.5 | 27.12 | 70.259 | 10.1934 | 15.7849 | 67.2941 | 22.7059 | 16.8715 | 16.76 | 67.2745 | 88.875 | 0.8 | 1 | 29.124 | 185.2735 | 0.7 | 6.4898 | 1.074 | 0.16317
2015-04-17 13:00 | 184.1333 | 94.9933 | 89.14 | 245.3432 | 10.2081 | 30.7875 | 68.6953 | 21.3047 | 32.7316 | 30.6396 | 211.0908 | 71.245 | 0.8 | 1 | 36.8267 | 319.1624 | 0.3 | 10.2738 | 1.0589 | 0.27713
2015-04-17 14:00 | 222.6467 | 71.4867 | 151.16 | 461.3323 | 10.2228 | 45.7902 | 70.8732 | 19.1268 | 48.2992 | 44.9161 | 326.6886 | 53.615 | 0.8 | 1 | 44.5293 | 424.8329 | -0.1 | 13.176 | 1.0473 | 0.36484
2015-04-17 15:00 | 261.16 | 47.98 | 213.18 | 757.4472 | 10.2376 | 60.7927 | 73.6535 | 16.3465 | 63.5275 | 59.2586 | 387.1803 | 35.985 | 0.8 | 1 | 52.232 | 475.3973 | -0.5 | 14.3562 | 1.0426 | 0.40642
2015-04-17 16:00 | 193.99 | 44.2033 | 149.7867 | 657.3829 | 10.2523 | 75.7953 | 76.8293 | 13.1707 | 78.4408 | 73.5669 | 185.9712 | 33.1525 | 0.8 | 1 | 38.798 | 257.9217 | -0.8 | 7.2601 | 1.071 | 0.2265
2015-04-17 17:00 | 126.82 | 40.4267 | 86.3933 | 506.5471 | 10.267 | 90.7979 | 80.18 | 9.82 | 93.1151 | 87.7703 | 19.7072 | 30.32 | 0.8 | 1 | 25.364 | 75.3912 | -1.2 | 1.156 | 1.0954 | 0.067717
2015-04-17 18:00 | 59.65 | 36.65 | 23 | 202.6972 | 10.2817 | 105.8005 | 83.4846 | 6.5154 | 107.6514 | 101.7809 | 0 | 27.4875 | 0.8 | 1 | 11.93 | 39.4175 | -1.9 | -0.6682 | 1.1027 | 0.035641
2015-04-17 19:00 | 40.19 | 24.7867 | 15.4033 | 254.558 | 10.2964 | 120.8031 | 86.5309 | 3.4691 | 122.1507 | 115.4519 | 0 | 18.59 | 0.8 | 1 | 8.038 | 26.628 | -2.2 | -1.3679 | 1.1055 | 0.024138
2015-04-17 20:00 | 20.73 | 12.9233 | 7.8067 | 0 | 10.3111 | 135.8057 | 89.1233 | 0.87672 | 136.6923 | 128.4964 | 0 | 9.6925 | 0.8 | 1 | 4.146 | 13.8385 | -2.7 | -2.2675 | 1.1091 | 0.012585
2015-04-17 21:00 | 1.27 | 1.06 | 0.21 | 0 | 10.3258 | 150.8083 | 91.0921 | -1.0921 | 151.3197 | 140.279 | 0 | 0.795 | 0.8 | 1 | 0.254 | 1.049 | -2.6 | -2.5672 | 1.1103 | 0.00095503
2015-04-17 22:00 | 0.84667 | 0.70667 | 0.14 | 0 | 10.3405 | 165.8109 | 92.3047 | -2.3047 | 166.0345 | 149.3002 | 0 | 0.53 | 0.8 | 1 | 0.16933 | 0.69933 | -2.4 | -2.3781 | 1.1095 | 0.00063625
2015-04-17 23:00 | 0.42333 | 0.35333 | 0.07 | 0 | 10.3551 | 180.8134 | 92.6769 | -2.6769 | -179.1989 | 152.6664 | 0 | 0.265 | 0.8 | 1 | 0.084667 | 0.34967 | -2.7 | -2.6891 | 1.1108 | 0.00031848
2015-04-18 | 0 | 0 | 0 | 0 | 10.3698 | -164.184 | 92.1819 | -2.1819 | -164.4374 | 148.5072 | 0 | 0 | 0.8 | 1 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-04-18 01:00 | 1.3833 | 1.2667 | 0.11667 | 0 | 10.3845 | -149.1814 | 90.8533 | -0.85326 | -149.736 | 139.0568 | 0 | 0.95 | 0.8 | 1 | 0.27667 | 1.2267 | -2.4 | -2.3617 | 1.1094 | 0.001116
2015-04-18 02:00 | 2.7667 | 2.5333 | 0.23333 | 0 | 10.3992 | -134.1789 | 88.7811 | 1.2189 | -135.1262 | 127.0811 | 0 | 1.9 | 0.8 | 1 | 0.55333 | 2.4533 | -1.9 | -1.8233 | 1.1073 | 0.0022276
2015-04-18 03:00 | 4.15 | 3.8 | 0.35 | 5.1492 | 10.4138 | -119.1763 | 86.1025 | 3.8975 | -120.6011 | 113.9445 | 0 | 2.85 | 0.8 | 1 | 0.83 | 3.68 | -1 | -0.885 | 1.1035 | 0.00333
2015-04-18 04:00 | 6.18 | 5.9467 | 0.23333 | 1.912 | 10.4285 | -104.1737 | 82.9904 | 7.0096 | -106.1116 | 100.2251 | 0 | 4.46 | 0.8 | 1 | 1.236 | 5.696 | -1.6 | -1.422 | 1.1057 | 0.0051644
2015-04-18 05:00 | 8.21 | 8.0933 | 0.11667 | 0.64888 | 10.4431 | -89.1712 | 79.642 | 10.358 | -91.5739 | 86.187 | 0.043151 | 6.07 | 0.8 | 1 | 1.642 | 7.7552 | -1.3 | -1.0577 | 1.1042 | 0.007022
2015-04-18 06:00 | 10.24 | 10.24 | 0 | 0 | 10.4578 | -74.1686 | 76.2706 | 13.7294 | -76.8845 | 71.9669 | 0 | 7.68 | 0.8 | 1 | 2.048 | 9.728 | -1.6 | -1.296 | 1.1052 | 0.008816
2015-04-18 07:00 | 22.65 | 22.65 | 0 | 0 | 10.4724 | -59.1661 | 73.0975 | 16.9025 | -61.9424 | 57.6481 | 0 | 16.9875 | 0.8 | 1 | 4.53 | 21.5175 | -2.1 | -1.4276 | 1.1057 | 0.01951
2015-04-18 08:00 | 35.06 | 35.06 | 0 | 0 | 10.4871 | -44.1635 | 70.3424 | 19.6576 | -46.6745 | 43.299 | 0 | 26.295 | 0.8 | 1 | 7.012 | 33.307 | -1.6 | -0.55916 | 1.1022 | 0.030104
2015-04-18 09:00 | 47.47 | 47.47 | 0 | 0 | 10.5017 | -29.161 | 68.2101 | 21.7899 | -31.0622 | 29.021 | 0 | 35.6025 | 0.8 | 1 | 9.494 | 45.0965 | -1.3 | 0.10927 | 1.0996 | 0.040661
2015-04-18 10:00 | 42.0833 | 42.0833 | 0 | 0 | 10.5163 | -14.1584 | 66.8707 | 23.1293 | -15.16 | 15.1811 | 0 | 31.5625 | 0.8 | 1 | 8.4167 | 39.9792 | -0.9 | 0.34935 | 1.0986 | 0.036015
2015-04-18 11:00 | 36.6967 | 36.6967 | 0 | 0 | 10.5309 | 0.84411 | 66.4372 | 23.5628 | 0.90538 | 6.4877 | 0 | 27.5225 | 0.8 | 1 | 7.3393 | 34.8618 | -1.8 | -0.71057 | 1.1028 | 0.031527
2015-04-18 12:00 | 31.31 | 31.31 | 0 | 0 | 10.5456 | 15.8466 | 66.9468 | 23.0532 | 16.9628 | 16.6664 | 0 | 23.4825 | 0.8 | 1 | 6.262 | 29.7445 | -1.7 | -0.77048 | 1.1031 | 0.026905
2015-04-18 13:00 | 52.9067 | 51.92 | 0.98667 | 2.6748 | 10.5602 | 30.8492 | 68.3535 | 21.6465 | 32.8432 | 30.6019 | 2.3022 | 38.94 | 0.8 | 1 | 10.5813 | 51.8236 | -1.8 | -0.18051 | 1.1007 | 0.046776
2015-04-18 14:00 | 74.5033 | 72.53 | 1.9733 | 5.9224 | 10.5748 | 45.8517 | 70.5369 | 19.4631 | 48.4263 | 44.8918 | 4.1956 | 54.3975 | 0.8 | 1 | 14.9007 | 73.4938 | -1.4 | 0.89668 | 1.0964 | 0.066075
2015-04-18 15:00 | 96.1 | 93.14 | 2.96 | 10.3136 | 10.5894 | 60.8542 | 73.3216 | 16.6784 | 63.6646 | 59.2343 | 5.2757 | 69.855 | 0.8 | 1 | 19.22 | 94.3507 | -1.1 | 1.8485 | 1.0926 | 0.084532
2015-04-18 16:00 | 78.2767 | 72.7933 | 5.4833 | 23.489 | 10.604 | 75.8568 | 76.5002 | 13.4998 | 78.5825 | 73.5356 | 6.6573 | 54.595 | 0.8 | 1 | 15.6553 | 76.9076 | 0.5 | 2.9034 | 1.0884 | 0.068638
2015-04-18 17:00 | 60.4533 | 52.4467 | 8.0067 | 45.4411 | 10.6186 | 90.8593 | 79.8516 | 10.1484 | 93.2564 | 87.7262 | 1.8028 | 39.335 | 0.8 | 1 | 12.0907 | 53.2285 | 0.2 | 1.8634 | 1.0925 | 0.047687
2015-04-18 18:00 | 42.63 | 32.1 | 10.53 | 88.3485 | 10.6332 | 105.8618 | 83.1548 | 6.8452 | 107.7879 | 101.7175 | 0 | 24.075 | 0.8 | 1 | 8.526 | 32.601 | 0 | 1.0188 | 1.0959 | 0.029297
2015-04-18 19:00 | 28.7967 | 21.7667 | 7.03 | 106.0168 | 10.6477 | 120.8643 | 86.1979 | 3.8021 | 122.2782 | 115.3604 | 0 | 16.325 | 0.8 | 1 | 5.7593 | 22.0843 | -0.1 | 0.59014 | 1.0976 | 0.019877
2015-04-18 20:00 | 14.9633 | 11.4333 | 3.53 | 0 | 10.6623 | 135.8668 | 88.7859 | 1.2141 | 136.8069 | 128.3629 | 0 | 8.575 | 0.8 | 1 | 2.9927 | 11.5677 | -0.2 | 0.16149 | 1.0994 | 0.010428
2015-04-18 21:00 | 1.13 | 1.1 | 0.03 | 0 | 10.6769 | 150.8693 | 90.7497 | -0.74972 | 151.418 | 140.0819 | 0 | 0.825 | 0.8 | 1 | 0.226 | 1.051 | -0.4 | -0.36716 | 1.1015 | 0.00094927
2015-04-18 22:00 | 0.82333 | 0.78 | 0.043333 | 0 | 10.6915 | 165.8718 | 91.9576 | -1.9576 | 166.1138 | 149.0152 | 0 | 0.585 | 0.8 | 1 | 0.16467 | 0.74967 | -0.5 | -0.47657 | 1.1019 | 0.00067737
2015-04-18 23:00 | 0.51667 | 0.46 | 0.056667 | 0 | 10.706 | 180.8743 | 92.3258 | -2.3258 | -179.1402 | 152.3138 | 0 | 0.345 | 0.8 | 1 | 0.10333 | 0.44833 | -0.5 | -0.48599 | 1.1019 | 0.00040511
2015-04-19 | 0.21 | 0.14 | 0.07 | 0 | 10.7206 | -164.1232 | 91.8281 | -1.8281 | -164.3992 | 148.1732 | 0 | 0.105 | 0.8 | 1 | 0.042 | 0.147 | -1 | -0.99541 | 1.104 | 0.00013307
2015-04-19 01:00 | 13.2133 | 7.8267 | 5.3867 | 0 | 10.7351 | -149.1207 | 90.4981 | -0.49807 | -149.7172 | 138.7788 | 0 | 5.87 | 0.8 | 1 | 2.6427 | 8.5127 | -1.6 | -1.334 | 1.1053 | 0.0077157
2015-04-19 02:00 | 26.2167 | 15.5133 | 10.7033 | 0 | 10.7497 | -134.1182 | 88.4255 | 1.5745 | -135.1241 | 126.8504 | 0 | 11.635 | 0.8 | 1 | 5.2433 | 16.8783 | -1.9 | -1.3726 | 1.1055 | 0.0153
2015-04-19 03:00 | 39.22 | 23.2 | 16.02 | 216.031 | 10.7642 | -119.1157 | 85.7473 | 4.2527 | -120.6119 | 113.7474 | 0 | 17.4 | 0.8 | 1 | 7.844 | 25.244 | -1.7 | -0.91113 | 1.1036 | 0.022846
2015-04-19 04:00 | 57.06 | 43.6267 | 13.4333 | 104.8009 | 10.7788 | -104.1132 | 82.6356 | 7.3644 | -106.1309 | 100.0516 | 0 | 32.72 | 0.8 | 1 | 11.412 | 44.132 | -0.5 | 0.87912 | 1.0965 | 0.03968
2015-04-19 05:00 | 74.9 | 64.0533 | 10.8467 | 58.353 | 10.7933 | -89.1107 | 79.2875 | 10.7125 | -91.5967 | 86.0303 | 4.0397 | 48.04 | 0.8 | 1 | 14.98 | 67.0597 | -0.1 | 1.9956 | 1.092 | 0.060049
2015-04-19 06:00 | 92.74 | 84.48 | 8.26 | 33.9442 | 10.8078 | -74.1082 | 75.9162 | 14.0838 | -76.9055 | 71.8216 | 10.5898 | 63.36 | 0.8 | 1 | 18.548 | 92.4978 | -0.3 | 2.5906 | 1.0896 | 0.082647
2015-04-19 07:00 | 134.1167 | 95.9867 | 38.13 | 128.5305 | 10.8223 | -59.1057 | 72.7428 | 17.2572 | -61.9558 | 57.5092 | 69.0421 | 71.99 | 0.8 | 1 | 26.8233 | 167.8554 | -0.1 | 5.1455 | 1.0794 | 0.14857
2015-04-19 08:00 | 175.4933 | 107.4933 | 68 | 198.7009 | 10.8368 | -44.1033 | 69.9876 | 20.0124 | -46.6745 | 43.1599 | 144.942 | 80.62 | 0.8 | 1 | 35.0987 | 260.6606 | -1.2 | 6.9456 | 1.0722 | 0.22918
2015-04-19 09:00 | 216.87 | 119 | 97.87 | 259.6447 | 10.8514 | -29.1008 | 67.8558 | 22.1442 | -31.0435 | 28.8687 | 227.3782 | 89.25 | 0.8 | 1 | 43.374 | 360.0022 | -1.7 | 9.5501 | 1.0618 | 0.31345
2015-04-19 10:00 | 230.07 | 117.3733 | 112.6967 | 282.8321 | 10.8659 | -14.0983 | 66.5182 | 23.4818 | -15.1187 | 14.974 | 273.228 | 88.03 | 0.8 | 1 | 46.014 | 407.272 | -2.7 | 10.0273 | 1.0599 | 0.35396
2015-04-19 11:00 | 243.27 | 115.7467 | 127.5233 | 314.6141 | 10.8804 | 0.90414 | 66.088 | 23.912 | 0.97125 | 6.1492 | 312.8039 | 86.81 | 0.8 | 1 | 48.654 | 448.2679 | -3.5 | 10.5084 | 1.058 | 0.38889
2015-04-19 12:00 | 256.47 | 114.12 | 142.35 | 358.4632 | 10.8949 | 15.9066 | 66.6022 | 23.3978 | 17.0522 | 16.5791 | 343.5606 | 85.59 | 0.8 | 1 | 51.294 | 480.4446 | -3.5 | 11.5139 | 1.0539 | 0.41522
2015-04-19 13:00 | 252.46 | 102.6933 | 149.7667 | 400.0454 | 10.9094 | 30.9091 | 68.0144 | 21.9856 | 32.953 | 30.5668 | 344.4538 | 77.02 | 0.8 | 1 | 50.492 | 471.9658 | -3.5 | 11.2489 | 1.055 | 0.4083
2015-04-19 14:00 | 248.45 | 91.2667 | 157.1833 | 464.0959 | 10.9238 | 45.9115 | 70.2031 | 19.7969 | 48.5514 | 44.8686 | 328.917 | 68.45 | 0.8 | 1 | 49.69 | 447.057 | -3.2 | 10.7705 | 1.0569 | 0.38745
2015-04-19 15:00 | 244.44 | 79.84 | 164.6 | 562.7323 | 10.9383 | 60.914 | 72.9922 | 17.0078 | 63.7996 | 59.2103 | 288.0564 | 59.88 | 0.8 | 1 | 48.888 | 396.8244 | -3.4 | 9.0008 | 1.064 | 0.34622
2015-04-19 16:00 | 186.8167 | 65.5667 | 121.25 | 507.3588 | 10.9528 | 75.9164 | 76.1735 | 13.8265 | 78.7221 | 73.5038 | 144.065 | 49.175 | 0.8 | 1 | 37.3633 | 230.6034 | -3.4 | 3.8064 | 1.0848 | 0.20513
2015-04-19 17:00 | 129.1933 | 51.2933 | 77.9 | 428.5008 | 10.9673 | 90.9189 | 79.5256 | 10.4744 | 93.3956 | 87.6812 | 17.3367 | 38.47 | 0.8 | 1 | 25.8387 | 81.6453 | -3.4 | -0.84858 | 1.1034 | 0.073871
2015-04-19 18:00 | 71.57 | 37.02 | 34.55 | 276.7143 | 10.9817 | 105.9213 | 82.8274 | 7.1726 | 107.9222 | 101.6529 | 0 | 27.765 | 0.8 | 1 | 14.314 | 42.079 | -3.5 | -2.185 | 1.1087 | 0.038257
2015-04-19 19:00 | 48.6433 | 25.3233 | 23.32 | 323.5978 | 10.9962 | 120.9237 | 85.8674 | 4.1326 | 122.4033 | 115.2674 | 0 | 18.9925 | 0.8 | 1 | 9.7287 | 28.7212 | -3.6 | -2.7025 | 1.1108 | 0.026161
2015-04-19 20:00 | 25.7167 | 13.6267 | 12.09 | 0 | 11.0106 | 135.9262 | 88.451 | 1.549 | 136.9192 | 128.2278 | 0 | 10.22 | 0.8 | 1 | 5.1433 | 15.3633 | -3.7 | -3.2199 | 1.1129 | 0.01402
2015-04-19 21:00 | 2.79 | 1.93 | 0.86 | 0 | 11.0251 | 150.9286 | 90.41 | -0.41 | 151.5141 | 139.8837 | 0 | 1.4475 | 0.8 | 1 | 0.558 | 2.0055 | -3.7 | -3.6373 | 1.1145 | 0.0018329
2015-04-19 22:00 | 2.0167 | 1.42 | 0.59667 | 0 | 11.0395 | 165.931 | 91.6132 | -1.6132 | 166.191 | 148.7307 | 0 | 1.065 | 0.8 | 1 | 0.40333 | 1.4683 | -3.6 | -3.5541 | 1.1142 | 0.0013416
2015-04-19 23:00 | 1.2433 | 0.91 | 0.33333 | 0 | 11.054 | 180.9335 | 91.9777 | -1.9777 | -179.0833 | 151.9642 | 0 | 0.6825 | 0.8 | 1 | 0.24867 | 0.93117 | -4.3 | -4.2709 | 1.1171 | 0.00085296
2015-04-20 | 0.47 | 0.4 | 0.07 | 0 | 11.0684 | -164.0641 | 91.4774 | -1.4774 | -164.3629 | 147.8423 | 0 | 0.3 | 0.8 | 1 | 0.094 | 0.394 | -4.2 | -4.1877 | 1.1168 | 0.0003608
2015-04-20 01:00 | 13.9333 | 9.7967 | 4.1367 | 0 | 11.0828 | -149.0617 | 90.146 | -0.14599 | -149.6999 | 138.5033 | 0 | 7.3475 | 0.8 | 1 | 2.7867 | 10.1342 | -4.1 | -3.7833 | 1.1151 | 0.0092668
2015-04-20 02:00 | 27.3967 | 19.1933 | 8.2033 | 0 | 11.0973 | -134.0593 | 88.0732 | 1.9268 | -135.1233 | 126.6218 | 0 | 14.395 | 0.8 | 1 | 5.4793 | 19.8743 | -4 | -3.3789 | 1.1135 | 0.018147
2015-04-20 03:00 | 40.86 | 28.59 | 12.27 | 152.837 | 11.1117 | -119.0568 | 85.3952 | 4.6048 | -120.624 | 113.5526 | 0 | 21.4425 | 0.8 | 1 | 8.172 | 29.6145 | -4 | -3.0745 | 1.1123 | 0.027011
2015-04-20 04:00 | 94.37 | 38.1233 | 56.2467 | 418.934 | 11.1261 | -104.0544 | 82.2841 | 7.7159 | -106.1515 | 99.8807 | 0 | 28.5925 | 0.8 | 1 | 18.874 | 47.4665 | -3.9 | -2.4167 | 1.1097 | 0.043191
2015-04-20 05:00 | 147.88 | 47.6567 | 100.2233 | 522.2718 | 11.1405 | -89.052 | 78.9364 | 11.0636 | -91.6208 | 85.8763 | 37.5563 | 35.7425 | 0.8 | 1 | 29.576 | 102.8748 | -3.9 | -0.68516 | 1.1027 | 0.093024
2015-04-20 06:00 | 201.39 | 57.19 | 144.2 | 578.464 | 11.1549 | -74.0496 | 75.565 | 14.435 | -76.9278 | 71.6794 | 181.8305 | 42.8925 | 0.8 | 1 | 40.278 | 265.001 | -3.5 | 4.7813 | 1.0809 | 0.23487
2015-04-20 07:00 | 250.5533 | 69.7533 | 180.8 | 597.6614 | 11.1693 | -59.0472 | 72.3914 | 17.6086 | -61.9706 | 57.3739 | 322.2317 | 52.315 | 0.8 | 1 | 50.1107 | 424.6574 | -3.4 | 9.8705 | 1.0605 | 0.36929
2015-04-20 08:00 | 299.7167 | 82.3167 | 217.4 | 624.7455 | 11.1837 | -44.0448 | 69.6361 | 20.3639 | -46.676 | 43.0252 | 456.7226 | 61.7375 | 0.8 | 1 | 59.9433 | 578.4034 | -3.1 | 14.9751 | 1.0401 | 0.49331
2015-04-20 09:00 | 348.88 | 94.88 | 254 | 663.8679 | 11.1981 | -29.0424 | 67.5048 | 22.4952 | -31.0264 | 28.7223 | 582.1849 | 71.16 | 0.8 | 1 | 69.776 | 723.1209 | -2.6 | 19.9975 | 1.02 | 0.60482
2015-04-20 10:00 | 345.31 | 107.1567 | 238.1533 | 589.4252 | 11.2125 | -14.04 | 66.1688 | 23.8312 | -15.0789 | 14.7753 | 569.9348 | 80.3675 | 0.8 | 1 | 69.062 | 719.3643 | -2.4 | 20.0801 | 1.0197 | 0.60149
2015-04-20 11:00 | 341.74 | 119.4333 | 222.3067 | 541.0905 | 11.2268 | 0.96235 | 65.7418 | 24.2582 | 1.0354 | 5.8152 | 538.306 | 89.575 | 0.8 | 1 | 68.348 | 696.229 | -2.2 | 19.5572 | 1.0218 | 0.58334
2015-04-20 12:00 | 338.17 | 131.71 | 206.46 | 512.8446 | 11.2412 | 15.9647 | 66.2606 | 23.7394 | 17.1399 | 16.4981 | 491.7302 | 98.7825 | 0.8 | 1 | 67.634 | 658.1467 | -2.4 | 18.1671 | 1.0273 | 0.55443
2015-04-20 13:00 | 316.16 | 106.5967 | 209.5633 | 551.7565 | 11.2556 | 30.9671 | 67.678 | 22.322 | 33.0608 | 30.5343 | 475.2418 | 79.9475 | 0.8 | 1 | 63.232 | 618.4213 | -1.8 | 17.5257 | 1.0299 | 0.52227
2015-04-20 14:00 | 294.15 | 81.4833 | 212.6667 | 618.004 | 11.2699 | 45.9695 | 69.872 | 20.128 | 48.6746 | 44.8464 | 438.165 | 61.1125 | 0.8 | 1 | 58.83 | 558.1075 | -2.2 | 15.2409 | 1.039 | 0.47551
2015-04-20 15:00 | 272.14 | 56.37 | 215.77 | 724.18 | 11.2843 | 60.9719 | 72.6654 | 17.3346 | 63.9325 | 59.1863 | 370.9598 | 42.2775 | 0.8 | 1 | 54.428 | 467.6653 | -2.4 | 12.2145 | 1.0511 | 0.4031
2015-04-20 16:00 | 210.15 | 50.1967 | 159.9533 | 654.2801 | 11.2986 | 75.9742 | 75.8494 | 14.1506 | 78.8594 | 73.4716 | 186.1361 | 37.6475 | 0.8 | 1 | 42.03 | 265.8136 | -2.1 | 6.2067 | 1.0752 | 0.23435
2015-04-20 17:00 | 148.16 | 44.0233 | 104.1367 | 555.8536 | 11.313 | 90.9766 | 79.2021 | 10.7979 | 93.5324 | 87.6354 | 22.934 | 33.0175 | 0.8 | 1 | 29.632 | 85.5835 | -5.2 | -2.5255 | 1.1101 | 0.077905
2015-04-20 18:00 | 86.17 | 37.85 | 48.32 | 370.3212 | 11.3273 | 105.979 | 82.5026 | 7.4974 | 108.054 | 101.5871 | 0 | 28.3875 | 0.8 | 1 | 17.234 | 45.6215 | -6.6 | -5.1743 | 1.1207 | 0.041925
2015-04-20 19:00 | 58.7833 | 26.0933 | 32.69 | 420.33 | 11.3416 | 120.9813 | 85.5395 | 4.4605 | 122.5261 | 115.1729 | 0 | 19.57 | 0.8 | 1 | 11.7567 | 31.3267 | -7.1 | -6.121 | 1.1245 | 0.028886
2015-04-20 20:00 | 31.3967 | 14.3367 | 17.06 | 0 | 11.356 | 135.9837 | 88.1188 | 1.8812 | 137.0291 | 128.0913 | 0 | 10.7525 | 0.8 | 1 | 6.2793 | 17.0318 | -6.3 | -5.7678 | 1.1231 | 0.015685
2015-04-20 21:00 | 4.01 | 2.58 | 1.43 | 0 | 11.3703 | 150.9861 | 90.073 | -0.073045 | 151.6079 | 139.6843 | 0 | 1.935 | 0.8 | 1 | 0.802 | 2.737 | -8.6 | -8.5145 | 1.1341 | 0.0025452
2015-04-20 22:00 | 2.97 | 1.9 | 1.07 | 0 | 11.3846 | 165.9884 | 91.2717 | -1.2717 | 166.2661 | 148.4468 | 0 | 1.425 | 0.8 | 1 | 0.594 | 2.019 | -8.8 | -8.7369 | 1.1349 | 0.001879
2015-04-20 23:00 | 1.93 | 1.22 | 0.71 | 0 | 11.3989 | 180.9908 | 91.6325 | -1.6325 | -179.0284 | 151.6175 | 0 | 0.915 | 0.8 | 1 | 0.386 | 1.301 | -8.7 | -8.6593 | 1.1346 | 0.0012105
2015-04-21 | 0.89 | 0.54 | 0.35 | 0 | 11.4132 | -164.0069 | 91.1297 | -1.1297 | -164.3282 | 147.5145 | 0 | 0.405 | 0.8 | 1 | 0.178 | 0.583 | -8.1 | -8.0818 | 1.1323 | 0.00054132
2015-04-21 01:00 | 5.81 | 5.4967 | 0.31333 | 0 | 11.4275 | -149.0045 | 89.7971 | 0.20287 | -149.6843 | 138.2302 | 0 | 4.1225 | 0.8 | 1 | 1.162 | 5.2845 | -7.8 | -7.6349 | 1.1305 | 0.004899
2015-04-21 02:00 | 10.73 | 10.4533 | 0.27667 | 0 | 11.4418 | -134.0022 | 87.7241 | 2.2759 | -135.124 | 126.3956 | 0 | 7.84 | 0.8 | 1 | 2.146 | 9.986 | -7 | -6.6879 | 1.1268 | 0.0092264
2015-04-21 03:00 | 15.65 | 15.41 | 0.24 | 2.7795 | 11.4561 | -118.9999 | 85.0466 | 4.9534 | -120.6374 | 113.3601 | 0 | 11.5575 | 0.8 | 1 | 3.13 | 14.6875 | -6.9 | -6.441 | 1.1258 | 0.013558
2015-04-21 04:00 | 27.8933 | 27.4267 | 0.46667 | 3.3267 | 11.4704 | -103.9975 | 81.936 | 8.064 | -106.1733 | 99.7123 | 0 | 20.57 | 0.8 | 1 | 5.5787 | 26.1487 | -6.7 | -5.8829 | 1.1235 | 0.024091
2015-04-21 05:00 | 40.1367 | 39.4433 | 0.69333 | 3.5043 | 11.4847 | -88.9952 | 78.5886 | 11.4114 | -91.6462 | 85.7253 | 0.26121 | 29.5825 | 0.8 | 1 | 8.0273 | 37.871 | -7 | -5.8165 | 1.1233 | 0.034882
2015-04-21 06:00 | 52.38 | 51.46 | 0.92 | 3.6057 | 11.4989 | -73.9929 | 75.2173 | 14.7827 | -76.9514 | 71.5405 | 1.1417 | 38.595 | 0.8 | 1 | 10.476 | 50.2127 | -6.1 | -4.5309 | 1.1181 | 0.046038
2015-04-21 07:00 | 57.42 | 56.8067 | 0.61333 | 1.9894 | 11.5132 | -58.9906 | 72.0434 | 17.9566 | -61.9868 | 57.2424 | 1.0764 | 42.605 | 0.8 | 1 | 11.484 | 55.1654 | -5.9 | -4.1761 | 1.1167 | 0.050515
2015-04-21 08:00 | 62.46 | 62.1533 | 0.30667 | 0.86709 | 11.5275 | -43.9882 | 69.2879 | 20.7121 | -46.6791 | 42.8951 | 0.63523 | 46.615 | 0.8 | 1 | 12.492 | 59.7422 | -5.8 | -3.9331 | 1.1157 | 0.054658
2015-04-21 09:00 | 67.5 | 67.5 | 0 | 0 | 11.5417 | -28.9859 | 67.157 | 22.843 | -31.011 | 28.5819 | 0 | 50.625 | 0.8 | 1 | 13.5 | 64.125 | -5.6 | -3.5961 | 1.1144 | 0.058597
2015-04-21 10:00 | 68.83 | 68.83 | 0 | 0 | 11.556 | -13.9836 | 65.8226 | 24.1774 | -15.041 | 14.5853 | 0 | 51.6225 | 0.8 | 1 | 13.766 | 65.3885 | -4.8 | -2.7566 | 1.111 | 0.059572
2015-04-21 11:00 | 70.16 | 70.16 | 0 | 0 | 11.5702 | 1.0187 | 65.3986 | 24.6014 | 1.0976 | 5.4859 | 0 | 52.62 | 0.8 | 1 | 14.032 | 66.652 | -4.8 | -2.7171 | 1.1109 | 0.060714
2015-04-21 12:00 | 71.49 | 71.49 | 0 | 0 | 11.5845 | 16.021 | 65.9218 | 24.0782 | 17.2256 | 16.4233 | 0 | 53.6175 | 0.8 | 1 | 14.298 | 67.9155 | -4.9 | -2.7776 | 1.1111 | 0.061879
2015-04-21 13:00 | 69.3133 | 69.3133 | 0 | 0 | 11.5987 | 31.0233 | 67.3445 | 22.6555 | 33.1667 | 30.5042 | 0 | 51.985 | 0.8 | 1 | 13.8627 | 65.8477 | -4.8 | -2.7423 | 1.111 | 0.059987
2015-04-21 14:00 | 67.1367 | 67.1367 | 0 | 0 | 11.6129 | 46.0256 | 69.5437 | 20.4563 | 48.7956 | 44.825 | 0 | 50.3525 | 0.8 | 1 | 13.4273 | 63.7798 | -4.6 | -2.6069 | 1.1104 | 0.058075
2015-04-21 15:00 | 64.96 | 64.96 | 0 | 0 | 11.6272 | 61.0279 | 72.3413 | 17.6587 | 64.0632 | 59.1624 | 0 | 48.72 | 0.8 | 1 | 12.992 | 61.712 | -4.675 | -2.7465 | 1.111 | 0.05622
2015-04-21 16:00 | 52.0933 | 52.0933 | 0 | 0 | 11.6414 | 76.0302 | 75.5278 | 14.4722 | 78.9944 | 73.4389 | 0 | 39.07 | 0.8 | 1 | 10.4187 | 49.4887 | -4.75 | -3.2035 | 1.1128 | 0.045159
2015-04-21 17:00 | 39.2267 | 39.2267 | 0 | 0 | 11.6556 | 91.0325 | 78.8812 | 11.1188 | 93.6668 | 87.5885 | 0 | 29.42 | 0.8 | 1 | 7.8453 | 37.2653 | -4.825 | -3.6605 | 1.1146 | 0.034061
2015-04-21 18:00 | 26.36 | 26.36 | 0 | 0 | 11.6698 | 106.0348 | 82.1803 | 7.8197 | 108.1834 | 101.5201 | 0 | 19.77 | 0.8 | 1 | 5.272 | 25.042 | -4.9 | -4.1174 | 1.1165 | 0.022926
2015-04-21 19:00 | 18.13 | 18.13 | 0 | 0 | 11.684 | 121.0371 | 85.2142 | 4.7858 | 122.6464 | 115.077 | 0 | 13.5975 | 0.8 | 1 | 3.626 | 17.2235 | -4.5 | -3.9618 | 1.1158 | 0.015759
2015-04-21 20:00 | 9.9 | 9.9 | 0 | 0 | 11.6982 | 136.0393 | 87.7893 | 2.2107 | 137.1366 | 127.9533 | 0 | 7.425 | 0.8 | 1 | 1.98 | 9.405 | -4.7 | -4.4061 | 1.1176 | 0.0086192
2015-04-21 21:00 | 1.67 | 1.67 | 0 | 0 | 11.7124 | 151.0416 | 89.7389 | 0.26107 | 151.6993 | 139.484 | 0 | 1.2525 | 0.8 | 1 | 0.334 | 1.5865 | -4.5333 | -4.4838 | 1.1179 | 0.0014544
2015-04-21 22:00 | 1.1833 | 1.1833 | 0 | 0 | 11.7266 | 166.0439 | 90.9332 | -0.93321 | 166.339 | 148.1636 | 0 | 0.8875 | 0.8 | 1 | 0.23667 | 1.1242 | -4.3667 | -4.3315 | 1.1173 | 0.00103
2015-04-21 23:00 | 0.69667 | 0.69667 | 0 | 0 | 11.7408 | 181.0462 | 91.2905 | -1.2905 | -178.9755 | 151.274 | 0 | 0.5225 | 0.8 | 1 | 0.13933 | 0.66183 | -4.2 | -4.1793 | 1.1167 | 0.00060605
2015-04-22 | 0.21 | 0.21 | 0 | 0 | 11.7549 | -163.9516 | 90.7853 | -0.78531 | -164.2954 | 147.1899 | 0 | 0.1575 | 0.8 | 1 | 0.042 | 0.1995 | -4.3 | -4.2938 | 1.1172 | 0.00018276
2015-04-22 01:00 | 2.3767 | 2.3767 | 0 | 0 | 11.7691 | -148.9493 | 89.4516 | 0.54843 | -149.6703 | 137.9598 | 0 | 1.7825 | 0.8 | 1 | 0.47533 | 2.2578 | -4.1 | -4.0294 | 1.1161 | 0.0020664
2015-04-22 02:00 | 4.5433 | 4.5433 | 0 | 0 | 11.7833 | -133.9471 | 87.3784 | 2.6216 | -135.1262 | 126.1717 | 0 | 3.4075 | 0.8 | 1 | 0.90867 | 4.3162 | -4.3 | -4.1651 | 1.1167 | 0.0039521
2015-04-22 03:00 | 6.71 | 6.71 | 0 | 0 | 11.7974 | -118.9448 | 84.7013 | 5.2987 | -120.6522 | 113.1701 | 0 | 5.0325 | 0.8 | 1 | 1.342 | 6.3745 | -3.9 | -3.7008 | 1.1148 | 0.0058272
2015-04-22 04:00 | 9.2433 | 9.2433 | 0 | 0 | 11.8116 | -103.9426 | 81.5913 | 8.4087 | -106.1965 | 99.5466 | 0 | 6.9325 | 0.8 | 1 | 1.8487 | 8.7812 | -3.5 | -3.2256 | 1.1129 | 0.0080135
2015-04-22 05:00 | 11.7767 | 11.7767 | 0 | 0 | 11.8257 | -88.9403 | 78.2443 | 11.7557 | -91.6729 | 85.5771 | 0 | 8.8325 | 0.8 | 1 | 2.3553 | 11.1878 | -3.4 | -3.0504 | 1.1122 | 0.010203
2015-04-22 06:00 | 14.31 | 14.31 | 0 | 0 | 11.8399 | -73.9381 | 74.873 | 15.127 | -76.9765 | 71.4049 | 0 | 10.7325 | 0.8 | 1 | 2.862 | 13.5945 | -3.5 | -3.0752 | 1.1123 | 0.012399
2015-04-22 07:00 | 52.59 | 52.59 | 0 | 0 | 11.854 | -58.9358 | 71.6988 | 18.3012 | -62.0045 | 57.1148 | 0 | 39.4425 | 0.8 | 1 | 10.518 | 49.9605 | -3.6 | -2.0387 | 1.1082 | 0.045398
2015-04-22 08:00 | 90.87 | 90.87 | 0 | 0 | 11.8681 | -43.9336 | 68.943 | 21.057 | -46.6837 | 42.7696 | 0 | 68.1525 | 0.8 | 1 | 18.174 | 86.3265 | -3.4 | -0.7023 | 1.1028 | 0.078065
2015-04-22 09:00 | 129.15 | 129.15 | 0 | 0 | 11.8823 | -28.9313 | 66.8125 | 23.1875 | -30.9972 | 28.4474 | 0 | 96.8625 | 0.8 | 1 | 25.83 | 122.6925 | -3.65 | 0.18414 | 1.0993 | 0.11059
2015-04-22 10:00 | 131.97 | 131.3333 | 0.63667 | 1.5341 | 11.8964 | -13.9291 | 65.4796 | 24.5204 | -15.0048 | 14.4041 | 1.4858 | 98.5 | 0.8 | 1 | 26.394 | 126.3798 | -3.9 | 0.04937 | 1.0998 | 0.11397
2015-04-22 11:00 | 134.79 | 133.5167 | 1.2733 | 3.0196 | 11.9105 | 1.0731 | 65.0586 | 24.9414 | 1.158 | 5.1618 | 3.0073 | 100.1375 | 0.8 | 1 | 26.958 | 130.1028 | -4.4 | -0.33429 | 1.1013 | 0.1175
2015-04-22 12:00 | 137.61 | 135.7 | 1.91 | 4.6211 | 11.9246 | 16.0753 | 65.5861 | 24.4139 | 17.3093 | 16.3545 | 4.4341 | 101.775 | 0.8 | 1 | 27.522 | 133.7311 | -4.95 | -0.7709 | 1.1031 | 0.12096
2015-04-22 13:00 | 115.7567 | 114.4833 | 1.2733 | 3.2607 | 11.9387 | 31.0776 | 67.0139 | 22.9861 | 33.2704 | 30.4764 | 2.8102 | 85.8625 | 0.8 | 1 | 23.1513 | 111.824 | -5.5 | -2.0055 | 1.108 | 0.1016
2015-04-22 14:00 | 93.9033 | 93.2667 | 0.63667 | 1.7944 | 11.9528 | 46.0798 | 69.2181 | 20.7819 | 48.9143 | 44.8044 | 1.2731 | 69.95 | 0.8 | 1 | 18.7807 | 90.0038 | -4.9 | -2.0874 | 1.1083 | 0.0818
2015-04-22 15:00 | 72.05 | 72.05 | 0 | 0 | 11.9669 | 61.082 | 72.0199 | 17.9801 | 64.1916 | 59.1384 | 0 | 54.0375 | 0.8 | 1 | 14.41 | 68.4475 | -4.3 | -2.161 | 1.1086 | 0.062225
2015-04-22 16:00 | 59.8033 | 59.6433 | 0.16 | 0.62673 | 11.981 | 76.0842 | 75.209 | 14.791 | 79.127 | 73.4056 | 0.17899 | 44.7325 | 0.8 | 1 | 11.9607 | 56.8722 | -4.65 | -2.8727 | 1.1115 | 0.051835
2015-04-22 17:00 | 47.5567 | 47.2367 | 0.32 | 1.6138 | 11.9951 | 91.0864 | 78.563 | 11.437 | 93.7988 | 87.5408 | 0.069245 | 35.4275 | 0.8 | 1 | 9.5113 | 45.0081 | -5 | -3.5935 | 1.1144 | 0.041128
2015-04-22 18:00 | 35.31 | 34.83 | 0.48 | 3.3903 | 12.0091 | 106.0886 | 81.8608 | 8.1392 | 108.3103 | 101.4518 | 0 | 26.1225 | 0.8 | 1 | 7.062 | 33.1845 | -5.4 | -4.363 | 1.1175 | 0.030407
2015-04-22 19:00 | 24.4867 | 24.13 | 0.35667 | 4.0057 | 12.0232 | 121.0908 | 84.8916 | 5.1084 | 122.7642 | 114.9797 | 0 | 18.0975 | 0.8 | 1 | 4.8973 | 22.9948 | -5.4667 | -4.7481 | 1.119 | 0.021099
2015-04-22 20:00 | 13.6633 | 13.43 | 0.23333 | 0 | 12.0373 | 136.093 | 87.4627 | 2.5373 | 137.2417 | 127.8139 | 0 | 10.0725 | 0.8 | 1 | 2.7327 | 12.8052 | -5.5333 | -5.1332 | 1.1205 | 0.011766
2015-04-22 21:00 | 2.84 | 2.73 | 0.11 | 0 | 12.0513 | 151.0952 | 89.4077 | 0.59226 | 151.7885 | 139.2829 | 0 | 2.0475 | 0.8 | 1 | 0.568 | 2.6155 | -5.6 | -5.5183 | 1.1221 | 0.0024065
2015-04-22 22:00 | 2.4467 | 2.3667 | 0.08 | 0 | 12.0654 | 166.0974 | 90.5978 | -0.59776 | 166.4097 | 147.8812 | 0 | 1.775 | 0.8 | 1 | 0.48933 | 2.2643 | -5.8 | -5.7292 | 1.1229 | 0.002085
2015-04-22 23:00 | 2.0533 | 2.0033 | 0.05 | 0 | 12.0794 | 181.0996 | 90.9516 | -0.95158 | -178.9246 | 150.9336 | 0 | 1.5025 | 0.8 | 1 | 0.41067 | 1.9132 | -6.1 | -6.0402 | 1.1242 | 0.0017636
2015-04-23 | 1.66 | 1.64 | 0.02 | 0 | 12.0935 | -163.8982 | 90.4442 | -0.44418 | -164.2645 | 146.8688 | 0 | 1.23 | 0.8 | 1 | 0.332 | 1.562 | -6.4 | -6.3512 | 1.1254 | 0.0014415
2015-04-23 01:00 | 13.4233 | 12.75 | 0.67333 | 0 | 12.1075 | -148.8961 | 89.1094 | 0.89059 | -149.6579 | 137.6922 | 0 | 9.5625 | 0.8 | 1 | 2.6847 | 12.2472 | -6.6 | -6.2173 | 1.1249 | 0.011297
2015-04-23 02:00 | 25.1867 | 23.86 | 1.3267 | 0 | 12.1215 | -133.8939 | 87.0362 | 2.9638 | -135.1299 | 125.9504 | 0 | 17.895 | 0.8 | 1 | 5.0373 | 22.9323 | -7.3 | -6.5834 | 1.1263 | 0.02118
2015-04-23 03:00 | 36.95 | 34.97 | 1.98 | 20.1456 | 12.1356 | -118.8917 | 84.3596 | 5.6404 | -120.6685 | 112.9826 | 0 | 26.2275 | 0.8 | 1 | 7.39 | 33.6175 | -7.55 | -6.4995 | 1.126 | 0.03104
2015-04-23 04:00 | 58.94 | 53.12 | 5.82 | 38.2594 | 12.1496 | -103.8895 | 81.2502 | 8.7498 | -106.221 | 99.3836 | 0 | 39.84 | 0.8 | 1 | 11.788 | 51.628 | -7.8 | -6.1866 | 1.1247 | 0.047616
2015-04-23 05:00 | 80.93 | 71.27 | 9.66 | 46.0974 | 12.1636 | -88.8874 | 77.9036 | 12.0964 | -91.701 | 85.432 | 3.6713 | 53.4525 | 0.8 | 1 | 16.186 | 73.3098 | -7.7 | -5.4091 | 1.1216 | 0.067426
2015-04-23 06:00 | 102.92 | 89.42 | 13.5 | 50.6196 | 12.1776 | -73.8852 | 74.5323 | 15.4677 | -77.0029 | 71.2727 | 16.2521 | 67.065 | 0.8 | 1 | 20.584 | 103.9011 | -7.8 | -4.5531 | 1.1182 | 0.09527
2015-04-23 07:00 | 159.03 | 111.5467 | 47.4833 | 148.5445 | 12.1916 | -58.8831 | 71.3578 | 18.6422 | -62.0237 | 56.991 | 80.9228 | 83.66 | 0.8 | 1 | 31.806 | 196.3888 | -7.5 | -1.3629 | 1.1055 | 0.17802
2015-04-23 08:00 | 215.14 | 133.6733 | 81.4667 | 223.289 | 12.2056 | -43.8809 | 68.6017 | 21.3983 | -46.6899 | 42.6487 | 164.2338 | 100.255 | 0.8 | 1 | 43.028 | 307.5168 | -7 | 2.6099 | 1.0896 | 0.27475
2015-04-23 09:00 | 271.25 | 155.8 | 115.45 | 289.1994 | 12.2196 | -28.8788 | 66.4715 | 23.5285 | -30.9852 | 28.3189 | 254.5883 | 116.85 | 0.8 | 1 | 54.25 | 425.6883 | -7.2 | 6.1028 | 1.0756 | 0.37545
2015-04-23 10:00 | 281.1 | 153.7933 | 127.3067 | 302.8205 | 12.2336 | -13.8766 | 65.14 | 24.86 | -14.9705 | 14.2319 | 293.5265 | 115.345 | 0.8 | 1 | 56.22 | 465.0915 | -7.4 | 7.1341 | 1.0715 | 0.40863
2015-04-23 11:00 | 290.95 | 151.7867 | 139.1633 | 325.8992 | 12.2475 | 1.1255 | 64.7218 | 25.2782 | 1.2164 | 4.8431 | 324.7356 | 113.84 | 0.8 | 1 | 58.19 | 496.7656 | -7.6 | 7.9239 | 1.0683 | 0.43517
2015-04-23 12:00 | 300.8 | 149.78 | 151.02 | 360.7708 | 12.2615 | 16.1277 | 65.2535 | 24.7465 | 17.3909 | 16.2915 | 346.2847 | 112.335 | 0.8 | 1 | 60.16 | 518.7797 | -7.8 | 8.4119 | 1.0664 | 0.45363
2015-04-23 13:00 | 264.9467 | 134.7033 | 130.2433 | 329.0931 | 12.2755 | 31.1298 | 66.6863 | 23.3137 | 33.3719 | 30.4508 | 283.6997 | 101.0275 | 0.8 | 1 | 52.9893 | 437.7165 | -8 | 5.6786 | 1.0773 | 0.38667
2015-04-23 14:00 | 229.0933 | 119.6267 | 109.4667 | 304.0153 | 12.2894 | 46.1319 | 68.8955 | 21.1045 | 49.0308 | 44.7845 | 215.7782 | 89.72 | 0.8 | 1 | 45.8187 | 351.3168 | -8.2 | 2.7787 | 1.0889 | 0.31369
2015-04-23 15:00 | 193.24 | 104.55 | 88.69 | 282.4794 | 12.3034 | 61.1341 | 71.7014 | 18.2986 | 64.3176 | 59.1143 | 145.0042 | 78.4125 | 0.8 | 1 | 38.648 | 262.0647 | -8.4 | -0.21048 | 1.1008 | 0.23656
2015-04-23 16:00 | 152.71 | 86.07 | 66.64 | 255.694 | 12.3173 | 76.1362 | 74.8929 | 15.1071 | 79.2571 | 73.3717 | 73.1698 | 64.5525 | 0.8 | 1 | 30.542 | 168.2643 | -8.3 | -3.0417 | 1.1122 | 0.15345
2015-04-23 17:00 | 112.18 | 67.59 | 44.59 | 218.9161 | 12.3313 | 91.1383 | 78.2474 | 11.7526 | 93.9282 | 87.492 | 9.5793 | 50.6925 | 0.8 | 1 | 22.436 | 82.7078 | -9 | -6.4154 | 1.1257 | 0.076343
2015-04-23 18:00 | 71.65 | 49.11 | 22.54 | 153.2802 | 12.3452 | 106.1404 | 81.5439 | 8.4561 | 108.4346 | 101.3823 | 0 | 36.8325 | 0.8 | 1 | 14.33 | 51.1625 | -9.1 | -7.5012 | 1.13 | 0.047407
2015-04-23 19:00 | 49.71 | 34.38 | 15.33 | 162.0558 | 12.3591 | 121.1426 | 84.5719 | 5.4281 | 122.8795 | 114.881 | 0 | 25.785 | 0.8 | 1 | 9.942 | 35.727 | -9.2 | -8.0835 | 1.1323 | 0.033173
2015-04-23 20:00 | 27.77 | 19.65 | 8.12 | 0 | 12.3731 | 136.1447 | 87.1389 | 2.8611 | 137.3442 | 127.6732 | 0 | 14.7375 | 0.8 | 1 | 5.554 | 20.2915 | -9.4 | -8.7659 | 1.1351 | 0.018886
2015-04-23 21:00 | 5.83 | 4.92 | 0.91 | 0 | 12.387 | 151.1468 | 89.0796 | 0.92043 | 151.8751 | 139.081 | 0 | 3.69 | 0.8 | 1 | 1.166 | 4.856 | -9.2 | -9.0482 | 1.1362 | 0.0045242
2015-04-23 22:00 | 4.2867 | 3.67 | 0.61667 | 0 | 12.4009 | 166.1489 | 90.2654 | -0.26545 | 166.4781 | 147.5999 | 0 | 2.7525 | 0.8 | 1 | 0.85733 | 3.6098 | -9.15 | -9.0372 | 1.1361 | 0.0033631
2015-04-23 23:00 | 2.7433 | 2.42 | 0.32333 | 0 | 12.4148 | 181.151 | 90.616 | -0.61597 | -178.8759 | 150.5965 | 0 | 1.815 | 0.8 | 1 | 0.54867 | 2.3637 | -9.1 | -9.0261 | 1.1361 | 0.002202
2015-04-24 | 1.2 | 1.17 | 0.03 | 0 | 12.4287 | -163.8469 | 90.1065 | -0.10646 | -164.2354 | 146.5512 | 0 | 0.8775 | 0.8 | 1 | 0.24 | 1.1175 | -9.2 | -9.1651 | 1.1367 | 0.0010416
2015-04-24 01:00 | 7.65 | 7.6267 | 0.023333 | 0 | 12.4426 | -148.8448 | 88.7708 | 1.2292 | -149.6472 | 137.4275 | 0 | 5.72 | 0.8 | 1 | 1.53 | 7.25 | -8.4 | -8.1734 | 1.1327 | 0.0067339
2015-04-24 02:00 | 14.1 | 14.0833 | 0.016667 | 0.28932 | 12.4565 | -133.8427 | 86.6975 | 3.3025 | -135.1351 | 125.7318 | 0 | 10.5625 | 0.8 | 1 | 2.82 | 13.3825 | -8.4 | -7.9818 | 1.1319 | 0.012421
2015-04-24 03:00 | 20.55 | 20.54 | 0.01 | 0.096011 | 12.4704 | -118.8407 | 84.0215 | 5.9785 | -120.6861 | 112.7979 | 0 | 15.405 | 0.8 | 1 | 4.11 | 19.515 | -8.5 | -7.8902 | 1.1316 | 0.018108
2015-04-24 04:00 | 30.5733 | 30.4367 | 0.13667 | 0.86532 | 12.4843 | -103.8386 | 80.9128 | 9.0872 | -106.2469 | 99.2234 | 0 | 22.8275 | 0.8 | 1 | 6.1147 | 28.9422 | -8.5 | -7.5956 | 1.1304 | 0.026827
2015-04-24 05:00 | 40.5967 | 40.3333 | 0.26333 | 1.2231 | 12.4981 | -88.8365 | 77.5667 | 12.4333 | -91.7305 | 85.29 | 0.10043 | 30.25 | 0.8 | 1 | 8.1193 | 38.4698 | -8.1 | -6.8978 | 1.1276 | 0.03557
2015-04-24 06:00 | 50.62 | 50.23 | 0.39 | 1.4319 | 12.512 | -73.8344 | 74.1953 | 15.8047 | -77.0308 | 71.1439 | 0.46279 | 37.6725 | 0.8 | 1 | 10.124 | 48.2593 | -8.2 | -6.6919 | 1.1268 | 0.044589
2015-04-24 07:00 | 72.55 | 67.97 | 4.58 | 14.0823 | 12.5259 | -58.8323 | 71.0204 | 18.9796 | -62.0445 | 56.8711 | 7.6963 | 50.9775 | 0.8 | 1 | 14.51 | 73.1838 | -7.9 | -5.613 | 1.1225 | 0.067359
2015-04-24 08:00 | 94.48 | 85.71 | 8.77 | 23.6816 | 12.5397 | -43.8303 | 68.264 | 21.736 | -46.6979 | 42.5325 | 17.4508 | 64.2825 | 0.8 | 1 | 18.896 | 100.6293 | -7.8 | -4.6553 | 1.1186 | 0.092304
2015-04-24 09:00 | 116.41 | 103.45 | 12.96 | 32.0317 | 12.5536 | -28.8282 | 66.134 | 23.866 | -30.975 | 28.1965 | 28.2306 | 77.5875 | 0.8 | 1 | 23.282 | 129.1001 | -6.85 | -2.8156 | 1.1113 | 0.11764
2015-04-24 10:00 | 123.61 | 114.7367 | 8.8733 | 20.8431 | 12.5674 | -13.8261 | 64.8038 | 25.1962 | -14.9382 | 14.0689 | 20.2179 | 86.0525 | 0.8 | 1 | 24.722 | 130.9924 | -5.9 | -1.8065 | 1.1072 | 0.11893
2015-04-24 11:00 | 130.81 | 126.0233 | 4.7867 | 11.0734 | 12.5812 | 1.1759 | 64.3884 | 25.6116 | 1.2727 | 4.5303 | 11.0388 | 94.5175 | 0.8 | 1 | 26.162 | 131.7183 | -4.7 | -0.5838 | 1.1023 | 0.11906
2015-04-24 12:00 | 138.01 | 137.31 | 0.7 | 1.6517 | 12.5951 | 16.178 | 64.9242 | 25.0758 | 17.4704 | 16.2343 | 1.5858 | 102.9825 | 0.8 | 1 | 27.602 | 132.1703 | -3.8333 | 0.29699 | 1.0988 | 0.11909
2015-04-24 13:00 | 150.19 | 122.3033 | 27.8867 | 69.5499 | 12.6089 | 31.18 | 66.3619 | 23.6381 | 33.4711 | 30.4272 | 59.9711 | 91.7275 | 0.8 | 1 | 30.038 | 181.7366 | -2.9667 | 2.7126 | 1.0891 | 0.16231
2015-04-24 14:00 | 162.37 | 107.2967 | 55.0733 | 150.775 | 12.6227 | 46.1821 | 68.5759 | 21.4241 | 49.145 | 44.7653 | 107.0499 | 80.4725 | 0.8 | 1 | 32.474 | 219.9964 | -2.1 | 4.7749 | 1.0809 | 0.19499
2015-04-24 15:00 | 174.55 | 92.29 | 82.26 | 257.7101 | 12.6365 | 61.1841 | 71.3857 | 18.6143 | 64.4411 | 59.0901 | 132.3831 | 69.2175 | 0.8 | 1 | 34.91 | 236.5106 | -1.9 | 5.491 | 1.078 | 0.20907
2015-04-24 16:00 | 141.7 | 76.1067 | 65.5933 | 246.6858 | 12.6503 | 76.1861 | 74.5797 | 15.4203 | 79.3847 | 73.3371 | 70.7346 | 57.08 | 0.8 | 1 | 28.34 | 156.1546 | -2.4 | 2.4798 | 1.0901 | 0.13958
2015-04-24 17:00 | 108.85 | 59.9233 | 48.9267 | 234.0705 | 12.6641 | 91.1882 | 77.9348 | 12.0652 | 94.055 | 87.4423 | 10.4454 | 44.9425 | 0.8 | 1 | 21.77 | 77.1579 | -3.7 | -1.2888 | 1.1052 | 0.069923
2015-04-24 18:00 | 76 | 43.74 | 32.26 | 211.5835 | 12.6779 | 106.1902 | 81.2299 | 8.7701 | 108.5563 | 101.3116 | 0 | 32.805 | 0.8 | 1 | 15.2 | 48.005 | -5.2 | -3.6998 | 1.1148 | 0.043883
2015-04-24 19:00 | 53.3633 | 30.9867 | 22.3767 | 223.5406 | 12.6917 | 121.1922 | 84.255 | 5.745 | 122.9921 | 114.7811 | 0 | 23.24 | 0.8 | 1 | 10.6727 | 33.9127 | -6.7 | -5.6402 | 1.1226 | 0.031217
2015-04-24 20:00 | 30.7267 | 18.2333 | 12.4933 | 225.0838 | 12.7055 | 136.1943 | 86.8181 | 3.1819 | 137.4442 | 127.5313 | 0 | 13.675 | 0.8 | 1 | 6.1453 | 19.8203 | -6.4 | -5.7806 | 1.1231 | 0.018254
2015-04-24 21:00 | 8.09 | 5.48 | 2.61 | 0 | 12.7193 | 151.1963 | 88.7545 | 1.2455 | 151.9593 | 138.8786 | 0 | 4.11 | 0.8 | 1 | 1.618 | 5.728 | -7.5 | -7.321 | 1.1293 | 0.0053042
2015-04-24 22:00 | 6.4933 | 4.3567 | 2.1367 | 0 | 12.7331 | 166.1983 | 89.9364 | 0.063625 | 166.5442 | 147.3197 | 0 | 3.2675 | 0.8 | 1 | 1.2987 | 4.5662 | -7.3 | -7.1573 | 1.1286 | 0.0042259
2015-04-24 23:00 | 4.8967 | 3.2333 | 1.6633 | 0 | 12.7468 | 181.2003 | 90.2837 | -0.28374 | -178.8293 | 150.2629 | 0 | 2.425 | 0.8 | 1 | 0.97933 | 3.4043 | -7.25 | -7.1436 | 1.1286 | 0.0031505
2015-04-25 | 3.3 | 2.11 | 1.19 | 0 | 12.7606 | -163.7977 | 89.7722 | 0.22778 | -164.2083 | 146.2372 | 0 | 1.5825 | 0.8 | 1 | 0.66 | 2.2425 | -7.2 | -7.1299 | 1.1285 | 0.0020752
2015-04-25 01:00 | 18.74 | 9.2567 | 9.4833 | 0 | 12.7743 | -148.7957 | 88.4357 | 1.5643 | -149.6383 | 137.1658 | 0 | 6.9425 | 0.8 | 1 | 3.748 | 10.6905 | -7 | -6.6659 | 1.1267 | 0.0098766
2015-04-25 02:00 | 34.18 | 16.4033 | 17.7767 | 280.2021 | 12.7881 | -133.7937 | 86.3626 | 3.6374 | -135.1419 | 125.516 | 0 | 12.3025 | 0.8 | 1 | 6.836 | 19.1385 | -6.8 | -6.2019 | 1.1248 | 0.017652
2015-04-25 03:00 | 49.62 | 23.55 | 26.07 | 237.0946 | 12.8018 | -118.7917 | 83.6872 | 6.3128 | -120.7052 | 112.6159 | 0 | 17.6625 | 0.8 | 1 | 9.924 | 27.5865 | -6.5 | -5.6379 | 1.1226 | 0.025393
2015-04-25 04:00 | 102.6367 | 31.1 | 71.5367 | 437.0407 | 12.8156 | -103.7897 | 80.5792 | 9.4208 | -106.2743 | 99.0662 | 0 | 23.325 | 0.8 | 1 | 20.5273 | 43.8523 | -6.2 | -4.8296 | 1.1193 | 0.040249
2015-04-25 05:00 | 155.6533 | 38.65 | 117.0033 | 529.4768 | 12.8293 | -88.7877 | 77.2335 | 12.7665 | -91.7614 | 85.1511 | 44.7557 | 28.9875 | 0.8 | 1 | 31.1307 | 104.8738 | -6.1 | -2.8227 | 1.1113 | 0.095567
2015-04-25 06:00 | 208.67 | 46.2 | 162.47 | 584.5284 | 12.843 | -73.7857 | 73.8621 | 16.1379 | -77.0602 | 71.0186 | 190.1241 | 34.65 | 0.8 | 1 | 41.734 | 266.5081 | -5.6 | 2.7284 | 1.0891 | 0.23801
2015-04-25 07:00 | 261.6067 | 55.9767 | 205.63 | 621.7444 | 12.8567 | -58.7837 | 70.6869 | 19.3131 | -62.0668 | 56.7552 | 340.8512 | 41.9825 | 0.8 | 1 | 52.3213 | 435.155 | -4.6 | 8.9986 | 1.064 | 0.37967
2015-04-25 08:00 | 314.5433 | 65.7533 | 248.79 | 662.1368 | 12.8704 | -43.7817 | 67.9301 | 22.0699 | -46.7075 | 42.421 | 488.7948 | 49.315 | 0.8 | 1 | 62.9087 | 601.0185 | -4.8 | 13.9818 | 1.0441 | 0.51456
2015-04-25 09:00 | 367.48 | 75.53 | 291.95 | 712.2105 | 12.8841 | -28.7797 | 65.8001 | 24.1999 | -30.9667 | 28.0801 | 628.3765 | 56.6475 | 0.8 | 1 | 73.496 | 758.52 | -4.35 | 19.3538 | 1.0226 | 0.63603
2015-04-25 10:00 | 372.7833 | 67.0433 | 305.74 | 709.4293 | 12.8978 | -13.7778 | 64.4711 | 25.5289 | -14.9079 | 13.9151 | 688.6097 | 50.2825 | 0.8 | 1 | 74.5567 | 813.4489 | -3.9 | 21.5203 | 1.0139 | 0.67631
2015-04-25 11:00 | 378.0867 | 58.5567 | 319.53 | 730.4277 | 12.9115 | 1.2242 | 64.0583 | 25.9417 | 1.327 | 4.224 | 728.4436 | 43.9175 | 0.8 | 1 | 75.6173 | 847.9784 | -3.8 | 22.6993 | 1.0092 | 0.70174
2015-04-25 12:00 | 383.39 | 50.07 | 333.32 | 777.0324 | 12.9252 | 16.2262 | 64.5981 | 25.4019 | 17.5476 | 16.1825 | 746.2454 | 37.5525 | 0.8 | 1 | 76.678 | 860.4759 | -3.6 | 23.2899 | 1.0068 | 0.71042
2015-04-25 13:00 | 363.0067 | 45.6933 | 317.3133 | 781.3867 | 12.9389 | 31.2281 | 66.0405 | 23.9595 | 33.5681 | 30.4055 | 673.9188 | 34.27 | 0.8 | 1 | 72.6013 | 780.7901 | -2.1 | 22.2997 | 1.0108 | 0.64716
2015-04-25 14:00 | 342.6233 | 41.3167 | 301.3067 | 813.4493 | 12.9526 | 46.2301 | 68.2593 | 21.7407 | 49.2567 | 44.7465 | 577.7349 | 30.9875 | 0.8 | 1 | 68.5247 | 677.247 | -2.5333 | 18.6306 | 1.0255 | 0.56949
2015-04-25 15:00 | 322.24 | 36.94 | 285.3 | 879.5697 | 12.9663 | 61.232 | 71.073 | 18.927 | 64.562 | 59.0656 | 452.1483 | 27.705 | 0.8 | 1 | 64.448 | 544.3013 | -2.9667 | 14.0427 | 1.0438 | 0.46589
2015-04-25 16:00 | 244.2133 | 37.59 | 206.6233 | 762.1221 | 12.9799 | 76.234 | 74.2693 | 15.7307 | 79.5097 | 73.3019 | 218.98 | 28.1925 | 0.8 | 1 | 48.8427 | 296.0151 | -3.4 | 5.8505 | 1.0766 | 0.26133
2015-04-25 17:00 | 166.1867 | 38.24 | 127.9467 | 597.0173 | 12.9936 | 91.2359 | 77.625 | 12.375 | 94.1791 | 87.3916 | 27.1702 | 28.68 | 0.8 | 1 | 33.2373 | 89.0875 | -3.6 | -0.81602 | 1.1033 | 0.080595
2015-04-25 18:00 | 88.16 | 38.89 | 49.27 | 312.1651 | 13.0072 | 106.2379 | 80.9189 | 9.0811 | 108.6753 | 101.2396 | 0 | 29.1675 | 0.8 | 1 | 17.632 | 46.7995 | -3 | -1.5375 | 1.1062 | 0.042449
2015-04-25 19:00 | 62 | 27.9133 | 34.0867 | 322.9414 | 13.0209 | 121.2398 | 83.9411 | 6.0589 | 123.102 | 114.6798 | 0 | 20.935 | 0.8 | 1 | 12.4 | 33.335 | -4.55 | -3.5083 | 1.114 | 0.030452
2015-04-25 20:00 | 35.84 | 16.9367 | 18.9033 | 309.6829 | 13.0345 | 136.2418 | 86.5004 | 3.4996 | 137.5415 | 127.3882 | 0 | 12.7025 | 0.8 | 1 | 7.168 | 19.8705 | -6.1 | -5.479 | 1.1219 | 0.01828
2015-04-25 21:00 | 9.68 | 5.96 | 3.72 | 0 | 13.0481 | 151.2437 | 88.4326 | 1.5674 | 152.041 | 138.6756 | 0 | 4.47 | 0.8 | 1 | 1.936 | 6.406 | -6.1 | -5.8998 | 1.1236 | 0.0059022
2015-04-25 22:00 | 8.1367 | 5.25 | 2.8867 | 0 | 13.0618 | 166.2456 | 89.6106 | 0.38937 | 166.6079 | 147.0409 | 0 | 3.9375 | 0.8 | 1 | 1.6273 | 5.5648 | -6.1 | -5.9261 | 1.1237 | 0.0051276
2015-04-25 23:00 | 6.5933 | 4.54 | 2.0533 | 0 | 13.0754 | 181.2475 | 89.955 | 0.045029 | -178.7848 | 149.9327 | 0 | 3.405 | 0.8 | 1 | 1.3187 | 4.7237 | -6.5667 | -6.4191 | 1.1257 | 0.0043602
2015-04-26 | 5.05 | 3.83 | 1.22 | 0 | 13.089 | -163.7505 | 89.4416 | 0.55843 | -164.1832 | 145.9269 | 0 | 2.8725 | 0.8 | 1 | 1.01 | 3.8825 | -7.0333 | -6.912 | 1.1276 | 0.00359
2015-04-26 01:00 | 17.9167 | 14.81 | 3.1067 | 0 | 13.1026 | -148.7486 | 88.1043 | 1.8957 | -149.6312 | 136.9072 | 0 | 11.1075 | 0.8 | 1 | 3.5833 | 14.6908 | -7.5 | -7.0409 | 1.1282 | 0.01359
2015-04-26 02:00 | 30.7833 | 25.79 | 4.9933 | 72.1478 | 13.1162 | -133.7467 | 86.0314 | 3.9686 | -135.1504 | 125.303 | 0 | 19.3425 | 0.8 | 1 | 6.1567 | 25.4992 | -7.9 | -7.1032 | 1.1284 | 0.023594
2015-04-26 03:00 | 43.65 | 36.77 | 6.88 | 59.4705 | 13.1298 | -118.7448 | 83.3567 | 6.6433 | -120.7259 | 112.4368 | 0 | 27.5775 | 0.8 | 1 | 8.73 | 36.3075 | -8.2 | -7.0654 | 1.1283 | 0.033591
2015-04-26 04:00 | 72.97 | 58.7267 | 14.2433 | 84.1013 | 13.1434 | -103.7429 | 80.2494 | 9.7506 | -106.3031 | 98.912 | 0 | 44.045 | 0.8 | 1 | 14.594 | 58.639 | -8.2 | -6.3675 | 1.1255 | 0.054117
2015-04-26 05:00 | 102.29 | 80.6833 | 21.6067 | 95.3596 | 13.157 | -88.741 | 76.9041 | 13.0959 | -91.7938 | 85.0155 | 8.2855 | 60.5125 | 0.8 | 1 | 20.458 | 89.256 | -8.2 | -5.4107 | 1.1216 | 0.082093
2015-04-26 06:00 | 131.61 | 102.64 | 28.97 | 102.1987 | 13.1705 | -73.7391 | 73.5327 | 16.4673 | -77.0911 | 70.8969 | 33.4465 | 76.98 | 0.8 | 1 | 26.322 | 136.7485 | -8.2 | -3.9266 | 1.1157 | 0.12511
2015-04-26 07:00 | 179.8733 | 119.5067 | 60.3667 | 179.5792 | 13.1841 | -58.7372 | 70.3571 | 19.6429 | -62.0908 | 56.6433 | 98.7417 | 89.63 | 0.8 | 1 | 35.9747 | 224.3463 | -8.2 | -1.1892 | 1.1048 | 0.20324
2015-04-26 08:00 | 228.1367 | 136.3733 | 91.7633 | 240.803 | 13.1977 | -43.7353 | 67.5999 | 22.4001 | -46.719 | 42.3142 | 178.0652 | 102.28 | 0.8 | 1 | 45.6273 | 325.9725 | -7.7 | 2.4866 | 1.0901 | 0.29137
2015-04-26 09:00 | 276.4 | 153.24 | 123.16 | 296.6498 | 13.2112 | -28.7334 | 65.47 | 24.53 | -30.9603 | 27.9698 | 261.9996 | 114.93 | 0.8 | 1 | 55.28 | 432.2096 | -7.2 | 6.3066 | 1.0748 | 0.38091
2015-04-26 10:00 | 298.28 | 152.98 | 145.3 | 333.1491 | 13.2248 | -13.7315 | 64.1421 | 25.8579 | -14.8796 | 13.7708 | 323.5729 | 114.735 | 0.8 | 1 | 59.656 | 497.9639 | -6.8 | 8.7614 | 1.065 | 0.43485
2015-04-26 11:00 | 320.16 | 152.72 | 167.44 | 378.3323 | 13.2383 | 1.2703 | 63.7318 | 26.2682 | 1.379 | 3.9248 | 377.4451 | 114.54 | 0.8 | 1 | 64.032 | 556.0171 | -6.4 | 10.9755 | 1.0561 | 0.48151
2015-04-26 12:00 | 342.04 | 152.46 | 189.58 | 436.7737 | 13.2519 | 16.2722 | 64.2754 | 25.7246 | 17.6225 | 16.1361 | 419.5666 | 114.345 | 0.8 | 1 | 68.408 | 602.3196 | -5.1 | 13.7225 | 1.0451 | 0.51618
2015-04-26 13:00 | 319.8967 | 131.17 | 188.7267 | 459.014 | 13.2654 | 31.2741 | 65.7225 | 24.2775 | 33.6626 | 30.3856 | 395.9642 | 98.3775 | 0.8 | 1 | 63.9793 | 558.3211 | -3.7 | 13.7475 | 1.045 | 0.47843
2015-04-26 14:00 | 297.7533 | 109.88 | 187.8733 | 500.3525 | 13.2789 | 46.276 | 67.9459 | 22.0541 | 49.3658 | 44.7282 | 355.4773 | 82.41 | 0.8 | 1 | 59.5507 | 497.438 | -5.1 | 10.4449 | 1.0582 | 0.43165
2015-04-26 15:00 | 275.61 | 88.59 | 187.02 | 567.6379 | 13.2924 | 61.2778 | 70.7634 | 19.2366 | 64.6804 | 59.0409 | 292.0081 | 66.4425 | 0.8 | 1 | 55.122 | 413.5726 | -4.95 | 7.9741 | 1.0681 | 0.36223
2015-04-26 16:00 | 212.0867 | 75.1267 | 136.96 | 495.7377 | 13.306 | 76.2797 | 73.962 | 16.038 | 79.6319 | 73.2659 | 142.7382 | 56.345 | 0.8 | 1 | 42.4173 | 241.5005 | -4.8 | 2.7469 | 1.089 | 0.21566
2015-04-26 17:00 | 148.5633 | 61.6633 | 86.9 | 395.832 | 13.3195 | 91.2815 | 77.3181 | 12.6819 | 94.3005 | 87.3398 | 18.3715 | 46.2475 | 0.8 | 1 | 29.7127 | 94.3317 | -5.1 | -2.1521 | 1.1086 | 0.085753
2015-04-26 18:00 | 85.04 | 48.2 | 36.84 | 225.8173 | 13.333 | 106.2834 | 80.6108 | 9.3892 | 108.7915 | 101.1665 | 0 | 36.15 | 0.8 | 1 | 17.008 | 53.158 | -5.4 | -3.7388 | 1.115 | 0.0486
2015-04-26 19:00 | 59.5 | 34.9167 | 24.5833 | 221.5832 | 13.3465 | 121.2852 | 83.6303 | 6.3697 | 123.2091 | 114.5772 | 0 | 26.1875 | 0.8 | 1 | 11.9 | 38.0875 | -5.6 | -4.4098 | 1.1176 | 0.034906
2015-04-26 20:00 | 33.96 | 21.6333 | 12.3267 | 185.3079 | 13.36 | 136.2871 | 86.1859 | 3.8141 | 137.6361 | 127.2441 | 0 | 16.225 | 0.8 | 1 | 6.792 | 23.017 | -6 | -5.2807 | 1.1211 | 0.02116
2015-04-26 21:00 | 8.42 | 8.35 | 0.07 | 0 | 13.3734 | 151.2889 | 88.114 | 1.886 | 152.1201 | 138.4723 | 0 | 6.2625 | 0.8 | 1 | 1.684 | 7.9465 | -6.9 | -6.6517 | 1.1266 | 0.0073411
2015-04-26 22:00 | 8.3067 | 7.3967 | 0.91 | 0 | 13.3869 | 166.2908 | 89.2883 | 0.71171 | 166.6692 | 146.7634 | 0 | 5.5475 | 0.8 | 1 | 1.6613 | 7.2088 | -7.2 | -6.9747 | 1.1279 | 0.0066673
2015-04-26 23:00 | 8.1933 | 6.4433 | 1.75 | 0 | 13.4004 | 181.2926 | 89.6298 | 0.37025 | -178.7426 | 149.6061 | 0 | 4.8325 | 0.8 | 1 | 1.6387 | 6.4712 | -7.5 | -7.2978 | 1.1292 | 0.0059919
2015-04-27 | 8.08 | 5.49 | 2.59 | 0 | 13.4138 | -163.7056 | 89.1146 | 0.8854 | -164.16 | 145.6204 | 0 | 4.1175 | 0.8 | 1 | 1.616 | 5.7335 | -8.7 | -8.5208 | 1.1341 | 0.0053319
2015-04-27 01:00 | 25.1467 | 17 | 8.1467 | 0 | 13.4273 | -148.7038 | 87.7767 | 2.2233 | -149.6259 | 136.6519 | 0 | 12.75 | 0.8 | 1 | 5.0293 | 17.7793 | -9.6 | -9.0444 | 1.1362 | 0.016564
2015-04-27 02:00 | 42.2133 | 28.51 | 13.7033 | 182.9364 | 13.4408 | -133.7019 | 85.7041 | 4.2959 | -135.1604 | 125.093 | 0 | 21.3825 | 0.8 | 1 | 8.4427 | 29.8252 | -9.2 | -8.268 | 1.1331 | 0.027711
2015-04-27 03:00 | 59.28 | 40.02 | 19.26 | 158.7184 | 13.4542 | -118.7001 | 83.0302 | 6.9698 | -120.748 | 112.2607 | 0 | 30.015 | 0.8 | 1 | 11.856 | 41.871 | -8.8 | -7.4915 | 1.13 | 0.038797
2015-04-27 04:00 | 105.25 | 56.2533 | 48.9967 | 280.0445 | 13.4676 | -103.6983 | 79.9237 | 10.0763 | -106.3333 | 98.7609 | 0 | 42.19 | 0.8 | 1 | 21.05 | 63.24 | -8 | -6.0237 | 1.1241 | 0.058292
2015-04-27 05:00 | 151.22 | 72.4867 | 78.7333 | 339.2107 | 13.4811 | -88.6965 | 76.5788 | 13.4212 | -91.8276 | 84.8831 | 30.2536 | 54.365 | 0.8 | 1 | 30.244 | 114.8626 | -8.1 | -4.5105 | 1.118 | 0.10531
2015-04-27 06:00 | 197.19 | 88.72 | 108.47 | 375.4482 | 13.4945 | -73.6947 | 73.2074 | 16.7926 | -77.1235 | 70.7787 | 123.6042 | 66.54 | 0.8 | 1 | 39.438 | 229.5822 | -7.4667 | -0.29222 | 1.1012 | 0.2073
2015-04-27 07:00 | 252.8367 | 92.01 | 160.8267 | 470.9342 | 13.5079 | -58.6929 | 70.0314 | 19.9686 | -62.1165 | 56.5354 | 259.6835 | 69.0075 | 0.8 | 1 | 50.5673 | 379.2583 | -6.8333 | 5.0185 | 1.0799 | 0.33585
2015-04-27 08:00 | 308.4833 | 95.3 | 213.1833 | 551.8156 | 13.5213 | -43.6911 | 67.2736 | 22.7264 | -46.7322 | 42.2122 | 408.7088 | 71.475 | 0.8 | 1 | 61.6967 | 541.8805 | -6.2 | 10.7338 | 1.0571 | 0.4697
2015-04-27 09:00 | 364.13 | 98.59 | 265.54 | 631.7206 | 13.5347 | -28.6893 | 65.1437 | 24.8563 | -30.9558 | 27.8655 | 558.4706 | 73.9425 | 0.8 | 1 | 72.826 | 705.2391 | -6.15 | 15.8887 | 1.0364 | 0.59937
2015-04-27 10:00 | 349.3 | 104.1667 | 245.1333 | 555.5511 | 13.5481 | -13.6875 | 63.8168 | 26.1832 | -14.8534 | 13.6359 | 539.892 | 78.125 | 0.8 | 1 | 69.86 | 687.877 | -6.1 | 15.3962 | 1.0384 | 0.58573
2015-04-27 11:00 | 334.47 | 109.7433 | 224.7267 | 502.0465 | 13.5615 | 1.3143 | 63.4088 | 26.5912 | 1.4288 | 3.6335 | 501.0373 | 82.3075 | 0.8 | 1 | 66.894 | 650.2388 | -5.8 | 14.52 | 1.0419 | 0.55555
2015-04-27 12:00 | 319.64 | 115.32 | 204.32 | 465.3587 | 13.5749 | 16.3161 | 63.9561 | 26.0439 | 17.6951 | 16.0949 | 447.1185 | 86.49 | 0.8 | 1 | 63.928 | 597.5365 | -4.3 | 14.373 | 1.0425 | 0.51081
2015-04-27 13:00 | 301.18 | 118.37 | 182.81 | 439.2806 | 13.5883 | 31.3179 | 65.4078 | 24.5922 | 33.7546 | 30.3674 | 379.0121 | 88.7775 | 0.8 | 1 | 60.236 | 528.0256 | -5.1 | 11.4008 | 1.0544 | 0.45653
2015-04-27 14:00 | 282.72 | 121.42 | 161.3 | 423.922 | 13.6017 | 46.3196 | 67.6357 | 22.3643 | 49.4724 | 44.7102 | 301.2706 | 91.065 | 0.8 | 1 | 56.544 | 448.8796 | -5 | 9.0275 | 1.0639 | 0.3916
2015-04-27 15:00 | 264.26 | 124.47 | 139.79 | 417.8861 | 13.615 | 61.3214 | 70.4568 | 19.5432 | 64.796 | 59.0158 | 215.1287 | 93.3525 | 0.8 | 1 | 52.852 | 361.3332 | -4.3 | 6.9917 | 1.072 | 0.31764
2015-04-27 16:00 | 198.3533 | 96.06 | 102.2933 | 363.5477 | 13.6284 | 76.3232 | 73.6577 | 16.3423 | 79.7514 | 73.2291 | 104.8999 | 72.045 | 0.8 | 1 | 39.6707 | 216.6156 | -5 | 1.7692 | 1.0929 | 0.19413
2015-04-27 17:00 | 132.4467 | 67.65 | 64.7967 | 288.3604 | 13.6418 | 91.3249 | 77.0143 | 12.9857 | 94.419 | 87.287 | 13.6489 | 50.7375 | 0.8 | 1 | 26.4893 | 90.8757 | -5.1 | -2.2601 | 1.109 | 0.082644
2015-04-27 18:00 | 66.54 | 39.24 | 27.3 | 162.1228 | 13.6551 | 106.3267 | 80.3057 | 9.6943 | 108.9048 | 101.0921 | 0 | 29.43 | 0.8 | 1 | 13.308 | 42.738 | -6.4 | -5.0644 | 1.1203 | 0.03926
2015-04-27 19:00 | 47.2133 | 28.4233 | 18.79 | 161.5929 | 13.6684 | 121.3284 | 83.3225 | 6.6775 | 123.3135 | 114.4735 | 0 | 21.3175 | 0.8 | 1 | 9.4427 | 30.7602 | -6.7 | -5.7387 | 1.123 | 0.028325
2015-04-27 20:00 | 27.8867 | 17.6067 | 10.28 | 142.8957 | 13.6818 | 136.3302 | 85.8745 | 4.1255 | 137.728 | 127.099 | 0 | 13.205 | 0.8 | 1 | 5.5773 | 18.7823 | -6.9 | -6.3131 | 1.1253 | 0.017331
2015-04-27 21:00 | 8.56 | 6.79 | 1.77 | 0 | 13.6951 | 151.3319 | 87.7988 | 2.2012 | 152.1966 | 138.2688 | 0 | 5.0925 | 0.8 | 1 | 1.712 | 6.8045 | -7.45 | -7.2374 | 1.1289 | 0.0062992
2015-04-27 22:00 | 8.2067 | 6.52 | 1.6867 | 0 | 13.7084 | 166.3337 | 88.9695 | 1.0305 | 166.728 | 146.4876 | 0 | 4.89 | 0.8 | 1 | 1.6413 | 6.5313 | -8 | -7.7959 | 1.1312 | 0.0060583
2015-04-27 23:00 | 7.8533 | 6.25 | 1.6033 | 0 | 13.7217 | 181.3354 | 89.3082 | 0.69182 | -178.7026 | 149.2833 | 0 | 4.6875 | 0.8 | 1 | 1.5707 | 6.2582 | -8.45 | -8.2544 | 1.133 | 0.0058143
2015-04-28 | 7.5 | 5.98 | 1.52 | 0 | 13.7351 | -163.6628 | 88.7914 | 1.2086 | -164.1389 | 145.3179 | 0 | 4.485 | 0.8 | 1 | 1.5 | 5.985 | -8.9 | -8.713 | 1.1349 | 0.0055695
2015-04-28 01:00 | 21.2833 | 15.9467 | 5.3367 | 0 | 13.7484 | -148.6611 | 87.453 | 2.547 | -149.6224 | 136.4 | 0 | 11.96 | 0.8 | 1 | 4.2567 | 16.2167 | -9.1 | -8.5932 | 1.1344 | 0.015085
2015-04-28 02:00 | 35.0667 | 25.9133 | 9.1533 | 113.6579 | 13.7617 | -133.6594 | 85.3807 | 4.6193 | -135.1722 | 124.8861 | 0 | 19.435 | 0.8 | 1 | 7.0133 | 26.4483 | -9.3 | -8.4735 | 1.1339 | 0.024591
2015-04-28 03:00 | 48.85 | 35.88 | 12.97 | 102.18 | 13.7749 | -118.6576 | 82.7076 | 7.2924 | -120.7717 | 112.0877 | 0 | 26.91 | 0.8 | 1 | 9.77 | 36.68 | -7.4 | -6.2538 | 1.125 | 0.033838
2015-04-28 04:00 | 81.88 | 53.3033 | 28.5767 | 158.3319 | 13.7882 | -103.6559 | 79.6019 | 10.3981 | -106.3651 | 98.6129 | 0 | 39.9775 | 0.8 | 1 | 16.376 | 56.3535 | -8.5 | -6.739 | 1.127 | 0.052076
2015-04-28 05:00 | 114.91 | 70.7267 | 44.1833 | 185.9903 | 13.8015 | -88.6542 | 76.2576 | 13.7424 | -91.863 | 84.7541 | 17.0052 | 53.045 | 0.8 | 1 | 22.982 | 93.0322 | -8.3 | -5.3927 | 1.1216 | 0.085561
2015-04-28 06:00 | 147.94 | 88.15 | 59.79 | 203.1798 | 13.8148 | -73.6525 | 72.8862 | 17.1138 | -77.1575 | 70.6641 | 67.2738 | 66.1125 | 0.8 | 1 | 29.588 | 162.9743 | -8.2 | -3.1071 | 1.1124 | 0.14866
2015-04-28 07:00 | 182.0167 | 109.11 | 72.9067 | 210.2404 | 13.828 | -58.6508 | 69.7097 | 20.2903 | -62.1438 | 56.4315 | 116.2489 | 81.8325 | 0.8 | 1 | 36.4033 | 234.4847 | -8.2 | -0.87235 | 1.1035 | 0.21218
2015-04-28 08:00 | 216.0933 | 130.07 | 86.0233 | 219.7205 | 13.8413 | -43.6491 | 66.9514 | 23.0486 | -46.7472 | 42.1149 | 162.9891 | 97.5525 | 0.8 | 1 | 43.2187 | 303.7603 | -8 | 1.4925 | 1.094 | 0.2725
2015-04-28 09:00 | 250.17 | 151.03 | 99.14 | 233.0277 | 13.8546 | -28.6474 | 64.8213 | 25.1787 | -30.9533 | 27.7674 | 206.1937 | 113.2725 | 0.8 | 1 | 50.034 | 369.5002 | -8 | 3.5469 | 1.0858 | 0.32899
2015-04-28 10:00 | 237.54 | 159.9167 | 77.6233 | 173.9372 | 13.8678 | -13.6457 | 63.4952 | 26.5048 | -14.8293 | 13.5107 | 169.1237 | 119.9375 | 0.8 | 1 | 47.508 | 336.5692 | -8 | 2.5178 | 1.0899 | 0.30081
2015-04-28 11:00 | 224.91 | 168.8033 | 56.1067 | 123.966 | 13.881 | 1.356 | 63.0896 | 26.9104 | 1.4763 | 3.351 | 123.7541 | 126.6025 | 0.8 | 1 | 44.982 | 295.3386 | -8.1 | 1.1293 | 1.0955 | 0.2653
2015-04-28 12:00 | 212.28 | 177.69 | 34.59 | 77.9049 | 13.8943 | 16.3577 | 63.6404 | 26.3596 | 17.7652 | 16.0586 | 74.865 | 133.2675 | 0.8 | 1 | 42.456 | 250.5885 | -8.05 | -0.21911 | 1.1009 | 0.22621
2015-04-28 13:00 | 204.57 | 175.5033 | 29.0667 | 69.0269 | 13.9075 | 31.3594 | 65.0964 | 24.9036 | 33.844 | 30.3507 | 59.5667 | 131.6275 | 0.8 | 1 | 40.914 | 232.1082 | -8 | -0.74662 | 1.103 | 0.20993
2015-04-28 14:00 | 196.86 | 173.3167 | 23.5433 | 61.0812 | 13.9207 | 46.3611 | 67.3288 | 22.6712 | 49.5763 | 44.6925 | 43.4222 | 129.9875 | 0.8 | 1 | 39.372 | 212.7817 | -8 | -1.3506 | 1.1054 | 0.19287
2015-04-28 15:00 | 189.15 | 171.13 | 18.02 | 53.0778 | 13.9339 | 61.3627 | 70.1535 | 19.8465 | 64.9089 | 58.9903 | 27.3448 | 128.3475 | 0.8 | 1 | 37.83 | 193.5223 | -7.8 | -1.7524 | 1.107 | 0.17567
2015-04-28 16:00 | 158.8367 | 139.26 | 19.5767 | 68.3507 | 13.9471 | 76.3644 | 73.3566 | 16.6434 | 79.8681 | 73.1916 | 19.7651 | 104.445 | 0.8 | 1 | 31.7673 | 155.9775 | -7.6 | -2.7257 | 1.1109 | 0.14209
2015-04-28 17:00 | 128.5233 | 107.39 | 21.1333 | 91.957 | 13.9603 | 91.3661 | 76.7137 | 13.2863 | 94.5347 | 87.2332 | 4.4389 | 80.5425 | 0.8 | 1 | 25.7047 | 110.686 | -8 | -4.5411 | 1.1182 | 0.10149
2015-04-28 18:00 | 98.21 | 75.52 | 22.69 | 130.7161 | 13.9735 | 106.3678 | 80.0038 | 9.9962 | 109.0153 | 101.0166 | 0 | 56.64 | 0.8 | 1 | 19.642 | 76.282 | -8 | -5.6162 | 1.1225 | 0.070212
2015-04-28 19:00 | 70.7333 | 54.9367 | 15.7967 | 129.953 | 13.9867 | 121.3694 | 83.018 | 6.982 | 123.415 | 114.3685 | 0 | 41.2025 | 0.8 | 1 | 14.1467 | 55.3492 | -8 | -6.2703 | 1.1251 | 0.051063
2015-04-28 20:00 | 43.2567 | 34.3533 | 8.9033 | 115.1769 | 13.9999 | 136.3711 | 85.5665 | 4.4335 | 137.8171 | 126.9529 | 0 | 25.765 | 0.8 | 1 | 8.6513 | 34.4163 | -8.4 | -7.3245 | 1.1293 | 0.03187
2015-04-28 21:00 | 15.78 | 13.77 | 2.01 | 0 | 14.0131 | 151.3727 | 87.487 | 2.513 | 152.2704 | 138.0651 | 0 | 10.3275 | 0.8 | 1 | 3.156 | 13.4835 | -9.2 | -8.7786 | 1.1351 | 0.01255
2015-04-28 22:00 | 13.27 | 11.7767 | 1.4933 | 0 | 14.0262 | 166.3744 | 88.6542 | 1.3458 | 166.7844 | 146.2134 | 0 | 8.8325 | 0.8 | 1 | 2.654 | 11.4865 | -9.7 | -9.341 | 1.1374 | 0.010713
2015-04-28 23:00 | 10.76 | 9.7833 | 0.97667 | 0 | 14.0394 | 181.376 | 88.9903 | 1.0097 | -178.6649 | 148.9642 | 0 | 7.3375 | 0.8 | 1 | 2.152 | 9.4895 | -10.2 | -9.9035 | 1.1396 | 0.0088678
2015-04-29 | 8.25 | 7.79 | 0.46 | 0 | 14.0525 | -163.6223 | 88.4721 | 1.5279 | -164.1198 | 145.0194 | 0 | 5.8425 | 0.8 | 1 | 1.65 | 7.4925 | -10.7 | -10.4659 | 1.1419 | 0.0070154
2015-04-29 01:00 | 24.2767 | 19.14 | 5.1367 | 0 | 14.0657 | -148.6207 | 87.1333 | 2.8667 | -149.6207 | 136.1516 | 0 | 14.355 | 0.8 | 1 | 4.8553 | 19.2103 | -10.65 | -10.0497 | 1.1402 | 0.017961
2015-04-29 02:00 | 40.3033 | 30.49 | 9.8133 | 113.9928 | 14.0788 | -133.6191 | 85.0614 | 4.9386 | -135.1855 | 124.6825 | 0 | 22.8675 | 0.8 | 1 | 8.0607 | 30.9282 | -10.6 | -9.6335 | 1.1385 | 0.028874
2015-04-29 03:00 | 56.33 | 41.84 | 14.49 | 109.4053 | 14.092 | -118.6174 | 82.3892 | 7.6108 | -120.797 | 111.9177 | 0 | 31.38 | 0.8 | 1 | 11.266 | 42.646 | -10.1333 | -8.8006 | 1.1352 | 0.039698
2015-04-29 04:00 | 91.2933 | 61.0733 | 30.22 | 162.5304 | 14.1051 | -103.6158 | 79.2844 | 10.7156 | -106.3983 | 98.4682 | 0 | 45.805 | 0.8 | 1 | 18.2587 | 64.0637 | -9.6667 | -7.6647 | 1.1307 | 0.059396
2015-04-29 05:00 | 126.2567 | 80.3067 | 45.95 | 189.1502 | 14.1182 | -88.6142 | 75.9405 | 14.0595 | -91.8998 | 84.6285 | 17.7071 | 60.23 | 0.8 | 1 | 25.2513 | 103.1884 | -9.2 | -5.9754 | 1.1239 | 0.095098
2015-04-29 06:00 | 161.22 | 99.54 | 61.68 | 205.9049 | 14.1313 | -73.6126 | 72.5691 | 17.4309 | -77.1931 | 70.5533 | 68.552 | 74.655 | 0.8 | 1 | 32.244 | 175.451 | -9.1 | -3.6172 | 1.1145 | 0.16034
2015-04-29 07:00 | 217.5467 | 117.9533 | 99.5933 | 282.9591 | 14.1444 | -58.611 | 69.3921 | 20.6079 | -62.1728 | 56.3318 | 156.8677 | 88.465 | 0.8 | 1 | 43.5093 | 288.8421 | -9 | 0.026315 | 1.0999 | 0.26051
2015-04-29 08:00 | 273.8733 | 136.3667 | 137.5067 | 346.6994 | 14.1575 | -43.6093 | 66.6332 | 23.3668 | -46.7641 | 42.0223 | 257.5576 | 102.275 | 0.8 | 1 | 54.7747 | 414.6072 | -8.9 | 4.0565 | 1.0838 | 0.36846
2015-04-29 09:00 | 330.2 | 154.78 | 175.42 | 407.5125 | 14.1706 | -28.6077 | 64.5029 | 25.4971 | -30.9529 | 27.6752 | 360.8909 | 116.085 | 0.8 | 1 | 66.04 | 543.0159 | -8.6 | 8.3692 | 1.0665 | 0.47489
2015-04-29 10:00 | 324.31 | 167.5667 | 156.7433 | 347.372 | 14.1837 | -13.6061 | 63.1776 | 26.8224 | -14.8075 | 13.395 | 337.9221 | 125.675 | 0.8 | 1 | 64.862 | 528.4591 | -8.4 | 8.1143 | 1.0675 | 0.46261
2015-04-29 11:00 | 318.42 | 180.3533 | 138.0667 | 301.7848 | 14.1968 | 1.3955 | 62.7741 | 27.2259 | 1.5214 | 3.0787 | 301.3492 | 135.265 | 0.8 | 1 | 63.684 | 500.2982 | -8.2333 | 7.401 | 1.0704 | 0.43912
2015-04-29 12:00 | 312.53 | 193.14 | 119.39 | 265.9751 | 14.2098 | 16.3971 | 63.3284 | 26.6716 | 17.8328 | 16.027 | 255.6371 | 144.855 | 0.8 | 1 | 62.506 | 462.9981 | -8.0667 | 6.402 | 1.0744 | 0.4079
2015-04-29 13:00 | 283.04 | 168.3633 | 114.6767 | 269.22 | 14.2229 | 31.3986 | 64.7886 | 25.2114 | 33.9308 | 30.3354 | 232.3594 | 126.2725 | 0.8 | 1 | 56.608 | 415.2399 | -7.9 | 5.0762 | 1.0797 | 0.36763
2015-04-29 14:00 | 253.55 | 143.5867 | 109.9633 | 281.7218 | 14.236 | 46.4002 | 67.0252 | 22.9748 | 49.6774 | 44.6749 | 200.3344 | 107.69 | 0.8 | 1 | 50.71 | 358.7344 | -7.9 | 3.3105 | 1.0868 | 0.31968
2015-04-29 15:00 | 224.06 | 118.81 | 105.25 | 305.5841 | 14.249 | 61.4018 | 69.8535 | 20.1465 | 65.019 | 58.9643 | 157.5504 | 89.1075 | 0.8 | 1 | 44.812 | 291.4699 | -8.05 | 1.0584 | 1.0958 | 0.26189
2015-04-29 16:00 | 177.54 | 101.9433 | 75.5967 | 259.4322 | 14.2621 | 76.4034 | 73.0586 | 16.9414 | 79.9818 | 73.1532 | 75.1868 | 76.4575 | 0.8 | 1 | 35.508 | 187.1523 | -8.2 | -2.3515 | 1.1094 | 0.17025
2015-04-29 17:00 | 131.02 | 85.0767 | 45.9433 | 195.6141 | 14.2751 | 91.405 | 76.4162 | 13.5838 | 94.6474 | 87.1783 | 9.6296 | 63.8075 | 0.8 | 1 | 26.204 | 99.6411 | -8.3 | -5.1862 | 1.1207 | 0.091571
2015-04-29 18:00 | 84.5 | 68.21 | 16.29 | 91.1516 | 14.2881 | 106.4065 | 79.7052 | 10.2948 | 109.1228 | 100.94 | 0 | 51.1575 | 0.8 | 1 | 16.9 | 68.0575 | -8.5 | -6.3732 | 1.1255 | 0.062811
2015-04-29 19:00 | 61.7067 | 50.31 | 11.3967 | 89.8982 | 14.3012 | 121.4081 | 82.7168 | 7.2832 | 123.5135 | 114.2625 | 0 | 37.7325 | 0.8 | 1 | 12.3413 | 50.0738 | -8.9 | -7.3352 | 1.1293 | 0.046371
2015-04-29 20:00 | 38.9133 | 32.41 | 6.5033 | 78.7321 | 14.3142 | 136.4097 | 85.2619 | 4.7381 | 137.9034 | 126.806 | 0 | 24.3075 | 0.8 | 1 | 7.7827 | 32.0902 | -9.4 | -8.3972 | 1.1336 | 0.029829
2015-04-29 21:00 | 16.12 | 14.51 | 1.61 | 0 | 14.3272 | 151.4112 | 87.1787 | 2.8213 | 152.3416 | 137.8615 | 0 | 10.8825 | 0.8 | 1 | 3.224 | 14.1065 | -9.9 | -9.4592 | 1.1378 | 0.013162
2015-04-29 22:00 | 13.96 | 12.7367 | 1.2233 | 0 | 14.3402 | 166.4128 | 88.3427 | 1.6573 | 166.8383 | 145.9411 | 0 | 9.5525 | 0.8 | 1 | 2.792 | 12.3445 | -10.3 | -9.9142 | 1.1397 | 0.011536
2015-04-29 23:00 | 11.8 | 10.9633 | 0.83667 | 0 | 14.3532 | 181.4143 | 88.6763 | 1.3237 | -178.6295 | 148.649 | 0 | 8.2225 | 0.8 | 1 | 2.36 | 10.5825 | -10.7 | -10.3693 | 1.1415 | 0.0099053
2015-04-30 | 9.64 | 9.19 | 0.45 | 0 | 14.3662 | -163.5841 | 88.1567 | 1.8433 | -164.1028 | 144.725 | 0 | 6.8925 | 0.8 | 1 | 1.928 | 8.8205 | -10.3 | -10.0244 | 1.1401 | 0.0082461
2015-04-30 01:00 | 22.4133 | 21.3633 | 1.05 | 18.9141 | 14.3792 | -148.5826 | 86.8176 | 3.1824 | -149.6209 | 135.9068 | 0 | 16.0225 | 0.8 | 1 | 4.4827 | 20.5052 | -10.45 | -9.8092 | 1.1392 | 0.019155
2015-04-30 02:00 | 35.1867 | 33.5367 | 1.65 | 18.0199 | 14.3922 | -133.581 | 84.7463 | 5.2537 | -135.2006 | 124.4821 | 0 | 25.1525 | 0.8 | 1 | 7.0373 | 32.1898 | -10.6 | -9.5941 | 1.1384 | 0.030048
2015-04-30 03:00 | 47.96 | 45.71 | 2.25 | 16.3189 | 14.4051 | -118.5795 | 82.075 | 7.925 | -120.8238 | 111.751 | 0 | 34.2825 | 0.8 | 1 | 9.592 | 43.8745 | -10.3 | -8.9289 | 1.1357 | 0.04086
2015-04-30 04:00 | 72.2067 | 63.4733 | 8.7333 | 45.6515 | 14.4181 | -103.578 | 78.9711 | 11.0289 | -106.4331 | 98.3267 | 0 | 47.605 | 0.8 | 1 | 14.4413 | 62.0463 | -10.05 | -8.1111 | 1.1324 | 0.057616
2015-04-30 05:00 | 96.4533 | 81.2367 | 15.2167 | 61.303 | 14.431 | -88.5765 | 75.6278 | 14.3722 | -91.9382 | 84.5063 | 5.8689 | 60.9275 | 0.8 | 1 | 19.2907 | 86.0871 | -9.8 | -7.1098 | 1.1284 | 0.079658
2015-04-30 06:00 | 120.7 | 99 | 21.7 | 71.2036 | 14.444 | -73.5749 | 72.2563 | 17.7437 | -77.2303 | 70.4461 | 23.8314 | 74.25 | 0.8 | 1 | 24.14 | 122.2214 | -9.6 | -5.7806 | 1.1231 | 0.11256
2015-04-30 07:00 | 154.8033 | 120.2767 | 34.5267 | 96.6906 | 14.4569 | -58.5734 | 69.0788 | 20.9212 | -62.2035 | 56.2361 | 53.7379 | 90.2075 | 0.8 | 1 | 30.9607 | 174.9061 | -9.4 | -3.9342 | 1.1157 | 0.16002
2015-04-30 08:00 | 188.9067 | 141.5533 | 47.3533 | 117.8996 | 14.4699 | -43.5719 | 66.3192 | 23.6808 | -46.7829 | 41.9345 | 87.7067 | 106.165 | 0.8 | 1 | 37.7813 | 231.653 | -9.2 | -1.9608 | 1.1078 | 0.21044
2015-04-30 09:00 | 223.01 | 162.83 | 60.18 | 138.2146 | 14.4828 | -28.5704 | 64.1886 | 25.8114 | -30.9545 | 27.5891 | 122.4985 | 122.1225 | 0.8 | 1 | 44.602 | 289.223 | -9 | 0.038218 | 1.0998 | 0.26084
2015-04-30 10:00 | 225.9133 | 172.5733 | 53.34 | 116.9469 | 14.4957 | -13.5689 | 62.864 | 27.136 | -14.7879 | 13.2889 | 113.8155 | 129.43 | 0.8 | 1 | 45.1827 | 288.4282 | -8.8 | 0.21338 | 1.0991 | 0.25996
2015-04-30 11:00 | 228.8167 | 182.3167 | 46.5 | 100.5775 | 14.5086 | 1.4326 | 62.4624 | 27.5376 | 1.5642 | 2.8183 | 100.4558 | 136.7375 | 0.8 | 1 | 45.7633 | 282.9567 | -8.8 | 0.042395 | 1.0998 | 0.25519
2015-04-30 12:00 | 231.72 | 192.06 | 39.66 | 87.4186 | 14.5216 | 16.4341 | 63.02 | 26.98 | 17.8979 | 16 | 84.0322 | 144.045 | 0.8 | 1 | 46.344 | 274.4212 | -8.7667 | -0.19101 | 1.1008 | 0.2477
2015-04-30 13:00 | 201.5033 | 171.2933 | 30.21 | 70.1323 | 14.5345 | 31.4356 | 64.4844 | 25.5156 | 34.015 | 30.3214 | 60.5387 | 128.47 | 0.8 | 1 | 40.3007 | 229.3094 | -8.7333 | -1.5674 | 1.1063 | 0.20802
2015-04-30 14:00 | 171.2867 | 150.5267 | 20.76 | 52.538 | 14.5474 | 46.4371 | 66.7251 | 23.2749 | 49.7758 | 44.6575 | 37.3714 | 112.895 | 0.8 | 1 | 34.2573 | 184.5237 | -8.7 | -2.9336 | 1.1117 | 0.16822
2015-04-30 15:00 | 141.07 | 129.76 | 11.31 | 32.381 | 14.5602 | 61.4386 | 69.5568 | 20.4432 | 65.1262 | 58.9379 | 16.7075 | 97.32 | 0.8 | 1 | 28.214 | 142.2415 | -9.1 | -4.655 | 1.1186 | 0.13047
2015-04-30 16:00 | 116.8433 | 107.1067 | 9.7367 | 32.86 | 14.5731 | 76.4401 | 72.764 | 17.236 | 80.0926 | 73.114 | 9.5448 | 80.33 | 0.8 | 1 | 23.3687 | 113.2434 | -9.2 | -5.6611 | 1.1226 | 0.10425
2015-04-30 17:00 | 92.6167 | 84.4533 | 8.1633 | 34.0345 | 14.586 | 91.4415 | 76.122 | 13.878 | 94.7572 | 87.1224 | 1.7086 | 63.34 | 0.8 | 1 | 18.5233 | 83.5719 | -9.4 | -6.7884 | 1.1272 | 0.077243
2015-04-30 18:00 | 68.39 | 61.8 | 6.59 | 35.8575 | 14.5989 | 106.443 | 79.4098 | 10.5902 | 109.2273 | 100.8622 | 0 | 46.35 | 0.8 | 1 | 13.678 | 60.028 | -9.7 | -7.8241 | 1.1313 | 0.055686
2015-04-30 19:00 | 50.15 | 45.7 | 4.45 | 33.7307 | 14.6117 | 121.4445 | 82.419 | 7.581 | 123.6092 | 114.1554 | 0 | 34.275 | 0.8 | 1 | 10.03 | 44.305 | -9.975 | -8.5905 | 1.1344 | 0.041211
2015-04-30 20:00 | 31.91 | 29.6 | 2.31 | 26.2986 | 14.6246 | 136.4459 | 84.9608 | 5.0392 | 137.9868 | 126.6584 | 0 | 22.2 | 0.8 | 1 | 6.382 | 28.582 | -10.25 | -9.3568 | 1.1374 | 0.026658
2015-04-30 21:00 | 13.67 | 13.5 | 0.17 | 3.1175 | 14.6374 | 151.4474 | 86.8741 | 3.1259 | 152.41 | 137.658 | 0 | 10.125 | 0.8 | 1 | 2.734 | 12.859 | -10.525 | -10.1232 | 1.1405 | 0.012026
2015-04-30 22:00 | 12.9067 | 12.6667 | 0.24 | 0 | 14.6503 | 166.4489 | 88.0349 | 1.9651 | 166.8896 | 145.6708 | 0 | 9.5 | 0.8 | 1 | 2.5813 | 12.0813 | -10.8 | -10.4225 | 1.1417 | 0.01131
2015-04-30 23:00 | 12.1433 | 11.8333 | 0.31 | 0 | 14.6631 | 181.4503 | 88.3662 | 1.6338 | -178.5964 | 148.3379 | 0 | 8.875 | 0.8 | 1 | 2.4287 | 11.3037 | -11.1 | -10.7468 | 1.143 | 0.010594
2015-05-01 | 11.38 | 11 | 0.38 | 0 | 14.6759 | -163.5482 | 87.8454 | 2.1546 | -164.0879 | 144.4349 | 0 | 8.25 | 0.8 | 1 | 2.276 | 10.526 | -10.9 | -10.5711 | 1.1423 | 0.0098594
2015-05-01 01:00 | 24.2133 | 23.7433 | 0.47 | 7.7123 | 14.6888 | -148.5468 | 86.5061 | 3.4939 | -149.623 | 135.6657 | 0 | 17.8075 | 0.8 | 1 | 4.8427 | 22.6502 | -11.3 | -10.5922 | 1.1424 | 0.021217
2015-05-01 02:00 | 37.0467 | 36.4867 | 0.56 | 5.7751 | 14.7016 | -133.5454 | 84.4354 | 5.5646 | -135.2174 | 124.2851 | 0 | 27.365 | 0.8 | 1 | 7.4093 | 34.7743 | -11.2 | -10.1133 | 1.1405 | 0.03252
2015-05-01 03:00 | 49.88 | 49.23 | 0.65 | 4.5381 | 14.7144 | -118.5439 | 81.7651 | 8.2349 | -120.8522 | 111.5877 | 0 | 36.9225 | 0.8 | 1 | 9.976 | 46.8985 | -10.8 | -9.3344 | 1.1373 | 0.043738
2015-05-01 04:00 | 74.88 | 73.1433 | 1.7367 | 8.8338 | 14.7272 | -103.5425 | 78.6621 | 11.3379 | -106.4693 | 98.1886 | 0 | 54.8575 | 0.8 | 1 | 14.976 | 69.8335 | -10.4 | -8.2177 | 1.1329 | 0.064872
2015-05-01 05:00 | 99.88 | 97.0567 | 2.8233 | 11.1404 | 14.74 | -88.5411 | 75.3194 | 14.6806 | -91.9781 | 84.3876 | 1.0895 | 72.7925 | 0.8 | 1 | 19.976 | 93.858 | -10.6 | -7.6669 | 1.1307 | 0.08702
2015-05-01 06:00 | 124.88 | 120.97 | 3.91 | 12.6177 | 14.7527 | -73.5396 | 71.9478 | 18.0522 | -77.2691 | 70.3426 | 4.2445 | 90.7275 | 0.8 | 1 | 24.976 | 119.948 | -10.5 | -6.7516 | 1.127 | 0.11085
2015-05-01 07:00 | 159.2 | 153.9267 | 5.2733 | 14.5626 | 14.7655 | -58.5382 | 68.7698 | 21.2302 | -62.236 | 56.1445 | 8.1128 | 115.445 | 0.8 | 1 | 31.84 | 155.3978 | -10.7 | -5.8438 | 1.1234 | 0.14315
2015-05-01 08:00 | 193.52 | 186.8833 | 6.6367 | 16.3229 | 14.7783 | -43.5368 | 66.0095 | 23.9905 | -46.8036 | 41.8513 | 12.1586 | 140.1625 | 0.8 | 1 | 38.704 | 191.0251 | -10.3 | -4.3305 | 1.1173 | 0.17502
2015-05-01 09:00 | 227.84 | 219.84 | 8 | 18.1704 | 14.7911 | -28.5354 | 63.8785 | 26.1215 | -30.9582 | 27.5089 | 16.1161 | 164.88 | 0.8 | 1 | 45.568 | 226.5641 | -9.7 | -2.6199 | 1.1105 | 0.20631
2015-05-01 10:00 | 237.7567 | 231.5733 | 6.1833 | 13.4156 | 14.8038 | -13.534 | 62.5544 | 27.4456 | -14.7705 | 13.1924 | 13.0616 | 173.68 | 0.8 | 1 | 47.5513 | 234.2929 | -9.8 | -2.4783 | 1.1099 | 0.21324
2015-05-01 11:00 | 247.6733 | 243.3067 | 4.3667 | 9.3488 | 14.8166 | 1.4674 | 62.1547 | 27.8453 | 1.6044 | 2.5719 | 9.3393 | 182.48 | 0.8 | 1 | 49.5347 | 241.354 | -9.85 | -2.3077 | 1.1092 | 0.21953
2015-05-01 12:00 | 257.59 | 255.04 | 2.55 | 5.5627 | 14.8293 | 16.4688 | 62.7155 | 27.2845 | 17.9603 | 15.9772 | 5.3478 | 191.28 | 0.8 | 1 | 51.518 | 248.1458 | -9.9 | -2.1454 | 1.1086 | 0.22557
2015-05-01 13:00 | 231.1533 | 229.3933 | 1.76 | 4.0415 | 14.842 | 31.4702 | 64.1838 | 25.8162 | 34.0963 | 30.3086 | 3.4891 | 172.045 | 0.8 | 1 | 46.2307 | 221.7647 | -9.95 | -3.0199 | 1.1121 | 0.20223
2015-05-01 14:00 | 204.7167 | 203.7467 | 0.97 | 2.4257 | 14.8548 | 46.4716 | 66.4286 | 23.5714 | 49.8712 | 44.6401 | 1.7259 | 152.81 | 0.8 | 1 | 40.9433 | 195.4793 | -10 | -3.8913 | 1.1156 | 0.17882
2015-05-01 15:00 | 178.28 | 178.1 | 0.18 | 0.50837 | 14.8675 | 61.473 | 69.2635 | 20.7365 | 65.2304 | 58.911 | 0.26251 | 133.575 | 0.8 | 1 | 35.656 | 169.4935 | -9.8 | -4.5033 | 1.118 | 0.15539
2015-05-01 16:00 | 142.0067 | 141.4467 | 0.56 | 1.8595 | 14.8802 | 76.4744 | 72.4728 | 17.5272 | 80.2004 | 73.074 | 0.54136 | 106.085 | 0.8 | 1 | 28.4013 | 135.0277 | -10.4 | -6.1804 | 1.1247 | 0.12453
2015-05-01 17:00 | 105.7333 | 104.7933 | 0.94 | 3.8402 | 14.8929 | 91.4758 | 75.8312 | 14.1688 | 94.8638 | 87.0655 | 0.1966 | 78.595 | 0.8 | 1 | 21.1467 | 99.9383 | -10.2 | -7.0769 | 1.1283 | 0.092464
2015-05-01 18:00 | 69.46 | 68.14 | 1.32 | 6.9919 | 14.9056 | 106.4771 | 79.1179 | 10.8821 | 109.3288 | 100.7833 | 0 | 51.105 | 0.8 | 1 | 13.892 | 64.997 | -10.7 | -8.6688 | 1.1347 | 0.060475
2015-05-01 19:00 | 51.6833 | 50.55 | 1.1333 | 8.2714 | 14.9183 | 121.4785 | 82.1247 | 7.8753 | 123.7018 | 114.0473 | 0 | 37.9125 | 0.8 | 1 | 10.3367 | 48.2492 | -11 | -9.4922 | 1.138 | 0.045023
2015-05-01 20:00 | 33.9067 | 32.96 | 0.94667 | 10.1782 | 14.931 | 136.4799 | 84.6633 | 5.3367 | 138.0674 | 126.5102 | 0 | 24.72 | 0.8 | 1 | 6.7813 | 31.5013 | -11.3 | -10.3156 | 1.1413 | 0.02948
2015-05-01 21:00 | 16.13 | 15.37 | 0.76 | 12.7145 | 14.9437 | 151.4812 | 86.5731 | 3.4269 | 152.4756 | 137.4547 | 0 | 11.5275 | 0.8 | 1 | 3.226 | 14.7535 | -11.4 | -10.939 | 1.1438 | 0.013837
2015-05-01 22:00 | 17.47 | 15.0567 | 2.4133 | 0 | 14.9564 | 166.4826 | 87.7309 | 2.2691 | 166.9383 | 145.4025 | 0 | 11.2925 | 0.8 | 1 | 3.494 | 14.7865 | -11.1667 | -10.7046 | 1.1428 | 0.013857
2015-05-01 23:00 | 18.81 | 14.7433 | 4.0667 | 0 | 14.969 | 181.4839 | 88.0601 | 1.9399 | -178.5656 | 148.0308 | 0 | 11.0575 | 0.8 | 1 | 3.762 | 14.8195 | -10.9333 | -10.4702 | 1.1419 | 0.013876
2015-05-02 | 20.15 | 14.43 | 5.72 | 0 | 14.9817 | -163.5147 | 87.5382 | 2.4618 | -164.0751 | 144.1491 | 0 | 10.8225 | 0.8 | 1 | 4.03 | 14.8525 | -10.7 | -10.2359 | 1.1409 | 0.013896
2015-05-02 01:00 | 40.7767 | 28.2 | 12.5767 | 189.7124 | 14.9943 | -148.5134 | 86.1989 | 3.8011 | -149.6269 | 135.4284 | 0 | 21.15 | 0.8 | 1 | 8.1553 | 29.3053 | -10.6 | -9.6842 | 1.1387 | 0.027364
2015-05-02 02:00 | 61.4033 | 41.97 | 19.4333 | 189.9806 | 15.007 | -133.512 | 84.1289 | 5.8711 | -135.2359 | 124.0916 | 0 | 31.4775 | 0.8 | 1 | 12.2807 | 43.7582 | -10.4 | -9.0326 | 1.1361 | 0.040766
2015-05-02 03:00 | 82.03 | 55.74 | 26.29 | 177.0295 | 15.0196 | -118.5107 | 81.4596 | 8.5404 | -120.8822 | 111.4277 | 0 | 41.805 | 0.8 | 1 | 16.406 | 58.211 | -10.2 | -8.3809 | 1.1335 | 0.054107
2015-05-02 04:00 | 107.9033 | 76.59 | 31.3133 | 155.1687 | 15.0322 | -103.5094 | 78.3576 | 11.6424 | -106.5071 | 98.0539 | 0 | 57.4425 | 0.8 | 1 | 21.5807 | 79.0232 | -9.9 | -7.4305 | 1.1297 | 0.073205
2015-05-02 05:00 | 133.7767 | 97.44 | 36.3367 | 140.5354 | 15.0449 | -88.508 | 75.0154 | 14.9846 | -92.0196 | 84.2725 | 14.0252 | 73.08 | 0.8 | 1 | 26.7553 | 113.8605 | -9.4 | -5.8419 | 1.1234 | 0.10488
2015-05-02 06:00 | 159.65 | 118.29 | 41.36 | 131.3339 | 15.0575 | -73.5067 | 71.6439 | 18.3561 | -77.3095 | 70.2429 | 44.3952 | 88.7175 | 0.8 | 1 | 31.93 | 165.0427 | -8.95 | -3.7924 | 1.1152 | 0.15092
2015-05-02 07:00 | 215.1833 | 142.76 | 72.4233 | 197.3036 | 15.0701 | -58.5054 | 68.4653 | 21.5347 | -62.2702 | 56.057 | 110.1679 | 107.07 | 0.8 | 1 | 43.0367 | 260.2746 | -8.5 | -0.36642 | 1.1015 | 0.23508
2015-05-02 08:00 | 270.7167 | 167.23 | 103.4867 | 251.518 | 15.0827 | -43.5041 | 65.7041 | 24.2959 | -46.8262 | 41.773 | 187.5797 | 125.4225 | 0.8 | 1 | 54.1433 | 367.1456 | -8.6 | 2.8733 | 1.0885 | 0.32771
2015-05-02 09:00 | 326.25 | 191.7 | 134.55 | 302.3178 | 15.0953 | -28.5028 | 63.5727 | 26.4273 | -30.964 | 27.4347 | 268.3181 | 143.775 | 0.8 | 1 | 65.25 | 477.3431 | -8.4 | 6.517 | 1.0739 | 0.42036
2015-05-02 10:00 | 310.96 | 191.1933 | 119.7667 | 257.2147 | 15.1079 | -13.5014 | 62.2491 | 27.7509 | -14.7555 | 13.1055 | 250.5154 | 143.395 | 0.8 | 1 | 62.192 | 456.1024 | -8.2 | 6.0532 | 1.0758 | 0.40235
2015-05-02 11:00 | 295.67 | 190.6867 | 104.9833 | 222.5331 | 15.1204 | 1.4999 | 61.8511 | 28.1489 | 1.6422 | 2.3422 | 222.3471 | 143.015 | 0.8 | 1 | 59.134 | 424.4961 | -7.7 | 5.5655 | 1.0777 | 0.37515
2015-05-02 12:00 | 280.38 | 190.18 | 90.2 | 194.7882 | 15.133 | 16.5012 | 62.4148 | 27.5852 | 18.0201 | 15.9586 | 187.2812 | 142.635 | 0.8 | 1 | 56.076 | 385.9922 | -7.7 | 4.3623 | 1.0826 | 0.34264
2015-05-02 13:00 | 244.8333 | 174.7833 | 70.05 | 159.1526 | 15.1456 | 31.5025 | 63.887 | 26.113 | 34.1749 | 30.2968 | 137.4162 | 131.0875 | 0.8 | 1 | 48.9667 | 317.4703 | -7.5 | 2.4209 | 1.0903 | 0.28384
2015-05-02 14:00 | 209.2867 | 159.3867 | 49.9 | 123.3399 | 15.1581 | 46.5037 | 66.1356 | 23.8644 | 49.9638 | 44.6227 | 87.7869 | 119.54 | 0.8 | 1 | 41.8573 | 249.1843 | -7.4 | 0.38701 | 1.0985 | 0.22445
2015-05-02 15:00 | 173.74 | 143.99 | 29.75 | 82.9164 | 15.1707 | 61.505 | 68.9738 | 21.0262 | 65.3316 | 58.8834 | 42.8496 | 107.9925 | 0.8 | 1 | 34.748 | 185.5901 | -7.3 | -1.5003 | 1.106 | 0.16832
2015-05-02 16:00 | 137.4667 | 110.3533 | 27.1133 | 88.6216 | 15.1832 | 76.5063 | 72.185 | 17.815 | 80.3051 | 73.0331 | 25.8615 | 82.765 | 0.8 | 1 | 27.4933 | 136.1199 | -7.3 | -3.0463 | 1.1122 | 0.12414
2015-05-02 17:00 | 101.1933 | 76.7167 | 24.4767 | 98.0479 | 15.1958 | 91.5076 | 75.5438 | 14.4562 | 94.9674 | 87.0075 | 5.1186 | 57.5375 | 0.8 | 1 | 20.2387 | 82.8948 | -7.1 | -4.5095 | 1.118 | 0.075997
2015-05-02 18:00 | 64.92 | 43.08 | 21.84 | 112.7333 | 15.2083 | 106.5089 | 78.8294 | 11.1706 | 109.4272 | 100.7034 | 0 | 32.31 | 0.8 | 1 | 12.984 | 45.294 | -7.3 | -5.8846 | 1.1235 | 0.041729
2015-05-02 19:00 | 47.5067 | 32.2867 | 15.22 | 107.1495 | 15.2208 | 121.5101 | 81.8338 | 8.1662 | 123.7914 | 113.9383 | 0 | 24.215 | 0.8 | 1 | 9.5013 | 33.7163 | -7.6 | -6.5464 | 1.1262 | 0.031136
2015-05-02 20:00 | 30.0933 | 21.4933 | 8.6 | 87.6522 | 15.2333 | 136.5114 | 84.3694 | 5.6306 | 138.1449 | 126.3614 | 0 | 16.12 | 0.8 | 1 | 6.0187 | 22.1387 | -8 | -7.3082 | 1.1292 | 0.0205
2015-05-02 21:00 | 12.68 | 10.7 | 1.98 | 30.4849 | 15.2459 | 151.5127 | 86.276 | 3.724 | 152.5385 | 137.2519 | 0 | 8.025 | 0.8 | 1 | 2.536 | 10.561 | -8.4 | -8.07 | 1.1323 | 0.0098056
2015-05-02 22:00 | 13.94 | 10.3567 | 3.5833 | 0 | 15.2584 | 166.5139 | 87.431 | 2.569 | 166.9845 | 145.1366 | 0 | 7.7675 | 0.8 | 1 | 2.788 | 10.5555 | -9.1 | -8.7701 | 1.1351 | 0.0098247
2015-05-02 23:00 | 15.2 | 10.0133 | 5.1867 | 0 | 15.2708 | 181.5152 | 87.7581 | 2.2419 | -178.5372 | 147.7279 | 0 | 7.51 | 0.8 | 1 | 3.04 | 10.55 | -9.4 | -9.0703 | 1.1363 | 0.00983
2015-05-03 | 16.46 | 9.67 | 6.79 | 0 | 15.2833 | -163.4836 | 87.2352 | 2.7648 | -164.0645 | 143.8677 | 0 | 7.2525 | 0.8 | 1 | 3.292 | 10.5445 | -9.5 | -9.1705 | 1.1367 | 0.0098283
2015-05-03 01:00 | 40.3433 | 17.9167 | 22.4267 | 313.3637 | 15.2958 | -148.4823 | 85.896 | 4.104 | -149.6328 | 135.195 | 0 | 13.4375 | 0.8 | 1 | 8.0687 | 21.5062 | -9.9 | -9.2279 | 1.1369 | 0.02005
2015-05-03 02:00 | 64.2267 | 26.1633 | 38.0633 | 353.9624 | 15.3083 | -133.4811 | 83.8268 | 6.1732 | -135.2561 | 123.9017 | 0 | 19.6225 | 0.8 | 1 | 12.8453 | 32.4678 | -9.8 | -8.7854 | 1.1351 | 0.030222
2015-05-03 03:00 | 88.11 | 34.41 | 53.7 | 349.3836 | 15.3207 | -118.4798 | 81.1586 | 8.8414 | -120.9137 | 111.2711 | 0 | 25.8075 | 0.8 | 1 | 17.622 | 43.4295 | -10.2 | -8.8428 | 1.1354 | 0.040433
2015-05-03 04:00 | 145.9367 | 45.4833 | 100.4533 | 485.4536 | 15.3332 | -103.4786 | 78.0577 | 11.9423 | -106.5465 | 97.9227 | 0 | 34.1125 | 0.8 | 1 | 29.1873 | 63.2998 | -10.2 | -8.2219 | 1.1329 | 0.058804
2015-05-03 05:00 | 203.7633 | 56.5567 | 147.2067 | 558.4412 | 15.3457 | -88.4774 | 74.7161 | 15.2839 | -92.0625 | 84.1609 | 56.8132 | 42.4175 | 0.8 | 1 | 40.7527 | 139.9834 | -10 | -5.6255 | 1.1225 | 0.12885
2015-05-03 06:00 | 261.59 | 67.63 | 193.96 | 606.3559 | 15.3581 | -73.4762 | 71.3444 | 18.6556 | -77.3515 | 70.147 | 205.9234 | 50.7225 | 0.8 | 1 | 52.318 | 308.9639 | -9.6 | 0.055122 | 1.0998 | 0.27863
2015-05-03 07:00 | 304.78 | 78.5233 | 226.2567 | 608.3294 | 15.3705 | -58.4749 | 68.1652 | 21.8348 | -62.3062 | 55.9737 | 340.4052 | 58.8925 | 0.8 | 1 | 60.956 | 460.2537 | -9.1 | 5.2829 | 1.0789 | 0.40717
2015-05-03 08:00 | 347.97 | 89.4167 | 258.5533 | 621.1809 | 15.383 | -43.4737 | 65.4033 | 24.5967 | -46.8507 | 41.6992 | 463.8029 | 67.0625 | 0.8 | 1 | 69.594 | 600.4594 | -9 | 9.7644 | 1.0609 | 0.52238
2015-05-03 09:00 | 391.16 | 100.31 | 290.85 | 646.6689 | 15.3954 | -28.4725 | 63.2713 | 26.7287 | -30.972 | 27.3663 | 574.2975 | 75.2325 | 0.8 | 1 | 78.232 | 727.762 | -8.7 | 14.0426 | 1.0438 | 0.62292
2015-05-03 10:00 | 397.79 | 100.5467 | 297.2433 | 632.0645 | 15.4078 | -13.4713 | 61.9479 | 28.0521 | -14.7429 | 13.028 | 615.7951 | 75.41 | 0.8 | 1 | 79.558 | 770.7631 | -8.4 | 15.6863 | 1.0373 | 0.65557
2015-05-03 11:00 | 404.42 | 100.7833 | 303.6367 | 637.3989 | 15.4202 | 1.5299 | 61.5515 | 28.4485 | 1.6774 | 2.1331 | 636.9572 | 75.5875 | 0.8 | 1 | 80.884 | 793.4287 | -8.9 | 15.8946 | 1.0364 | 0.67431
2015-05-03 12:00 | 411.05 | 101.02 | 310.03 | 662.9523 | 15.4326 | 16.5311 | 62.1181 | 27.8819 | 18.0772 | 15.9438 | 637.4496 | 75.765 | 0.8 | 1 | 82.21 | 795.4246 | -8 | 16.857 | 1.0326 | 0.67349
2015-05-03 13:00 | 372.9433 | 98.2933 | 274.65 | 617.5657 | 15.445 | 31.5323 | 63.5939 | 26.4061 | 34.2506 | 30.2859 | 533.2802 | 73.72 | 0.8 | 1 | 74.5887 | 681.5888 | -7.8 | 13.4997 | 1.046 | 0.58461
2015-05-03 14:00 | 334.8367 | 95.5667 | 239.27 | 584.7484 | 15.4574 | 46.5335 | 65.8464 | 24.1536 | 50.0534 | 44.6051 | 416.3192 | 71.675 | 0.8 | 1 | 66.9673 | 554.9616 | -8 | 9.3425 | 1.0626 | 0.48357
2015-05-03 15:00 | 296.73 | 92.84 | 203.89 | 560.9818 | 15.4697 | 61.5347 | 68.6876 | 21.3124 | 65.4297 | 58.8553 | 290.1405 | 69.63 | 0.8 | 1 | 59.346 | 419.1165 | -7.9 | 5.1974 | 1.0792 | 0.3709
2015-05-03 16:00 | 241.9933 | 79.1167 | 162.8767 | 524.2847 | 15.4821 | 76.5359 | 71.9007 | 18.0993 | 80.4066 | 72.9912 | 153.3627 | 59.3375 | 0.8 | 1 | 48.3987 | 261.0988 | -7.9 | 0.25934 | 1.099 | 0.23529
2015-05-03 17:00 | 187.2567 | 65.3933 | 121.8633 | 478.9579 | 15.4945 | 91.537 | 75.2599 | 14.7401 | 95.0679 | 86.9485 | 25.4968 | 49.045 | 0.8 | 1 | 37.4513 | 111.9931 | -8 | -4.5002 | 1.118 | 0.10267
2015-05-03 18:00 | 132.52 | 51.67 | 80.85 | 407.0832 | 15.5068 | 106.5382 | 78.5444 | 11.4556 | 109.5225 | 100.6224 | 0 | 38.7525 | 0.8 | 1 | 26.504 | 65.2565 | -8.2 | -6.1607 | 1.1246 | 0.06018
2015-05-03 19:00 | 98.33 | 40.3433 | 57.9867 | 394.4556 | 15.5192 | 121.5394 | 81.5466 | 8.4534 | 123.8779 | 113.8283 | 0 | 30.2575 | 0.8 | 1 | 19.666 | 49.9235 | -9 | -7.4399 | 1.1298 | 0.046249
2015-05-03 20:00 | 64.14 | 29.0167 | 35.1233 | 340.4962 | 15.5315 | 136.5405 | 84.0792 | 5.9208 | 138.2196 | 126.2121 | 0 | 21.7625 | 0.8 | 1 | 12.828 | 34.5905 | -8.8923 | -7.8114 | 1.1312 | 0.032087
2015-05-03 21:00 | 29.95 | 17.69 | 12.26 | 175.001 | 15.5439 | 151.5417 | 85.9828 | 4.0172 | 152.5986 | 137.0496 | 0 | 13.2675 | 0.8 | 1 | 5.99 | 19.2575 | -8.7846 | -8.1828 | 1.1327 | 0.017887
2015-05-03 22:00 | 27.2067 | 16.1933 | 11.0133 | 0 | 15.5562 | 166.5429 | 87.135 | 2.865 | 167.0281 | 144.873 | 0 | 12.145 | 0.8 | 1 | 5.4413 | 17.5863 | -8.6769 | -8.1274 | 1.1325 | 0.016332
2015-05-03 23:00 | 24.4633 | 14.6967 | 9.7667 | 0 | 15.5685 | 181.544 | 87.4603 | 2.5397 | -178.5112 | 147.4292 | 0 | 11.0225 | 0.8 | 1 | 4.8927 | 15.9152 | -8.5692 | -8.0719 | 1.1323 | 0.014777
2015-05-04 | 21.72 | 13.2 | 8.52 | 159.4268 | 15.5808 | -163.4548 | 86.9366 | 3.0634 | -164.0559 | 143.5908 | 0 | 9.9 | 0.8 | 1 | 4.344 | 14.244 | -8.4615 | -8.0164 | 1.1321 | 0.013223
2015-05-04 01:00 | 45.0767 | 21.6433 | 23.4333 | 305.2701 | 15.5931 | -148.4537 | 85.5975 | 4.4025 | -149.6406 | 134.9656 | 0 | 16.2325 | 0.8 | 1 | 9.0153 | 25.2478 | -8.3538 | -7.5649 | 1.1303 | 0.0234
2015-05-04 02:00 | 68.4333 | 30.0867 | 38.3467 | 340.2621 | 15.6054 | -133.4525 | 83.5292 | 6.4708 | -135.2781 | 123.7154 | 0 | 22.565 | 0.8 | 1 | 13.6867 | 36.2517 | -8.2462 | -7.1133 | 1.1285 | 0.033545
2015-05-04 03:00 | 91.79 | 38.53 | 53.26 | 335.3715 | 15.6177 | -118.4514 | 80.8622 | 9.1378 | -120.9469 | 111.1181 | 0 | 28.8975 | 0.8 | 1 | 18.358 | 47.2555 | -8.1385 | -6.6617 | 1.1266 | 0.043657
2015-05-04 04:00 | 134.4867 | 51.24 | 83.2467 | 392.7341 | 15.63 | -103.4503 | 77.7624 | 12.2376 | -106.5873 | 97.795 | 0 | 38.43 | 0.8 | 1 | 26.8973 | 65.3273 | -8.0308 | -5.9893 | 1.124 | 0.060209
2015-05-04 05:00 | 177.1833 | 63.95 | 113.2333 | 421.6292 | 15.6422 | -88.4491 | 74.4213 | 15.5787 | -92.107 | 84.0529 | 43.6848 | 47.9625 | 0.8 | 1 | 35.4367 | 127.084 | -7.9231 | -3.9517 | 1.1158 | 0.11628
2015-05-04 06:00 | 219.88 | 76.66 | 143.22 | 441.0184 | 15.6545 | -73.448 | 71.0497 | 18.9503 | -77.3952 | 70.0549 | 150.4403 | 57.495 | 0.8 | 1 | 43.976 | 251.9113 | -7.8154 | 0.056842 | 1.0998 | 0.22718
2015-05-04 07:00 | 243.2133 | 102.9033 | 140.31 | 372.4594 | 15.6668 | -58.4469 | 67.8698 | 22.1302 | -62.3439 | 55.8944 | 208.8454 | 77.1775 | 0.8 | 1 | 48.6427 | 334.6656 | -7.7077 | 2.7506 | 1.089 | 0.29885
2015-05-04 08:00 | 266.5467 | 129.1467 | 137.4 | 326.4236 | 15.679 | -43.4458 | 65.107 | 24.893 | -46.8772 | 41.6302 | 243.9848 | 96.86 | 0.8 | 1 | 53.3093 | 394.1541 | -7.6 | 4.7173 | 1.0811 | 0.34943
2015-05-04 09:00 | 289.88 | 155.39 | 134.49 | 295.9795 | 15.6913 | -28.4447 | 62.9743 | 27.0257 | -30.9821 | 27.3037 | 263.0037 | 116.5425 | 0.8 | 1 | 57.976 | 437.5222 | -7.3 | 6.3726 | 1.0745 | 0.3855
2015-05-04 10:00 | 319.7633 | 144.9167 | 174.8467 | 368.2233 | 15.7035 | -13.4436 | 61.6512 | 28.3488 | -14.7326 | 12.9599 | 358.8437 | 108.6875 | 0.8 | 1 | 63.9527 | 531.4838 | -7 | 9.6089 | 1.0616 | 0.46265
2015-05-04 11:00 | 349.6467 | 134.4433 | 215.2033 | 447.5066 | 15.7157 | 1.5575 | 61.2562 | 28.7438 | 1.7101 | 1.949 | 447.2477 | 100.8325 | 0.8 | 1 | 69.9293 | 618.0095 | -5.4 | 13.9128 | 1.0443 | 0.52924
2015-05-04 12:00 | 379.53 | 123.97 | 255.56 | 541.2583 | 15.728 | 16.5586 | 61.8255 | 28.1745 | 18.1315 | 15.9326 | 520.4659 | 92.9775 | 0.8 | 1 | 75.906 | 689.3494 | -4.4 | 17.1422 | 1.0314 | 0.58303
2015-05-04 13:00 | 367.5933 | 111.79 | 255.8033 | 569.4087 | 15.7402 | 31.5597 | 63.3048 | 26.6952 | 34.3234 | 30.2758 | 491.7461 | 83.8425 | 0.8 | 1 | 73.5187 | 649.1072 | -4 | 16.2846 | 1.0349 | 0.55082
2015-05-04 14:00 | 355.6567 | 99.61 | 256.0467 | 618.8803 | 15.7524 | 46.5608 | 65.5609 | 24.4391 | 50.1399 | 44.5874 | 440.7542 | 74.7075 | 0.8 | 1 | 71.1313 | 586.593 | -4.4 | 13.931 | 1.0443 | 0.5023
2015-05-04 15:00 | 343.72 | 87.43 | 256.29 | 696.3636 | 15.7646 | 61.5619 | 68.4052 | 21.5948 | 65.5247 | 58.8265 | 360.4597 | 65.5725 | 0.8 | 1 | 68.744 | 494.7762 | -4.5 | 10.9618 | 1.0562 | 0.4285
2015-05-04 16:00 | 271.2733 | 74.6367 | 196.6367 | 623.6166 | 15.7768 | 76.563 | 71.6201 | 18.3799 | 80.505 | 72.9485 | 182.8635 | 55.9775 | 0.8 | 1 | 54.2547 | 293.0957 | -4.6 | 4.5592 | 1.0818 | 0.25999
2015-05-04 17:00 | 198.8267 | 61.8433 | 136.9833 | 528.5627 | 15.7889 | 91.5641 | 74.9797 | 15.0203 | 95.1651 | 86.8885 | 28.6902 | 46.3825 | 0.8 | 1 | 39.7653 | 114.8381 | -4.7 | -1.1113 | 1.1044 | 0.104
2015-05-04 18:00 | 126.38 | 49.05 | 77.33 | 380.1539 | 15.8011 | 106.5651 | 78.2631 | 11.7369 | 109.6146 | 100.5405 | 0 | 36.7875 | 0.8 | 1 | 25.276 | 62.0635 | -5 | -3.0605 | 1.1122 | 0.056604
2015-05-04 19:00 | 96.7 | 39.18 | 57.52 | 378.6792 | 15.8133 | 121.5662 | 81.2632 | 8.7368 | 123.9613 | 113.7176 | 0 | 29.385 | 0.8 | 1 | 19.34 | 48.725 | -5.3 | -3.7773 | 1.1151 | 0.044554
2015-05-04 20:00 | 67.02 | 29.31 | 37.71 | 348.7707 | 15.8254 | 136.5673 | 83.7929 | 6.2071 | 138.2912 | 126.0625 | 0 | 21.9825 | 0.8 | 1 | 13.404 | 35.3865 | -6.8 | -5.6942 | 1.1228 | 0.03258
2015-05-04 21:00 | 37.34 | 19.44 | 17.9 | 238.3732 | 15.8376 | 151.5683 | 85.6935 | 4.3065 | 152.6559 | 136.8479 | 0 | 14.58 | 0.8 | 1 | 7.468 | 22.048 | -7.8 | -7.111 | 1.1284 | 0.020402
2015-05-04 22:00 | 30.8333 | 16.5767 | 14.2567 | 258.8877 | 15.8497 | 166.5694 | 86.8432 | 3.1568 | 167.069 | 144.6119 | 0 | 12.4325 | 0.8 | 1 | 6.1667 | 18.5992 | -7.6 | -7.0188 | 1.1281 | 0.017205
2015-05-04 23:00 | 24.3267 | 13.7133 | 10.6133 | 0 | 15.8619 | 181.5704 | 87.1668 | 2.8332 | -178.4875 | 147.1349 | 0 | 10.285 | 0.8 | 1 | 4.8653 | 15.1503 | -8 | -7.5266 | 1.1301 | 0.01404
2015-05-05 | 17.82 | 10.85 | 6.97 | 119.0055 | 15.874 | -163.4285 | 86.6423 | 3.3577 | -164.0495 | 143.3186 | 0 | 8.1375 | 0.8 | 1 | 3.564 | 11.7015 | -7.5 | -7.1343 | 1.1285 | 0.010829
2015-05-05 01:00 | 33.7467 | 17.3 | 16.4467 | 200.8705 | 15.8861 | -148.4275 | 85.3035 | 4.6965 | -149.6502 | 134.7403 | 0 | 12.975 | 0.8 | 1 | 6.7493 | 19.7243 | -6.8 | -6.1836 | 1.1247 | 0.018191
2015-05-05 02:00 | 49.6733 | 23.75 | 25.9233 | 220.1053 | 15.8983 | -133.4264 | 83.2362 | 6.7638 | -135.3017 | 123.5329 | 0 | 17.8125 | 0.8 | 1 | 9.9347 | 27.7472 | -6.9 | -6.0329 | 1.1241 | 0.025577
2015-05-05 03:00 | 65.6 | 30.2 | 35.4 | 216.0725 | 15.9104 | -118.4254 | 80.5705 | 9.4295 | -120.9816 | 110.9687 | 0 | 22.65 | 0.8 | 1 | 13.12 | 35.77 | -6.7 | -5.5822 | 1.1223 | 0.032919
2015-05-05 04:00 | 106.2667 | 52.4267 | 53.84 | 248.2007 | 15.9225 | -103.4244 | 77.4717 | 12.5283 | -106.6297 | 97.6708 | 0 | 39.32 | 0.8 | 1 | 21.2533 | 60.5733 | -6.4 | -4.5071 | 1.118 | 0.055533
2015-05-05 05:00 | 146.9333 | 74.6533 | 72.28 | 264.3422 | 15.9346 | -88.4233 | 74.1313 | 15.8687 | -92.1531 | 83.9486 | 27.8671 | 55.99 | 0.8 | 1 | 29.3867 | 113.2437 | -6.1 | -2.5611 | 1.1102 | 0.1031
2015-05-05 06:00 | 187.6 | 96.88 | 90.72 | 275.2995 | 15.9466 | -73.4223 | 70.7596 | 19.2404 | -77.4404 | 69.9665 | 94.309 | 72.66 | 0.8 | 1 | 37.52 | 204.489 | -5.7 | 0.69028 | 1.0972 | 0.18399
2015-05-05 07:00 | 187.3233 | 106.1367 | 81.1867 | 212.8608 | 15.9587 | -58.4213 | 67.5791 | 22.4209 | -62.3834 | 55.8192 | 119.5864 | 79.6025 | 0.8 | 1 | 37.4647 | 236.6536 | -5.6 | 1.7954 | 1.0928 | 0.21207
2015-05-05 08:00 | 187.0467 | 115.3933 | 71.6533 | 168.3831 | 15.9708 | -43.4203 | 64.8153 | 25.1847 | -46.9057 | 41.5657 | 125.9834 | 86.545 | 0.8 | 1 | 37.4093 | 249.9377 | -4.9 | 2.9106 | 1.0884 | 0.22306
2015-05-05 09:00 | 186.77 | 124.65 | 62.12 | 135.3584 | 15.9829 | -28.4193 | 62.6819 | 27.3181 | -30.9944 | 27.2469 | 120.3393 | 93.4875 | 0.8 | 1 | 37.354 | 251.1808 | -5.2 | 2.6494 | 1.0894 | 0.22438
2015-05-05 10:00 | 173.8833 | 126.43 | 47.4533 | 99.0008 | 15.9949 | -13.4183 | 61.3588 | 28.6412 | -14.7247 | 12.9011 | 96.5017 | 94.8225 | 0.8 | 1 | 34.7767 | 226.1009 | -4.4 | 2.6657 | 1.0893 | 0.20197
2015-05-05 11:00 | 160.9967 | 128.21 | 32.7867 | 67.5538 | 16.007 | 1.5827 | 60.9651 | 29.0349 | 1.7401 | 1.7956 | 67.5206 | 96.1575 | 0.8 | 1 | 32.1993 | 195.8774 | -3.8 | 2.3212 | 1.0907 | 0.17519
2015-05-05 12:00 | 148.11 | 129.99 | 18.12 | 38.02 | 16.019 | 16.5837 | 61.537 | 28.463 | 18.183 | 15.9249 | 36.5608 | 97.4925 | 0.8 | 1 | 29.622 | 163.6753 | -3.7 | 1.4149 | 1.0943 | 0.14688
2015-05-05 13:00 | 182.0733 | 147.32 | 34.7533 | 76.6025 | 16.031 | 31.5847 | 63.0197 | 26.9803 | 34.3933 | 30.2665 | 66.1608 | 110.49 | 0.8 | 1 | 36.4147 | 213.0655 | -3.9 | 2.7583 | 1.089 | 0.19026
2015-05-05 14:00 | 216.0367 | 164.65 | 51.3867 | 122.8771 | 16.0431 | 46.5857 | 65.2793 | 24.7207 | 50.2234 | 44.5695 | 87.5377 | 123.4875 | 0.8 | 1 | 43.2073 | 254.2325 | -3.4 | 4.5448 | 1.0818 | 0.22553
2015-05-05 15:00 | 250 | 181.98 | 68.02 | 182.575 | 16.0551 | 61.5867 | 68.1265 | 21.8735 | 65.6165 | 58.797 | 94.5869 | 136.485 | 0.8 | 1 | 50 | 281.0719 | -3.6 | 5.1835 | 1.0793 | 0.24875
2015-05-05 16:00 | 189.8867 | 132.7767 | 57.11 | 178.5245 | 16.0671 | 76.5877 | 71.3431 | 18.6569 | 80.6002 | 72.9049 | 52.4788 | 99.5825 | 0.8 | 1 | 37.9773 | 190.0386 | -3.8 | 2.1387 | 1.0914 | 0.17008
2015-05-05 17:00 | 129.7733 | 83.5733 | 46.2 | 175.1184 | 16.0791 | 91.5886 | 74.7031 | 15.2969 | 95.2591 | 86.8275 | 9.6916 | 62.68 | 0.8 | 1 | 25.9547 | 98.3262 | -3.6 | -0.52731 | 1.1021 | 0.08886
2015-05-05 18:00 | 69.66 | 34.37 | 35.29 | 169.534 | 16.0911 | 106.5896 | 77.9855 | 12.0145 | 109.7035 | 100.4576 | 0 | 25.7775 | 0.8 | 1 | 13.932 | 39.7095 | -3.9 | -2.6591 | 1.1106 | 0.036164
2015-05-05 19:00 | 50.88 | 26.31 | 24.57 | 156.7771 | 16.1031 | 121.5906 | 80.9835 | 9.0165 | 124.0416 | 113.6061 | 0 | 19.7325 | 0.8 | 1 | 10.176 | 29.9085 | -3.8 | -2.8654 | 1.1115 | 0.027259
2015-05-05 20:00 | 32.1 | 18.25 | 13.85 | 122.5432 | 16.115 | 136.5915 | 83.5105 | 6.4895 | 138.3599 | 125.9127 | 0 | 13.6875 | 0.8 | 1 | 6.42 | 20.1075 | -3.7 | -3.0716 | 1.1123 | 0.01834
2015-05-05 21:00 | 13.32 | 10.19 | 3.13 | 39.0979 | 16.127 | 151.5925 | 85.4082 | 4.5918 | 152.7103 | 136.647 | 0 | 7.6425 | 0.8 | 1 | 2.664 | 10.3065 | -4.8 | -4.4779 | 1.1179 | 0.0094478
2015-05-05 22:00 | 15.25 | 12.76 | 2.49 | 41.4445 | 16.139 | 166.5935 | 86.5556 | 3.4444 | 167.1074 | 144.3535 | 0 | 9.57 | 0.8 | 1 | 3.05 | 12.62 | -4.6 | -4.2056 | 1.1168 | 0.011557
2015-05-05 23:00 | 17.18 | 15.33 | 1.85 | 33.9641 | 16.1509 | 181.5944 | 86.8776 | 3.1224 | -178.4663 | 146.8451 | 0 | 11.4975 | 0.8 | 1 | 3.436 | 14.9335 | -4 | -3.5333 | 1.1141 | 0.013643
2015-05-06 | 19.11 | 17.9 | 1.21 | 19.0203 | 16.1629 | -163.4047 | 86.3526 | 3.6474 | -164.0452 | 143.051 | 0 | 13.425 | 0.8 | 1 | 3.822 | 17.247 | -3.6 | -3.061 | 1.1122 | 0.01573
2015-05-06 01:00 | 31.22 | 28.29 | 2.93 | 33.7134 | 16.1748 | -148.4037 | 85.0142 | 4.9858 | -149.6618 | 134.5192 | 0 | 21.2175 | 0.8 | 1 | 6.244 | 27.4615 | -3.5 | -2.6418 | 1.1106 | 0.025008
2015-05-06 02:00 | 43.33 | 38.68 | 4.65 | 37.8751 | 16.1867 | -133.4028 | 82.9479 | 7.0521 | -135.3271 | 123.3542 | 0 | 29.01 | 0.8 | 1 | 8.666 | 37.676 | -3.5 | -2.3226 | 1.1093 | 0.034271
2015-05-06 03:00 | 55.44 | 49.07 | 6.37 | 37.7431 | 16.1987 | -118.4018 | 80.2835 | 9.7165 | -121.018 | 110.8229 | 0 | 36.8025 | 0.8 | 1 | 11.088 | 47.8905 | -3.2 | -1.7034 | 1.1068 | 0.043465
2015-05-06 04:00 | 79.9167 | 71.28 | 8.6367 | 38.9411 | 16.2106 | -103.4009 | 77.1859 | 12.8141 | -106.6736 | 97.5503 | 0 | 53.46 | 0.8 | 1 | 15.9833 | 69.4433 | -3.1 | -0.9299 | 1.1037 | 0.06285
2015-05-06 05:00 | 104.3933 | 93.49 | 10.9033 | 39.19 | 16.2225 | -88.4 | 73.8461 | 16.1539 | -92.2007 | 83.848 | 4.1999 | 70.1175 | 0.8 | 1 | 20.8787 | 95.196 | -2.9 | 0.074876 | 1.0997 | 0.085843
2015-05-06 06:00 | 128.87 | 115.7 | 13.17 | 39.4043 | 16.2344 | -73.3991 | 70.4744 | 19.5256 | -77.4872 | 69.882 | 13.5533 | 86.775 | 0.8 | 1 | 25.774 | 126.1023 | -2.5 | 1.4407 | 1.0942 | 0.11315
2015-05-06 07:00 | 165.5 | 151.0133 | 14.4867 | 37.5287 | 16.2463 | -58.3982 | 67.2932 | 22.7068 | -62.4246 | 55.7482 | 21.1224 | 113.26 | 0.8 | 1 | 33.1 | 167.4824 | -2.9 | 2.3338 | 1.0907 | 0.14979
2015-05-06 08:00 | 202.13 | 186.3267 | 15.8033 | 36.7465 | 16.2582 | -43.3972 | 64.5284 | 25.4716 | -46.936 | 41.5059 | 27.519 | 139.745 | 0.8 | 1 | 40.426 | 207.69 | -2.3 | 4.1903 | 1.0832 | 0.18448
2015-05-06 09:00 | 238.76 | 221.64 | 17.12 | 36.9454 | 16.2701 | -28.3963 | 62.3942 | 27.6058 | -31.0089 | 27.1957 | 32.8611 | 166.23 | 0.8 | 1 | 47.752 | 246.8431 | -1.6 | 6.1138 | 1.0755 | 0.2177
2015-05-06 10:00 | 244.64 | 226.1733 | 18.4667 | 38.1759 | 16.2819 | -13.3954 | 61.071 | 28.929 | -14.7193 | 12.8513 | 37.2196 | 169.63 | 0.8 | 1 | 48.928 | 255.7776 | -1.6 | 6.3931 | 1.0744 | 0.22535
2015-05-06 11:00 | 250.52 | 230.7067 | 19.8133 | 40.4593 | 16.2938 | 1.6055 | 60.6785 | 29.3215 | 1.7675 | 1.679 | 40.4419 | 173.03 | 0.8 | 1 | 50.104 | 263.5759 | -1.3 | 6.9367 | 1.0723 | 0.23175
2015-05-06 12:00 | 256.4 | 235.24 | 21.16 | 43.9965 | 16.3056 | 16.6064 | 61.2527 | 28.7473 | 18.2316 | 15.9203 | 42.3089 | 176.43 | 0.8 | 1 | 51.28 | 270.0189 | -1.7 | 6.7381 | 1.073 | 0.23759
2015-05-06 13:00 | 254.0067 | 211.2967 | 42.71 | 93.2431 | 16.3175 | 31.6072 | 62.7386 | 27.2614 | 34.4601 | 30.2577 | 80.5404 | 158.4725 | 0.8 | 1 | 50.8013 | 289.8142 | -2.1 | 6.9567 | 1.0722 | 0.2548
2015-05-06 14:00 | 251.6133 | 187.3533 | 64.26 | 152.0612 | 16.3293 | 46.6081 | 65.0016 | 24.9984 | 50.3037 | 44.5512 | 108.3624 | 140.515 | 0.8 | 1 | 50.3227 | 299.2001 | -1.1 | 8.25 | 1.067 | 0.26178
2015-05-06 15:00 | 249.22 | 163.41 | 85.81 | 227.6085 | 16.3412 | 61.609 | 67.8516 | 22.1484 | 65.7052 | 58.7668 | 118.0201 | 122.5575 | 0.8 | 1 | 49.844 | 290.4216 | -0.7 | 8.3757 | 1.0665 | 0.25398
2015-05-06 16:00 | 202.72 | 125.4567 | 77.2633 | 238.1629 | 16.353 | 76.6099 | 71.0699 | 18.9301 | 80.6921 | 72.8604 | 70.187 | 94.0925 | 0.8 | 1 | 40.544 | 204.8235 | -0.8 | 5.6007 | 1.0776 | 0.18099
2015-05-06 17:00 | 156.22 | 87.5033 | 68.7167 | 256.0123 | 16.3648 | 91.6108 | 74.4302 | 15.5698 | 95.3499 | 86.7655 | 14.445 | 65.6275 | 0.8 | 1 | 31.244 | 111.3165 | -0.8 | 2.6786 | 1.0893 | 0.099429
2015-05-06 18:00 | 109.72 | 49.55 | 60.17 | 282.7132 | 16.3766 | 106.6116 | 77.7117 | 12.2883 | 109.7892 | 100.3738 | 0 | 37.1625 | 0.8 | 1 | 21.944 | 59.1065 | -0.9 | 0.94708 | 1.0962 | 0.05313
2015-05-06 19:00 | 85.7567 | 40.09 | 45.6667 | 282.8153 | 16.3884 | 121.6125 | 80.7077 | 9.2923 | 124.1188 | 113.494 | 0 | 30.0675 | 0.8 | 1 | 17.1513 | 47.2188 | -1 | 0.47559 | 1.0981 | 0.042518
2015-05-06 20:00 | 61.7933 | 30.63 | 31.1633 | 264.4367 | 16.4002 | 136.6134 | 83.2321 | 6.7679 | 138.4255 | 125.7627 | 0 | 22.9725 | 0.8 | 1 | 12.3587 | 35.3312 | -1.1 | 0.004099 | 1.1 | 0.031868
2015-05-06 21:00 | 37.83 | 21.17 | 16.66 | 196.1281 | 16.412 | 151.6142 | 85.1272 | 4.8728 | 152.7619 | 136.4471 | 0 | 15.8775 | 0.8 | 1 | 7.566 | 23.4435 | -1.2 | -0.46739 | 1.1019 | 0.021182
2015-05-06 22:00 | 36.4867 | 20.5533 | 15.9333 | 245.0697 | 16.4238 | 166.6151 | 86.2723 | 3.7277 | 167.1431 | 144.0978 | 0 | 15.415 | 0.8 | 1 | 7.2973 | 22.7123 | -1.4 | -0.69024 | 1.1028 | 0.020538
2015-05-06 23:00 | 35.1433 | 19.9367 | 15.2067 | 255.8721 | 16.4355 | 181.6159 | 86.5929 | 3.4071 | -178.4474 | 146.5598 | 0 | 14.9525 | 0.8 | 1 | 7.0287 | 21.9812 | -1.5 | -0.81309 | 1.1033 | 0.019886
2015-05-07 | 33.8 | 19.32 | 14.48 | 211.1338 | 16.4473 | -163.3833 | 86.0674 | 3.9326 | -164.0431 | 142.7881 | 0 | 14.49 | 0.8 | 1 | 6.76 | 21.25 | -1.8 | -1.1359 | 1.1045 | 0.019247
2015-05-07 01:00 | 66.7767 | 26.41 | 40.3667 | 439.4502 | 16.459 | -148.3824 | 84.7295 | 5.2705 | -149.6753 | 134.3024 | 0 | 19.8075 | 0.8 | 1 | 13.3553 | 33.1628 | -1.9 | -0.86366 | 1.1035 | 0.030007
2015-05-07 02:00 | 99.7533 | 33.5 | 66.2533 | 518.8968 | 16.4708 | -133.3816 | 82.6644 | 7.3356 | -135.3541 | 123.1794 | 0 | 25.125 | 0.8 | 1 | 19.9507 | 45.0757 | -2.2 | -0.79139 | 1.1032 | 0.040775
2015-05-07 03:00 | 132.73 | 40.59 | 92.14 | 530.6871 | 16.4825 | -118.3807 | 80.0014 | 9.9986 | -121.0559 | 110.6809 | 0 | 30.4425 | 0.8 | 1 | 26.546 | 56.9885 | -1.7 | 0.080891 | 1.0997 | 0.051389
2015-05-07 04:00 | 175.96 | 57.0233 | 118.9367 | 524.9527 | 16.4943 | -103.3799 | 76.905 | 13.095 | -106.719 | 97.4335 | 0 | 42.7675 | 0.8 | 1 | 35.192 | 77.9595 | -1.4 | 1.0362 | 1.0959 | 0.070054
2015-05-07 05:00 | 219.19 | 73.4567 | 145.7333 | 515.1179 | 16.506 | -88.3791 | 73.5659 | 16.4341 | -92.2497 | 83.751 | 56.0703 | 55.0925 | 0.8 | 1 | 43.838 | 155.0008 | -1.7 | 3.1438 | 1.0874 | 0.13821
2015-05-07 06:00 | 262.42 | 89.89 | 172.53 | 509.186 | 16.5177 | -73.3783 | 70.1941 | 19.8059 | -77.5357 | 69.8013 | 175.81 | 67.4175 | 0.8 | 1 | 52.484 | 295.7115 | -1.7 | 7.541 | 1.0698 | 0.25942
2015-05-07 07:00 | 308.54 | 94.08 | 214.46 | 549.1437 | 16.5294 | -58.3775 | 67.0122 | 22.9878 | -62.4676 | 55.6811 | 309.6061 | 70.56 | 0.8 | 1 | 61.708 | 441.8741 | -1.8 | 12.0086 | 1.052 | 0.38117
2015-05-07 08:00 | 354.66 | 98.27 | 256.39 | 590.0753 | 16.5411 | -43.3767 | 64.2463 | 25.7537 | -46.9684 | 41.4505 | 442.2777 | 73.7025 | 0.8 | 1 | 70.932 | 586.9122 | -1.2 | 17.141 | 1.0314 | 0.4964
2015-05-07 09:00 | 400.78 | 102.46 | 298.32 | 637.7657 | 16.5528 | -28.3759 | 62.1111 | 27.8889 | -31.0256 | 27.15 | 567.4935 | 76.845 | 0.8 | 1 | 80.156 | 724.4945 | -1.2 | 21.4405 | 1.0142 | 0.60254
2015-05-07 10:00 | 407.21 | 121.7 | 285.51 | 585.0067 | 16.5645 | -13.3751 | 60.7878 | 29.2122 | -14.7163 | 12.8104 | 570.4455 | 91.275 | 0.8 | 1 | 81.442 | 743.1625 | -0.9 | 22.3238 | 1.0107 | 0.61592
2015-05-07 11:00 | 413.64 | 140.94 | 272.7 | 552.0257 | 16.5761 | 1.6257 | 60.3963 | 29.6037 | 1.7922 | 1.6048 | 551.8092 | 105.705 | 0.8 | 1 | 82.728 | 740.2422 | -0.9 | 22.2326 | 1.0111 | 0.61372
2015-05-07 12:00 | 420.07 | 160.18 | 259.89 | 535.6057 | 16.5878 | 16.6265 | 60.9727 | 29.0273 | 18.2774 | 15.9186 | 515.0665 | 120.135 | 0.8 | 1 | 84.014 | 719.2155 | -1 | 21.4755 | 1.0141 | 0.59807
2015-05-07 13:00 | 404.6867 | 132.9733 | 271.7133 | 587.6904 | 16.5995 | 31.6273 | 62.4617 | 27.5383 | 34.5239 | 30.2493 | 507.6712 | 99.73 | 0.8 | 1 | 80.9373 | 688.3386 | -1 | 20.5106 | 1.018 | 0.57457
2015-05-07 14:00 | 389.3033 | 105.7667 | 283.5367 | 664.1494 | 16.6111 | 46.6281 | 64.7279 | 25.2721 | 50.3808 | 44.5326 | 473.44 | 79.325 | 0.8 | 1 | 77.8607 | 630.6256 | -1.1 | 18.6071 | 1.0256 | 0.53034
2015-05-07 15:00 | 373.92 | 78.56 | 295.36 | 774.4444 | 16.6228 | 61.6289 | 67.5806 | 22.4194 | 65.7905 | 58.7359 | 401.9242 | 58.92 | 0.8 | 1 | 74.784 | 535.6282 | -1.3 | 15.4384 | 1.0382 | 0.45601
2015-05-07 16:00 | 274.5833 | 63.6167 | 210.9667 | 641.5156 | 16.6344 | 76.6296 | 70.8006 | 19.1994 | 80.7807 | 72.8149 | 189.5419 | 47.7125 | 0.8 | 1 | 54.9167 | 292.1711 | -1.3 | 7.8303 | 1.0687 | 0.25603
2015-05-07 17:00 | 175.2467 | 48.6733 | 126.5733 | 463.7557 | 16.646 | 91.6304 | 74.1612 | 15.8388 | 95.4373 | 86.7026 | 26.675 | 36.505 | 0.8 | 1 | 35.0493 | 98.2293 | -1.5 | 1.5697 | 1.0937 | 0.088097
2015-05-07 18:00 | 75.91 | 33.73 | 42.18 | 193.9924 | 16.6576 | 106.6312 | 77.4418 | 12.5582 | 109.8716 | 100.2891 | 0 | 25.2975 | 0.8 | 1 | 15.182 | 40.4795 | -1.7 | -0.43502 | 1.1017 | 0.03657
2015-05-07 19:00 | 57.7667 | 26.3633 | 31.4033 | 189.0034 | 16.6693 | 121.6319 | 80.4358 | 9.5642 | 124.1927 | 113.3812 | 0 | 19.7725 | 0.8 | 1 | 11.5533 | 31.3258 | -1.7 | -0.72107 | 1.1029 | 0.02833
2015-05-07 20:00 | 39.6233 | 18.9967 | 20.6267 | 168.2421 | 16.6809 | 136.6327 | 82.9578 | 7.0422 | 138.488 | 125.6126 | 0 | 14.2475 | 0.8 | 1 | 7.9247 | 22.1722 | -1.9 | -1.2071 | 1.1048 | 0.020087
2015-05-07 21:00 | 21.48 | 11.63 | 9.85 | 109.7395 | 16.6925 | 151.6334 | 84.8503 | 5.1497 | 152.8106 | 136.2482 | 0 | 8.7225 | 0.8 | 1 | 4.296 | 13.0185 | -2.3 | -1.8932 | 1.1076 | 0.011824
2015-05-07 22:00 | 20.2967 | 12.29 | 8.0067 | 114.5893 | 16.704 | 166.6342 | 85.9933 | 4.0067 | 167.1761 | 143.845 | 0 | 9.2175 | 0.8 | 1 | 4.0593 | 13.2768 | -1.9 | -1.4851 | 1.1059 | 0.01204
2015-05-07 23:00 | 19.1133 | 12.95 | 6.1633 | 95.8353 | 16.7156 | 181.6349 | 86.3127 | 3.6873 | -178.4309 | 146.2792 | 0 | 9.7125 | 0.8 | 1 | 3.8227 | 13.5352 | -1.8 | -1.377 | 1.1055 | 0.01227
2015-05-08 | 17.93 | 13.61 | 4.32 | 58.8035 | 16.7272 | -163.3643 | 85.787 | 4.213 | -164.0431 | 142.5302 | 0 | 10.2075 | 0.8 | 1 | 3.586 | 13.7935 | -2.2 | -1.769 | 1.1071 | 0.012522
2015-05-08 01:00 | 29.6567 | 19.7267 | 9.93 | 102.6675 | 16.7388 | -148.3636 | 84.4497 | 5.5503 | -149.6907 | 134.0899 | 0 | 14.795 | 0.8 | 1 | 5.9313 | 20.7263 | -2.4 | -1.7523 | 1.107 | 0.018814
2015-05-08 02:00 | 41.3833 | 25.8433 | 15.54 | 117.2805 | 16.7503 | -133.3629 | 82.3858 | 7.6142 | -135.3829 | 123.0086 | 0 | 19.3825 | 0.8 | 1 | 8.2767 | 27.6592 | -2.5 | -1.6357 | 1.1065 | 0.025097
2015-05-08 03:00 | 53.11 | 31.96 | 21.15 | 118.5629 | 16.7619 | -118.3621 | 79.7242 | 10.2758 | -121.0953 | 110.5426 | 0 | 23.97 | 0.8 | 1 | 10.622 | 34.592 | -2.5 | -1.419 | 1.1057 | 0.031363
2015-05-08 04:00 | 80.7433 | 61.3067 | 19.4367 | 84.0487 | 16.7734 | -103.3614 | 76.629 | 13.371 | -106.7659 | 97.3203 | 0 | 45.98 | 0.8 | 1 | 16.1487 | 62.1287 | -2.6 | -0.65848 | 1.1026 | 0.056174
2015-05-08 05:00 | 108.3767 | 90.6533 | 17.7233 | 61.6427 | 16.7849 | -88.3607 | 73.2906 | 16.7094 | -92.3003 | 83.6578 | 6.8095 | 67.99 | 0.8 | 1 | 21.6753 | 96.4748 | -2.4 | 0.61484 | 1.0975 | 0.086826
2015-05-08 06:00 | 136.01 | 120 | 16.01 | 46.6285 | 16.7964 | -73.36 | 69.9188 | 20.0812 | -77.5857 | 69.7244 | 16.1584 | 90 | 0.8 | 1 | 27.202 | 133.3604 | -2.5 | 1.6675 | 1.0933 | 0.11956
2015-05-08 07:00 | 183.8267 | 149.0233 | 34.8033 | 88.1172 | 16.808 | -58.3593 | 66.7361 | 23.2639 | -62.5123 | 55.6182 | 49.7603 | 111.7675 | 0.8 | 1 | 36.7653 | 198.2931 | -2.4 | 3.7967 | 1.0848 | 0.17639
2015-05-08 08:00 | 231.6433 | 178.0467 | 53.5967 | 122.1281 | 16.8195 | -43.3586 | 63.9691 | 26.0309 | -47.0027 | 41.3997 | 91.6101 | 133.535 | 0.8 | 1 | 46.3287 | 271.4737 | -2.3 | 6.1836 | 1.0753 | 0.23936
2015-05-08 09:00 | 279.46 | 207.07 | 72.39 | 153.3543 | 16.831 | -28.3579 | 61.8329 | 28.1671 | -31.0444 | 27.1098 | 136.506 | 155.3025 | 0.8 | 1 | 55.892 | 347.7005 | -3.1 | 7.7656 | 1.0689 | 0.30477
2015-05-08 10:00 | 257.87 | 201.25 | 56.62 | 115.0152 | 16.8425 | -13.3572 | 60.5093 | 29.4907 | -14.7157 | 12.7781 | 112.1667 | 150.9375 | 0.8 | 1 | 51.574 | 314.6782 | -3.3 | 6.5337 | 1.0739 | 0.2771
2015-05-08 11:00 | 236.28 | 195.43 | 40.85 | 81.9941 | 16.8539 | 1.6435 | 60.1186 | 29.8814 | 1.8142 | 1.5765 | 81.9631 | 146.5725 | 0.8 | 1 | 47.256 | 275.7916 | -3.4 | 5.2185 | 1.0791 | 0.24404
2015-05-08 12:00 | 214.69 | 189.61 | 25.08 | 51.2437 | 16.8654 | 16.6442 | 60.6971 | 29.3029 | 18.3203 | 15.9196 | 49.2783 | 142.2075 | 0.8 | 1 | 42.938 | 234.4238 | -3.1 | 4.2257 | 1.0831 | 0.2082
2015-05-08 13:00 | 227.9467 | 187.8 | 40.1467 | 86.0491 | 16.8769 | 31.6449 | 62.1891 | 27.8109 | 34.5845 | 30.2414 | 74.3388 | 140.85 | 0.8 | 1 | 45.5893 | 260.7781 | -3.3 | 4.8493 | 1.0806 | 0.23107
2015-05-08 14:00 | 241.2033 | 185.99 | 55.2133 | 128.0556 | 16.8883 | 46.6456 | 64.4584 | 25.5416 | 50.4548 | 44.5135 | 91.3145 | 139.4925 | 0.8 | 1 | 48.2407 | 279.0477 | -3.3 | 5.4202 | 1.0783 | 0.24674
2015-05-08 15:00 | 254.46 | 184.18 | 70.28 | 182.2206 | 16.8998 | 61.6463 | 67.3136 | 22.6864 | 65.8726 | 58.7042 | 94.6557 | 138.135 | 0.8 | 1 | 50.892 | 283.6827 | -3.5 | 5.3651 | 1.0785 | 0.25089
2015-05-08 16:00 | 193.29 | 134.2867 | 59.0033 | 177.0662 | 16.9112 | 76.6469 | 70.5352 | 19.4648 | 80.866 | 72.7685 | 52.4528 | 100.715 | 0.8 | 1 | 38.658 | 191.8258 | -3.4 | 2.5946 | 1.0896 | 0.17139
2015-05-08 17:00 | 132.12 | 84.3933 | 47.7267 | 172.0631 | 16.9227 | 91.6476 | 73.8962 | 16.1038 | 95.5214 | 86.6387 | 10.0884 | 63.295 | 0.8 | 1 | 26.424 | 99.8074 | -4.1 | -0.98102 | 1.1039 | 0.090347
2015-05-08 18:00 | 70.95 | 34.5 | 36.45 | 164.2191 | 16.9341 | 106.6483 | 77.1758 | 12.8242 | 109.9507 | 100.2036 | 0 | 25.875 | 0.8 | 1 | 14.19 | 40.065 | -3.9 | -2.648 | 1.1106 | 0.036487
2015-05-08 19:00 | 54.9467 | 27.6833 | 27.2633 | 159.6594 | 16.9455 | 121.6489 | 80.168 | 9.832 | 124.2635 | 113.2679 | 0 | 20.7625 | 0.8 | 1 | 10.9893 | 31.7518 | -4.4 | -3.4078 | 1.1136 | 0.028995
2015-05-08 20:00 | 38.9433 | 20.8667 | 18.0767 | 142.0236 | 16.9569 | 136.6496 | 82.6876 | 7.3124 | 138.5475 | 125.4626 | 0 | 15.65 | 0.8 | 1 | 7.7887 | 23.4387 | -4.6 | -3.8675 | 1.1155 | 0.021439
2015-05-08 21:00 | 22.94 | 14.05 | 8.89 | 94.0796 | 16.9683 | 151.6502 | 84.5778 | 5.4222 | 152.8564 | 136.0504 | 0 | 10.5375 | 0.8 | 1 | 4.588 | 15.1255 | -4.6 | -4.1273 | 1.1165 | 0.013848
2015-05-08 22:00 | 18.22 | 11.6 | 6.62 | 88.68 | 16.9797 | 166.6509 | 85.7189 | 4.2811 | 167.2065 | 143.5952 | 0 | 8.7 | 0.8 | 1 | 3.644 | 12.344 | -5 | -4.6143 | 1.1185 | 0.011321
2015-05-08 23:00 | 13.5 | 9.15 | 4.35 | 62.9425 | 16.9911 | 181.6515 | 86.0371 | 3.9629 | -178.4168 | 146.0033 | 0 | 6.8625 | 0.8 | 1 | 2.7 | 9.5625 | -5.2 | -4.9012 | 1.1196 | 0.0087791
2015-05-09 | 8.78 | 6.7 | 2.08 | 26.5769 | 17.0025 | -163.3479 | 85.5112 | 4.4888 | -164.0452 | 142.2771 | 0 | 5.025 | 0.8 | 1 | 1.756 | 6.781 | -5.4 | -5.1881 | 1.1208 | 0.0062319
2015-05-09 01:00 | 27.94 | 12.32 | 15.62 | 153.8977 | 17.0138 | -148.3472 | 84.1747 | 5.8253 | -149.708 | 133.8818 | 0 | 9.24 | 0.8 | 1 | 5.588 | 14.828 | -5.4 | -4.9366 | 1.1197 | 0.013615
2015-05-09 02:00 | 47.1 | 17.94 | 29.16 | 212.481 | 17.0252 | -133.3466 | 82.1121 | 7.8879 | -135.4134 | 122.8418 | 0 | 13.455 | 0.8 | 1 | 9.42 | 22.875 | -5.6 | -4.8852 | 1.1195 | 0.021
2015-05-09 03:00 | 66.26 | 23.56 | 42.7 | 233.2591 | 17.0366 | -118.346 | 79.4521 | 10.5479 | -121.1363 | 110.4081 | 0 | 17.67 | 0.8 | 1 | 13.252 | 30.922 | -5.5 | -4.5337 | 1.1181 | 0.028351
2015-05-09 04:00 | 60.1967 | 23.96 | 36.2367 | 153.6416 | 17.0479 | -103.3454 | 76.3582 | 13.6418 | -106.8142 | 97.2109 | 0 | 17.97 | 0.8 | 1 | 12.0393 | 30.0093 | -5.2 | -4.2622 | 1.117 | 0.027488
2015-05-09 05:00 | 54.1333 | 24.36 | 29.7733 | 101.9528 | 17.0592 | -88.3448 | 73.0204 | 16.9796 | -92.3523 | 83.5682 | 11.4207 | 18.27 | 0.8 | 1 | 10.8267 | 40.5174 | -5.5 | -4.2338 | 1.1169 | 0.037109
2015-05-09 06:00 | 48.07 | 24.76 | 23.31 | 67.0255 | 17.0706 | -73.3441 | 69.6485 | 20.3515 | -77.6372 | 69.6514 | 23.3069 | 18.57 | 0.8 | 1 | 9.614 | 51.4909 | -5.6 | -3.9909 | 1.116 | 0.047119
2015-05-09 07:00 | 59.7067 | 26.5367 | 33.17 | 83.0688 | 17.0819 | -58.3435 | 66.4651 | 23.5349 | -62.5587 | 55.5592 | 46.98 | 19.9025 | 0.8 | 1 | 11.9413 | 78.8238 | -5.6 | -3.1368 | 1.1125 | 0.07191
2015-05-09 08:00 | 71.3433 | 28.3133 | 43.03 | 97.1068 | 17.0932 | -43.3429 | 63.6969 | 26.3031 | -47.0389 | 41.3532 | 72.8933 | 21.235 | 0.8 | 1 | 14.2687 | 108.397 | -5.7 | -2.3126 | 1.1093 | 0.098596
2015-05-09 09:00 | 82.98 | 30.09 | 52.89 | 111.0565 | 17.1045 | -28.3423 | 61.5596 | 28.4404 | -31.0655 | 27.0749 | 98.8861 | 22.5675 | 0.8 | 1 | 16.596 | 138.0496 | -5.8 | -1.4859 | 1.1059 | 0.12519
2015-05-09 10:00 | 114.9567 | 48.67 | 66.2867 | 133.5253 | 17.1158 | -13.3417 | 60.2356 | 29.7644 | -14.7176 | 12.7543 | 130.2306 | 36.5025 | 0.8 | 1 | 22.9913 | 189.7244 | -6 | -0.071112 | 1.1003 | 0.17118
2015-05-09 11:00 | 146.9333 | 67.25 | 79.6833 | 158.6267 | 17.1271 | 1.6588 | 59.8456 | 30.1544 | 1.8334 | 1.594 | 158.5653 | 50.4375 | 0.8 | 1 | 29.3867 | 238.3895 | -5.7 | 1.7497 | 1.093 | 0.21366
2015-05-09 12:00 | 178.91 | 85.83 | 93.08 | 188.5939 | 17.1384 | 16.6594 | 60.426 | 29.574 | 18.3602 | 15.9231 | 181.3577 | 64.3725 | 0.8 | 1 | 35.782 | 281.5122 | -5.8 | 2.9973 | 1.088 | 0.25116
2015-05-09 13:00 | 185.22 | 89.6667 | 95.5533 | 203.0056 | 17.1496 | 31.66 | 61.9207 | 28.0793 | 34.6421 | 30.2337 | 175.3926 | 67.25 | 0.8 | 1 | 37.044 | 279.6866 | -5.6 | 3.1402 | 1.0874 | 0.2494
2015-05-09 14:00 | 191.53 | 93.5033 | 98.0267 | 225.1719 | 17.1609 | 46.6606 | 64.193 | 25.807 | 50.5255 | 44.494 | 160.6204 | 70.1275 | 0.8 | 1 | 38.306 | 269.0539 | -5.3 | 3.1079 | 1.0876 | 0.23994
2015-05-09 15:00 | 197.84 | 97.34 | 100.5 | 257.748 | 17.1721 | 61.6612 | 67.0507 | 22.9493 | 65.9513 | 58.6717 | 134.0138 | 73.005 | 0.8 | 1 | 39.568 | 246.5868 | -5.6 | 2.1058 | 1.0916 | 0.22072
2015-05-09 16:00 | 162.9033 | 76.92 | 85.9833 | 254.7464 | 17.1834 | 76.6617 | 70.2738 | 19.7262 | 80.9479 | 72.7213 | 75.6649 | 57.69 | 0.8 | 1 | 32.5807 | 165.9356 | -5.4 | -0.21451 | 1.1009 | 0.14979
2015-05-09 17:00 | 127.9667 | 56.5 | 71.4667 | 253.6495 | 17.1946 | 91.6623 | 73.6351 | 16.3649 | 95.6021 | 86.5739 | 15.1582 | 42.375 | 0.8 | 1 | 25.5933 | 83.1265 | -5.8 | -3.2023 | 1.1128 | 0.075853
2015-05-09 18:00 | 93.03 | 36.08 | 56.95 | 251.5298 | 17.2059 | 106.6628 | 76.9139 | 13.0861 | 110.0264 | 100.1173 | 0 | 27.06 | 0.8 | 1 | 18.606 | 45.666 | -6.3 | -4.8729 | 1.1195 | 0.041921
2015-05-09 19:00 | 73.8133 | 29.7567 | 44.0567 | 251.3334 | 17.2171 | 121.6634 | 79.9044 | 10.0956 | 124.331 | 113.1542 | 0 | 22.3175 | 0.8 | 1 | 14.7627 | 37.0802 | -6.3 | -5.1412 | 1.1206 | 0.034072
2015-05-09 20:00 | 54.5967 | 23.4333 | 31.1633 | 236.2988 | 17.2283 | 136.6639 | 82.4217 | 7.5783 | 138.6039 | 125.3128 | 0 | 17.575 | 0.8 | 1 | 10.9193 | 28.4943 | -6.3 | -5.4096 | 1.1216 | 0.026207
2015-05-09 21:00 | 35.38 | 17.11 | 18.27 | 184.2619 | 17.2395 | 151.6645 | 84.3096 | 5.6904 | 152.8993 | 135.854 | 0 | 12.8325 | 0.8 | 1 | 7.076 | 19.9085 | -6.4 | -5.7779 | 1.1231 | 0.018335
2015-05-09 22:00 | 34.19 | 16.9133 | 17.2767 | 217.735 | 17.2507 | 166.665 | 85.449 | 4.551 | 167.2343 | 143.3486 | 0 | 12.685 | 0.8 | 1 | 6.838 | 19.523 | -6 | -5.3899 | 1.1216 | 0.017955
2015-05-09 23:00 | 33 | 16.7167 | 16.2833 | 220.5634 | 17.2619 | 181.6656 | 85.7662 | 4.2338 | -178.4051 | 145.7322 | 0 | 12.5375 | 0.8 | 1 | 6.6 | 19.1375 | -6.3 | -5.702 | 1.1228 | 0.01762
2015-05-10 | 31.81 | 16.52 | 15.29 | 184.2703 | 17.2731 | -163.3339 | 85.2404 | 4.7596 | -164.0495 | 142.0291 | 0 | 12.39 | 0.8 | 1 | 6.362 | 18.752 | -5.9 | -5.314 | 1.1213 | 0.017241
2015-05-10 01:00 | 46.2533 | 21.39 | 24.8633 | 234.1539 | 17.2842 | -148.3334 | 83.9046 | 6.0954 | -149.7271 | 133.6783 | 0 | 16.0425 | 0.8 | 1 | 9.2507 | 25.2932 | -6.2 | -5.4096 | 1.1216 | 0.023263
2015-05-10 02:00 | 60.6967 | 26.26 | 34.4367 | 242.7194 | 17.2954 | -133.3329 | 81.8434 | 8.1566 | -135.4455 | 122.6791 | 0 | 19.695 | 0.8 | 1 | 12.1393 | 31.8343 | -6.3 | -5.3052 | 1.1212 | 0.029269
2015-05-10 03:00 | 75.14 | 31.13 | 44.01 | 234.5466 | 17.3066 | -118.3323 | 79.185 | 10.815 | -121.1788 | 110.2775 | 0 | 23.3475 | 0.8 | 1 | 15.028 | 38.3755 | -6 | -4.8008 | 1.1192 | 0.035219
2015-05-10 04:00 | 93.4367 | 47.6567 | 45.78 | 190.467 | 17.3177 | -103.3318 | 76.0924 | 13.9076 | -106.864 | 97.1052 | 0 | 35.7425 | 0.8 | 1 | 18.6873 | 54.4298 | -6.5 | -4.7991 | 1.1192 | 0.049952
2015-05-10 05:00 | 111.7333 | 64.1833 | 47.55 | 160.3973 | 17.3288 | -88.3313 | 72.7554 | 17.2446 | -92.4058 | 83.4825 | 18.2062 | 48.1375 | 0.8 | 1 | 22.3467 | 88.6904 | -5.8 | -3.0284 | 1.1121 | 0.08088
2015-05-10 06:00 | 130.03 | 80.71 | 49.32 | 140.0691 | 17.34 | -73.3308 | 69.3835 | 20.6165 | -77.6903 | 69.5821 | 48.8652 | 60.5325 | 0.8 | 1 | 26.006 | 135.4037 | -6.1 | -1.8686 | 1.1075 | 0.12296
2015-05-10 07:00 | 147.71 | 95.7167 | 51.9933 | 128.8375 | 17.3511 | -58.3303 | 66.1992 | 23.8008 | -62.6068 | 55.5042 | 72.9666 | 71.7875 | 0.8 | 1 | 29.542 | 174.2961 | -6 | -0.55325 | 1.1022 | 0.15753
2015-05-10 08:00 | 165.39 | 110.7233 | 54.6667 | 122.2162 | 17.3622 | -43.3298 | 63.4297 | 26.5703 | -47.077 | 41.3112 | 91.8009 | 83.0425 | 0.8 | 1 | 33.078 | 207.9214 | -5.8 | 0.69754 | 1.0972 | 0.18707
2015-05-10 09:00 | 183.07 | 125.73 | 57.34 | 119.3696 | 17.3733 | -28.3293 | 61.2913 | 28.7087 | -31.0887 | 27.0452 | 106.3164 | 94.2975 | 0.8 | 1 | 36.614 | 237.2279 | -4.9 | 2.5134 | 1.0899 | 0.21202
2015-05-10 10:00 | 218.0233 | 158.33 | 59.6933 | 119.2666 | 17.3844 | -13.3288 | 59.9667 | 30.0333 | -14.722 | 12.7387 | 116.3309 | 118.7475 | 0.8 | 1 | 43.6047 | 278.6831 | -4.9 | 3.8088 | 1.0848 | 0.24789
2015-05-10 11:00 | 252.9767 | 190.93 | 62.0467 | 122.5308 | 17.3955 | 1.6717 | 59.5773 | 30.4227 | 1.85 | 1.6536 | 122.4798 | 143.1975 | 0.8 | 1 | 50.5953 | 316.2726 | -5.2 | 4.6835 | 1.0813 | 0.28042
2015-05-10 12:00 | 287.93 | 223.53 | 64.4 | 129.4243 | 17.4066 | 16.6721 | 60.1594 | 29.8406 | 18.3971 | 15.9288 | 124.4549 | 167.6475 | 0.8 | 1 | 57.586 | 349.6884 | -5.2 | 5.7278 | 1.0771 | 0.30885
2015-05-10 13:00 | 239.3767 | 191.46 | 47.9167 | 100.9297 | 17.4176 | 31.6726 | 61.6567 | 28.3433 | 34.6965 | 30.2261 | 87.2079 | 143.595 | 0.8 | 1 | 47.8753 | 278.6782 | -5.2 | 3.5087 | 1.086 | 0.24816
2015-05-10 14:00 | 190.8233 | 159.39 | 31.4333 | 71.5304 | 17.4287 | 46.6731 | 63.9318 | 26.0682 | 50.5928 | 44.474 | 51.0419 | 119.5425 | 0.8 | 1 | 38.1647 | 208.749 | -5.1 | 1.4234 | 1.0943 | 0.18732
2015-05-10 15:00 | 142.27 | 127.32 | 14.95 | 37.9374 | 17.4398 | 61.6736 | 66.792 | 23.208 | 66.0266 | 58.6384 | 19.7441 | 95.49 | 0.8 | 1 | 28.454 | 143.6881 | -4.6 | -0.10975 | 1.1004 | 0.12966
2015-05-10 16:00 | 124.9967 | 101.76 | 23.2367 | 67.9934 | 17.4508 | 76.674 | 70.0165 | 19.9835 | 81.0264 | 72.6731 | 20.25 | 76.32 | 0.8 | 1 | 24.9993 | 121.5694 | -4.7 | -0.90096 | 1.1036 | 0.11001
2015-05-10 17:00 | 107.7233 | 76.2 | 31.5233 | 110.2005 | 17.4618 | 91.6745 | 73.3781 | 16.6219 | 95.6795 | 86.5083 | 6.7116 | 57.15 | 0.8 | 1 | 21.5447 | 85.4063 | -4.2 | -1.5311 | 1.1061 | 0.077465
2015-05-10 18:00 | 90.45 | 50.64 | 39.81 | 172.491 | 17.4729 | 106.6749 | 76.6561 | 13.3439 | 110.0989 | 100.0304 | 0 | 37.98 | 0.8 | 1 | 18.09 | 56.07 | -4.5 | -2.7478 | 1.111 | 0.05108
2015-05-10 19:00 | 66.34 | 39.7967 | 26.5433 | 147.6696 | 17.4839 | 121.6754 | 79.6449 | 10.3551 | 124.3953 | 113.0401 | 0 | 29.8475 | 0.8 | 1 | 13.268 | 43.1155 | -4.3 | -2.9526 | 1.1118 | 0.039308
2015-05-10 20:00 | 42.23 | 28.9533 | 13.2767 | 97.3327 | 17.4949 | 136.6758 | 82.1601 | 7.8399 | 138.6573 | 125.1632 | 0 | 21.715 | 0.8 | 1 | 8.446 | 30.161 | -3.8 | -2.8575 | 1.1114 | 0.027488
2015-05-10 21:00 | 18.12 | 18.11 | 0.01 | 0.096404 | 17.5059 | 151.6763 | 84.046 | 5.954 | 152.9394 | 135.659 | 0 | 13.5825 | 0.8 | 1 | 3.624 | 17.2065 | -3.7 | -3.1623 | 1.1126 | 0.015699
2015-05-10 22:00 | 22.9567 | 19.4467 | 3.51 | 41.8049 | 17.5169 | 166.6767 | 85.1837 | 4.8163 | 167.2594 | 143.1052 | 0 | 14.585 | 0.8 | 1 | 4.5913 | 19.1763 | -4.2 | -3.6007 | 1.1144 | 0.017524
2015-05-10 23:00 | 27.7933 | 20.7833 | 7.01 | 89.3489 | 17.5279 | 181.6771 | 85.5001 | 4.4999 | -178.3958 | 145.4659 | 0 | 15.5875 | 0.8 | 1 | 5.5587 | 21.1462 | -4.2 | -3.5392 | 1.1142 | 0.019319
2015-05-11 | 32.63 | 22.12 | 10.51 | 119.976 | 17.5389 | -163.3224 | 84.9744 | 5.0256 | -164.0558 | 141.7862 | 0 | 16.59 | 0.8 | 1 | 6.526 | 23.116 | -4.4 | -3.6776 | 1.1147 | 0.021129
2015-05-11 01:00 | 49.6267 | 35.9867 | 13.64 | 123.1251 | 17.5498 | -148.322 | 83.6396 | 6.3604 | -149.7481 | 133.4794 | 0 | 26.99 | 0.8 | 1 | 9.9253 | 36.9153 | -4.4 | -3.2464 | 1.113 | 0.033691
2015-05-11 02:00 | 66.6233 | 49.8533 | 16.77 | 114.526 | 17.5608 | -133.3216 | 81.5799 | 8.4201 | -135.4792 | 122.5206 | 0 | 37.39 | 0.8 | 1 | 13.3247 | 50.7147 | -4.5 | -2.9152 | 1.1117 | 0.04623
2015-05-11 03:00 | 83.62 | 63.72 | 19.9 | 103.5778 | 17.5718 | -118.3212 | 78.9231 | 11.0769 | -121.2228 | 110.1508 | 0 | 47.79 | 0.8 | 1 | 16.724 | 64.514 | -4.7 | -2.6839 | 1.1107 | 0.05876
2015-05-11 04:00 | 125.92 | 76.6733 | 49.2467 | 201.1975 | 17.5827 | -103.3208 | 75.8319 | 14.1681 | -106.9152 | 97.0033 | 0 | 57.505 | 0.8 | 1 | 25.184 | 82.689 | -4.8 | -2.216 | 1.1089 | 0.075186
2015-05-11 05:00 | 168.22 | 89.6267 | 78.5933 | 261.2998 | 17.5936 | -88.3203 | 72.4956 | 17.5044 | -92.4607 | 83.4004 | 30.031 | 67.22 | 0.8 | 1 | 33.644 | 130.895 | -4.9 | -0.80953 | 1.1032 | 0.11841
2015-05-11 06:00 | 210.52 | 102.58 | 107.94 | 302.9021 | 17.6046 | -73.3199 | 69.1236 | 20.8764 | -77.7449 | 69.5167 | 105.9961 | 76.935 | 0.8 | 1 | 42.104 | 225.0351 | -4.8 | 2.2323 | 1.0911 | 0.20133
2015-05-11 07:00 | 261.7333 | 136.9267 | 124.8067 | 306.1121 | 17.6155 | -58.3195 | 65.9386 | 24.0614 | -62.6565 | 55.4532 | 173.5899 | 102.695 | 0.8 | 1 | 52.3467 | 328.6316 | -5 | 5.2697 | 1.0789 | 0.29075
2015-05-11 08:00 | 312.9467 | 171.2733 | 141.6733 | 313.8676 | 17.6264 | -43.3192 | 63.1678 | 26.8322 | -47.117 | 41.2734 | 235.8937 | 128.455 | 0.8 | 1 | 62.5893 | 426.938 | -4.9 | 8.4418 | 1.0662 | 0.37328
2015-05-11 09:00 | 364.16 | 205.62 | 158.54 | 327.3042 | 17.6373 | -28.3188 | 61.0281 | 28.9719 | -31.1141 | 27.0206 | 291.5767 | 154.215 | 0.8 | 1 | 72.832 | 518.6237 | -4.8 | 11.407 | 1.0544 | 0.44839
2015-05-11 10:00 | 366.97 | 220.7433 | 146.2267 | 289.8529 | 17.6482 | -13.3184 | 59.7028 | 30.2972 | -14.7288 | 12.731 | 282.727 | 165.5575 | 0.8 | 1 | 73.394 | 521.6785 | -4.7 | 11.6025 | 1.0536 | 0.4507
2015-05-11 11:00 | 369.78 | 235.8667 | 133.9133 | 262.4021 | 17.6591 | 1.682 | 59.3138 | 30.6862 | 1.8638 | 1.7487 | 262.2799 | 176.9 | 0.8 | 1 | 73.956 | 513.1359 | -4.7 | 11.3355 | 1.0547 | 0.44377
2015-05-11 12:00 | 372.59 | 250.99 | 121.6 | 242.4493 | 17.67 | 16.6824 | 59.8975 | 30.1025 | 18.4311 | 15.9365 | 233.1312 | 188.2425 | 0.8 | 1 | 74.518 | 495.8917 | -4.7 | 10.7966 | 1.0568 | 0.42973
2015-05-11 13:00 | 335.22 | 222.0967 | 113.1233 | 236.2969 | 17.6808 | 31.6828 | 61.3973 | 28.6027 | 34.7477 | 30.2186 | 204.1869 | 166.5725 | 0.8 | 1 | 67.044 | 437.8034 | -4.7 | 8.9814 | 1.0641 | 0.382
2015-05-11 14:00 | 297.85 | 193.2033 | 104.6467 | 235.9768 | 17.6917 | 46.6831 | 63.675 | 26.325 | 50.6569 | 44.4534 | 168.4451 | 144.9025 | 0.8 | 1 | 59.57 | 372.9176 | -4.8 | 6.8537 | 1.0726 | 0.32799
2015-05-11 15:00 | 260.48 | 164.31 | 96.17 | 241.5427 | 17.7025 | 61.6835 | 66.5375 | 23.4625 | 66.0986 | 58.6042 | 125.8308 | 123.2325 | 0.8 | 1 | 52.096 | 301.1593 | -4.9 | 4.5112 | 1.082 | 0.26719
2015-05-11 16:00 | 215.1233 | 133.1067 | 82.0167 | 237.1128 | 17.7134 | 76.6838 | 69.7634 | 20.2366 | 81.1014 | 72.624 | 70.8117 | 99.83 | 0.8 | 1 | 43.0247 | 213.6663 | -4.9 | 1.7771 | 1.0929 | 0.19148
2015-05-11 17:00 | 169.7667 | 101.9033 | 67.8633 | 233.7862 | 17.7242 | 91.6842 | 73.1253 | 16.8747 | 95.7534 | 86.4418 | 14.5092 | 76.4275 | 0.8 | 1 | 33.9533 | 124.89 | -5 | -1.0972 | 1.1044 | 0.1131
2015-05-11 18:00 | 124.41 | 70.7 | 53.71 | 228.4572 | 17.735 | 106.6846 | 76.4026 | 13.5974 | 110.1679 | 99.9427 | 0 | 53.025 | 0.8 | 1 | 24.882 | 77.907 | -5.3 | -2.8654 | 1.1115 | 0.071004
2015-05-11 19:00 | 92.45 | 56.55 | 35.9 | 194.974 | 17.7459 | 121.6849 | 79.3898 | 10.6102 | 124.4563 | 112.9257 | 0 | 42.4125 | 0.8 | 1 | 18.49 | 60.9025 | -5.5 | -3.5968 | 1.1144 | 0.055653
2015-05-11 20:00 | 60.49 | 42.4 | 18.09 | 128.4348 | 17.7567 | 136.6852 | 81.903 | 8.097 | 138.7075 | 125.014 | 0 | 31.8 | 0.8 | 1 | 12.098 | 43.898 | -5.6 | -4.2282 | 1.1169 | 0.040205
2015-05-11 21:00 | 28.53 | 28.25 | 0.28 | 2.5872 | 17.7675 | 151.6856 | 83.7869 | 6.2131 | 152.9765 | 135.4655 | 0 | 21.1875 | 0.8 | 1 | 5.706 | 26.8935 | -5.7 | -4.8596 | 1.1194 | 0.024687
2015-05-11 22:00 | 28.42 | 26.5033 | 1.9167 | 21.6593 | 17.7783 | 166.6859 | 84.9232 | 5.0768 | 167.2818 | 142.8652 | 0 | 19.8775 | 0.8 | 1 | 5.684 | 25.5615 | -5.8 | -5.0012 | 1.12 | 0.023476
2015-05-11 23:00 | 28.31 | 24.7567 | 3.5533 | 42.811 | 17.789 | 181.6862 | 85.239 | 4.761 | -178.3888 | 145.2047 | 0 | 18.5675 | 0.8 | 1 | 5.662 | 24.2295 | -6.1 | -5.3428 | 1.1214 | 0.02228
2015-05-12 | 28.2 | 23.01 | 5.19 | 56.3293 | 17.7998 | -163.3134 | 84.7135 | 5.2865 | -164.0643 | 141.5484 | 0 | 17.2575 | 0.8 | 1 | 5.64 | 22.8975 | -6.3 | -5.5845 | 1.1223 | 0.021073
2015-05-12 01:00 | 52.88 | 34.0233 | 18.8567 | 163.5607 | 17.8106 | -148.3131 | 83.3797 | 6.6203 | -149.7709 | 133.2851 | 0 | 25.5175 | 0.8 | 1 | 10.576 | 36.0935 | -6.5 | -5.3721 | 1.1215 | 0.033192
2015-05-12 02:00 | 77.56 | 45.0367 | 32.5233 | 215.5462 | 17.8213 | -133.3128 | 81.3216 | 8.6784 | -135.5146 | 122.3663 | 0 | 33.7775 | 0.8 | 1 | 15.512 | 49.2895 | -6.7 | -5.1597 | 1.1206 | 0.045293
2015-05-12 03:00 | 102.24 | 56.05 | 46.19 | 235.0402 | 17.8321 | -118.3125 | 78.6665 | 11.3335 | -121.2682 | 110.0281 | 0 | 42.0375 | 0.8 | 1 | 20.448 | 62.4855 | -6.7 | -4.7473 | 1.119 | 0.057335
2015-05-12 04:00 | 145.5367 | 85.2 | 60.3367 | 242.234 | 17.8428 | -103.3122 | 75.5767 | 14.4233 | -106.9677 | 96.9052 | 0 | 63.9 | 0.8 | 1 | 29.1073 | 93.0073 | -6.8 | -3.8935 | 1.1156 | 0.08508
2015-05-12 05:00 | 188.8333 | 114.35 | 74.4833 | 244.199 | 17.8536 | -88.3119 | 72.2412 | 17.7588 | -92.5169 | 83.3222 | 28.397 | 85.7625 | 0.8 | 1 | 37.7667 | 151.9262 | -6.6 | -1.8523 | 1.1074 | 0.13796
2015-05-12 06:00 | 232.13 | 143.5 | 88.63 | 245.8532 | 17.8643 | -73.3116 | 68.8691 | 21.1309 | -77.801 | 69.455 | 86.2806 | 107.625 | 0.8 | 1 | 46.426 | 240.3316 | -6.6 | 0.91036 | 1.0964 | 0.21606
2015-05-12 07:00 | 269.0167 | 166.06 | 102.9567 | 250.0276 | 17.875 | -58.3113 | 65.6832 | 24.3168 | -62.7079 | 55.4061 | 141.9549 | 124.545 | 0.8 | 1 | 53.8033 | 320.3032 | -6.5 | 3.5095 | 1.086 | 0.28523
2015-05-12 08:00 | 305.9033 | 188.62 | 117.2833 | 257.5545 | 17.8857 | -43.311 | 62.9111 | 27.0889 | -47.1589 | 41.2398 | 193.6699 | 141.465 | 0.8 | 1 | 61.1807 | 396.3156 | -6.3 | 6.0849 | 1.0757 | 0.34957
2015-05-12 09:00 | 342.79 | 211.18 | 131.61 | 269.5175 | 17.8964 | -28.3107 | 60.77 | 29.23 | -31.1417 | 27.001 | 240.1398 | 158.385 | 0.8 | 1 | 68.558 | 467.0828 | -6.1 | 8.4963 | 1.066 | 0.40829
2015-05-12 10:00 | 352.7133 | 207.99 | 144.7233 | 284.6745 | 17.9071 | -13.3104 | 59.4439 | 30.5561 | -14.7382 | 12.7308 | 277.6761 | 155.9925 | 0.8 | 1 | 70.5427 | 504.2113 | -6.1 | 9.6566 | 1.0614 | 0.43883
2015-05-12 11:00 | 362.6367 | 204.8 | 157.8367 | 306.9481 | 17.9178 | 1.6899 | 59.0551 | 30.9449 | 1.8748 | 1.8718 | 306.7843 | 153.6 | 0.8 | 1 | 72.5273 | 532.9116 | -5.9 | 10.7535 | 1.057 | 0.46189
2015-05-12 12:00 | 372.56 | 201.61 | 170.95 | 338.2291 | 17.9284 | 16.6901 | 59.6403 | 30.3597 | 18.462 | 15.9459 | 325.2145 | 151.2075 | 0.8 | 1 | 74.512 | 550.934 | -5.7 | 11.5167 | 1.0539 | 0.47613
2015-05-12 13:00 | 339.62 | 187.3633 | 152.2567 | 315.4694 | 17.9391 | 31.6904 | 61.1423 | 28.8577 | 34.7958 | 30.211 | 272.6216 | 140.5225 | 0.8 | 1 | 67.924 | 481.0681 | -5.6 | 9.4334 | 1.0623 | 0.41904
2015-05-12 14:00 | 306.68 | 173.1167 | 133.5633 | 298.5286 | 17.9497 | 46.6907 | 63.4227 | 26.5773 | 50.7176 | 44.4321 | 213.1734 | 129.8375 | 0.8 | 1 | 61.336 | 404.3469 | -5.3 | 7.3358 | 1.0707 | 0.35499
2015-05-12 15:00 | 273.74 | 158.87 | 114.87 | 285.6389 | 17.9604 | 61.6909 | 66.2873 | 23.7127 | 66.1671 | 58.5693 | 148.9513 | 119.1525 | 0.8 | 1 | 54.748 | 322.8518 | -5.5 | 4.5891 | 1.0816 | 0.28635
2015-05-12 16:00 | 227.01 | 129.1467 | 97.8633 | 279.6341 | 17.971 | 76.6912 | 69.5146 | 20.4854 | 81.173 | 72.574 | 83.743 | 96.86 | 0.8 | 1 | 45.402 | 226.005 | -5.6 | 1.4627 | 1.0941 | 0.20277
2015-05-12 17:00 | 180.28 | 99.4233 | 80.8567 | 274.6226 | 17.9817 | 91.6914 | 72.8767 | 17.1233 | 95.8238 | 86.3746 | 17.3654 | 74.5675 | 0.8 | 1 | 36.056 | 127.9889 | -5.5 | -1.5003 | 1.106 | 0.11608
2015-05-12 18:00 | 133.55 | 69.7 | 63.85 | 266.7915 | 17.9923 | 106.6917 | 76.1533 | 13.8467 | 110.2336 | 99.8545 | 0 | 52.275 | 0.8 | 1 | 26.71 | 78.985 | -5.5 | -3.0317 | 1.1121 | 0.07203
2015-05-12 19:00 | 105.5267 | 56.7433 | 48.7833 | 258.8973 | 18.0029 | 121.6919 | 79.139 | 10.861 | 124.5141 | 112.8111 | 0 | 42.5575 | 0.8 | 1 | 21.1053 | 63.6628 | -5.7 | -3.7105 | 1.1148 | 0.058199
2015-05-12 20:00 | 77.5033 | 43.7867 | 33.7167 | 232.1865 | 18.0135 | 136.6922 | 81.6503 | 8.3497 | 138.7546 | 124.8653 | 0 | 32.84 | 0.8 | 1 | 15.5007 | 48.3407 | -6 | -4.4894 | 1.118 | 0.044315
2015-05-12 21:00 | 49.48 | 30.83 | 18.65 | 165.5716 | 18.0241 | 151.6924 | 83.5325 | 6.4675 | 153.0108 | 135.2738 | 0 | 23.1225 | 0.8 | 1 | 9.896 | 33.0185 | -6.3 | -5.2682 | 1.1211 | 0.030353
2015-05-12 22:00 | 48.49 | 30.9967 | 17.4933 | 188.2284 | 18.0347 | 166.6926 | 84.6674 | 5.3326 | 167.3017 | 142.6287 | 0 | 23.2475 | 0.8 | 1 | 9.698 | 32.9455 | -6.5 | -5.4705 | 1.1219 | 0.030308
2015-05-12 23:00 | 47.5 | 31.1633 | 16.3367 | 186.7979 | 18.0452 | 181.6929 | 84.9827 | 5.0173 | -178.3842 | 144.9485 | 0 | 23.3725 | 0.8 | 1 | 9.5 | 32.8725 | -6.7 | -5.6727 | 1.1227 | 0.030263
2015-05-13 | 46.51 | 31.33 | 15.18 | 157.1714 | 18.0558 | -163.3069 | 84.4576 | 5.5424 | -164.0748 | 141.3159 | 0 | 23.4975 | 0.8 | 1 | 9.302 | 32.7995 | -6.9 | -5.875 | 1.1235 | 0.030217
2015-05-13 01:00 | 72.9833 | 42.8967 | 30.0867 | 251.3445 | 18.0664 | -148.3067 | 83.125 | 6.875 | -149.7955 | 133.0955 | 0 | 32.1725 | 0.8 | 1 | 14.5967 | 46.7692 | -7.1 | -5.6385 | 1.1226 | 0.043051
2015-05-13 02:00 | 99.4567 | 54.4633 | 44.9933 | 289.8082 | 18.0769 | -133.3065 | 81.0686 | 8.9314 | -135.5515 | 122.2163 | 0 | 40.8475 | 0.8 | 1 | 19.8913 | 60.7388 | -6.9 | -5.0019 | 1.12 | 0.055783
2015-05-13 03:00 | 125.93 | 66.03 | 59.9 | 298.2805 | 18.0875 | -118.3063 | 78.4152 | 11.5848 | -121.3151 | 109.9094 | 0 | 49.5225 | 0.8 | 1 | 25.186 | 74.7085 | -7.2 | -4.8654 | 1.1195 | 0.068579
2015-05-13 04:00 | 165.15 | 94.34 | 70.81 | 279.5446 | 18.098 | -103.3061 | 75.3268 | 14.6732 | -107.0217 | 96.811 | 0 | 70.755 | 0.8 | 1 | 33.03 | 103.785 | -7.1 | -3.8567 | 1.1154 | 0.094927
2015-05-13 05:00 | 204.37 | 122.65 | 81.72 | 264.3397 | 18.1085 | -88.3059 | 71.9921 | 18.0079 | -92.5746 | 83.2477 | 31.0805 | 91.9875 | 0.8 | 1 | 40.874 | 163.942 | -7.3 | -2.1768 | 1.1087 | 0.14905
2015-05-13 06:00 | 243.59 | 150.96 | 92.63 | 254.0929 | 18.119 | -73.3057 | 68.62 | 21.38 | -77.8585 | 69.397 | 89.4127 | 113.22 | 0.8 | 1 | 48.718 | 251.3507 | -6.9 | 0.95471 | 1.0962 | 0.22593
2015-05-13 07:00 | 276.6333 | 169.4267 | 107.2067 | 257.8614 | 18.1295 | -58.3055 | 65.4332 | 24.5668 | -62.761 | 55.3628 | 146.5628 | 127.07 | 0.8 | 1 | 55.3267 | 328.9594 | -6.8 | 3.48 | 1.0861 | 0.29297
2015-05-13 08:00 | 309.6767 | 187.8933 | 121.7833 | 265.1644 | 18.14 | -43.3053 | 62.6597 | 27.3403 | -47.2027 | 41.2104 | 199.482 | 140.92 | 0.8 | 1 | 61.9353 | 402.3373 | -6.6 | 5.973 | 1.0761 | 0.35503
2015-05-13 09:00 | 342.72 | 206.36 | 136.36 | 277.0624 | 18.1505 | -28.3051 | 60.5171 | 29.4829 | -31.1714 | 26.9862 | 246.8948 | 154.77 | 0.8 | 1 | 68.544 | 470.2088 | -6.6 | 8.094 | 1.0676 | 0.41165
2015-05-13 10:00 | 356.72 | 213.23 | 143.49 | 280.1495 | 18.161 | -13.3049 | 59.1901 | 30.8099 | -14.7499 | 12.7379 | 273.2548 | 159.9225 | 0.8 | 1 | 71.344 | 504.5213 | -7.3 | 8.4663 | 1.0661 | 0.44107
2015-05-13 11:00 | 370.72 | 220.1 | 150.62 | 290.7695 | 18.1715 | 1.6952 | 58.8015 | 31.1985 | 1.8831 | 2.0158 | 290.5895 | 165.075 | 0.8 | 1 | 74.144 | 529.8085 | -7.1 | 9.4565 | 1.0622 | 0.46145
2015-05-13 12:00 | 384.72 | 226.97 | 157.75 | 309.7858 | 18.1819 | 16.6954 | 59.3879 | 30.6121 | 18.4899 | 15.957 | 297.8493 | 170.2275 | 0.8 | 1 | 76.944 | 545.0208 | -7.1 | 9.9319 | 1.0603 | 0.47385
2015-05-13 13:00 | 348.5133 | 198.9067 | 149.6067 | 307.5438 | 18.1924 | 31.6956 | 60.8921 | 29.1079 | 34.8406 | 30.2033 | 265.7933 | 149.18 | 0.8 | 1 | 69.7027 | 484.6759 | -7.4 | 7.7461 | 1.069 | 0.42486
2015-05-13 14:00 | 312.3067 | 170.8433 | 141.4633 | 313.478 | 18.2028 | 46.6957 | 63.1748 | 26.8252 | 50.775 | 44.4102 | 223.9323 | 128.1325 | 0.8 | 1 | 62.4613 | 414.5262 | -7.5 | 5.4539 | 1.0782 | 0.36649
2015-05-13 15:00 | 276.1 | 142.78 | 133.32 | 328.3134 | 18.2133 | 61.6959 | 66.0415 | 23.9585 | 66.2321 | 58.5335 | 171.3798 | 107.085 | 0.8 | 1 | 55.22 | 333.6848 | -7.8 | 2.6277 | 1.0895 | 0.29811
2015-05-13 16:00 | 228.2533 | 123.06 | 105.1933 | 297.1866 | 18.2237 | 76.6961 | 69.27 | 20.73 | 81.2411 | 72.5232 | 89.251 | 92.295 | 0.8 | 1 | 45.6507 | 227.1967 | -7.5 | -0.4001 | 1.1016 | 0.20523
2015-05-13 17:00 | 180.4067 | 103.34 | 77.0667 | 258.1802 | 18.2341 | 91.6962 | 72.6325 | 17.3675 | 95.8908 | 86.3065 | 16.6317 | 77.505 | 0.8 | 1 | 36.0813 | 130.218 | -7.5 | -3.4307 | 1.1137 | 0.11892
2015-05-13 18:00 | 132.56 | 83.62 | 48.94 | 201.0074 | 18.2445 | 106.6964 | 75.9083 | 14.0917 | 110.296 | 99.7658 | 0 | 62.715 | 0.8 | 1 | 26.512 | 89.227 | -7 | -4.2117 | 1.1168 | 0.081715
2015-05-13 19:00 | 104.68 | 67.75 | 36.93 | 191.6972 | 18.2549 | 121.6965 | 78.8927 | 11.1073 | 124.5686 | 112.6964 | 0 | 50.8125 | 0.8 | 1 | 20.936 | 71.7485 | -7.2 | -4.9579 | 1.1198 | 0.065884
2015-05-13 20:00 | 76.8 | 51.88 | 24.92 | 166.6937 | 18.2653 | 136.6966 | 81.4023 | 8.5977 | 138.7987 | 124.7173 | 0 | 38.91 | 0.8 | 1 | 15.36 | 54.27 | -7.2 | -5.5041 | 1.122 | 0.049931
2015-05-13 21:00 | 48.92 | 36.01 | 12.91 | 110.3709 | 18.2757 | 151.6968 | 83.2828 | 6.7172 | 153.0422 | 135.0838 | 0 | 27.0075 | 0.8 | 1 | 9.784 | 36.7915 | -7.2 | -6.0503 | 1.1242 | 0.033916
2015-05-13 22:00 | 47.52 | 33.8233 | 13.6967 | 140.7749 | 18.2861 | 166.6969 | 84.4166 | 5.5834 | 167.3189 | 142.3958 | 0 | 25.3675 | 0.8 | 1 | 9.504 | 34.8715 | -7.1 | -6.0103 | 1.124 | 0.032142
2015-05-13 23:00 | 46.12 | 31.6367 | 14.4833 | 157.731 | 18.2964 | 181.697 | 84.7315 | 5.2685 | -178.382 | 144.6974 | 0 | 23.7275 | 0.8 | 1 | 9.224 | 32.9515 | -7.2 | -6.1703 | 1.1247 | 0.030389
2015-05-14 | 44.72 | 29.45 | 15.27 | 151.2835 | 18.3068 | -163.3029 | 84.2069 | 5.7931 | -164.0874 | 141.0886 | 0 | 22.0875 | 0.8 | 1 | 8.944 | 31.0315 | -7.3 | -6.3303 | 1.1253 | 0.028635
2015-05-14 01:00 | 69.65 | 41.1333 | 28.5167 | 229.9295 | 18.3171 | -148.3028 | 82.8756 | 7.1244 | -149.8219 | 132.9108 | 0 | 30.85 | 0.8 | 1 | 13.93 | 44.78 | -7.2 | -5.8006 | 1.1232 | 0.041244
2015-05-14 02:00 | 94.58 | 52.8167 | 41.7633 | 261.8048 | 18.3275 | -133.3026 | 80.8209 | 9.1791 | -135.59 | 122.0706 | 0 | 39.6125 | 0.8 | 1 | 18.916 | 58.5285 | -7.3 | -5.471 | 1.1219 | 0.053843
2015-05-14 03:00 | 119.51 | 64.5 | 55.01 | 268.3161 | 18.3378 | -118.3025 | 78.1694 | 11.8306 | -121.3634 | 109.7947 | 0 | 48.375 | 0.8 | 1 | 23.902 | 72.277 | -7.3 | -5.0413 | 1.1202 | 0.066389
2015-05-14 04:00 | 150.1533 | 84.26 | 65.8933 | 255.9674 | 18.3481 | -103.3024 | 75.0825 | 14.9175 | -107.0769 | 96.7206 | 0 | 63.195 | 0.8 | 1 | 30.0307 | 93.2257 | -7.4 | -4.4867 | 1.1179 | 0.085461
2015-05-14 05:00 | 180.7967 | 104.02 | 76.7767 | 245.1458 | 18.3584 | -88.3023 | 71.7486 | 18.2514 | -92.6335 | 83.1769 | 29.1243 | 78.015 | 0.8 | 1 | 36.1593 | 143.2987 | -7.3 | -2.8219 | 1.1113 | 0.13058
2015-05-14 06:00 | 211.44 | 123.78 | 87.66 | 237.8782 | 18.3687 | -73.3022 | 68.3764 | 21.6236 | -77.9174 | 69.3429 | 83.9174 | 92.835 | 0.8 | 1 | 42.288 | 219.0404 | -7.3 | -0.45499 | 1.1018 | 0.1979
2015-05-14 07:00 | 249.1067 | 160.46 | 88.6467 | 211.2492 | 18.379 | -58.3021 | 65.1887 | 24.8113 | -62.8155 | 55.3234 | 120.189 | 120.345 | 0.8 | 1 | 49.8213 | 290.3554 | -7.3 | 1.7736 | 1.0929 | 0.26021
2015-05-14 08:00 | 286.7733 | 197.14 | 89.6333 | 193.5572 | 18.3893 | -43.3021 | 62.4137 | 27.5863 | -47.2482 | 41.185 | 145.6687 | 147.855 | 0.8 | 1 | 57.3547 | 350.8783 | -7.1 | 3.8649 | 1.0845 | 0.31204
2015-05-14 09:00 | 324.44 | 233.82 | 90.62 | 182.7312 | 18.3996 | -28.302 | 60.2696 | 29.7304 | -31.2033 | 26.976 | 162.8493 | 175.365 | 0.8 | 1 | 64.888 | 403.1023 | -7 | 5.5969 | 1.0776 | 0.3562
2015-05-14 10:00 | 340.6333 | 233.5267 | 107.1067 | 207.6065 | 18.4098 | -13.3019 | 58.9416 | 31.0584 | -14.7641 | 12.7519 | 202.4859 | 175.145 | 0.8 | 1 | 68.1267 | 445.7575 | -6.8 | 7.1299 | 1.0715 | 0.39165
2015-05-14 11:00 | 356.8267 | 233.2333 | 123.5933 | 236.8998 | 18.4201 | 1.6982 | 58.5529 | 31.4471 | 1.8886 | 2.1748 | 236.7291 | 174.925 | 0.8 | 1 | 71.3653 | 483.0195 | -6.7 | 8.3944 | 1.0664 | 0.42238
2015-05-14 12:00 | 373.02 | 232.94 | 140.08 | 273.0945 | 18.4303 | 16.6982 | 59.1404 | 30.8596 | 18.5148 | 15.9693 | 262.5556 | 174.705 | 0.8 | 1 | 74.604 | 511.8646 | -6.1 | 9.8958 | 1.0604 | 0.44509
2015-05-14 13:00 | 379.5 | 188.1667 | 191.3333 | 390.3196 | 18.4406 | 31.6983 | 60.6465 | 29.3535 | 34.8821 | 30.1954 | 337.3591 | 141.125 | 0.8 | 1 | 75.9 | 554.3841 | -5.6 | 11.7245 | 1.0531 | 0.47873
2015-05-14 14:00 | 385.98 | 143.3933 | 242.5867 | 533.0921 | 18.4508 | 46.6984 | 62.9315 | 27.0685 | 50.8289 | 44.3876 | 380.9604 | 107.545 | 0.8 | 1 | 77.196 | 565.7014 | -5.7 | 11.9782 | 1.0521 | 0.48804
2015-05-14 15:00 | 392.46 | 98.62 | 293.84 | 716.8211 | 18.461 | 61.6984 | 65.8001 | 24.1999 | 66.2937 | 58.4968 | 374.5724 | 73.965 | 0.8 | 1 | 78.492 | 527.0294 | -5.4 | 11.0697 | 1.0557 | 0.45624
2015-05-14 16:00 | 313.35 | 88.36 | 224.99 | 628.6741 | 18.4713 | 76.6985 | 69.0299 | 20.9701 | 81.3057 | 72.4715 | 189.3442 | 66.27 | 0.8 | 1 | 62.67 | 318.2842 | -5 | 4.9464 | 1.0802 | 0.28193
2015-05-14 17:00 | 234.24 | 78.1 | 156.14 | 516.1791 | 18.4815 | 91.6985 | 72.3927 | 17.6073 | 95.9543 | 86.2377 | 33.87 | 58.575 | 0.8 | 1 | 46.848 | 139.293 | -5.1 | -0.74709 | 1.103 | 0.12598
2015-05-14 18:00 | 155.13 | 67.84 | 87.29 | 352.6269 | 18.4917 | 106.6986 | 75.6679 | 14.3321 | 110.3549 | 99.6766 | 0 | 50.88 | 0.8 | 1 | 31.026 | 81.906 | -4.8 | -2.2404 | 1.109 | 0.074481
2015-05-14 19:00 | 123.1033 | 56.88 | 66.2233 | 336.5238 | 18.5018 | 121.6986 | 78.6509 | 11.3491 | 124.6199 | 112.5817 | 0 | 42.66 | 0.8 | 1 | 24.6207 | 67.2807 | -5 | -2.8975 | 1.1116 | 0.061327
2015-05-14 20:00 | 91.0767 | 45.92 | 45.1567 | 293.8081 | 18.512 | 136.6986 | 81.1589 | 8.8411 | 138.8396 | 124.5699 | 0 | 34.44 | 0.8 | 1 | 18.2153 | 52.6553 | -4.9 | -3.2545 | 1.113 | 0.048057
2015-05-14 21:00 | 59.05 | 34.96 | 24.09 | 198.7415 | 18.5222 | 151.6987 | 83.0379 | 6.9621 | 153.0708 | 134.8958 | 0 | 26.22 | 0.8 | 1 | 11.81 | 38.03 | -5.1 | -3.9116 | 1.1156 | 0.034791
2015-05-14 22:00 | 52.1367 | 31.73 | 20.4067 | 200.9229 | 18.5323 | 166.6987 | 84.1707 | 5.8293 | 167.3335 | 142.1666 | 0 | 23.7975 | 0.8 | 1 | 10.4273 | 34.2248 | -4.9 | -3.8305 | 1.1153 | 0.031301
2015-05-14 23:00 | 45.2233 | 28.5 | 16.7233 | 174.0222 | 18.5425 | 181.6987 | 84.4854 | 5.5146 | -178.382 | 144.4515 | 0 | 21.375 | 0.8 | 1 | 9.0447 | 30.4197 | -5.2 | -4.2494 | 1.117 | 0.027863
2015-05-15 | 38.31 | 25.27 | 13.04 | 123.9577 | 18.5526 | -163.3013 | 83.9615 | 6.0385 | -164.1019 | 140.8668 | 0 | 18.9525 | 0.8 | 1 | 7.662 | 26.6145 | -4.9 | -4.0683 | 1.1163 | 0.024361
2015-05-15 01:00 | 64.1933 | 34.0633 | 30.13 | 234.9336 | 18.5628 | -148.3013 | 82.6316 | 7.3684 | -149.8501 | 132.7309 | 0 | 25.5475 | 0.8 | 1 | 12.8387 | 38.3862 | -4.3 | -3.1004 | 1.1124 | 0.035015
2015-05-15 02:00 | 90.0767 | 42.8567 | 47.22 | 288.4668 | 18.5729 | -133.3013 | 80.5787 | 9.4213 | -135.6301 | 121.9293 | 0 | 32.1425 | 0.8 | 1 | 18.0153 | 50.1578 | -4.8 | -3.2326 | 1.1129 | 0.045774
2015-05-15 03:00 | 115.96 | 51.65 | 64.31 | 307.5217 | 18.583 | -118.3013 | 77.929 | 12.071 | -121.413 | 109.6841 | 0 | 38.7375 | 0.8 | 1 | 23.192 | 61.9295 | -4.3 | -2.3647 | 1.1095 | 0.056341
2015-05-15 04:00 | 139.39 | 68.7467 | 70.6433 | 270.1936 | 18.5931 | -103.3013 | 74.8436 | 15.1564 | -107.1334 | 96.6341 | 0 | 51.56 | 0.8 | 1 | 27.878 | 79.438 | -4.4 | -1.9176 | 1.1077 | 0.072153
2015-05-15 05:00 | 162.82 | 85.8433 | 76.9767 | 242.7288 | 18.6032 | -88.3013 | 71.5105 | 18.4895 | -92.6937 | 83.1099 | 29.119 | 64.3825 | 0.8 | 1 | 32.564 | 126.0655 | -4.1 | -0.16045 | 1.1006 | 0.11378
2015-05-15 06:00 | 186.25 | 102.94 | 83.31 | 223.7305 | 18.6133 | -73.3013 | 68.1383 | 21.8617 | -77.9776 | 69.2924 | 79.1109 | 77.205 | 0.8 | 1 | 37.25 | 193.5659 | -3.9 | 2.1489 | 1.0914 | 0.17323
2015-05-15 07:00 | 207.5933 | 131.9367 | 75.6567 | 178.6827 | 18.6234 | -58.3013 | 64.9497 | 25.0503 | -62.8717 | 55.2877 | 101.752 | 98.9525 | 0.8 | 1 | 41.5187 | 242.2232 | -3.8 | 3.7695 | 1.0849 | 0.21549
2015-05-15 08:00 | 228.9367 | 160.9333 | 68.0033 | 145.6796 | 18.6334 | -43.3013 | 62.1732 | 27.8268 | -47.2956 | 41.1636 | 109.6724 | 120.7 | 0.8 | 1 | 45.7873 | 276.1597 | -3.3 | 5.33 | 1.0787 | 0.24427
2015-05-15 09:00 | 250.28 | 189.93 | 60.35 | 120.8002 | 18.6435 | -28.3013 | 60.0274 | 29.9726 | -31.2372 | 26.9705 | 107.662 | 142.4475 | 0.8 | 1 | 50.056 | 300.1655 | -1.3 | 8.0802 | 1.0677 | 0.26279
2015-05-15 10:00 | 262.32 | 197.2633 | 65.0567 | 125.2186 | 18.6535 | -13.3013 | 58.6983 | 31.3017 | -14.7808 | 12.7725 | 122.1201 | 147.9475 | 0.8 | 1 | 52.464 | 322.5316 | -2 | 8.0791 | 1.0677 | 0.28238
2015-05-15 11:00 | 274.36 | 204.5967 | 69.7633 | 132.7985 | 18.6636 | 1.6986 | 58.3094 | 31.6906 | 1.8914 | 2.344 | 132.6874 | 153.4475 | 0.8 | 1 | 54.872 | 341.0069 | -0.4 | 10.2565 | 1.059 | 0.29612
2015-05-15 12:00 | 286.4 | 211.93 | 74.47 | 144.1637 | 18.6736 | 16.6986 | 58.8979 | 31.1021 | 18.5367 | 15.9828 | 138.591 | 158.9475 | 0.8 | 1 | 57.28 | 354.8185 | -0.7 | 10.3881 | 1.0584 | 0.30796
2015-05-15 13:00 | 300.3633 | 189.4167 | 110.9467 | 224.6544 | 18.6836 | 31.6986 | 60.4057 | 29.5943 | 34.9204 | 30.1872 | 194.1884 | 142.0625 | 0.8 | 1 | 60.0727 | 396.3236 | -1.5 | 10.8851 | 1.0565 | 0.34333
2015-05-15 14:00 | 314.3267 | 166.9033 | 147.4233 | 321.3513 | 18.6937 | 46.6985 | 62.6928 | 27.3072 | 50.8795 | 44.3643 | 229.7369 | 125.1775 | 0.8 | 1 | 62.8653 | 417.7797 | -1.8 | 11.2556 | 1.055 | 0.36141
2015-05-15 15:00 | 328.29 | 144.39 | 183.9 | 444.5391 | 18.7037 | 61.6985 | 65.5633 | 24.4367 | 66.3518 | 58.4592 | 232.5407 | 108.2925 | 0.8 | 1 | 65.658 | 406.4912 | -1.5 | 11.2028 | 1.0552 | 0.35172
2015-05-15 16:00 | 258.3467 | 114.0167 | 144.33 | 399.0135 | 18.7137 | 76.6984 | 68.7943 | 21.2057 | 81.3668 | 72.419 | 120.5237 | 85.5125 | 0.8 | 1 | 51.6693 | 257.7055 | -1.6 | 6.4533 | 1.0742 | 0.227
2015-05-15 17:00 | 188.4033 | 83.6433 | 104.76 | 341.9011 | 18.7237 | 91.6984 | 72.1573 | 17.8427 | 96.0144 | 86.1683 | 22.848 | 62.7325 | 0.8 | 1 | 37.6807 | 123.2611 | -2 | 1.8519 | 1.0926 | 0.11043
2015-05-15 18:00 | 118.46 | 53.27 | 65.19 | 259.1743 | 18.7336 | 106.6983 | 75.432 | 14.568 | 110.4104 | 99.587 | 0 | 39.9525 | 0.8 | 1 | 23.692 | 63.6445 | -1.6 | 0.38889 | 1.0984 | 0.057326
2015-05-15 19:00 | 95.12 | 43.69 | 51.43 | 256.071 | 18.7436 | 121.6982 | 78.4138 | 11.5862 | 124.6678 | 112.467 | 0 | 32.7675 | 0.8 | 1 | 19.024 | 51.7915 | -1.5 | 0.11848 | 1.0995 | 0.046696
2015-05-15 20:00 | 71.78 | 34.11 | 37.67 | 238.7072 | 18.7536 | 136.6982 | 80.9203 | 9.0797 | 138.8775 | 124.4233 | 0 | 25.5825 | 0.8 | 1 | 14.356 | 39.9385 | -1.3 | -0.051922 | 1.1002 | 0.036031
2015-05-15 21:00 | 48.44 | 24.53 | 23.91 | 190.7169 | 18.7635 | 151.6981 | 82.7979 | 7.2021 | 153.0964 | 134.7099 | 0 | 18.3975 | 0.8 | 1 | 9.688 | 28.0855 | -1.5 | -0.62233 | 1.1025 | 0.02539
2015-05-15 22:00 | 40 | 20.6767 | 19.3233 | 182.7353 | 18.7734 | 166.698 | 83.9299 | 6.0701 | 167.3455 | 141.9412 | 0 | 15.5075 | 0.8 | 1 | 8 | 23.5075 | -2.1 | -1.3654 | 1.1055 | 0.021309
2015-05-15 23:00 | 31.56 | 16.8233 | 14.7367 | 146.9513 | 18.7834 | 181.698 | 84.2446 | 5.7554 | -178.3844 | 144.211 | 0 | 12.6175 | 0.8 | 1 | 6.312 | 18.9295 | -1.7 | -1.1085 | 1.1044 | 0.017143
2015-05-16 | 23.12 | 12.97 | 10.15 | 92.8097 | 18.7933 | -163.3021 | 83.7214 | 6.2786 | -164.1185 | 140.6503 | 0 | 9.7275 | 0.8 | 1 | 4.624 | 14.3515 | -1.5 | -1.0515 | 1.1042 | 0.012995
2015-05-16 01:00 | 21.8033 | 15.0267 | 6.7767 | 51.1917 | 18.8032 | -148.3022 | 82.393 | 7.607 | -149.88 | 132.5559 | 0 | 11.27 | 0.8 | 1 | 4.3607 | 15.6307 | -1.1 | -0.61154 | 1.1024 | 0.01413
2015-05-16 02:00 | 20.4867 | 17.0833 | 3.4033 | 20.286 | 18.8131 | -133.3023 | 80.342 | 9.658 | -135.6716 | 121.7925 | 0 | 12.8125 | 0.8 | 1 | 4.0973 | 16.9098 | -1.4 | -0.87157 | 1.1035 | 0.015301
2015-05-16 03:00 | 19.17 | 19.14 | 0.03 | 0.14076 | 18.823 | -118.3024 | 77.6942 | 12.3058 | -121.464 | 109.5776 | 0 | 14.355 | 0.8 | 1 | 3.834 | 18.189 | -1 | -0.43159 | 1.1017 | 0.016432
2015-05-16 04:00 | 69.1333 | 50.0933 | 19.04 | 71.7458 | 18.8329 | -103.3025 | 74.6104 | 15.3896 | -107.1912 | 96.5514 | 0 | 37.57 | 0.8 | 1 | 13.8267 | 51.3967 | -1 | 0.60615 | 1.0976 | 0.046258
2015-05-16 05:00 | 119.0967 | 81.0467 | 38.05 | 118.5453 | 18.8428 | -88.3026 | 71.2781 | 18.7219 | -92.7552 | 83.0466 | 14.3513 | 60.785 | 0.8 | 1 | 23.8193 | 98.9556 | -0.7 | 2.3924 | 1.0904 | 0.088481
2015-05-16 06:00 | 169.06 | 112 | 57.06 | 151.7029 | 18.8527 | -73.3027 | 67.9058 | 22.0942 | -78.0392 | 69.2456 | 53.7579 | 84 | 0.8 | 1 | 33.812 | 171.5699 | -1.3 | 4.0616 | 1.0838 | 0.15247
2015-05-16 07:00 | 206.26 | 139.7533 | 66.5067 | 155.7168 | 18.8625 | -58.3028 | 64.7163 | 25.2837 | -62.9293 | 55.2557 | 88.7453 | 104.815 | 0.8 | 1 | 41.252 | 234.8123 | -1.2 | 6.1379 | 1.0754 | 0.20707
2015-05-16 08:00 | 243.46 | 167.5067 | 75.9533 | 161.4574 | 18.8724 | -43.303 | 61.9382 | 28.0618 | -47.3447 | 41.1461 | 121.5829 | 125.63 | 0.8 | 1 | 48.692 | 295.9049 | -0.1 | 9.147 | 1.0634 | 0.25803
2015-05-16 09:00 | 280.66 | 195.26 | 85.4 | 169.7276 | 18.8822 | -28.3031 | 59.7908 | 30.2092 | -31.2732 | 26.9693 | 151.2697 | 146.445 | 0.8 | 1 | 56.132 | 353.8467 | 0.2 | 11.2577 | 1.055 | 0.3061
2015-05-16 10:00 | 291.14 | 194.1533 | 96.9867 | 185.4115 | 18.892 | -13.3032 | 58.4603 | 31.5397 | -14.7998 | 12.7993 | 180.8044 | 145.615 | 0.8 | 1 | 58.228 | 384.6474 | 0.1 | 12.1202 | 1.0515 | 0.33166
2015-05-16 11:00 | 301.62 | 193.0467 | 108.5733 | 205.2946 | 18.9019 | 1.6967 | 58.0711 | 31.9289 | 1.8914 | 2.52 | 205.096 | 144.785 | 0.8 | 1 | 60.324 | 410.205 | 0.1 | 12.9189 | 1.0483 | 0.35262
2015-05-16 12:00 | 312.1 | 191.94 | 120.16 | 231.0279 | 18.9117 | 16.6965 | 58.6603 | 31.3397 | 18.5555 | 15.9971 | 222.0815 | 143.955 | 0.8 | 1 | 62.42 | 428.4565 | 0.7 | 14.0893 | 1.0436 | 0.36667
2015-05-16 13:00 | 313.8833 | 190.5833 | 123.3 | 247.8738 | 18.9215 | 31.6964 | 60.1699 | 29.8301 | 34.9554 | 30.1785 | 214.2778 | 142.9375 | 0.8 | 1 | 62.7767 | 419.992 | 0.5 | 13.6247 | 1.0455 | 0.36006
2015-05-16 14:00 | 315.6667 | 189.2267 | 126.44 | 273.4522 | 18.9313 | 46.6963 | 62.4589 | 27.5411 | 50.9266 | 44.3401 | 195.5739 | 141.92 | 0.8 | 1 | 63.1333 | 400.6272 | 0.5 | 13.0196 | 1.0479 | 0.34426
2015-05-16 15:00 | 317.45 | 187.87 | 129.58 | 310.4662 | 18.9411 | 61.6961 | 65.3312 | 24.6688 | 66.4063 | 58.4208 | 162.5838 | 140.9025 | 0.8 | 1 | 63.49 | 366.9763 | 0.9 | 12.368 | 1.0505 | 0.31613
2015-05-16 16:00 | 267.26 | 147.11 | 120.15 | 328.7516 | 18.9508 | 76.696 | 68.5633 | 21.4367 | 81.4243 | 72.3656 | 99.5925 | 110.3325 | 0.8 | 1 | 53.452 | 263.377 | 1 | 9.2305 | 1.0631 | 0.22959
2015-05-16 17:00 | 217.07 | 106.35 | 110.72 | 356.8896 | 18.9606 | 91.6958 | 71.9265 | 18.0735 | 96.0709 | 86.0982 | 24.2852 | 79.7625 | 0.8 | 1 | 43.414 | 147.4617 | 1.4 | 6.0082 | 1.076 | 0.1301
2015-05-16 18:00 | 166.88 | 65.59 | 101.29 | 396.5394 | 18.9704 | 106.6956 | 75.2006 | 14.7994 | 110.4625 | 99.497 | 0 | 49.1925 | 0.8 | 1 | 33.376 | 82.5685 | 1.2 | 3.7803 | 1.0849 | 0.073453
2015-05-16 19:00 | 130.44 | 55.1467 | 75.2933 | 367.616 | 18.9801 | 121.6955 | 78.1813 | 11.8187 | 124.7125 | 112.3525 | 0 | 41.36 | 0.8 | 1 | 26.088 | 67.448 | 0.6 | 2.7077 | 1.0892 | 0.060239
2015-05-16 20:00 | 94 | 44.7033 | 49.2967 | 304.608 | 18.9898 | 136.6953 | 80.6865 | 9.3135 | 138.9123 | 124.2777 | 0 | 33.5275 | 0.8 | 1 | 18.8 | 52.3275 | 0.8 | 2.4352 | 1.0903 | 0.046781
2015-05-16 21:00 | 57.56 | 34.26 | 23.3 | 180.0103 | 18.9996 | 151.6951 | 82.5629 | 7.4371 | 153.1193 | 134.5261 | 0 | 25.695 | 0.8 | 1 | 11.512 | 37.207 | 0.5 | 1.6627 | 1.0933 | 0.033358
2015-05-16 22:00 | 55.49 | 36.12 | 19.37 | 176.3567 | 19.0093 | 166.695 | 83.6942 | 6.3058 | 167.355 | 141.7198 | 0 | 27.09 | 0.8 | 1 | 11.098 | 38.188 | 0.4 | 1.5934 | 1.0936 | 0.034246
2015-05-16 23:00 | 53.42 | 37.98 | 15.44 | 147.931 | 19.019 | 181.6948 | 84.009 | 5.991 | -178.389 | 143.9758 | 0 | 28.485 | 0.8 | 1 | 10.684 | 39.169 | 0.9 | 2.124 | 1.0915 | 0.035058
2015-05-17 | 51.35 | 39.84 | 11.51 | 101.4684 | 19.0287 | -163.3054 | 83.4867 | 6.5133 | -164.1371 | 140.4394 | 0 | 29.88 | 0.74 | 0.9 | 9.4998 | 39.3798 | 0.8 | 2.0306 | 1.0919 | 0.035258
2015-05-17 01:00 | 72.72 | 50.0167 | 22.7033 | 166.4347 | 19.0384 | -148.3056 | 82.1598 | 7.8402 | -149.9116 | 132.386 | 0 | 37.5125 | 0.73984 | 0.89974 | 13.4504 | 50.9629 | 2.5 | 4.0926 | 1.0836 | 0.045284
2015-05-17 02:00 | 94.09 | 60.1933 | 33.8967 | 197.3688 | 19.0481 | -133.3058 | 80.1108 | 9.8892 | -135.7146 | 121.6601 | 0 | 45.145 | 0.73969 | 0.89948 | 17.3993 | 62.5443 | 2.5 | 4.4545 | 1.0822 | 0.055501
2015-05-17 03:00 | 115.46 | 70.37 | 45.09 | 207.7548 | 19.0578 | -118.306 | 77.4651 | 12.5349 | -121.5163 | 109.4752 | 0 | 52.7775 | 0.73953 | 0.89922 | 21.3466 | 74.1241 | 2.5 | 4.8164 | 1.0807 | 0.065689
2015-05-17 04:00 | 148.0433 | 102.1467 | 45.8967 | 170.4874 | 19.0674 | -103.3062 | 74.3828 | 15.6172 | -107.2501 | 96.4727 | 0 | 76.61 | 0.73938 | 0.89896 | 27.3649 | 103.9749 | 1.4 | 4.6492 | 1.0814 | 0.0922
2015-05-17 05:00 | 180.6267 | 133.9233 | 46.7033 | 143.8268 | 19.0771 | -88.3064 | 71.0514 | 18.9486 | -92.8178 | 82.9871 | 17.5602 | 100.4425 | 0.73922 | 0.8987 | 33.3807 | 151.3834 | 0.6 | 5.3307 | 1.0787 | 0.1339
2015-05-17 06:00 | 213.21 | 165.7 | 47.51 | 125.0942 | 19.0867 | -73.3066 | 67.6791 | 22.3209 | -78.102 | 69.2025 | 44.4167 | 124.275 | 0.73906 | 0.89844 | 39.3939 | 208.0856 | 0.5 | 7.0027 | 1.072 | 0.18291
2015-05-17 07:00 | 258.3467 | 190.2067 | 68.14 | 158.2111 | 19.0964 | -58.3068 | 64.4886 | 25.5114 | -62.9883 | 55.2274 | 90.231 | 142.655 | 0.73891 | 0.89818 | 47.7235 | 280.6095 | 0.1 | 8.869 | 1.0645 | 0.24495
2015-05-17 08:00 | 303.4833 | 214.7133 | 88.77 | 187.2976 | 19.106 | -43.307 | 61.7089 | 28.2911 | -47.3955 | 41.1324 | 141.071 | 161.035 | 0.73875 | 0.89792 | 56.0496 | 358.1555 | 0.4 | 11.5924 | 1.0536 | 0.30944
2015-05-17 09:00 | 348.62 | 239.22 | 109.4 | 215.932 | 19.1156 | -28.3073 | 59.5597 | 30.4403 | -31.3113 | 26.9723 | 192.4442 | 179.415 | 0.73859 | 0.89766 | 64.3721 | 436.2313 | 0.4 | 14.0322 | 1.0439 | 0.3734
2015-05-17 10:00 | 335.9067 | 248.59 | 87.3167 | 165.8302 | 19.1252 | -13.3075 | 58.2278 | 31.7722 | -14.8213 | 12.832 | 161.6886 | 186.4425 | 0.73844 | 0.8974 | 62.0115 | 410.1426 | 0.8 | 13.617 | 1.0455 | 0.35163
2015-05-17 11:00 | 323.1933 | 257.96 | 65.2333 | 122.547 | 19.1348 | 1.6923 | 57.8381 | 32.1619 | 1.8887 | 2.6999 | 122.4109 | 193.47 | 0.73828 | 0.89714 | 59.6519 | 375.5328 | 0.8 | 12.5354 | 1.0499 | 0.32329
2015-05-17 12:00 | 310.48 | 267.33 | 43.15 | 82.4149 | 19.1444 | 16.6921 | 58.428 | 31.572 | 18.5712 | 16.0122 | 79.2175 | 200.4975 | 0.73813 | 0.89687 | 57.2933 | 337.0082 | 1.5 | 12.0315 | 1.0519 | 0.29068
2015-05-17 13:00 | 324.6067 | 230.78 | 93.8267 | 187.3076 | 19.154 | 31.6918 | 59.9389 | 30.0611 | 34.9871 | 30.1694 | 161.9356 | 173.085 | 0.73797 | 0.89661 | 59.8874 | 394.908 | 1 | 13.3409 | 1.0466 | 0.33893
2015-05-17 14:00 | 338.7333 | 194.23 | 144.5033 | 310.1423 | 19.1636 | 46.6916 | 62.2298 | 27.7702 | 50.9703 | 44.3152 | 221.9091 | 145.6725 | 0.73781 | 0.89635 | 62.4804 | 430.062 | 1.3 | 14.7394 | 1.041 | 0.36712
2015-05-17 15:00 | 352.86 | 157.68 | 195.18 | 463.6366 | 19.1731 | 61.6913 | 65.1038 | 24.8962 | 66.4574 | 58.3816 | 243.0661 | 118.26 | 0.73766 | 0.89609 | 65.0723 | 426.3985 | 1.4 | 14.725 | 1.0411 | 0.36402
2015-05-17 16:00 | 274.4767 | 138.0933 | 136.3833 | 369.4538 | 19.1827 | 76.6911 | 68.3369 | 21.6631 | 81.4783 | 72.3115 | 112.2554 | 103.57 | 0.7375 | 0.89583 | 50.6066 | 266.432 | 1.5 | 9.826 | 1.0607 | 0.23173
2015-05-17 17:00 | 196.0933 | 118.5067 | 77.5867 | 247.1028 | 19.1922 | 91.6908 | 71.7004 | 18.2996 | 96.1239 | 86.0275 | 17.1187 | 88.88 | 0.73734 | 0.89557 | 36.147 | 142.1457 | 1 | 5.4421 | 1.0782 | 0.12568
2015-05-17 18:00 | 117.71 | 98.92 | 18.79 | 72.4764 | 19.2018 | 106.6906 | 74.974 | 15.026 | 110.5112 | 99.4068 | 0 | 74.19 | 0.73719 | 0.89531 | 21.6936 | 95.8836 | 1 | 3.9964 | 1.084 | 0.08523
2015-05-17 19:00 | 95.54 | 80.33 | 15.21 | 72.8789 | 19.2113 | 121.6903 | 77.9537 | 12.0463 | 124.754 | 112.2382 | 0 | 60.2475 | 0.73703 | 0.89505 | 17.604 | 77.8515 | 1.2 | 3.6329 | 1.0855 | 0.069294
2015-05-17 20:00 | 73.37 | 61.74 | 11.63 | 70.1544 | 19.2208 | 136.69 | 80.4576 | 9.5424 | 138.944 | 124.1331 | 0 | 46.305 | 0.73688 | 0.89479 | 13.5161 | 59.8211 | 0.6 | 2.4694 | 1.0901 | 0.053474
2015-05-17 21:00 | 51.2 | 43.15 | 8.05 | 60.3379 | 19.2303 | 151.6898 | 82.333 | 7.667 | 153.1393 | 134.3447 | 0 | 32.3625 | 0.73672 | 0.89453 | 9.43 | 41.7925 | 0.8 | 2.106 | 1.0916 | 0.037408
2015-05-17 22:00 | 47.8833 | 41.6533 | 6.23 | 54.7301 | 19.2398 | 166.6895 | 83.4638 | 6.5362 | 167.3619 | 141.5024 | 0 | 31.24 | 0.73656 | 0.89427 | 8.8173 | 40.0573 | 0.8 | 2.0518 | 1.0918 | 0.035862
2015-05-17 23:00 | 44.5667 | 40.1567 | 4.41 | 40.6944 | 19.2493 | 181.6892 | 83.7787 | 6.2213 | -178.3958 | 143.746 | 0 | 30.1175 | 0.73641 | 0.89401 | 8.2048 | 38.3223 | 0.5 | 1.6976 | 1.0932 | 0.034353
2015-05-18 | 41.25 | 38.66 | 2.59 | 22.0598 | 19.2588 | -163.3111 | 83.2575 | 6.7425 | -164.1576 | 140.2341 | 0 | 28.995 | 0.73625 | 0.89375 | 7.5926 | 36.5876 | -0.4 | 0.74336 | 1.097 | 0.032913
2015-05-18 01:00 | 58.0533 | 54.6233 | 3.43 | 24.4402 | 19.2682 | -148.3114 | 81.9323 | 8.0677 | -149.9448 | 132.221 | 0 | 40.9675 | 0.73609 | 0.89349 | 10.6832 | 51.6507 | 0.3 | 1.9141 | 1.0923 | 0.046265
2015-05-18 02:00 | 74.8567 | 70.5867 | 4.27 | 24.3141 | 19.2777 | -133.3117 | 79.8854 | 10.1146 | -135.759 | 121.5323 | 0 | 52.94 | 0.73594 | 0.89323 | 13.7725 | 66.7125 | 0.2 | 2.2848 | 1.0909 | 0.059675
2015-05-18 03:00 | 91.66 | 86.55 | 5.11 | 23.139 | 19.2871 | -118.312 | 77.2416 | 12.7584 | -121.5698 | 109.377 | 0 | 64.9125 | 0.73578 | 0.89297 | 16.8604 | 81.7729 | -0.1 | 2.4554 | 1.0902 | 0.073101
2015-05-18 04:00 | 119.26 | 113.2067 | 6.0533 | 22.1787 | 19.2966 | -103.3123 | 74.161 | 15.839 | -107.3102 | 96.3978 | 0 | 84.905 | 0.73563 | 0.89271 | 21.9327 | 106.8377 | -0.3 | 3.0387 | 1.0878 | 0.095303
2015-05-18 05:00 | 146.86 | 139.8633 | 6.9967 | 21.3077 | 19.306 | -88.3126 | 70.8305 | 19.1695 | -92.8816 | 82.9313 | 2.6221 | 104.8975 | 0.73547 | 0.89245 | 27.0027 | 134.5223 | 0.2 | 4.4038 | 1.0824 | 0.1194
2015-05-18 06:00 | 174.46 | 166.52 | 7.94 | 20.7117 | 19.3154 | -73.3129 | 67.4581 | 22.5419 | -78.1661 | 69.163 | 7.3674 | 124.89 | 0.73531 | 0.89219 | 32.0707 | 164.328 | -0.1 | 5.0353 | 1.0799 | 0.14551
2015-05-18 07:00 | 237.6933 | 194.7067 | 42.9867 | 99.0058 | 19.3248 | -58.3132 | 64.2667 | 25.7333 | -63.0488 | 55.2027 | 56.5001 | 146.03 | 0.73516 | 0.89193 | 43.6854 | 246.2155 | 0.1 | 7.7942 | 1.0688 | 0.21579
2015-05-18 08:00 | 300.9267 | 222.8933 | 78.0333 | 163.4601 | 19.3342 | -43.3135 | 61.4853 | 28.5147 | -47.448 | 41.1224 | 123.1355 | 167.17 | 0.735 | 0.89167 | 55.2953 | 345.6008 | 0 | 10.8 | 1.0568 | 0.29949
2015-05-18 09:00 | 364.16 | 251.08 | 113.08 | 221.7124 | 19.3436 | -28.3138 | 59.3342 | 30.6658 | -31.3513 | 26.9794 | 197.5833 | 188.31 | 0.73484 | 0.89141 | 66.9002 | 452.7935 | 0.6 | 14.7498 | 1.041 | 0.38651
2015-05-18 10:00 | 365.4233 | 253.95 | 111.4733 | 210.3641 | 19.353 | -13.3142 | 58.0008 | 31.9992 | -14.8451 | 12.8702 | 205.0792 | 190.4625 | 0.73469 | 0.89115 | 67.118 | 462.6596 | 0.6 | 15.0581 | 1.0398 | 0.39447
2015-05-18 11:00 | 366.6867 | 256.82 | 109.8667 | 205.1007 | 19.3624 | 1.6855 | 57.6105 | 32.3895 | 1.8832 | 2.8816 | 204.8414 | 192.615 | 0.73453 | 0.89089 | 67.3357 | 464.7921 | 0.8 | 15.3248 | 1.0387 | 0.39588
2015-05-18 12:00 | 367.95 | 259.69 | 108.26 | 205.4486 | 19.3718 | 16.6852 | 58.2008 | 31.7992 | 18.584 | 16.0277 | 197.4625 | 194.7675 | 0.73438 | 0.89062 | 67.5533 | 459.7833 | 0.5 | 14.8682 | 1.0405 | 0.3923
2015-05-18 13:00 | 319.78 | 233.0533 | 86.7267 | 171.9638 | 19.3811 | 31.6848 | 59.713 | 30.287 | 35.0156 | 30.1597 | 148.6848 | 174.79 | 0.73422 | 0.89036 | 58.6971 | 382.1719 | 0.6 | 12.5429 | 1.0498 | 0.329
2015-05-18 14:00 | 271.61 | 206.4167 | 65.1933 | 138.8911 | 19.3905 | 46.6845 | 62.0056 | 27.9944 | 51.0105 | 44.2894 | 99.4212 | 154.8125 | 0.73406 | 0.8901 | 49.8447 | 304.0784 | 0.8 | 10.3024 | 1.0588 | 0.264
2015-05-18 15:00 | 223.44 | 179.78 | 43.66 | 102.8509 | 19.3998 | 61.6842 | 64.8811 | 25.1189 | 66.5049 | 58.3414 | 53.982 | 134.835 | 0.73391 | 0.88984 | 40.996 | 229.813 | 1 | 8.1817 | 1.0673 | 0.20112
2015-05-18 16:00 | 181.4033 | 144.4167 | 36.9867 | 99.2288 | 19.4091 | 76.6838 | 68.1152 | 21.8848 | 81.5288 | 72.2567 | 30.2404 | 108.3125 | 0.73375 | 0.88958 | 33.2762 | 171.829 | 0.1 | 5.4697 | 1.0781 | 0.15191
2015-05-18 17:00 | 139.3667 | 109.0533 | 30.3133 | 95.4295 | 19.4184 | 91.6835 | 71.479 | 18.521 | 96.1735 | 85.9563 | 6.7295 | 81.79 | 0.73359 | 0.88932 | 25.5596 | 114.0791 | -0.2 | 3.365 | 1.0865 | 0.10164
2015-05-18 18:00 | 97.33 | 73.69 | 23.64 | 89.8879 | 19.4277 | 106.6831 | 74.7522 | 15.2478 | 110.5564 | 99.3164 | 0 | 55.2675 | 0.73344 | 0.88906 | 17.8464 | 73.1139 | 0.3 | 2.5848 | 1.0897 | 0.065329
2015-05-18 19:00 | 80.3233 | 61.3733 | 18.95 | 89.175 | 19.437 | 121.6827 | 77.7309 | 12.2691 | 124.7922 | 112.1243 | 0 | 46.03 | 0.73328 | 0.8888 | 14.7249 | 60.7549 | 0.4 | 2.2986 | 1.0908 | 0.054343
2015-05-18 20:00 | 63.3167 | 49.0567 | 14.26 | 84.0657 | 19.4463 | 136.6824 | 80.2337 | 9.7663 | 138.9727 | 123.9897 | 0 | 36.7925 | 0.73313 | 0.88854 | 11.6048 | 48.3973 | 0.2 | 1.7124 | 1.0932 | 0.043382
2015-05-18 21:00 | 46.31 | 36.74 | 9.57 | 69.7002 | 19.4556 | 151.682 | 82.1082 | 7.8918 | 153.1565 | 134.1657 | 0 | 27.555 | 0.73297 | 0.88828 | 8.4859 | 36.0409 | 0 | 1.1263 | 1.0955 | 0.032376
2015-05-18 22:00 | 46.0033 | 37.0667 | 8.9367 | 75.9051 | 19.4649 | 166.6816 | 83.2386 | 6.7614 | 167.3663 | 141.2892 | 0 | 27.8 | 0.73281 | 0.88802 | 8.428 | 36.228 | -0.6 | 0.53212 | 1.0979 | 0.032614
2015-05-18 23:00 | 45.6967 | 37.3933 | 8.3033 | 73.9598 | 19.4741 | 181.6812 | 83.5539 | 6.4461 | -178.4049 | 143.5218 | 0 | 28.045 | 0.73266 | 0.88776 | 8.37 | 36.415 | -1.1 | 0.037968 | 1.0998 | 0.032842
2015-05-19 | 45.39 | 37.72 | 7.67 | 63.2401 | 19.4834 | -163.3191 | 83.0338 | 6.9662 | -164.18 | 140.0344 | 0 | 28.29 | 0.7325 | 0.8875 | 8.312 | 36.602 | -0.1 | 1.0438 | 1.0958 | 0.03289
2015-05-19 01:00 | 63.8533 | 49.87 | 13.9833 | 96.9881 | 19.4926 | -148.3195 | 81.7105 | 8.2895 | -149.9796 | 132.0612 | 0 | 37.4025 | 0.73234 | 0.88724 | 11.6906 | 49.0931 | -0.5 | 1.0342 | 1.0959 | 0.044115
2015-05-19 02:00 | 82.3167 | 62.02 | 20.2967 | 113.1411 | 19.5019 | -133.3199 | 79.6656 | 10.3344 | -135.8048 | 121.4091 | 0 | 46.515 | 0.73219 | 0.88698 | 15.0678 | 61.5828 | -0.5 | 1.4245 | 1.0943 | 0.05526
2015-05-19 03:00 | 100.78 | 74.17 | 26.61 | 118.5074 | 19.5111 | -118.3203 | 77.024 | 12.976 | -121.6245 | 109.2829 | 0 | 55.6275 | 0.73203 | 0.88672 | 18.4435 | 74.071 | -1.3 | 1.0147 | 1.0959 | 0.066566
2015-05-19 04:00 | 137.4333 | 93.7733 | 43.66 | 157.8682 | 19.5203 | -103.3207 | 73.945 | 16.055 | -107.3714 | 96.3268 | 0 | 70.33 | 0.73188 | 0.88646 | 25.146 | 95.476 | -1.7 | 1.2836 | 1.0949 | 0.085717
2015-05-19 05:00 | 174.0867 | 113.3767 | 60.71 | 182.9124 | 19.5295 | -88.3211 | 70.6154 | 19.3846 | -92.9464 | 82.8792 | 22.6742 | 85.0325 | 0.73172 | 0.8862 | 31.8456 | 139.5523 | -1.1 | 3.261 | 1.087 | 0.12438
2015-05-19 06:00 | 210.74 | 132.98 | 77.76 | 201.0214 | 19.5387 | -73.3215 | 67.2429 | 22.7571 | -78.2313 | 69.127 | 71.6234 | 99.735 | 0.73156 | 0.88594 | 38.5424 | 209.9007 | -0.6 | 5.9594 | 1.0762 | 0.18523
2015-05-19 07:00 | 289.7433 | 159.9733 | 129.77 | 296.5638 | 19.5479 | -58.3219 | 64.0505 | 25.9495 | -63.1106 | 55.1816 | 169.3313 | 119.98 | 0.73141 | 0.88568 | 52.98 | 342.2913 | -0.6 | 10.0966 | 1.0596 | 0.29741
2015-05-19 08:00 | 368.7467 | 186.9667 | 181.78 | 378.1394 | 19.5571 | -43.3224 | 61.2674 | 28.7326 | -47.5021 | 41.116 | 284.8827 | 140.225 | 0.73125 | 0.88542 | 67.4115 | 492.5192 | -0.4 | 14.9912 | 1.04 | 0.42003
2015-05-19 09:00 | 447.75 | 213.96 | 233.79 | 455.4415 | 19.5662 | -28.3228 | 59.1144 | 30.8856 | -31.3933 | 26.9905 | 405.8358 | 160.47 | 0.73109 | 0.88516 | 81.8368 | 648.1426 | -0.3 | 19.9545 | 1.0202 | 0.5422
2015-05-19 10:00 | 452.83 | 209.8933 | 242.9367 | 455.6373 | 19.5754 | -13.3232 | 57.7794 | 32.2206 | -14.8712 | 12.9135 | 444.1137 | 157.42 | 0.73094 | 0.8849 | 82.7476 | 684.2813 | 0 | 21.3838 | 1.0145 | 0.56923
2015-05-19 11:00 | 457.91 | 205.8267 | 252.0833 | 467.7372 | 19.5845 | 1.6764 | 57.3883 | 32.6117 | 1.8751 | 3.0637 | 467.0687 | 154.37 | 0.73078 | 0.88464 | 83.658 | 705.0967 | 0.3 | 22.3343 | 1.0107 | 0.58434
2015-05-19 12:00 | 462.99 | 201.76 | 261.23 | 492.671 | 19.5936 | 16.6759 | 57.9789 | 32.0211 | 18.5937 | 16.0435 | 473.4825 | 151.32 | 0.73063 | 0.88438 | 84.568 | 709.3705 | 0.7 | 22.8678 | 1.0085 | 0.58664
2015-05-19 13:00 | 428.6967 | 175.3867 | 253.31 | 498.981 | 19.6028 | 31.6755 | 59.4923 | 30.5077 | 35.0408 | 30.1494 | 431.4785 | 131.54 | 0.73047 | 0.88411 | 78.2874 | 641.3058 | 0.6 | 20.6408 | 1.0174 | 0.53504
2015-05-19 14:00 | 394.4033 | 149.0133 | 245.39 | 519.0587 | 19.6119 | 46.6751 | 61.7864 | 28.2136 | 51.0473 | 44.2628 | 371.7218 | 111.76 | 0.73031 | 0.88385 | 72.0094 | 555.4912 | 1.1 | 18.4591 | 1.0262 | 0.46742
2015-05-19 15:00 | 360.11 | 122.64 | 237.47 | 554.9189 | 19.621 | 61.6746 | 64.6633 | 25.3367 | 66.5489 | 58.3004 | 291.5906 | 91.98 | 0.73016 | 0.88359 | 65.7341 | 449.3047 | 0.2 | 14.2408 | 1.043 | 0.38429
2015-05-19 16:00 | 304.3967 | 109.5167 | 194.88 | 517.9531 | 19.6301 | 76.6742 | 67.8984 | 22.1016 | 81.5756 | 72.2011 | 158.3268 | 82.1375 | 0.73 | 0.88333 | 55.5524 | 296.0166 | 0.1 | 9.3505 | 1.0626 | 0.25793
2015-05-19 17:00 | 248.6833 | 96.3933 | 152.29 | 474.0783 | 19.6392 | 91.6737 | 71.2624 | 18.7376 | 96.2195 | 85.8846 | 34.0229 | 72.295 | 0.72984 | 0.88307 | 45.375 | 151.6929 | -0.2 | 4.5404 | 1.0818 | 0.13457
2015-05-19 18:00 | 192.97 | 83.27 | 109.7 | 411.4066 | 19.6483 | 106.6733 | 74.5352 | 15.4648 | 110.5983 | 99.2258 | 0 | 62.4525 | 0.72969 | 0.88281 | 35.2019 | 97.6544 | -0.1 | 2.9517 | 1.0882 | 0.087139
2015-05-19 19:00 | 150.99 | 74.4033 | 76.5867 | 354.2123 | 19.6573 | 121.6728 | 77.5131 | 12.4869 | 124.8271 | 112.0108 | 0 | 55.8025 | 0.72953 | 0.88255 | 27.538 | 83.3405 | -0.1 | 2.5044 | 1.09 | 0.074489
2015-05-19 20:00 | 109.01 | 65.5367 | 43.4733 | 250.7236 | 19.6664 | 136.6723 | 80.0149 | 9.9851 | 138.9983 | 123.8476 | 0 | 49.1525 | 0.72938 | 0.88229 | 19.8773 | 69.0298 | -0.8 | 1.3572 | 1.0946 | 0.061958
2015-05-19 21:00 | 67.03 | 56.67 | 10.36 | 73.4245 | 19.6754 | 151.6719 | 81.8887 | 8.1113 | 153.1709 | 133.9893 | 0 | 42.5025 | 0.72922 | 0.88203 | 12.2199 | 54.7224 | -1 | 0.71007 | 1.0972 | 0.049232
2015-05-19 22:00 | 55.2667 | 45.4633 | 9.8033 | 80.6571 | 19.6845 | 166.6714 | 83.0188 | 6.9812 | 167.3682 | 141.0803 | 0 | 34.0975 | 0.72906 | 0.88177 | 10.0732 | 44.1707 | -1.3 | 0.080335 | 1.0997 | 0.03983
2015-05-19 23:00 | 43.5033 | 34.2567 | 9.2467 | 79.6642 | 19.6935 | 181.6709 | 83.3346 | 6.6654 | -178.4161 | 143.3031 | 0 | 25.6925 | 0.72891 | 0.88151 | 7.9275 | 33.62 | -1.1 | -0.049376 | 1.1002 | 0.030331
2015-05-20 | 31.74 | 23.05 | 8.69 | 69.4866 | 19.7025 | -163.3295 | 82.8158 | 7.1842 | -164.2042 | 139.8403 | 0 | 17.2875 | 0.72875 | 0.88125 | 5.7826 | 23.0701 | -1.3 | -0.57906 | 1.1023 | 0.020853
2015-05-20 01:00 | 47.5867 | 30.1333 | 17.4533 | 118.0015 | 19.7115 | -148.33 | 81.4943 | 8.5057 | -150.0161 | 131.9065 | 0 | 22.6 | 0.72859 | 0.88099 | 8.6678 | 31.2678 | -1 | -0.02288 | 1.1001 | 0.028206
2015-05-20 02:00 | 63.4333 | 37.2167 | 26.2167 | 143.2099 | 19.7205 | -133.3305 | 79.4517 | 10.5483 | -135.8519 | 121.2904 | 0 | 27.9125 | 0.72844 | 0.88073 | 11.5518 | 39.4643 | -0.9 | 0.33326 | 1.0987 | 0.035554
2015-05-20 03:00 | 79.28 | 44.3 | 34.98 | 153.3244 | 19.7295 | -118.331 | 76.8122 | 13.1878 | -121.6803 | 109.193 | 0 | 33.225 | 0.72828 | 0.88047 | 14.4345 | 47.6595 | -0.2 | 1.2894 | 1.0948 | 0.042787
2015-05-20 04:00 | 77.4933 | 48.03 | 29.4633 | 105.1954 | 19.7385 | -103.3315 | 73.7349 | 16.2651 | -107.4336 | 96.2597 | 0 | 36.0225 | 0.72813 | 0.88021 | 14.1062 | 50.1287 | -0.7 | 0.86652 | 1.0965 | 0.045074
2015-05-20 05:00 | 75.7067 | 51.76 | 23.9467 | 71.4081 | 19.7475 | -88.332 | 70.4062 | 19.5938 | -93.0123 | 82.8307 | 8.9118 | 38.82 | 0.72797 | 0.87995 | 13.778 | 61.5098 | 0 | 1.9222 | 1.0923 | 0.055094
2015-05-20 06:00 | 73.92 | 55.49 | 18.43 | 47.2334 | 19.7564 | -73.3325 | 67.0337 | 22.9663 | -78.2976 | 69.0946 | 16.8541 | 41.6175 | 0.72781 | 0.87969 | 13.45 | 71.9216 | 0.4 | 2.6475 | 1.0894 | 0.064249
2015-05-20 07:00 | 98.9167 | 75.8 | 23.1167 | 52.4335 | 19.7654 | -58.333 | 63.8402 | 26.1598 | -63.1737 | 55.1639 | 29.9517 | 56.85 | 0.72766 | 0.87943 | 17.9943 | 104.796 | 0.5 | 3.7749 | 1.0849 | 0.093228
2015-05-20 08:00 | 123.9133 | 96.11 | 27.8033 | 57.4492 | 19.7743 | -43.3335 | 61.0554 | 28.9446 | -47.5577 | 41.113 | 43.283 | 72.0825 | 0.7275 | 0.87917 | 22.5367 | 137.9023 | 0.5 | 4.8094 | 1.0808 | 0.12221
2015-05-20 09:00 | 148.91 | 116.42 | 32.49 | 62.9007 | 19.7833 | -28.334 | 58.9003 | 31.0997 | -31.4372 | 27.0052 | 56.0423 | 87.315 | 0.72734 | 0.87891 | 27.0772 | 170.4345 | 0.6 | 5.9261 | 1.0763 | 0.15042
2015-05-20 10:00 | 131.0567 | 103.44 | 27.6167 | 51.4889 | 19.7922 | -13.3346 | 57.5637 | 32.4363 | -14.8997 | 12.9615 | 50.177 | 77.58 | 0.72719 | 0.87865 | 23.8257 | 151.5827 | 0.5 | 5.237 | 1.0791 | 0.13412
2015-05-20 11:00 | 113.2033 | 90.46 | 22.7433 | 41.9523 | 19.8011 | 1.6649 | 57.1717 | 32.8283 | 1.8642 | 3.2449 | 41.885 | 67.845 | 0.72703 | 0.87839 | 20.5756 | 130.3056 | 0.6 | 4.6721 | 1.0813 | 0.11554
2015-05-20 12:00 | 95.35 | 77.48 | 17.87 | 33.5 | 19.81 | 16.6644 | 57.7623 | 32.2377 | 18.6004 | 16.0595 | 32.1927 | 58.11 | 0.72688 | 0.87813 | 17.3269 | 107.6295 | 0.7 | 4.0634 | 1.0837 | 0.095647
2015-05-20 13:00 | 143.6867 | 91.2967 | 52.39 | 102.546 | 19.8189 | 31.6638 | 59.2767 | 30.7233 | 35.0627 | 30.1383 | 88.6834 | 68.4725 | 0.72672 | 0.87786 | 26.1049 | 183.2609 | 0.4 | 6.1269 | 1.0755 | 0.16162
2015-05-20 14:00 | 192.0233 | 105.1133 | 86.91 | 182.5648 | 19.8278 | 46.6633 | 61.5722 | 28.4278 | 51.0806 | 44.2353 | 130.8042 | 78.835 | 0.72656 | 0.8776 | 34.8792 | 244.5184 | -0.1 | 7.5412 | 1.0698 | 0.21451
2015-05-20 15:00 | 240.36 | 118.93 | 121.43 | 281.5501 | 19.8367 | 61.6628 | 64.4505 | 25.5495 | 66.5893 | 58.2586 | 148.1197 | 89.1975 | 0.72641 | 0.87734 | 43.6498 | 280.9669 | 0.3 | 9.0802 | 1.0637 | 0.24506
2015-05-20 16:00 | 211.8167 | 95.1133 | 116.7033 | 307.3768 | 19.8455 | 76.6622 | 67.6864 | 22.3136 | 81.619 | 72.1448 | 94.2458 | 71.335 | 0.72625 | 0.87708 | 38.458 | 204.0387 | 0.5 | 6.8762 | 1.0725 | 0.17944
2015-05-20 17:00 | 183.2733 | 71.2967 | 111.9767 | 344.8293 | 19.8544 | 91.6617 | 71.0507 | 18.9493 | 96.262 | 85.8124 | 25.1803 | 53.4725 | 0.72609 | 0.87682 | 33.2684 | 111.9212 | 0.4 | 3.8975 | 1.0844 | 0.099522
2015-05-20 18:00 | 154.73 | 47.48 | 107.25 | 396.9116 | 19.8632 | 106.6611 | 74.3232 | 15.6768 | 110.6368 | 99.1352 | 0 | 35.61 | 0.72594 | 0.87656 | 28.0811 | 63.6911 | 0.2 | 2.1903 | 1.0912 | 0.056992
2015-05-20 19:00 | 119.1867 | 40.48 | 78.7067 | 358.0154 | 19.8721 | 121.6606 | 77.3003 | 12.6997 | 124.8588 | 111.8978 | 0 | 30.36 | 0.72578 | 0.8763 | 21.6259 | 51.9859 | 0.2 | 1.8246 | 1.0927 | 0.04658
2015-05-20 20:00 | 83.6433 | 33.48 | 50.1633 | 283.3082 | 19.8809 | 136.66 | 79.8013 | 10.1987 | 139.0209 | 123.7068 | 0 | 25.11 | 0.72563 | 0.87604 | 15.1734 | 40.2834 | 0.2 | 1.4589 | 1.0942 | 0.036143
2015-05-20 21:00 | 48.1 | 26.48 | 21.62 | 149.3109 | 19.8897 | 151.6594 | 81.6744 | 8.3256 | 153.1826 | 133.8155 | 0 | 19.86 | 0.72547 | 0.87578 | 8.7238 | 28.5838 | 0.1 | 0.99324 | 1.096 | 0.025689
2015-05-20 22:00 | 57.6 | 28.2433 | 29.3567 | 234.3736 | 19.8985 | 166.6589 | 82.8045 | 7.1955 | 167.3677 | 140.8757 | 0 | 21.1825 | 0.72531 | 0.87552 | 10.4445 | 31.627 | 0.2 | 1.1883 | 1.0952 | 0.028404
2015-05-20 23:00 | 67.1 | 30.0067 | 37.0933 | 309.693 | 19.9073 | 181.6583 | 83.1209 | 6.8791 | -178.4295 | 143.0901 | 0 | 22.505 | 0.72516 | 0.87526 | 12.1645 | 34.6695 | 0 | 1.0834 | 1.0957 | 0.031149
2015-05-21 | 76.6 | 31.77 | 44.83 | 348.2321 | 19.9161 | -163.3423 | 82.6034 | 7.3966 | -164.2303 | 139.6521 | 0 | 23.8275 | 0.725 | 0.875 | 13.8837 | 37.7112 | -0.1 | 1.0785 | 1.0957 | 0.033882
2015-05-21 01:00 | 83.9333 | 35.9467 | 47.9867 | 316.6652 | 19.9249 | -148.3428 | 81.284 | 8.716 | -150.054 | 131.757 | 0 | 26.96 | 0.72484 | 0.87474 | 15.2096 | 42.1696 | 0.3 | 1.6178 | 1.0935 | 0.037813
2015-05-21 02:00 | 91.2667 | 40.1233 | 51.1433 | 274.0306 | 19.9336 | -133.3434 | 79.2436 | 10.7564 | -135.9003 | 121.1764 | 0 | 30.0925 | 0.72469 | 0.87448 | 16.535 | 46.6275 | 0.3 | 1.7571 | 1.093 | 0.041789
2015-05-21 03:00 | 98.6 | 44.3 | 54.3 | 234.4145 | 19.9424 | -118.344 | 76.6063 | 13.3937 | -121.7372 | 109.1074 | 0 | 33.225 | 0.72453 | 0.87422 | 17.8597 | 51.0847 | 0.3 | 1.8964 | 1.0924 | 0.045761
2015-05-21 04:00 | 113.46 | 62.4967 | 50.9633 | 179.7641 | 19.9511 | -103.3446 | 73.5307 | 16.4693 | -107.4968 | 96.1965 | 0 | 46.8725 | 0.72438 | 0.87396 | 20.5469 | 67.4194 | 0.2 | 2.3069 | 1.0908 | 0.060302
2015-05-21 05:00 | 128.32 | 80.6933 | 47.6267 | 140.6205 | 19.9599 | -88.3452 | 70.203 | 19.797 | -93.0791 | 82.786 | 17.6586 | 60.52 | 0.72422 | 0.8737 | 23.2329 | 101.4115 | 0.7 | 3.8691 | 1.0845 | 0.090186
2015-05-21 06:00 | 143.18 | 98.89 | 44.29 | 112.5671 | 19.9686 | -73.3458 | 66.8304 | 23.1696 | -78.365 | 69.0657 | 40.2199 | 74.1675 | 0.72406 | 0.87344 | 25.9178 | 140.3052 | 0.8 | 5.1845 | 1.0793 | 0.12417
2015-05-21 07:00 | 177.3967 | 122.0133 | 55.3833 | 124.7166 | 19.9773 | -58.3464 | 63.6359 | 26.3641 | -63.238 | 55.1496 | 71.2676 | 91.51 | 0.72391 | 0.87318 | 32.1046 | 194.8822 | 0.7 | 6.7901 | 1.0728 | 0.17144
2015-05-21 08:00 | 211.6133 | 145.1367 | 66.4767 | 136.4721 | 19.986 | -43.347 | 60.8493 | 29.1507 | -47.6149 | 41.1135 | 102.8192 | 108.8525 | 0.72375 | 0.87292 | 38.2888 | 249.9605 | 0.5 | 8.3113 | 1.0668 | 0.21865
2015-05-21 09:00 | 245.83 | 168.26 | 77.57 | 149.2775 | 19.9947 | -28.3476 | 58.6921 | 31.3079 | -31.483 | 27.0236 | 132.9793 | 126.195 | 0.72359 | 0.87266 | 44.4703 | 303.6446 | -0.3 | 9.1889 | 1.0632 | 0.26474
2015-05-21 10:00 | 256.23 | 177.38 | 78.85 | 146.1669 | 20.0034 | -13.3482 | 57.3537 | 32.6463 | -14.9304 | 13.0139 | 142.4126 | 133.035 | 0.72344 | 0.8724 | 46.3416 | 321.7892 | 0.7 | 10.7559 | 1.057 | 0.2789
2015-05-21 11:00 | 266.63 | 186.5 | 80.13 | 146.9694 | 20.0121 | 1.6511 | 56.9606 | 33.0394 | 1.8508 | 3.4243 | 146.707 | 139.875 | 0.72328 | 0.87214 | 48.2121 | 334.7941 | 0.4 | 10.8623 | 1.0566 | 0.29006
2015-05-21 12:00 | 277.03 | 195.62 | 81.41 | 151.7298 | 20.0208 | 16.6505 | 57.5512 | 32.4488 | 18.6041 | 16.0753 | 145.7969 | 146.715 | 0.72313 | 0.87188 | 50.0818 | 342.5937 | 0.8 | 11.5061 | 1.054 | 0.29609
2015-05-21 13:00 | 252.0733 | 177.7033 | 74.37 | 144.6762 | 20.0294 | 31.6499 | 59.0664 | 30.9336 | 35.0814 | 30.1265 | 125.1332 | 133.2775 | 0.72297 | 0.87161 | 45.5603 | 303.971 | 0.6 | 10.0991 | 1.0596 | 0.26411
2015-05-21 14:00 | 227.1167 | 159.7867 | 67.33 | 140.4887 | 20.0381 | 46.6493 | 61.3632 | 28.6368 | 51.1106 | 44.2069 | 100.7061 | 119.84 | 0.72281 | 0.87135 | 41.0407 | 261.5868 | 1.4 | 9.5746 | 1.0617 | 0.22774
2015-05-21 15:00 | 202.16 | 141.87 | 60.29 | 138.7379 | 20.0467 | 61.6486 | 64.2427 | 25.7573 | 66.6262 | 58.2159 | 73.076 | 106.4025 | 0.72266 | 0.87109 | 36.523 | 216.0015 | 2 | 8.75 | 1.065 | 0.18863
2015-05-21 16:00 | 161.4133 | 105.93 | 55.4833 | 144.8595 | 20.0553 | 76.648 | 67.4794 | 22.5206 | 81.6588 | 72.0878 | 44.5529 | 79.4475 | 0.7225 | 0.87083 | 29.1553 | 153.1557 | 1.3 | 6.0861 | 1.0757 | 0.13509
2015-05-21 17:00 | 120.6667 | 69.99 | 50.6767 | 154.4355 | 20.0639 | 91.6473 | 70.844 | 19.156 | 96.301 | 85.7399 | 11.4723 | 52.4925 | 0.72234 | 0.87057 | 21.7907 | 85.7555 | 1.1 | 3.7799 | 1.0849 | 0.076288
2015-05-21 18:00 | 79.92 | 34.05 | 45.87 | 167.5993 | 20.0726 | 106.6467 | 74.1161 | 15.8839 | 110.6719 | 99.0446 | 0 | 25.5375 | 0.72219 | 0.87031 | 14.4293 | 39.9668 | 1 | 2.249 | 1.091 | 0.035755
2015-05-21 19:00 | 68.57 | 30.27 | 38.3 | 171.4595 | 20.0812 | 121.646 | 77.0926 | 12.9074 | 124.8873 | 111.7854 | 0 | 22.7025 | 0.72203 | 0.87005 | 12.3774 | 35.0799 | 1.3 | 2.3962 | 1.0904 | 0.031366
2015-05-21 20:00 | 57.22 | 26.49 | 30.73 | 170.1157 | 20.0897 | 136.6454 | 79.5929 | 10.4071 | 139.0405 | 123.5675 | 0 | 19.8675 | 0.72188 | 0.86979 | 10.3264 | 30.1939 | 0.9 | 1.8436 | 1.0926 | 0.027052
2015-05-21 21:00 | 45.87 | 22.71 | 23.16 | 156.0593 | 20.0983 | 151.6447 | 81.4655 | 8.5345 | 153.1915 | 133.6446 | 0 | 17.0325 | 0.72172 | 0.86953 | 8.2763 | 25.3088 | 0.9 | 1.6909 | 1.0932 | 0.022688
2015-05-21 22:00 | 50.22 | 27.74 | 22.48 | 174.4378 | 20.1069 | 166.6441 | 82.5956 | 7.4044 | 167.3647 | 140.6756 | 0 | 20.805 | 0.72156 | 0.86927 | 9.0592 | 29.8642 | 0.9 | 1.8333 | 1.0927 | 0.026758
2015-05-21 23:00 | 54.57 | 32.77 | 21.8 | 176.6916 | 20.1154 | 181.6434 | 82.9129 | 7.0871 | -178.445 | 142.8828 | 0 | 24.5775 | 0.72141 | 0.86901 | 9.8418 | 34.4193 | 0.8 | 1.8756 | 1.0925 | 0.030834
2015-05-22 | 58.92 | 37.8 | 21.12 | 159.6249 | 20.124 | -163.3573 | 82.3969 | 7.6031 | -164.2582 | 139.4696 | 0 | 28.35 | 0.72125 | 0.86875 | 10.624 | 38.974 | 0.8 | 2.0179 | 1.0919 | 0.034897
2015-05-22 01:00 | 84.2333 | 51.3 | 32.9333 | 212.385 | 20.1325 | -148.3579 | 81.0795 | 8.9205 | -150.0934 | 131.6127 | 0 | 38.475 | 0.72109 | 0.86849 | 15.185 | 53.66 | 0.8 | 2.4769 | 1.0901 | 0.047965
2015-05-22 02:00 | 109.5467 | 64.8 | 44.7467 | 235.3866 | 20.1411 | -133.3586 | 79.0415 | 10.9585 | -135.9499 | 121.067 | 0 | 48.6 | 0.72094 | 0.86823 | 19.7441 | 68.3441 | 0.6 | 2.7358 | 1.0891 | 0.061033
2015-05-22 03:00 | 134.86 | 78.3 | 56.56 | 240.6463 | 20.1496 | -118.3593 | 76.4064 | 13.5936 | -121.7952 | 109.0259 | 0 | 58.725 | 0.72078 | 0.86797 | 24.3011 | 83.0261 | 0.4 | 2.9946 | 1.088 | 0.074074
2015-05-22 04:00 | 170.3333 | 101.1367 | 69.1967 | 241.2579 | 20.1581 | -103.36 | 73.3326 | 16.6674 | -107.5609 | 96.1372 | 0 | 75.8525 | 0.72063 | 0.86771 | 30.6866 | 106.5391 | 0 | 3.3293 | 1.0867 | 0.094935
2015-05-22 05:00 | 205.8067 | 123.9733 | 81.8333 | 239.3306 | 20.1666 | -88.3607 | 70.0057 | 19.9943 | -93.1468 | 82.7448 | 30.2247 | 92.98 | 0.72047 | 0.86745 | 37.0693 | 160.274 | -0.3 | 4.7086 | 1.0812 | 0.14209
2015-05-22 06:00 | 241.28 | 146.81 | 94.47 | 238.1896 | 20.1751 | -73.3614 | 66.6331 | 23.3669 | -78.4333 | 69.0403 | 85.2032 | 110.1075 | 0.72031 | 0.86719 | 43.4492 | 238.76 | -0.2 | 7.2612 | 1.071 | 0.20967
2015-05-22 07:00 | 276.96 | 177.0333 | 99.9267 | 223.4637 | 20.1836 | -58.3621 | 63.4376 | 26.5624 | -63.3034 | 55.1386 | 127.7304 | 132.775 | 0.72016 | 0.86693 | 49.8636 | 310.3691 | -0.1 | 9.599 | 1.0616 | 0.27018
2015-05-22 08:00 | 312.64 | 207.2567 | 105.3833 | 214.9998 | 20.192 | -43.3628 | 60.6492 | 29.3508 | -47.6735 | 41.1173 | 161.9733 | 155.4425 | 0.72 | 0.86667 | 56.2752 | 373.691 | -0.3 | 11.3778 | 1.0545 | 0.32312
2015-05-22 09:00 | 348.32 | 237.48 | 110.84 | 212.0733 | 20.2005 | -28.3635 | 58.4899 | 31.5101 | -31.5305 | 27.0453 | 188.8825 | 178.11 | 0.71984 | 0.86641 | 62.684 | 429.6765 | -0.4 | 13.0274 | 1.0479 | 0.36921
2015-05-22 10:00 | 370.6033 | 228.8033 | 141.8 | 261.4068 | 20.2089 | -13.3642 | 57.1494 | 32.8506 | -14.9633 | 13.0704 | 254.6345 | 171.6025 | 0.71969 | 0.86615 | 66.6796 | 492.9166 | -0.4 | 15.0036 | 1.04 | 0.42035
2015-05-22 11:00 | 392.8867 | 220.1267 | 172.76 | 315.1303 | 20.2174 | 1.6351 | 56.7552 | 33.2448 | 1.8347 | 3.6011 | 314.5081 | 165.095 | 0.71953 | 0.86589 | 70.6736 | 550.2767 | -0.1 | 17.0961 | 1.0316 | 0.46549
2015-05-22 12:00 | 415.17 | 211.45 | 203.72 | 377.5592 | 20.2258 | 16.6344 | 57.3456 | 32.6544 | 18.6048 | 16.0909 | 362.7676 | 158.5875 | 0.71938 | 0.86562 | 74.6657 | 596.0209 | 0 | 18.6257 | 1.0255 | 0.5012
2015-05-22 13:00 | 401.9233 | 193.4333 | 208.49 | 403.1832 | 20.2342 | 31.6337 | 58.8614 | 31.1386 | 35.0968 | 30.1138 | 348.7658 | 145.075 | 0.71922 | 0.86536 | 72.2677 | 566.1085 | 0 | 17.6909 | 1.0292 | 0.47778
2015-05-22 14:00 | 388.6767 | 175.4167 | 213.26 | 442.104 | 20.2426 | 46.6329 | 61.1594 | 28.8406 | 51.137 | 44.1776 | 317.0698 | 131.5625 | 0.71906 | 0.8651 | 69.8707 | 518.503 | 0.5 | 16.7032 | 1.0332 | 0.43928
2015-05-22 15:00 | 375.43 | 157.4 | 218.03 | 498.0763 | 20.251 | 61.6322 | 64.04 | 25.96 | 66.6596 | 58.1724 | 262.668 | 118.05 | 0.71891 | 0.86484 | 67.4747 | 448.1927 | 0.4 | 14.406 | 1.0424 | 0.38309
2015-05-22 16:00 | 315.2533 | 127.06 | 188.1933 | 487.209 | 20.2594 | 76.6315 | 67.2775 | 22.7225 | 81.6951 | 72.0302 | 150.3115 | 95.295 | 0.71875 | 0.86458 | 56.6471 | 302.2536 | 0.5 | 9.9454 | 1.0602 | 0.26277
2015-05-22 17:00 | 255.0767 | 96.72 | 158.3567 | 477.7484 | 20.2678 | 91.6307 | 70.6423 | 19.3577 | 96.3366 | 85.667 | 36.0955 | 72.54 | 0.71859 | 0.86432 | 45.8241 | 154.4596 | 0.5 | 5.3269 | 1.0787 | 0.13662
2015-05-22 18:00 | 194.9 | 66.38 | 128.52 | 463.8424 | 20.2762 | 106.63 | 73.9142 | 16.0858 | 110.7036 | 98.9541 | 0 | 49.785 | 0.71844 | 0.86406 | 35.0059 | 84.7909 | 0 | 2.6497 | 1.0894 | 0.075744
2015-05-22 19:00 | 162.2033 | 56.4767 | 105.7267 | 466.1256 | 20.2845 | 121.6293 | 76.8901 | 13.1099 | 124.9126 | 111.6737 | 0 | 42.3575 | 0.71828 | 0.8638 | 29.1269 | 71.4844 | 0.2 | 2.4339 | 1.0903 | 0.063908
2015-05-22 20:00 | 129.5067 | 46.5733 | 82.9333 | 450.413 | 20.2929 | 136.6285 | 79.3897 | 10.6103 | 139.0571 | 123.4298 | 0 | 34.93 | 0.71813 | 0.86354 | 23.2505 | 58.1805 | 0.3 | 2.1181 | 1.0915 | 0.052075
2015-05-22 21:00 | 96.81 | 36.67 | 60.14 | 395.8776 | 20.3012 | 151.6278 | 81.262 | 8.738 | 153.1977 | 133.4765 | 0 | 27.5025 | 0.71797 | 0.86328 | 17.3766 | 44.8791 | -0.7 | 0.70247 | 1.0972 | 0.040378
2015-05-22 22:00 | 92.5033 | 36.4033 | 56.1 | 423.7547 | 20.3096 | 166.627 | 82.3924 | 7.6076 | 167.3593 | 140.48 | 0 | 27.3025 | 0.71781 | 0.86302 | 16.6 | 43.9025 | -0.6 | 0.77195 | 1.0969 | 0.039489
2015-05-22 23:00 | 88.1967 | 36.1367 | 52.06 | 410.3013 | 20.3179 | 181.6262 | 82.7105 | 7.2895 | -178.4625 | 142.6813 | 0 | 27.1025 | 0.71766 | 0.86276 | 15.8237 | 42.9262 | -0.6 | 0.74144 | 1.097 | 0.038615
2015-05-23 | 83.89 | 35.87 | 48.02 | 353.6559 | 20.3262 | -163.3745 | 82.1962 | 7.8038 | -164.2878 | 139.2929 | 0 | 26.9025 | 0.7175 | 0.8625 | 15.0478 | 41.9503 | -0.7 | 0.61095 | 1.0976 | 0.037755
2015-05-23 01:00 | 104.5467 | 47.3633 | 57.1833 | 360.8079 | 20.3345 | -148.3753 | 80.8809 | 9.1191 | -150.1343 | 131.4738 | 0 | 35.5225 | 0.71734 | 0.86224 | 18.749 | 54.2715 | -0.6 | 1.096 | 1.0956 | 0.048758
2015-05-23 02:00 | 125.2033 | 58.8567 | 66.3467 | 342.9503 | 20.3428 | -133.3761 | 78.8453 | 11.1547 | -136.0007 | 120.9624 | 0 | 44.1425 | 0.71719 | 0.86198 | 22.4486 | 66.5911 | -0.7 | 1.381 | 1.0945 | 0.059764
2015-05-23 03:00 | 145.86 | 70.35 | 75.51 | 316.8412 | 20.3511 | -118.3768 | 76.2125 | 13.7875 | -121.8541 | 108.9487 | 0 | 52.7625 | 0.71703 | 0.86172 | 26.1465 | 78.909 | -0.7 | 1.7659 | 1.0929 | 0.070719
2015-05-23 04:00 | 155.96 | 82.4467 | 73.5133 | 253.4712 | 20.3593 | -103.3776 | 73.1405 | 16.8595 | -107.6259 | 96.0818 | 0 | 61.835 | 0.71688 | 0.86146 | 27.951 | 89.786 | -0.8 | 2.0058 | 1.092 | 0.080396
2015-05-23 05:00 | 166.06 | 94.5433 | 71.5167 | 207.2593 | 20.3676 | -88.3784 | 69.8146 | 20.1854 | -93.2153 | 82.7073 | 26.3092 | 70.9075 | 0.71672 | 0.8612 | 29.7546 | 126.9713 | -1.3 | 2.6679 | 1.0893 | 0.11342
2015-05-23 06:00 | 176.16 | 106.64 | 69.52 | 173.9402 | 20.3758 | -73.3792 | 66.442 | 23.558 | -78.5026 | 69.0182 | 62.283 | 79.98 | 0.71656 | 0.86094 | 31.5574 | 173.8204 | -1.5 | 3.9319 | 1.0843 | 0.15454
2015-05-23 07:00 | 192.6733 | 133.64 | 59.0333 | 131.1356 | 20.3841 | -58.38 | 63.2454 | 26.7546 | -63.37 | 55.1308 | 74.9708 | 100.23 | 0.71641 | 0.86068 | 34.5081 | 209.7089 | -1.6 | 4.9534 | 1.0802 | 0.18575
2015-05-23 08:00 | 209.1867 | 160.64 | 48.5467 | 98.4509 | 20.3923 | -43.3808 | 60.4551 | 29.5449 | -47.7334 | 41.1242 | 74.1617 | 120.48 | 0.71625 | 0.86042 | 37.4575 | 232.0991 | -1.5 | 5.7531 | 1.077 | 0.20497
2015-05-23 09:00 | 225.7 | 187.64 | 38.06 | 72.417 | 20.4005 | -28.3816 | 58.2936 | 31.7064 | -31.5798 | 27.0703 | 64.4836 | 140.73 | 0.71609 | 0.86016 | 40.4056 | 245.6192 | -1.5 | 6.1756 | 1.0753 | 0.21657
2015-05-23 10:00 | 254.55 | 193.4167 | 61.1333 | 112.0983 | 20.4087 | -13.3824 | 56.9511 | 33.0489 | -14.9983 | 13.1305 | 109.1675 | 145.0625 | 0.71594 | 0.8599 | 45.5605 | 299.7905 | -1.7 | 7.6685 | 1.0693 | 0.26287
2015-05-23 11:00 | 283.4 | 199.1933 | 84.2067 | 152.7894 | 20.4169 | 1.6168 | 56.5555 | 33.4445 | 1.816 | 3.7748 | 152.4579 | 149.395 | 0.71578 | 0.85964 | 50.7131 | 352.566 | -1.6 | 9.4177 | 1.0623 | 0.30712
2015-05-23 12:00 | 312.25 | 204.97 | 107.28 | 197.7485 | 20.4251 | 16.616 | 57.1455 | 32.8545 | 18.6026 | 16.106 | 189.9868 | 153.7275 | 0.71563 | 0.85938 | 55.8635 | 399.5778 | -1.7 | 10.7868 | 1.0569 | 0.34628
2015-05-23 13:00 | 299.8133 | 185.0933 | 114.72 | 220.5782 | 20.4333 | 31.6152 | 58.6619 | 31.3381 | 35.1089 | 30.1002 | 190.8331 | 138.82 | 0.71547 | 0.85911 | 53.6268 | 383.2798 | -1.7 | 10.2775 | 1.0589 | 0.3328
2015-05-23 14:00 | 287.3767 | 165.2167 | 122.16 | 251.6645 | 20.4415 | 46.6144 | 60.9608 | 29.0392 | 51.1601 | 44.1473 | 180.5823 | 123.9125 | 0.71531 | 0.85885 | 51.391 | 355.8858 | -1.7 | 9.4214 | 1.0623 | 0.31001
2015-05-23 15:00 | 274.94 | 145.34 | 129.6 | 293.9832 | 20.4496 | 61.6136 | 63.8424 | 26.1576 | 66.6895 | 58.1281 | 155.2296 | 109.005 | 0.71516 | 0.85859 | 49.1563 | 313.3908 | -1.6 | 8.1935 | 1.0672 | 0.27426
2015-05-23 16:00 | 216.7267 | 127.9867 | 88.74 | 227.8688 | 20.4578 | 76.6128 | 67.0807 | 22.9193 | 81.7278 | 71.972 | 70.5211 | 95.99 | 0.715 | 0.85833 | 38.7399 | 205.251 | -1.7 | 4.7141 | 1.0811 | 0.18196
2015-05-23 17:00 | 158.5133 | 110.6333 | 47.88 | 143.0537 | 20.4659 | 91.6119 | 70.4457 | 19.5543 | 96.3687 | 85.5938 | 10.9903 | 82.975 | 0.71484 | 0.85807 | 28.3281 | 122.2933 | -1.9 | 1.9217 | 1.0923 | 0.10954
2015-05-23 18:00 | 100.3 | 93.28 | 7.02 | 25.0379 | 20.4741 | 106.6111 | 73.7174 | 16.2826 | 110.732 | 98.8638 | 0 | 69.96 | 0.71469 | 0.85781 | 17.9208 | 87.8808 | -1.9 | 0.84627 | 1.0966 | 0.079025
2015-05-23 19:00 | 88.54 | 75.8867 | 12.6533 | 54.9734 | 20.4822 | 121.6103 | 76.6928 | 13.3072 | 124.9347 | 111.5628 | 0 | 56.915 | 0.71453 | 0.85755 | 15.8161 | 72.7311 | -1.9 | 0.37285 | 1.0985 | 0.065515
2015-05-23 20:00 | 76.78 | 58.4933 | 18.2867 | 97.5194 | 20.4903 | 136.6094 | 79.192 | 10.808 | 139.0708 | 123.2939 | 0 | 43.87 | 0.71437 | 0.85729 | 13.7124 | 57.5824 | -2.1 | -0.30055 | 1.1012 | 0.051996
2015-05-23 21:00 | 65.02 | 41.1 | 23.92 | 153.9956 | 20.4984 | 151.6086 | 81.0641 | 8.9359 | 153.2013 | 133.3115 | 0 | 30.825 | 0.71422 | 0.85703 | 11.6096 | 42.4346 | -2.1 | -0.77392 | 1.1031 | 0.038384
2015-05-23 22:00 | 69.26 | 41.3033 | 27.9567 | 205.8588 | 20.5065 | 166.6077 | 82.1948 | 7.8052 | 167.3516 | 140.2891 | 0 | 30.9775 | 0.71406 | 0.85677 | 12.364 | 43.3415 | -2 | -0.64558 | 1.1026 | 0.039186
2015-05-23 23:00 | 73.5 | 41.5067 | 31.9933 | 245.566 | 20.5145 | 181.6069 | 82.514 | 7.486 | -178.4821 | 142.4856 | 0 | 31.13 | 0.71391 | 0.85651 | 13.118 | 44.248 | -2.1 | -0.71725 | 1.1029 | 0.040016
2015-05-24 | 77.74 | 41.71 | 36.03 | 258.9303 | 20.5226 | -163.394 | 82.0014 | 7.9986 | -164.319 | 139.1222 | 0 | 31.2825 | 0.71375 | 0.85625 | 13.8717 | 45.1542 | -2.2 | -0.78893 | 1.1032 | 0.040846
2015-05-24 01:00 | 105.34 | 55.1767 | 50.1633 | 310.0245 | 20.5307 | -148.3948 | 80.6884 | 9.3116 | -150.1765 | 131.3401 | 0 | 41.3825 | 0.71359 | 0.85599 | 18.7925 | 60.175 | -2.3 | -0.41953 | 1.1017 | 0.054361
2015-05-24 02:00 | 132.94 | 68.6433 | 64.2967 | 326.8559 | 20.5387 | -133.3957 | 78.6552 | 11.3448 | -136.0525 | 120.8624 | 0 | 51.4825 | 0.71344 | 0.85573 | 23.7111 | 75.1936 | -2.2 | 0.1498 | 1.0994 | 0.067788
2015-05-24 03:00 | 160.54 | 82.11 | 78.43 | 324.758 | 20.5467 | -118.3966 | 76.0247 | 13.9753 | -121.9139 | 108.8757 | 0 | 61.5825 | 0.71328 | 0.85547 | 28.6275 | 90.21 | -2.2 | 0.61906 | 1.0975 | 0.081186
2015-05-24 04:00 | 203.6367 | 103.9133 | 99.7233 | 340.2004 | 20.5548 | -103.3974 | 72.9545 | 17.0455 | -107.6916 | 96.0302 | 0 | 77.935 | 0.71313 | 0.85521 | 36.3046 | 114.2396 | -2.2 | 1.37 | 1.0945 | 0.10253
2015-05-24 05:00 | 246.7333 | 125.7167 | 121.0167 | 347.6616 | 20.5628 | -88.3983 | 69.6296 | 20.3704 | -93.2846 | 82.6733 | 44.3362 | 94.2875 | 0.71297 | 0.85495 | 43.9783 | 182.602 | -1.7 | 4.0063 | 1.084 | 0.16231
2015-05-24 06:00 | 289.83 | 147.52 | 142.31 | 353.446 | 20.5708 | -73.3992 | 66.2569 | 23.7431 | -78.5727 | 68.9995 | 126.6668 | 110.64 | 0.71281 | 0.85469 | 51.6486 | 288.9554 | -1.4 | 7.6299 | 1.0695 | 0.25341
2015-05-24 07:00 | 323.7267 | 163.68 | 160.0467 | 353.2509 | 20.5788 | -58.4001 | 63.0593 | 26.9407 | -63.4375 | 55.1263 | 201.9782 | 122.76 | 0.71266 | 0.85443 | 57.6765 | 382.4146 | -1.9 | 10.0505 | 1.0598 | 0.33233
2015-05-24 08:00 | 357.6233 | 179.84 | 177.7833 | 358.4652 | 20.5868 | -43.4009 | 60.2671 | 29.7329 | -47.7947 | 41.1342 | 269.9856 | 134.88 | 0.7125 | 0.85417 | 63.7017 | 468.5673 | -1.6 | 13.0427 | 1.0478 | 0.4026
2015-05-24 09:00 | 391.52 | 196 | 195.52 | 370.0298 | 20.5948 | -28.4018 | 58.1033 | 31.8967 | -31.6308 | 27.0984 | 329.4101 | 147 | 0.71234 | 0.85391 | 69.7242 | 546.1343 | -1.7 | 15.3667 | 1.0385 | 0.46509
2015-05-24 10:00 | 395.6467 | 196.1033 | 199.5433 | 364.0196 | 20.6027 | -13.4027 | 56.7587 | 33.2413 | -15.0355 | 13.1939 | 354.4107 | 147.0775 | 0.71219 | 0.85365 | 70.4437 | 571.9319 | -1.6 | 16.2729 | 1.0349 | 0.48536
2015-05-24 11:00 | 399.7733 | 196.2067 | 203.5667 | 367.4825 | 20.6107 | 1.5964 | 56.3616 | 33.6384 | 1.7948 | 3.9449 | 366.6118 | 147.155 | 0.71203 | 0.85339 | 71.1628 | 584.9296 | -1.4 | 16.8791 | 1.0325 | 0.49522
2015-05-24 12:00 | 403.9 | 196.31 | 207.59 | 380.6515 | 20.6186 | 16.5955 | 56.9511 | 33.0489 | 18.5974 | 16.1206 | 365.6841 | 147.2325 | 0.71188 | 0.85313 | 71.8816 | 584.7982 | -1.5 | 16.7749 | 1.0329 | 0.49531
2015-05-24 13:00 | 379.2267 | 184.95 | 194.2767 | 371.4818 | 20.6266 | 31.5946 | 58.4678 | 31.5322 | 35.1179 | 30.0857 | 321.4345 | 138.7125 | 0.71172 | 0.85286 | 67.4757 | 527.6227 | -1.6 | 14.8882 | 1.0404 | 0.45015
2015-05-24 14:00 | 354.5533 | 173.59 | 180.9633 | 370.558 | 20.6345 | 46.5937 | 60.7676 | 29.2324 | 51.1797 | 44.1161 | 266.035 | 130.1925 | 0.71156 | 0.8526 | 63.0717 | 459.2992 | -1.3 | 13.0531 | 1.0478 | 0.39462
2015-05-24 15:00 | 329.88 | 162.23 | 167.65 | 377.7165 | 20.6424 | 61.5928 | 63.6501 | 26.3499 | 66.7158 | 58.083 | 199.695 | 121.6725 | 0.71141 | 0.85234 | 58.6697 | 380.0372 | -1.3 | 10.5762 | 1.0577 | 0.32961
2015-05-24 16:00 | 269.37 | 138.0833 | 131.2867 | 334.4773 | 20.6503 | 76.5919 | 66.889 | 23.111 | 81.757 | 71.9133 | 103.8404 | 103.5625 | 0.71125 | 0.85208 | 47.8974 | 255.3002 | -1 | 6.9781 | 1.0721 | 0.22444
2015-05-24 17:00 | 208.86 | 113.9367 | 94.9233 | 280.9668 | 20.6582 | 91.5909 | 70.2543 | 19.7457 | 96.3973 | 85.5205 | 21.9442 | 85.4525 | 0.71109 | 0.85182 | 37.1298 | 144.5264 | -1.2 | 3.3165 | 1.0867 | 0.12879
2015-05-24 18:00 | 148.35 | 89.79 | 58.56 | 206.5008 | 20.6661 | 106.59 | 73.5259 | 16.4741 | 110.7571 | 98.7738 | 0 | 67.3425 | 0.71094 | 0.85156 | 26.3669 | 93.7094 | -1.3 | 1.6284 | 1.0935 | 0.084025
2015-05-24 19:00 | 128.28 | 73.5133 | 54.7667 | 234.617 | 20.674 | 121.5891 | 76.5009 | 13.4991 | 124.9536 | 111.4528 | 0 | 55.135 | 0.71078 | 0.8513 | 22.7948 | 77.9298 | -1.7 | 0.7353 | 1.0971 | 0.070105
2015-05-24 20:00 | 108.21 | 57.2367 | 50.9733 | 267.1369 | 20.6818 | 136.5882 | 78.9997 | 11.0003 | 139.0816 | 123.1598 | 0 | 42.9275 | 0.71063 | 0.85104 | 19.2242 | 62.1517 | -2.1 | -0.15776 | 1.1006 | 0.056093
2015-05-24 21:00 | 88.14 | 40.96 | 47.18 | 297.395 | 20.6897 | 151.5872 | 80.8718 | 9.1282 | 153.2022 | 133.1496 | 0 | 30.72 | 0.71047 | 0.85078 | 15.6552 | 46.3752 | -2.5 | -1.0508 | 1.1042 | 0.04199
2015-05-24 22:00 | 90.3267 | 40.77 | 49.5567 | 356.2113 | 20.6975 | 166.5863 | 82.003 | 7.997 | 167.3415 | 140.1029 | 0 | 30.5775 | 0.71031 | 0.85052 | 16.04 | 46.6175 | -2.8 | -1.3432 | 1.1054 | 0.042254
2015-05-24 23:00 | 92.5133 | 40.58 | 51.9333 | 388.7727 | 20.7053 | 181.5854 | 82.3233 | 7.6767 | -178.5036 | 142.2959 | 0 | 30.435 | 0.71016 | 0.85026 | 16.4247 | 46.8597 | -2.8 | -1.3356 | 1.1053 | 0.042473
2015-05-25 | 94.7 | 40.39 | 54.31 | 381.3572 | 20.7132 | -163.4156 | 81.8125 | 8.1875 | -164.3519 | 138.9574 | 0 | 30.2925 | 0.71 | 0.85 | 16.8092 | 47.1018 | -3.4 | -1.9281 | 1.1077 | 0.042784
2015-05-25 01:00 | 123.46 | 51.0333 | 72.4267 | 438.9074 | 20.721 | -148.4165 | 80.5018 | 9.4982 | -150.22 | 131.2118 | 0 | 38.275 | 0.70984 | 0.84974 | 21.9093 | 60.1843 | -3.3 | -1.4192 | 1.1057 | 0.054566
2015-05-25 02:00 | 152.22 | 61.6767 | 90.5433 | 453.034 | 20.7288 | -133.4175 | 78.4712 | 11.5288 | -136.1055 | 120.7673 | 0 | 46.2575 | 0.70969 | 0.84948 | 27.0072 | 73.2647 | -2.9 | -0.61048 | 1.1024 | 0.066231
2015-05-25 03:00 | 180.98 | 72.32 | 108.66 | 444.2759 | 20.7366 | -118.4184 | 75.8431 | 14.1569 | -121.9746 | 108.807 | 0 | 54.24 | 0.70953 | 0.84922 | 32.1027 | 86.3427 | -3 | -0.30179 | 1.1012 | 0.077967
2015-05-25 04:00 | 231.0333 | 88.0233 | 143.01 | 482.9301 | 20.7444 | -103.4194 | 72.7747 | 17.2253 | -107.7581 | 95.9825 | 0 | 66.0175 | 0.70938 | 0.84896 | 40.9723 | 106.9898 | -2.4 | 0.94343 | 1.0962 | 0.096174
2015-05-25 05:00 | 281.0867 | 103.7267 | 177.36 | 505.2829 | 20.7521 | -88.4204 | 69.4508 | 20.5492 | -93.3546 | 82.6429 | 64.7034 | 77.795 | 0.70922 | 0.8487 | 49.838 | 192.3364 | -2.5 | 3.5105 | 1.086 | 0.17127
2015-05-25 06:00 | 331.14 | 119.43 | 211.71 | 522.1079 | 20.7599 | -73.4213 | 66.0781 | 23.9219 | -78.6435 | 68.984 | 187.2426 | 89.5725 | 0.70906 | 0.84844 | 58.6997 | 335.5148 | -2.1 | 8.3848 | 1.0665 | 0.29341
2015-05-25 07:00 | 385.18 | 128.1633 | 257.0167 | 563.8 | 20.7676 | -58.4223 | 62.8794 | 27.1206 | -63.5061 | 55.1248 | 322.3757 | 96.1225 | 0.70891 | 0.84818 | 68.2641 | 486.7623 | -1.4 | 13.8113 | 1.0448 | 0.41701
2015-05-25 08:00 | 439.22 | 136.8967 | 302.3233 | 606.2105 | 20.7754 | -43.4233 | 60.0853 | 29.9147 | -47.8572 | 41.1471 | 456.49 | 102.6725 | 0.70875 | 0.84792 | 77.8243 | 636.9868 | -1.35 | 18.5558 | 1.0258 | 0.53579
2015-05-25 09:00 | 493.26 | 145.63 | 347.63 | 654.5272 | 20.7831 | -28.4242 | 57.9191 | 32.0809 | -31.6834 | 27.1293 | 582.5159 | 109.2225 | 0.70859 | 0.84766 | 87.3802 | 779.1187 | -1.3 | 23.0475 | 1.0078 | 0.64387
2015-05-25 10:00 | 493.7533 | 153.19 | 340.5633 | 618.2117 | 20.7908 | -13.4252 | 56.5723 | 33.4277 | -15.0748 | 13.2602 | 601.7293 | 114.8925 | 0.70844 | 0.8474 | 87.4483 | 804.0702 | -1.3 | 23.8272 | 1.0047 | 0.66243
2015-05-25 11:00 | 494.2467 | 160.75 | 333.4967 | 599.0835 | 20.7985 | 1.5738 | 56.1736 | 33.8264 | 1.7711 | 4.1109 | 597.5422 | 120.5625 | 0.70828 | 0.84714 | 87.5164 | 805.6211 | -1.2 | 23.9757 | 1.0041 | 0.66332
2015-05-25 12:00 | 494.74 | 168.31 | 326.43 | 595.5538 | 20.8062 | 16.5728 | 56.7624 | 33.2376 | 18.5894 | 16.1343 | 572.0966 | 126.2325 | 0.70813 | 0.84688 | 87.5844 | 785.9135 | -1 | 23.5598 | 1.0058 | 0.64816
2015-05-25 13:00 | 465.5567 | 148.1 | 317.4567 | 603.7835 | 20.8139 | 31.5718 | 58.2793 | 31.7207 | 35.1236 | 30.0702 | 522.5218 | 111.075 | 0.70797 | 0.84661 | 82.3999 | 715.9967 | -0.3 | 22.0749 | 1.0117 | 0.59399
2015-05-25 14:00 | 436.3733 | 127.89 | 308.4833 | 628.0055 | 20.8216 | 46.5708 | 60.5798 | 29.4202 | 51.1959 | 44.0839 | 451.1099 | 95.9175 | 0.70781 | 0.84635 | 77.2176 | 624.245 | -0.7 | 18.8077 | 1.0248 | 0.52456
2015-05-25 15:00 | 407.19 | 107.68 | 299.51 | 670.3847 | 20.8293 | 61.5698 | 63.4632 | 26.5368 | 66.7387 | 58.0371 | 354.8813 | 80.76 | 0.70766 | 0.84609 | 72.0376 | 507.6789 | -0.3 | 15.565 | 1.0377 | 0.43201
2015-05-25 16:00 | 344.9033 | 110.9967 | 233.9067 | 591.4165 | 20.8369 | 76.5688 | 66.7027 | 23.2973 | 81.7827 | 71.8541 | 184.1896 | 83.2475 | 0.7075 | 0.84583 | 61.0048 | 328.4419 | -0.5 | 9.7638 | 1.0609 | 0.28574
2015-05-25 17:00 | 282.6167 | 114.3133 | 168.3033 | 493.7016 | 20.8446 | 91.5678 | 70.0682 | 19.9318 | 96.4224 | 85.447 | 39.1906 | 85.735 | 0.70734 | 0.84557 | 49.9768 | 174.9024 | -0.8 | 4.6657 | 1.0813 | 0.15509
2015-05-25 18:00 | 220.33 | 117.63 | 102.7 | 358.2171 | 20.8522 | 106.5668 | 73.3396 | 16.6604 | 110.7788 | 98.6841 | 0 | 88.2225 | 0.70719 | 0.84531 | 38.9537 | 127.1762 | -1.4 | 2.5743 | 1.0897 | 0.11364
2015-05-25 19:00 | 182.18 | 97.7167 | 84.4633 | 356.9967 | 20.8598 | 121.5658 | 76.3144 | 13.6856 | 124.9695 | 111.3439 | 0 | 73.2875 | 0.70703 | 0.84505 | 32.2017 | 105.4892 | -1.3 | 1.9965 | 1.092 | 0.09446
2015-05-25 20:00 | 144.03 | 77.8033 | 66.2267 | 341.3534 | 20.8674 | 136.5648 | 78.813 | 11.187 | 139.0895 | 123.0276 | 0 | 58.3525 | 0.70688 | 0.84479 | 25.4528 | 83.8053 | -1.6 | 1.0189 | 1.0959 | 0.075312
2015-05-25 21:00 | 105.88 | 57.89 | 47.99 | 296.4907 | 20.875 | 151.5638 | 80.6851 | 9.3149 | 153.2005 | 132.9909 | 0 | 43.4175 | 0.70672 | 0.84453 | 18.7068 | 62.1243 | -1.7 | 0.24139 | 1.099 | 0.055987
2015-05-25 22:00 | 97.95 | 54.8733 | 43.0767 | 302.6404 | 20.8826 | 166.5627 | 81.8169 | 8.1831 | 167.3292 | 139.9216 | 0 | 41.155 | 0.70656 | 0.84427 | 17.3019 | 58.4569 | -1 | 0.82678 | 1.0967 | 0.05257
2015-05-25 23:00 | 90.02 | 51.8567 | 38.1633 | 279.0176 | 20.8902 | 181.5617 | 82.1386 | 7.8614 | -178.5271 | 142.1121 | 0 | 38.8925 | 0.70641 | 0.84401 | 15.8977 | 54.7902 | -1.8 | -0.087807 | 1.1004 | 0.049437
2015-05-26 | 82.09 | 48.84 | 33.25 | 228.413 | 20.8978 | -163.4393 | 81.6297 | 8.3703 | -164.3864 | 138.7986 | 0 | 36.63 | 0.70625 | 0.84375 | 14.494 | 51.124 | -1.9 | -0.30237 | 1.1012 | 0.046165
2015-05-26 01:00 | 116.76 | 50.5133 | 66.2467 | 394.0432 | 20.9054 | -148.4403 | 80.3215 | 9.6785 | -150.2648 | 131.0889 | 0 | 37.885 | 0.70609 | 0.84349 | 20.6109 | 58.4959 | -1.7 | 0.128 | 1.0995 | 0.052739
2015-05-26 02:00 | 151.43 | 52.1867 | 99.2433 | 489.125 | 20.9129 | -133.4414 | 78.2934 | 11.7066 | -136.1594 | 120.6768 | 0 | 39.14 | 0.70594 | 0.84323 | 26.725 | 65.865 | -2 | 0.058282 | 1.0998 | 0.059398
2015-05-26 03:00 | 186.1 | 53.86 | 132.24 | 534.2056 | 20.9205 | -118.4424 | 75.6677 | 14.3323 | -122.0361 | 108.7425 | 0 | 40.395 | 0.70578 | 0.84297 | 32.8365 | 73.2315 | -2.1 | 0.18848 | 1.0992 | 0.06601
2015-05-26 04:00 | 231.5467 | 63.02 | 168.5267 | 563.5933 | 20.928 | -103.4435 | 72.6011 | 17.3989 | -107.8252 | 95.9386 | 0 | 47.265 | 0.70563 | 0.84271 | 40.8463 | 88.1113 | -1.9 | 0.85348 | 1.0966 | 0.07923
2015-05-26 05:00 | 276.9933 | 72.18 | 204.8133 | 578.8472 | 20.9355 | -88.4445 | 69.2783 | 20.7217 | -93.4253 | 82.6159 | 74.3935 | 54.135 | 0.70547 | 0.84245 | 48.8525 | 177.381 | -1.9 | 3.6432 | 1.0854 | 0.15788
2015-05-26 06:00 | 322.44 | 81.34 | 241.1 | 590.5805 | 20.943 | -73.4456 | 65.9055 | 24.0945 | -78.7151 | 68.9718 | 211.9162 | 61.005 | 0.70531 | 0.84219 | 56.8552 | 329.7765 | -1.7 | 8.6055 | 1.0656 | 0.28815
2015-05-26 07:00 | 362.8067 | 103.5967 | 259.21 | 565.2688 | 20.9505 | -58.4466 | 62.7057 | 27.2943 | -63.5755 | 55.1263 | 323.2031 | 77.6975 | 0.70516 | 0.84193 | 63.9588 | 464.8594 | -1.2 | 13.3269 | 1.0467 | 0.39898
2015-05-26 08:00 | 403.1733 | 125.8533 | 277.32 | 553.1306 | 20.958 | -43.4477 | 59.9097 | 30.0903 | -47.9209 | 41.1629 | 416.4194 | 94.39 | 0.705 | 0.84167 | 71.0593 | 581.8687 | -0.7 | 17.4834 | 1.0301 | 0.49148
2015-05-26 09:00 | 443.54 | 148.11 | 295.43 | 553.5028 | 20.9655 | -28.4487 | 57.7411 | 32.2589 | -31.7376 | 27.163 | 492.4579 | 111.0825 | 0.70484 | 0.84141 | 78.1566 | 681.697 | -0.5 | 20.803 | 1.0168 | 0.56838
2015-05-26 10:00 | 439.2133 | 155.7933 | 283.42 | 512.0425 | 20.973 | -13.4498 | 56.3919 | 33.6081 | -15.116 | 13.3291 | 498.2491 | 116.845 | 0.70469 | 0.84115 | 77.377 | 692.4711 | -0.6 | 21.0397 | 1.0158 | 0.57682
2015-05-26 11:00 | 434.8867 | 163.4767 | 271.41 | 485.2543 | 20.9804 | 1.5491 | 55.9916 | 34.0084 | 1.7449 | 4.2726 | 483.9057 | 122.6075 | 0.70453 | 0.84089 | 76.5978 | 683.111 | -0.3 | 21.0472 | 1.0158 | 0.56901
2015-05-26 12:00 | 430.56 | 171.16 | 259.4 | 470.9695 | 20.9879 | 16.5481 | 56.5795 | 33.4205 | 18.5785 | 16.1472 | 452.3899 | 128.37 | 0.70438 | 0.84063 | 75.8189 | 656.5789 | -0.6 | 19.9181 | 1.0203 | 0.54934
2015-05-26 13:00 | 415.6633 | 152.0333 | 263.63 | 498.8353 | 20.9953 | 31.547 | 58.0964 | 31.9036 | 35.1262 | 30.0535 | 431.7707 | 114.025 | 0.70422 | 0.84036 | 73.1795 | 618.9752 | -1.2 | 18.143 | 1.0274 | 0.52148
2015-05-26 14:00 | 400.7667 | 132.9067 | 267.86 | 542.2486 | 21.0027 | 46.5459 | 60.3975 | 29.6025 | 51.2088 | 44.0508 | 389.7268 | 99.68 | 0.70406 | 0.8401 | 70.5412 | 559.948 | -0.9 | 16.5984 | 1.0336 | 0.47459
2015-05-26 15:00 | 385.87 | 113.78 | 272.09 | 605.1739 | 21.0102 | 61.5448 | 63.2816 | 26.7184 | 66.7581 | 57.9905 | 320.7783 | 85.335 | 0.70391 | 0.83984 | 67.9041 | 474.0174 | -1.5 | 13.313 | 1.0467 | 0.40686
2015-05-26 16:00 | 323.8267 | 108.2367 | 215.59 | 541.1365 | 21.0176 | 76.5437 | 66.5217 | 23.4783 | 81.8049 | 71.7944 | 169.0661 | 81.1775 | 0.70375 | 0.83958 | 56.9733 | 307.2168 | -1.5 | 8.1005 | 1.0676 | 0.26895
2015-05-26 17:00 | 261.7833 | 102.6933 | 159.09 | 462.652 | 21.025 | 91.5426 | 69.8875 | 20.1125 | 96.4442 | 85.3734 | 37.318 | 77.02 | 0.70359 | 0.83932 | 46.0473 | 160.3853 | -1.6 | 3.412 | 1.0864 | 0.14287
2015-05-26 18:00 | 199.74 | 97.15 | 102.59 | 354.1007 | 21.0323 | 106.5415 | 73.1588 | 16.8412 | 110.7972 | 98.5948 | 0 | 72.8625 | 0.70344 | 0.83906 | 35.1262 | 107.9887 | -1.5 | 1.8746 | 1.0925 | 0.096742
2015-05-26 19:00 | 166.69 | 80.84 | 85.85 | 358.2116 | 21.0397 | 121.5404 | 76.1334 | 13.8666 | 124.9822 | 111.236 | 0 | 60.63 | 0.70328 | 0.8388 | 29.3075 | 89.9375 | -1.5 | 1.3105 | 1.0948 | 0.080737
2015-05-26 20:00 | 133.64 | 64.53 | 69.11 | 350.6118 | 21.0471 | 136.5393 | 78.6318 | 11.3682 | 139.0945 | 122.8974 | 0 | 48.3975 | 0.70312 | 0.83854 | 23.4914 | 71.8889 | -1.5 | 0.74653 | 1.097 | 0.064668
2015-05-26 21:00 | 100.59 | 48.22 | 52.37 | 317.4413 | 21.0544 | 151.5382 | 80.5042 | 9.4958 | 153.1963 | 132.8356 | 0 | 36.165 | 0.70297 | 0.83828 | 17.6779 | 53.8429 | -1.9 | -0.21741 | 1.1009 | 0.048605
2015-05-26 22:00 | 101.4933 | 45.7 | 55.7933 | 383.5967 | 21.0618 | 166.5371 | 81.6368 | 8.3632 | 167.3146 | 139.7452 | 0 | 34.275 | 0.70281 | 0.83802 | 17.8327 | 52.1077 | -2.2 | -0.57163 | 1.1023 | 0.047099
2015-05-26 23:00 | 102.3967 | 43.18 | 59.2167 | 423.3777 | 21.0691 | 181.536 | 81.9598 | 8.0402 | -178.5525 | 141.9344 | 0 | 32.385 | 0.70266 | 0.83776 | 17.9874 | 50.3724 | -2.4 | -0.82586 | 1.1033 | 0.045572
2015-05-27 | 103.3 | 40.66 | 62.64 | 421.4769 | 21.0764 | -163.4651 | 81.453 | 8.547 | -164.4224 | 138.6458 | 0 | 30.495 | 0.7025 | 0.8375 | 18.1421 | 48.6371 | -2.6 | -1.0801 | 1.1043 | 0.044043
2015-05-27 01:00 | 124.4667 | 53.17 | 71.2967 | 416.6545 | 21.0838 | -148.4662 | 80.1472 | 9.8528 | -150.3108 | 130.9715 | 0 | 39.8775 | 0.70234 | 0.83724 | 21.8546 | 61.7321 | -2.8 | -0.87087 | 1.1035 | 0.055859
2015-05-27 02:00 | 145.6333 | 65.68 | 79.9533 | 388.4413 | 21.0911 | -133.4673 | 78.1218 | 11.8782 | -136.2142 | 120.5912 | 0 | 49.26 | 0.70219 | 0.83698 | 25.5655 | 74.8255 | -2.8 | -0.4617 | 1.1018 | 0.067606
2015-05-27 03:00 | 166.8 | 78.19 | 88.61 | 353.8676 | 21.0984 | -118.4685 | 75.4986 | 14.5014 | -122.0982 | 108.6822 | 0 | 58.6425 | 0.70203 | 0.83672 | 29.2747 | 87.9172 | -2.7 | 0.047413 | 1.0998 | 0.079288
2015-05-27 04:00 | 206.2567 | 99.57 | 106.6867 | 353.4937 | 21.1056 | -103.4696 | 72.4339 | 17.5661 | -107.8929 | 95.8985 | 0 | 74.6775 | 0.70188 | 0.83646 | 36.1916 | 110.8691 | -2.9 | 0.56466 | 1.0977 | 0.099799
2015-05-27 05:00 | 245.7133 | 120.95 | 124.7633 | 349.9259 | 21.1129 | -88.4707 | 69.112 | 20.888 | -93.4964 | 82.5924 | 45.1147 | 90.7125 | 0.70172 | 0.8362 | 43.1054 | 178.9326 | -2.7 | 2.8916 | 1.0884 | 0.1597
2015-05-27 06:00 | 285.17 | 142.33 | 142.84 | 347.6357 | 21.1202 | -73.4719 | 65.7393 | 24.2607 | -78.7872 | 68.9628 | 124.7922 | 106.7475 | 0.70156 | 0.83594 | 50.0161 | 281.5559 | -2.8 | 5.9986 | 1.076 | 0.24842
2015-05-27 07:00 | 312.1967 | 189.26 | 122.9367 | 266.5846 | 21.1274 | -58.473 | 62.5384 | 27.4616 | -63.6457 | 55.1308 | 152.4077 | 141.945 | 0.70141 | 0.83568 | 54.7442 | 349.0969 | -2.7 | 8.2093 | 1.0672 | 0.30549
2015-05-27 08:00 | 339.2233 | 236.19 | 103.0333 | 204.4639 | 21.1347 | -43.4741 | 59.7404 | 30.2596 | -47.9857 | 41.1814 | 153.8853 | 177.1425 | 0.70125 | 0.83542 | 59.4701 | 390.4979 | -2.7 | 9.5031 | 1.062 | 0.34006
2015-05-27 09:00 | 366.25 | 283.12 | 83.13 | 155.0125 | 21.1419 | -28.4753 | 57.5693 | 32.4307 | -31.7933 | 27.1992 | 137.8717 | 212.34 | 0.70109 | 0.83516 | 64.1939 | 414.4056 | -2.6 | 10.3502 | 1.0586 | 0.35973
2015-05-27 10:00 | 321.07 | 248.33 | 72.74 | 130.8183 | 21.1491 | -13.4764 | 56.2177 | 33.7823 | -15.1592 | 13.4002 | 127.2567 | 186.2475 | 0.70094 | 0.8349 | 56.2625 | 369.7667 | -2.3 | 9.2552 | 1.063 | 0.3223
2015-05-27 11:00 | 275.89 | 213.54 | 62.35 | 110.9708 | 21.1563 | 1.5224 | 55.8155 | 34.1845 | 1.7164 | 4.4297 | 110.6393 | 160.155 | 0.70078 | 0.83464 | 48.3346 | 319.1289 | -2.3 | 7.6728 | 1.0693 | 0.27982
2015-05-27 12:00 | 230.71 | 178.75 | 51.96 | 93.8999 | 21.1635 | 16.5212 | 56.4025 | 33.5975 | 18.5648 | 16.159 | 90.1902 | 134.0625 | 0.70063 | 0.83437 | 40.4103 | 264.663 | -2.2 | 6.0707 | 1.0757 | 0.23346
2015-05-27 13:00 | 227.4633 | 167.3733 | 60.09 | 113.1396 | 21.1707 | 31.5201 | 57.9193 | 32.0807 | 35.1257 | 30.0358 | 97.9464 | 125.53 | 0.70047 | 0.83411 | 39.8327 | 263.3092 | -2.1 | 6.1284 | 1.0755 | 0.23221
2015-05-27 14:00 | 224.2167 | 155.9967 | 68.22 | 137.3577 | 21.1779 | 46.5189 | 60.2208 | 29.7792 | 51.2184 | 44.0167 | 98.7789 | 116.9975 | 0.70031 | 0.83385 | 39.2554 | 255.0319 | -2.2 | 5.7697 | 1.0769 | 0.22521
2015-05-27 15:00 | 220.97 | 144.62 | 76.35 | 168.7853 | 21.185 | 61.5178 | 63.1055 | 26.8945 | 66.774 | 57.9432 | 89.5845 | 108.465 | 0.70016 | 0.83359 | 38.6784 | 236.7279 | -2.4 | 4.9977 | 1.08 | 0.20965
2015-05-27 16:00 | 196.4433 | 126.81 | 69.6333 | 173.5577 | 21.1922 | 76.5166 | 66.3461 | 23.6539 | 81.8237 | 71.7343 | 54.3971 | 95.1075 | 0.7 | 0.83333 | 34.3776 | 183.8822 | -2.7 | 3.0463 | 1.0878 | 0.16402
2015-05-27 17:00 | 171.9167 | 109 | 62.9167 | 181.4532 | 21.1993 | 91.5154 | 69.7121 | 20.2879 | 96.4626 | 85.2998 | 14.8685 | 81.75 | 0.69984 | 0.83307 | 30.0787 | 126.6972 | -2.6 | 1.3593 | 1.0946 | 0.11372
2015-05-27 18:00 | 147.39 | 91.19 | 56.2 | 192.0396 | 21.2065 | 106.5142 | 72.9834 | 17.0166 | 110.8124 | 98.5059 | 0 | 68.3925 | 0.69969 | 0.83281 | 25.7817 | 94.1742 | -2.3 | 0.64294 | 1.0974 | 0.084747
2015-05-27 19:00 | 124.1 | 73.6767 | 50.4233 | 207.8155 | 21.2136 | 121.5131 | 75.9579 | 14.0421 | 124.9919 | 111.1293 | 0 | 55.2575 | 0.69953 | 0.83255 | 21.703 | 76.9605 | -2.5 | -0.094986 | 1.1004 | 0.069442
2015-05-27 20:00 | 100.81 | 56.1633 | 44.6467 | 223.1059 | 21.2207 | 136.5119 | 78.4564 | 11.5436 | 139.0967 | 122.7694 | 0 | 42.1225 | 0.69938 | 0.83229 | 17.626 | 59.7485 | -2.7 | -0.83286 | 1.1033 | 0.054056
2015-05-27 21:00 | 77.52 | 38.65 | 38.87 | 231.3839 | 21.2278 | 151.5107 | 80.3291 | 9.6709 | 153.1896 | 132.6838 | 0 | 28.9875 | 0.69922 | 0.83203 | 13.5509 | 42.5384 | -3.2 | -1.8707 | 1.1075 | 0.038631
2015-05-27 22:00 | 81.7133 | 38.73 | 42.9833 | 289.5364 | 21.2349 | 166.5095 | 81.4626 | 8.5374 | 167.2979 | 139.5738 | 0 | 29.0475 | 0.69906 | 0.83177 | 14.2807 | 43.3282 | -3.1 | -1.746 | 1.107 | 0.03933
2015-05-27 23:00 | 85.9067 | 38.81 | 47.0967 | 329.6909 | 21.242 | 181.5083 | 81.7871 | 8.2129 | -178.5796 | 141.7628 | 0 | 29.1075 | 0.69891 | 0.83151 | 15.0102 | 44.1177 | -2.8 | -1.4213 | 1.1057 | 0.04
2015-05-28 | 90.1 | 38.89 | 51.21 | 337.8789 | 21.249 | -163.4929 | 81.2825 | 8.7175 | -164.4599 | 138.4992 | 0 | 29.1675 | 0.69875 | 0.83125 | 15.7393 | 44.9068 | -2.5 | -1.0967 | 1.1044 | 0.040668
2015-05-28 01:00 | 107.28 | 49.7767 | 57.5033 | 330.4694 | 21.2561 | -148.4941 | 79.9792 | 10.0208 | -150.358 | 130.8595 | 0 | 37.3325 | 0.69859 | 0.83099 | 18.7363 | 56.0688 | -2.7 | -0.94785 | 1.1038 | 0.050748
2015-05-28 02:00 | 124.46 | 60.6633 | 63.7967 | 305.7539 | 21.2632 | -133.4953 | 77.9565 | 12.0435 | -136.2699 | 120.5103 | 0 | 45.4975 | 0.69844 | 0.83073 | 21.7319 | 67.2294 | -2.7 | -0.59908 | 1.1024 | 0.060773
2015-05-28 03:00 | 141.64 | 71.55 | 70.09 | 276.8661 | 21.2702 | -118.4965 | 75.3357 | 14.6643 | -122.1611 | 108.6262 | 0 | 53.6625 | 0.69828 | 0.83047 | 24.7261 | 78.3886 | -2.5 | -0.050355 | 1.1002 | 0.070719
2015-05-28 04:00 | 158.95 | 99.23 | 59.72 | 196.1357 | 21.2772 | -103.4977 | 72.2729 | 17.7271 | -107.9612 | 95.8622 | 0 | 74.4225 | 0.69813 | 0.83021 | 27.7417 | 102.1642 | -1.9 | 1.2926 | 1.0948 | 0.091719
2015-05-28 05:00 | 176.26 | 126.91 | 49.35 | 137.4084 | 21.2842 | -88.4989 | 68.9521 | 21.0479 | -93.5681 | 82.5724 | 17.7633 | 95.1825 | 0.69797 | 0.82995 | 30.756 | 143.7018 | -1.9 | 2.5907 | 1.0896 | 0.1284
2015-05-28 06:00 | 193.57 | 154.59 | 38.98 | 94.2837 | 21.2912 | -73.5002 | 65.5793 | 24.4207 | -78.8599 | 68.9569 | 33.8545 | 115.9425 | 0.69781 | 0.82969 | 33.7689 | 183.5659 | -2.3 | 3.4364 | 1.0863 | 0.16351
2015-05-28 07:00 | 224.88 | 189.53 | 35.35 | 76.2435 | 21.2982 | -58.5014 | 62.3774 | 27.6226 | -63.7166 | 55.1381 | 43.5808 | 142.1475 | 0.69766 | 0.82943 | 39.2222 | 224.9505 | -1.7 | 5.3297 | 1.0787 | 0.19897
2015-05-28 08:00 | 256.19 | 224.47 | 31.72 | 62.6413 | 21.3052 | -43.5026 | 59.5773 | 30.4227 | -48.0515 | 41.2025 | 47.1304 | 168.3525 | 0.6975 | 0.82917 | 44.6731 | 260.1561 | -1.9 | 6.2299 | 1.0751 | 0.22934
2015-05-28 09:00 | 287.5 | 259.41 | 28.09 | 52.1425 | 21.3122 | -28.5038 | 57.4038 | 32.5962 | -31.8503 | 27.2378 | 46.3607 | 194.5575 | 0.69734 | 0.82891 | 50.1216 | 291.0398 | -1.7 | 7.395 | 1.0704 | 0.25546
2015-05-28 10:00 | 288.65 | 244.56 | 44.09 | 78.9473 | 21.3192 | -13.5051 | 56.0497 | 33.9503 | -15.2042 | 13.4733 | 76.7746 | 183.42 | 0.69719 | 0.82865 | 50.3108 | 310.5054 | -1.5 | 8.2033 | 1.0672 | 0.27172
2015-05-28 11:00 | 289.8 | 229.71 | 60.09 | 106.4838 | 21.3261 | 1.4937 | 55.6455 | 34.3545 | 1.6855 | 4.582 | 106.1434 | 172.2825 | 0.69703 | 0.82839 | 50.4999 | 328.9259 | -1.3 | 8.9789 | 1.0641 | 0.287
2015-05-28 12:00 | 290.95 | 214.86 | 76.09 | 136.8919 | 21.3331 | 16.4925 | 56.2314 | 33.7686 | 18.5484 | 16.1696 | 131.4767 | 161.145 | 0.69688 | 0.82812 | 50.6889 | 343.3106 | -1 | 9.7285 | 1.0611 | 0.29871
2015-05-28 13:00 | 256.3933 | 195.71 | 60.6833 | 113.7146 | 21.34 | 31.4912 | 57.7479 | 32.2521 | 35.1221 | 30.017 | 98.4629 | 146.7825 | 0.69672 | 0.82786 | 44.6585 | 289.9039 | -1.4 | 7.6595 | 1.0694 | 0.25421
2015-05-28 14:00 | 221.8367 | 176.56 | 45.2767 | 90.6895 | 21.3469 | 46.49 | 60.0497 | 29.9503 | 51.2246 | 43.9817 | 65.2567 | 132.42 | 0.69656 | 0.8276 | 38.6308 | 236.3075 | -1 | 6.3846 | 1.0745 | 0.2082
2015-05-28 15:00 | 187.28 | 157.41 | 29.87 | 65.648 | 21.3538 | 61.4887 | 62.9349 | 27.0651 | 66.7866 | 57.8951 | 34.89 | 118.0575 | 0.69641 | 0.82734 | 32.6057 | 185.5532 | -1.3 | 4.4985 | 1.082 | 0.16463
2015-05-28 16:00 | 167.7033 | 134.5533 | 33.15 | 82.0688 | 21.3607 | 76.4875 | 66.1759 | 23.8241 | 81.839 | 71.6738 | 25.8046 | 100.915 | 0.69625 | 0.82708 | 29.1909 | 155.9104 | -0.9 | 3.9722 | 1.0841 | 0.1386
2015-05-28 17:00 | 148.1267 | 111.6967 | 36.43 | 104.2295 | 21.3676 | 91.4862 | 69.5422 | 20.4578 | 96.4776 | 85.2263 | 8.674 | 83.7725 | 0.69609 | 0.82682 | 25.7775 | 118.2241 | -0.4 | 3.2945 | 1.0868 | 0.10536
2015-05-28 18:00 | 128.55 | 88.84 | 39.71 | 134.391 | 21.3745 | 106.485 | 72.8136 | 17.1864 | 110.8244 | 98.4177 | 0 | 66.63 | 0.69594 | 0.82656 | 22.3657 | 88.9957 | -0.6 | 2.1811 | 1.0913 | 0.079637
2015-05-28 19:00 | 111.8567 | 73.46 | 38.3967 | 156.3955 | 21.3813 | 121.4837 | 75.788 | 14.212 | 124.9985 | 111.0238 | 0 | 55.095 | 0.69578 | 0.8263 | 19.4569 | 74.5519 | -0.8 | 1.5297 | 1.0939 | 0.066872
2015-05-28 20:00 | 95.1633 | 58.08 | 37.0833 | 182.6622 | 21.3882 | 136.4824 | 78.2866 | 11.7134 | 139.0962 | 122.6436 | 0 | 43.56 | 0.69563 | 0.82604 | 16.5495 | 60.1095 | -1.1 | 0.77842 | 1.0969 | 0.054065
2015-05-28 21:00 | 78.47 | 42.7 | 35.77 | 209.303 | 21.3951 | 151.4812 | 80.1598 | 9.8402 | 153.1804 | 132.5356 | 0 | 32.025 | 0.69547 | 0.82578 | 13.6434 | 45.6684 | -1 | 0.42714 | 1.0983 | 0.041129
2015-05-28 22:00 | 71.8333 | 37.8533 | 33.98 | 224.4998 | 21.4019 | 166.4799 | 81.2943 | 8.7057 | 167.2791 | 139.4075 | 0 | 28.39 | 0.69531 | 0.82552 | 12.4867 | 40.8767 | -0.7 | 0.5774 | 1.0977 | 0.036793
2015-05-28 23:00 | 65.1967 | 33.0067 | 32.19 | 220.8912 | 21.4087 | 181.4786 | 81.6206 | 8.3794 | -178.6086 | 141.5973 | 0 | 24.755 | 0.69516 | 0.82526 | 11.3305 | 36.0855 | -0.8 | 0.32767 | 1.0987 | 0.03251
2015-05-29 | 58.56 | 28.16 | 30.4 | 196.8941 | 21.4155 | -163.5227 | 81.1181 | 8.8819 | -164.4989 | 138.3586 | 0 | 21.12 | 0.695 | 0.825 | 10.1748 | 31.2948 | -0.6 | 0.37796 | 1.0985 | 0.028189
2015-05-29 01:00 | 63.1067 | 32.8433 | 30.2633 | 171.1886 | 21.4223 | -148.5239 | 79.8175 | 10.1825 | -150.4062 | 130.7529 | 0 | 24.6325 | 0.69484 | 0.82474 | 10.9623 | 35.5948 | -0.7 | 0.41234 | 1.0984 | 0.032058
2015-05-29 02:00 | 67.6533 | 37.5267 | 30.1267 | 142.5329 | 21.4291 | -133.5252 | 77.7976 | 12.2024 | -136.3264 | 120.4342 | 0 | 28.145 | 0.69469 | 0.82448 | 11.7495 | 39.8945 | -0.8 | 0.4467 | 1.0982 | 0.035926
2015-05-29 03:00 | 72.2 | 42.21 | 29.99 | 117.2419 | 21.4359 | -118.5265 | 75.1792 | 14.8208 | -122.2245 | 108.5744 | 0 | 31.6575 | 0.69453 | 0.82422 | 12.5363 | 44.1938 | -0.7 | 0.68106 | 1.0973 | 0.039764
2015-05-29 04:00 | 100.6733 | 48.5567 | 52.1167 | 169.7326 | 21.4427 | -103.5278 | 72.1184 | 17.8816 | -108.0298 | 95.8296 | 0 | 36.4175 | 0.69438 | 0.82396 | 17.4763 | 53.8938 | -1.5 | 0.18418 | 1.0993 | 0.04858
2015-05-29 05:00 | 129.1467 | 54.9033 | 74.2433 | 205.2919 | 21.4494 | -88.5291 | 68.7986 | 21.2014 | -93.6401 | 82.5557 | 26.5981 | 41.1775 | 0.69422 | 0.8237 | 22.414 | 90.1896 | -1 | 1.8184 | 1.0927 | 0.080813
2015-05-29 06:00 | 157.62 | 61.25 | 96.37 | 231.7303 | 21.4562 | -73.5304 | 65.4258 | 24.5742 | -78.933 | 68.954 | 83.2183 | 45.9375 | 0.69406 | 0.82344 | 27.3495 | 156.5054 | -1 | 3.8908 | 1.0844 | 0.13917
2015-05-29 07:00 | 168.5233 | 84.66 | 83.8633 | 179.9504 | 21.4629 | -58.5317 | 62.2227 | 27.7773 | -63.7881 | 55.1482 | 102.8337 | 63.495 | 0.69391 | 0.82318 | 29.2348 | 195.5635 | -1.2 | 4.9114 | 1.0804 | 0.17325
2015-05-29 08:00 | 179.4267 | 108.07 | 71.3567 | 140.2642 | 21.4697 | -43.533 | 59.4207 | 30.5793 | -48.1182 | 41.2262 | 105.4947 | 81.0525 | 0.69375 | 0.82292 | 31.1193 | 217.6665 | -1 | 5.8021 | 1.0768 | 0.19219
2015-05-29 09:00 | 190.33 | 131.48 | 58.85 | 108.7691 | 21.4764 | -28.5343 | 57.2446 | 32.7554 | -31.9087 | 27.2786 | 96.6728 | 98.61 | 0.69359 | 0.82266 | 33.0029 | 228.2857 | -0.6 | 6.5339 | 1.0739 | 0.20102
2015-05-29 10:00 | 208.1733 | 148.3633 | 59.81 | 106.6486 | 21.4831 | -13.5356 | 55.8879 | 34.1121 | -15.2511 | 13.548 | 103.681 | 111.2725 | 0.69344 | 0.8224 | 36.0888 | 251.0423 | -0.8 | 7.0451 | 1.0718 | 0.22064
2015-05-29 11:00 | 226.0167 | 165.2467 | 60.77 | 107.2405 | 21.4898 | 1.4631 | 55.4816 | 34.5184 | 1.6523 | 4.7292 | 106.8754 | 123.935 | 0.69328 | 0.82214 | 39.1733 | 269.9837 | -0.6 | 7.837 | 1.0687 | 0.23659
2015-05-29 12:00 | 243.86 | 182.13 | 61.73 | 110.581 | 21.4965 | 16.4617 | 56.0663 | 33.9337 | 18.5292 | 16.1788 | 106.2016 | 136.5975 | 0.69313 | 0.82188 | 42.2564 | 285.0555 | 0.7 | 9.608 | 1.0616 | 0.24814
2015-05-29 13:00 | 221.1733 | 164.0667 | 57.1067 | 106.525 | 21.5031 | 31.4604 | 57.5823 | 32.4177 | 35.1154 | 29.9969 | 92.2562 | 123.05 | 0.69297 | 0.82161 | 38.3166 | 253.6228 | 1.5 | 9.4257 | 1.0623 | 0.22093
2015-05-29 14:00 | 198.4867 | 146.0033 | 52.4833 | 104.6009 | 21.5098 | 46.4591 | 59.8843 | 30.1157 | 51.2275 | 43.9457 | 75.3124 | 109.5025 | 0.69281 | 0.82135 | 34.3785 | 219.1934 | 0.8 | 7.6498 | 1.0694 | 0.19221
2015-05-29 15:00 | 175.8 | 127.94 | 47.86 | 104.5972 | 21.5164 | 61.4578 | 62.7699 | 27.2301 | 66.7957 | 57.8464 | 55.6656 | 95.955 | 0.69266 | 0.82109 | 30.4422 | 182.0629 | 1.3 | 6.9895 | 1.072 | 0.16005
2015-05-29 16:00 | 136.08 | 104.16 | 31.92 | 78.5133 | 21.5231 | 76.4564 | 66.0114 | 23.9886 | 81.8509 | 71.6131 | 24.7657 | 78.12 | 0.6925 | 0.82083 | 23.5588 | 126.4445 | -0.1 | 3.8514 | 1.0846 | 0.11246
2015-05-29 17:00 | 96.36 | 80.38 | 15.98 | 45.3716 | 21.5297 | 91.4551 | 69.3779 | 20.6221 | 96.4892 | 85.1529 | 3.8338 | 60.285 | 0.69234 | 0.82057 | 16.6786 | 80.7974 | 0.1 | 2.6249 | 1.0895 | 0.072184
2015-05-29 18:00 | 56.64 | 56.6 | 0.04 | 0.13413 | 21.5363 | 106.4538 | 72.6494 | 17.3506 | 110.8332 | 98.3301 | 0 | 42.45 | 0.69219 | 0.82031 | 9.8014 | 52.2514 | 0.3 | 1.9329 | 1.0923 | 0.046799
2015-05-29 19:00 | 47.05 | 47.0233 | 0.026667 | 0.1074 | 21.543 | 121.4524 | 75.6239 | 14.3761 | 125.0022 | 110.9198 | 0 | 35.2675 | 0.69203 | 0.82005 | 8.14 | 43.4075 | 0.3 | 1.6565 | 1.0934 | 0.038918
2015-05-29 20:00 | 37.46 | 37.4467 | 0.013333 | 0.064783 | 21.5496 | 136.4511 | 78.1227 | 11.8773 | 139.0929 | 122.5202 | 0 | 28.085 | 0.69188 | 0.81979 | 6.4794 | 34.5644 | 0.3 | 1.3801 | 1.0945 | 0.031021
2015-05-29 21:00 | 27.87 | 27.87 | 0 | 0 | 21.5561 | 151.4497 | 79.9965 | 10.0035 | 153.1688 | 132.391 | 0 | 20.9025 | 0.69172 | 0.81953 | 4.8196 | 25.7221 | -0.2 | 0.60381 | 1.0976 | 0.02315
2015-05-29 22:00 | 30.6467 | 29.4967 | 1.15 | 7.46 | 21.5627 | 166.4484 | 81.1322 | 8.8678 | 167.2581 | 139.2464 | 0 | 22.1225 | 0.69156 | 0.81927 | 5.2985 | 27.421 | -0.3 | 0.55691 | 1.0978 | 0.024684
2015-05-29 23:00 | 33.4233 | 31.1233 | 2.3 | 15.4885 | 21.5693 | 181.447 | 81.4602 | 8.5398 | -178.6392 | 141.438 | 0 | 23.3425 | 0.69141 | 0.81901 | 5.7773 | 29.1198 | -0.1 | 0.80999 | 1.0968 | 0.026189
2015-05-30 | 36.2 | 32.75 | 3.45 | 21.9573 | 21.5758 | -163.5543 | 80.9601 | 9.0399 | -164.5391 | 138.2242 | 0 | 24.5625 | 0.69125 | 0.81875 | 6.2558 | 30.8183 | 0.1 | 1.0631 | 1.0957 | 0.027691
2015-05-30 01:00 | 42.91 | 40.5467 | 2.3633 | 13.1697 | 21.5824 | -148.5557 | 79.6622 | 10.3378 | -150.4555 | 130.6519 | 0 | 30.41 | 0.69109 | 0.81849 | 7.4137 | 37.8237 | 0.4 | 1.582 | 1.0937 | 0.033921
2015-05-30 02:00 | 49.62 | 48.3433 | 1.2767 | 5.9666 | 21.5889 | -133.557 | 77.645 | 12.355 | -136.3837 | 120.363 | 0 | 36.2575 | 0.69094 | 0.81823 | 8.5711 | 44.8286 | 0.2 | 1.6009 | 1.0936 | 0.0402
2015-05-30 03:00 | 56.33 | 56.14 | 0.19 | 0.7355 | 21.5954 | -118.5584 | 75.0292 | 14.9708 | -122.2884 | 108.5268 | 0 | 42.105 | 0.69078 | 0.81797 | 9.7279 | 51.8329 | -0.2 | 1.4198 | 1.0943 | 0.046512
2015-05-30 04:00 | 77.26 | 77.0867 | 0.17333 | 0.56002 | 21.602 | -103.5598 | 71.9702 | 18.0298 | -108.0988 | 95.8008 | 0 | 57.815 | 0.69063 | 0.81771 | 13.3394 | 71.1544 | -0.5 | 1.7236 | 1.0931 | 0.063779
2015-05-30 05:00 | 98.19 | 98.0333 | 0.15667 | 0.43036 | 21.6085 | -88.5612 | 68.6515 | 21.3485 | -93.7124 | 82.5423 | 0.055857 | 73.525 | 0.69047 | 0.81745 | 16.9493 | 90.5301 | -0.6 | 2.2291 | 1.0911 | 0.080996
2015-05-30 06:00 | 119.12 | 118.98 | 0.14 | 0.33476 | 21.6149 | -73.5625 | 65.2787 | 24.7213 | -79.0065 | 68.9541 | 0.12022 | 89.235 | 0.69031 | 0.81719 | 20.5575 | 109.9127 | -0.7 | 2.7348 | 1.0891 | 0.098155
2015-05-30 07:00 | 168.4567 | 156.2967 | 12.16 | 25.965 | 21.6214 | -58.5639 | 62.0745 | 27.9255 | -63.8602 | 55.161 | 14.8331 | 117.2225 | 0.69016 | 0.81693 | 29.0654 | 161.121 | -0.9 | 4.135 | 1.0835 | 0.14315
2015-05-30 08:00 | 217.7933 | 193.6133 | 24.18 | 47.3203 | 21.6279 | -43.5653 | 59.2705 | 30.7295 | -48.1857 | 41.2521 | 35.5761 | 145.21 | 0.69 | 0.81667 | 37.5694 | 218.3555 | -0.6 | 6.2236 | 1.0751 | 0.1925
2015-05-30 09:00 | 267.13 | 230.93 | 36.2 | 66.6304 | 21.6344 | -28.5667 | 57.0917 | 32.9083 | -31.9684 | 27.3214 | 59.1975 | 173.1975 | 0.68984 | 0.81641 | 46.0695 | 278.4645 | -0.6 | 8.102 | 1.0676 | 0.24377
2015-05-30 10:00 | 314.21 | 233.3333 | 80.8767 | 143.6382 | 21.6408 | -13.5681 | 55.7324 | 34.2676 | -15.2996 | 13.624 | 139.5966 | 175 | 0.68969 | 0.81615 | 54.1767 | 368.7732 | -0.4 | 11.1242 | 1.0555 | 0.31918
2015-05-30 11:00 | 361.29 | 235.7367 | 125.5533 | 220.6812 | 21.6472 | 1.4305 | 55.324 | 34.676 | 1.6169 | 4.8713 | 219.8841 | 176.8025 | 0.68953 | 0.81589 | 62.2802 | 458.9668 | -0.3 | 14.0427 | 1.0438 | 0.39285
2015-05-30 12:00 | 408.37 | 238.14 | 170.23 | 303.6921 | 21.6537 | 16.4291 | 55.9072 | 34.0928 | 18.5074 | 16.1865 | 291.6535 | 178.605 | 0.68938 | 0.81563 | 70.38 | 540.6385 | -0.3 | 16.595 | 1.0336 | 0.45823
2015-05-30 13:00 | 410.5667 | 198.08 | 212.4867 | 394.6359 | 21.6601 | 31.4278 | 57.4227 | 32.5773 | 35.1057 | 29.9756 | 341.8487 | 148.56 | 0.68922 | 0.81536 | 70.7426 | 561.1513 | 0.2 | 17.736 | 1.0291 | 0.47351
2015-05-30 14:00 | 412.7633 | 158.02 | 254.7433 | 505.2867 | 21.6665 | 46.4263 | 59.7247 | 30.2753 | 51.2272 | 43.9088 | 364.0312 | 118.515 | 0.68906 | 0.8151 | 71.1049 | 553.6511 | 1.3 | 18.6016 | 1.0256 | 0.46561
2015-05-30 15:00 | 414.96 | 117.96 | 297 | 645.6029 | 21.6729 | 61.4249 | 62.6106 | 27.3894 | 66.8014 | 57.7971 | 344.0542 | 88.47 | 0.68891 | 0.81484 | 71.4671 | 503.9913 | 1 | 16.7497 | 1.033 | 0.42691
2015-05-30 16:00 | 360.9133 | 100.1733 | 260.74 | 637.3687 | 21.6793 | 76.4235 | 65.8524 | 24.1476 | 81.8595 | 71.552 | 201.6913 | 75.13 | 0.68875 | 0.81458 | 62.1448 | 338.966 | 0.1 | 10.6927 | 1.0572 | 0.29386
2015-05-30 17:00 | 306.8667 | 82.3867 | 224.48 | 632.7055 | 21.6856 | 91.4221 | 69.2192 | 20.7808 | 96.4976 | 85.0796 | 54.2683 | 61.79 | 0.68859 | 0.81432 | 52.8266 | 168.8849 | -0.4 | 4.8777 | 1.0805 | 0.14963
2015-05-30 18:00 | 252.82 | 64.6 | 188.22 | 625.6097 | 21.692 | 106.4207 | 72.4908 | 17.5092 | 110.8388 | 98.2433 | 0 | 48.45 | 0.68844 | 0.81406 | 43.5127 | 91.9627 | -0.7 | 2.1738 | 1.0913 | 0.082295
2015-05-30 19:00 | 212.34 | 57.82 | 154.52 | 615.7066 | 21.6983 | 121.4193 | 75.4655 | 14.5345 | 125.0029 | 110.8172 | 0 | 43.365 | 0.68828 | 0.8138 | 36.5374 | 79.9024 | -0.7 | 1.797 | 1.0928 | 0.071601
2015-05-30 20:00 | 171.86 | 51.04 | 120.82 | 579.4297 | 21.7047 | 136.4179 | 77.9646 | 12.0354 | 139.087 | 122.3993 | 0 | 38.28 | 0.68813 | 0.81354 | 29.5653 | 67.8453 | -0.6 | 1.5202 | 1.0939 | 0.060858
2015-05-30 21:00 | 131.38 | 44.26 | 87.12 | 493.8445 | 21.711 | 151.4165 | 79.8392 | 10.1608 | 153.1548 | 132.2502 | 0 | 33.195 | 0.68797 | 0.81328 | 22.5963 | 55.7913 | -0.8 | 0.94348 | 1.0962 | 0.050151
2015-05-30 22:00 | 122.9833 | 41.59 | 81.3933 | 518.9375 | 21.7173 | 166.415 | 80.9761 | 9.0239 | 167.2352 | 139.0905 | 0 | 31.1925 | 0.68781 | 0.81302 | 21.1474 | 52.3399 | -1.2 | 0.43562 | 1.0983 | 0.047136
2015-05-30 23:00 | 114.5867 | 38.92 | 75.6667 | 500.5828 | 21.7236 | 181.4136 | 81.306 | 8.694 | -178.6715 | 141.2849 | 0 | 29.19 | 0.68766 | 0.81276 | 19.6991 | 48.8891 | -1 | 0.52778 | 1.0979 | 0.044013
2015-05-31 | 106.19 | 36.25 | 69.94 | 437.8421 | 21.7299 | -163.5878 | 80.8083 | 9.1917 | -164.5807 | 138.096 | 0 | 27.1875 | 0.6875 | 0.8125 | 18.2514 | 45.4389 | -1.6 | -0.18003 | 1.1007 | 0.041013
2015-05-31 01:00 | 139.46 | 40.8167 | 98.6433 | 541.968 | 21.7362 | -148.5893 | 79.5132 | 10.4868 | -150.5057 | 130.5564 | 0 | 30.6125 | 0.68734 | 0.81224 | 23.9642 | 54.5767 | -1.2 | 0.50552 | 1.098 | 0.049138
2015-05-31 02:00 | 172.73 | 45.3833 | 127.3467 | 588.3152 | 21.7425 | -133.5907 | 77.4988 | 12.5012 | -136.4415 | 120.2965 | 0 | 34.0375 | 0.68719 | 0.81198 | 29.6745 | 63.712 | -1.4 | 0.591 | 1.0976 | 0.057345
2015-05-31 03:00 | 206 | 49.95 | 156.05 | 598.4713 | 21.7487 | -118.5921 | 74.8856 | 15.1144 | -122.3527 | 108.4834 | 0 | 37.4625 | 0.68703 | 0.81172 | 35.3821 | 72.8446 | -1.6 | 0.67639 | 1.0973 | 0.065544
2015-05-31 04:00 | 257.1233 | 65.48 | 191.6433 | 614.5147 | 21.755 | -103.5936 | 71.8286 | 18.1714 | -108.1681 | 95.7757 | 0 | 49.11 | 0.68688 | 0.81146 | 44.1529 | 93.2629 | -1.6 | 1.3145 | 1.0947 | 0.083721
2015-05-31 05:00 | 308.2467 | 81.01 | 227.2367 | 620.3155 | 21.7612 | -88.595 | 68.5109 | 21.4891 | -93.785 | 82.5323 | 80.6211 | 60.7575 | 0.68672 | 0.8112 | 52.9197 | 194.2983 | -1.6 | 4.4718 | 1.0821 | 0.17241
2015-05-31 06:00 | 359.37 | 96.54 | 262.83 | 625.1418 | 21.7675 | -73.5965 | 65.1381 | 24.8619 | -79.0803 | 68.9572 | 224.4672 | 72.405 | 0.68656 | 0.81094 | 61.6825 | 358.5547 | -1.4 | 9.8048 | 1.0608 | 0.31189
2015-05-31 07:00 | 408.8267 | 111.31 | 297.5167 | 632.3331 | 21.7737 | -58.5979 | 61.9328 | 28.0672 | -63.9327 | 55.1763 | 361.0959 | 83.4825 | 0.68641 | 0.81068 | 70.1553 | 514.7336 | -1.5 | 14.5854 | 1.0417 | 0.43966
2015-05-31 08:00 | 458.2833 | 126.08 | 332.2033 | 647.3922 | 21.7799 | -43.5994 | 59.1267 | 30.8733 | -48.254 | 41.2804 | 486.5088 | 94.56 | 0.68625 | 0.81042 | 78.6242 | 659.693 | -1.1 | 19.5154 | 1.0219 | 0.55282
2015-05-31 09:00 | 507.74 | 140.85 | 366.89 | 672.6512 | 21.7861 | -28.6009 | 56.9453 | 33.0547 | -32.0292 | 27.3661 | 597.3731 | 105.6375 | 0.68609 | 0.81016 | 87.0893 | 790.0999 | -0.9 | 23.7906 | 1.0048 | 0.65102
2015-05-31 10:00 | 522.0433 | 145.34 | 376.7033 | 666.4873 | 21.7923 | -13.6023 | 55.5833 | 34.4167 | -15.3499 | 13.701 | 647.5223 | 109.005 | 0.68594 | 0.8099 | 89.5223 | 846.0496 | -0.8 | 25.639 | 0.99744 | 0.69199
2015-05-31 11:00 | 536.3467 | 149.83 | 386.5167 | 676.7853 | 21.7984 | 1.3962 | 55.1726 | 34.8274 | 1.5793 | 5.0079 | 674.2017 | 112.3725 | 0.68578 | 0.80964 | 91.9541 | 878.5283 | -0.4 | 27.054 | 0.99178 | 0.71447
2015-05-31 12:00 | 550.65 | 154.32 | 396.33 | 704.2815 | 21.8046 | 16.3947 | 55.7542 | 34.2458 | 18.4829 | 16.1927 | 676.3421 | 115.74 | 0.68563 | 0.80937 | 94.3849 | 886.467 | -0.2 | 27.5021 | 0.98999 | 0.71963
2015-05-31 13:00 | 517.9067 | 147.98 | 369.9267 | 684.1682 | 21.8108 | 31.3933 | 57.269 | 32.731 | 35.093 | 29.9531 | 592.787 | 110.985 | 0.68547 | 0.80911 | 88.7522 | 792.5242 | 0.3 | 25.0664 | 0.99973 | 0.6497
2015-05-31 14:00 | 485.1633 | 141.64 | 343.5233 | 678.267 | 21.8169 | 46.3918 | 59.5709 | 30.4291 | 51.2237 | 43.8709 | 488.9648 | 106.23 | 0.68531 | 0.80885 | 83.1221 | 678.3169 | 0.3 | 21.4974 | 1.014 | 0.56401
2015-05-31 15:00 | 452.42 | 135.3 | 317.12 | 685.7939 | 21.823 | 61.3903 | 62.4571 | 27.5429 | 66.8039 | 57.7472 | 365.9783 | 101.475 | 0.68516 | 0.80859 | 77.4946 | 544.9479 | -0.1 | 16.9296 | 1.0323 | 0.46128
2015-05-31 16:00 | 387.6667 | 115.7067 | 271.96 | 660.8552 | 21.8292 | 76.3888 | 65.6992 | 24.3008 | 81.8647 | 71.4908 | 209.7935 | 86.78 | 0.685 | 0.80833 | 66.3879 | 362.9614 | 0.1 | 11.4425 | 1.0542 | 0.31377
2015-05-31 17:00 | 322.9133 | 96.1133 | 226.8 | 634.7797 | 21.8353 | 91.3874 | 69.0662 | 20.9338 | 96.5027 | 85.0066 | 55.252 | 72.085 | 0.68484 | 0.80807 | 55.2863 | 182.6233 | 0.6 | 6.307 | 1.0748 | 0.16095
2015-05-31 18:00 | 258.16 | 76.52 | 181.64 | 598.6795 | 21.8414 | 106.3859 | 72.338 | 17.662 | 110.8413 | 98.1573 | 0 | 57.39 | 0.68469 | 0.80781 | 44.1897 | 101.5797 | 2.5 | 5.6744 | 1.0773 | 0.089734
2015-05-31 19:00 | 217.0367 | 65.9067 | 151.13 | 596.078 | 21.8475 | 121.3844 | 75.3129 | 14.6871 | 125.0007 | 110.7162 | 0 | 49.43 | 0.68453 | 0.80755 | 37.1421 | 86.5721 | 0.4 | 3.1054 | 1.0876 | 0.077206
2015-05-31 20:00 | 175.9133 | 55.2933 | 120.62 | 571.3573 | 21.8535 | 136.3829 | 77.8125 | 12.1875 | 139.0784 | 122.2809 | 0 | 41.47 | 0.68438 | 0.80729 | 30.0977 | 71.5677 | 0.2 | 2.4365 | 1.0903 | 0.063982
2015-05-31 21:00 | 134.79 | 44.68 | 90.11 | 503.3803 | 21.8596 | 151.3814 | 79.6879 | 10.3121 | 153.1384 | 132.1132 | 0 | 33.51 | 0.68422 | 0.80703 | 23.0565 | 56.5665 | -0.1 | 1.6677 | 1.0933 | 0.050714
2015-05-31 22:00 | 130.7 | 41.5567 | 89.1433 | 559.1419 | 21.8656 | 166.3799 | 80.8263 | 9.1737 | 167.2103 | 138.94 | 0 | 31.1675 | 0.68406 | 0.80677 | 22.3517 | 53.5192 | -1.1 | 0.57248 | 1.0977 | 0.048174
2015-05-31 23:00 | 126.61 | 38.4333 | 88.1767 | 573.6638 | 21.8717 | 181.3784 | 81.1581 | 8.8419 | -178.7055 | 141.1382 | 0 | 28.825 | 0.68391 | 0.80651 | 21.6473 | 50.4723 | -1.2 | 0.37726 | 1.0985 | 0.045464
2015-06-01 | 122.52 | 35.31 | 87.21 | 537.5297 | 21.8777 | -163.6231 | 80.6629 | 9.3371 | -164.6234 | 137.974 | 0 | 26.4825 | 0.68375 | 0.80625 | 20.9433 | 47.4258 | -1.3 | 0.18206 | 1.0993 | 0.04275
2015-06-01 01:00 | 159.4133 | 37.9633 | 121.45 | 658.4246 | 21.8837 | -148.6246 | 79.3706 | 10.6294 | -150.5568 | 130.4665 | 0 | 28.4725 | 0.68359 | 0.80599 | 27.2435 | 55.716 | -0.4 | 1.3411 | 1.0946 | 0.050011
2015-06-01 02:00 | 196.3067 | 40.6167 | 155.69 | 711.4343 | 21.8898 | -133.6261 | 77.3591 | 12.6409 | -136.5 | 120.2349 | 0 | 30.4625 | 0.68344 | 0.80573 | 33.5408 | 64.0033 | -0.4 | 1.6001 | 1.0936 | 0.057395
2015-06-01 03:00 | 233.2 | 43.27 | 189.93 | 722.0098 | 21.8958 | -118.6276 | 74.7484 | 15.2516 | -122.4173 | 108.4442 | 0 | 32.4525 | 0.68328 | 0.80547 | 39.8353 | 72.2878 | 0.8 | 3.059 | 1.0878 | 0.064478
2015-06-01 04:00 | 281.8867 | 54.44 | 227.4467 | 724.1177 | 21.9017 | -103.6292 | 71.6934 | 18.3066 | -108.2376 | 95.7543 | 0 | 40.83 | 0.68312 | 0.80521 | 48.141 | 88.971 | 0 | 2.7803 | 1.0889 | 0.07944
2015-06-01 05:00 | 330.5733 | 65.61 | 264.9633 | 719.0302 | 21.9077 | -88.6307 | 68.3768 | 21.6232 | -93.8577 | 82.5254 | 93.5359 | 49.2075 | 0.68297 | 0.80495 | 56.4428 | 199.1862 | -0.2 | 6.0246 | 1.0759 | 0.17573
2015-06-01 06:00 | 379.26 | 76.78 | 302.48 | 715.8362 | 21.9137 | -73.6322 | 65.004 | 24.996 | -79.1543 | 68.963 | 256.9638 | 57.585 | 0.68281 | 0.80469 | 64.7409 | 379.2897 | 0.7 | 12.5528 | 1.0498 | 0.3265
2015-06-01 07:00 | 391.7967 | 112.8867 | 278.91 | 590.1772 | 21.9196 | -58.6337 | 61.7977 | 28.2023 | -64.0056 | 55.1941 | 336.8718 | 84.665 | 0.68266 | 0.80443 | 66.8656 | 488.4024 | 0.1 | 15.3626 | 1.0385 | 0.41593
2015-06-01 08:00 | 404.3333 | 148.9933 | 255.34 | 495.618 | 21.9256 | -43.6353 | 58.9895 | 31.0105 | -48.323 | 41.3108 | 372.2785 | 111.745 | 0.6825 | 0.80417 | 68.9894 | 553.0129 | 0 | 17.2817 | 1.0309 | 0.46747
2015-06-01 09:00 | 416.87 | 185.1 | 231.77 | 423.3367 | 21.9315 | -28.6368 | 56.8054 | 33.1946 | -32.091 | 27.4125 | 375.8023 | 138.825 | 0.68234 | 0.80391 | 71.1122 | 585.7395 | 0 | 18.3044 | 1.0268 | 0.49317
2015-06-01 10:00 | 438.2567 | 170.8533 | 267.4033 | 471.3946 | 21.9374 | -13.6383 | 55.4406 | 34.5594 | -15.4017 | 13.7788 | 457.8291 | 128.14 | 0.68219 | 0.80365 | 74.7433 | 660.7124 | -0.1 | 20.5473 | 1.0178 | 0.55143
2015-06-01 11:00 | 459.6433 | 156.6067 | 303.0367 | 528.69 | 21.9433 | 1.3601 | 55.0274 | 34.9726 | 1.5397 | 5.1391 | 526.5647 | 117.455 | 0.68203 | 0.80339 | 78.3728 | 722.3925 | -0.1 | 22.4748 | 1.0101 | 0.59835
2015-06-01 12:00 | 481.03 | 142.36 | 338.67 | 599.5649 | 21.9492 | 16.3586 | 55.6075 | 34.3925 | 18.4559 | 16.1972 | 575.7666 | 106.77 | 0.68188 | 0.80312 | 82.0006 | 764.5372 | 0 | 23.8918 | 1.0044 | 0.6297
2015-06-01 13:00 | 474.6367 | 120.6267 | 354.01 | 652.1184 | 21.9551 | 31.3571 | 57.1214 | 32.8786 | 35.0774 | 29.9293 | 565.1533 | 90.47 | 0.68172 | 0.80286 | 80.8922 | 736.5155 | 0.2 | 23.2161 | 1.0071 | 0.60825
2015-06-01 14:00 | 468.2433 | 98.8933 | 369.35 | 726.0723 | 21.961 | 46.3555 | 59.423 | 30.577 | 51.217 | 43.8321 | 523.7684 | 74.17 | 0.68156 | 0.8026 | 79.7843 | 677.7227 | -0.1 | 21.0788 | 1.0157 | 0.56445
2015-06-01 15:00 | 461.85 | 77.16 | 384.69 | 827.8283 | 21.9669 | 61.354 | 62.3093 | 27.6907 | 66.803 | 57.6967 | 442.3927 | 57.87 | 0.68141 | 0.80234 | 78.6769 | 578.9395 | -0.1 | 17.9919 | 1.028 | 0.48804
2015-06-01 16:00 | 391.86 | 74.0433 | 317.8167 | 767.9103 | 21.9727 | 76.3524 | 65.5517 | 24.4483 | 81.8666 | 71.4293 | 244.5593 | 55.5325 | 0.68125 | 0.80208 | 66.7387 | 366.8305 | -0.3 | 11.1635 | 1.0553 | 0.31745
2015-06-01 17:00 | 321.87 | 70.9267 | 250.9433 | 697.6685 | 21.9786 | 91.3509 | 68.9189 | 21.0811 | 96.5046 | 84.9339 | 61.6075 | 53.195 | 0.68109 | 0.80182 | 54.8059 | 169.6084 | 0 | 5.3003 | 1.0788 | 0.15004
2015-06-01 18:00 | 251.88 | 67.81 | 184.07 | 601.8407 | 21.9844 | 106.3493 | 72.191 | 17.809 | 110.8407 | 98.0722 | 0 | 50.8575 | 0.68094 | 0.80156 | 42.8786 | 93.7361 | 0.1 | 3.0293 | 1.0879 | 0.083619
2015-06-01 19:00 | 212.7633 | 61.1833 | 151.58 | 592.0713 | 21.9902 | 121.3477 | 75.1662 | 14.8338 | 124.9957 | 110.6169 | 0 | 45.8875 | 0.68078 | 0.8013 | 36.2113 | 82.0988 | -0.3 | 2.2656 | 1.0909 | 0.073443
2015-06-01 20:00 | 173.6467 | 54.5567 | 119.09 | 557.5283 | 21.996 | 136.3462 | 77.6664 | 12.3336 | 139.0672 | 122.1652 | 0 | 40.9175 | 0.68063 | 0.80104 | 29.5471 | 70.4646 | -0.2 | 2.002 | 1.092 | 0.063096
2015-06-01 21:00 | 134.53 | 47.93 | 86.6 | 477.131 | 22.0018 | 151.3446 | 79.5428 | 10.4572 | 153.1198 | 131.9802 | 0 | 35.9475 | 0.68047 | 0.80078 | 22.8859 | 58.8334 | -0.2 | 1.6385 | 1.0934 | 0.052752
2015-06-01 22:00 | 119.1133 | 44.91 | 74.2033 | 458.3198 | 22.0076 | 166.343 | 80.6826 | 9.3174 | 167.1834 | 138.7949 | 0 | 33.6825 | 0.68031 | 0.80052 | 20.2586 | 53.9411 | -0.4 | 1.2857 | 1.0949 | 0.048427
2015-06-01 23:00 | 103.6967 | 41.89 | 61.8067 | 395.8201 | 22.0134 | 181.3415 | 81.0166 | 8.9834 | -178.7409 | 140.9978 | 0 | 31.4175 | 0.68016 | 0.80026 | 17.6325 | 49.05 | -0.1 | 1.4328 | 1.0943 | 0.044013
2015-06-02 | 88.28 | 38.87 | 49.41 | 300.1188 | 22.0192 | -163.6601 | 80.524 | 9.476 | -164.6674 | 137.8582 | 0 | 29.1525 | 0.68 | 0.8 | 15.0076 | 44.1601 | -0.2 | 1.18 | 1.0953 | 0.039661
2015-06-02 01:00 | 109.2767 | 50.66 | 58.6167 | 313.8119 | 22.0249 | -148.6617 | 79.2345 | 10.7655 | -150.6087 | 130.3822 | 0 | 37.995 | 0.67984 | 0.79974 | 18.5728 | 56.5678 | 0.1 | 1.8677 | 1.0925 | 0.050678
2015-06-02 02:00 | 130.2733 | 62.45 | 67.8233 | 306.7443 | 22.0307 | -133.6633 | 77.2259 | 12.7741 | -136.559 | 120.1781 | 0 | 46.8375 | 0.67969 | 0.79948 | 22.1363 | 68.9738 | 0.8 | 2.9554 | 1.0882 | 0.061546
2015-06-02 03:00 | 151.27 | 74.24 | 77.03 | 290.3991 | 22.0364 | -118.6648 | 74.6179 | 15.3821 | -122.4823 | 108.4092 | 0 | 55.68 | 0.67953 | 0.79922 | 25.6982 | 81.3782 | 1.3 | 3.8431 | 1.0846 | 0.072377
2015-06-02 04:00 | 182.84 | 96.1433 | 86.6967 | 274.155 | 22.0421 | -103.6664 | 71.5648 | 18.4352 | -108.3072 | 95.7364 | 0 | 72.1075 | 0.67938 | 0.79896 | 31.0542 | 103.1617 | 2.5 | 5.7238 | 1.0771 | 0.091115
2015-06-02 05:00 | 214.41 | 118.0467 | 96.3633 | 260.0412 | 22.0478 | -88.668 | 68.2493 | 21.7507 | -93.9304 | 82.5218 | 33.8442 | 88.535 | 0.67922 | 0.7987 | 36.4078 | 158.787 | 2.4 | 7.3621 | 1.0706 | 0.13939
2015-06-02 06:00 | 245.98 | 139.95 | 106.03 | 249.7344 | 22.0535 | -73.6696 | 64.8765 | 25.1235 | -79.2284 | 68.9717 | 89.6119 | 104.9625 | 0.67906 | 0.79844 | 41.7589 | 236.3334 | 2.9 | 10.2854 | 1.0589 | 0.2052
2015-06-02 07:00 | 230.1933 | 155.63 | 74.5633 | 157.1196 | 22.0592 | -58.6712 | 61.669 | 28.331 | -64.0788 | 55.2144 | 89.6379 | 116.7225 | 0.67891 | 0.79818 | 39.0699 | 245.4304 | 2.5 | 10.1697 | 1.0593 | 0.21319
2015-06-02 08:00 | 214.4067 | 171.31 | 43.0967 | 83.3351 | 22.0649 | -43.6728 | 58.8588 | 31.1412 | -48.3926 | 41.3432 | 62.5652 | 128.4825 | 0.67875 | 0.79792 | 36.3821 | 227.4299 | 1.8 | 8.9072 | 1.0644 | 0.1985
2015-06-02 09:00 | 198.62 | 186.99 | 11.63 | 21.1674 | 22.0706 | -28.6744 | 56.672 | 33.328 | -32.1539 | 27.4605 | 18.7824 | 140.2425 | 0.67859 | 0.79766 | 33.6956 | 192.7205 | 1 | 7.0225 | 1.0719 | 0.16939
2015-06-02 10:00 | 211.5567 | 182.1367 | 29.42 | 51.685 | 22.0762 | -13.676 | 55.3044 | 34.6956 | -15.455 | 13.857 | 50.1808 | 136.6025 | 0.67844 | 0.7974 | 35.882 | 222.6653 | 0.8 | 7.7583 | 1.069 | 0.19518
2015-06-02 11:00 | 224.4933 | 177.2833 | 47.21 | 82.0805 | 22.0819 | 1.3224 | 54.8887 | 35.1113 | 1.498 | 5.2647 | 81.7343 | 132.9625 | 0.67828 | 0.79714 | 38.0674 | 252.7642 | 1.4 | 9.2989 | 1.0628 | 0.22028
2015-06-02 12:00 | 237.43 | 172.43 | 65 | 114.6622 | 22.0875 | 16.3208 | 55.4669 | 34.5331 | 18.4264 | 16.1998 | 110.1095 | 129.3225 | 0.67813 | 0.79688 | 40.2518 | 279.6838 | 1.1 | 9.8401 | 1.0606 | 0.24325
2015-06-02 13:00 | 282.1633 | 175.0933 | 107.07 | 196.4822 | 22.0931 | 31.3192 | 56.9798 | 33.0202 | 35.0589 | 29.9041 | 170.3227 | 131.32 | 0.67797 | 0.79661 | 47.8245 | 349.4672 | 1.9 | 12.8209 | 1.0487 | 0.30052
2015-06-02 14:00 | 326.8967 | 177.7567 | 149.14 | 291.9581 | 22.0988 | 46.3175 | 59.2811 | 30.7189 | 51.2072 | 43.7924 | 210.7506 | 133.3175 | 0.67781 | 0.79635 | 55.3937 | 399.4617 | 2.5 | 14.9832 | 1.0401 | 0.34068
2015-06-02 15:00 | 371.63 | 180.42 | 191.21 | 409.5406 | 22.1044 | 61.3159 | 62.1675 | 27.8325 | 66.799 | 57.6457 | 219.1673 | 135.315 | 0.67766 | 0.79609 | 62.9593 | 417.4416 | 2.1 | 15.1451 | 1.0394 | 0.3558
2015-06-02 16:00 | 317.79 | 138.7233 | 179.0667 | 430.3227 | 22.1099 | 76.3143 | 65.41 | 24.59 | 81.8652 | 71.3678 | 137.4844 | 104.0425 | 0.6775 | 0.79583 | 53.8257 | 295.3525 | 1.2 | 10.4298 | 1.0583 | 0.2563
2015-06-02 17:00 | 263.95 | 97.0267 | 166.9233 | 461.1262 | 22.1155 | 91.3127 | 68.7775 | 21.2225 | 96.5032 | 84.8616 | 41.2992 | 72.77 | 0.67734 | 0.79557 | 44.6962 | 158.7655 | 1.7 | 6.6614 | 1.0734 | 0.13974
2015-06-02 18:00 | 210.11 | 55.33 | 154.78 | 502.2233 | 22.1211 | 106.3111 | 72.0498 | 17.9502 | 110.8371 | 97.9881 | 0 | 41.4975 | 0.67719 | 0.79531 | 35.571 | 77.0685 | 1.4 | 3.8084 | 1.0848 | 0.068553
2015-06-02 19:00 | 178.1333 | 49.9 | 128.2333 | 496.2778 | 22.1266 | 121.3094 | 75.0254 | 14.9746 | 124.9878 | 110.5193 | 0 | 37.425 | 0.67703 | 0.79505 | 30.1505 | 67.5755 | 1.4 | 3.5117 | 1.086 | 0.060175
2015-06-02 20:00 | 146.1567 | 44.47 | 101.6867 | 470.7911 | 22.1322 | 136.3078 | 77.5263 | 12.4737 | 139.0535 | 122.0522 | 0 | 33.3525 | 0.67688 | 0.79479 | 24.7324 | 58.0849 | 1.7 | 3.5152 | 1.0859 | 0.051723
2015-06-02 21:00 | 114.18 | 39.04 | 75.14 | 408.6225 | 22.1377 | 151.3062 | 79.4038 | 10.5962 | 153.099 | 131.8513 | 0 | 29.28 | 0.67672 | 0.79453 | 19.3169 | 48.5969 | 1.7 | 3.2187 | 1.0871 | 0.043321
2015-06-02 22:00 | 93.75 | 41.1267 | 52.6233 | 320.3509 | 22.1432 | 166.3045 | 80.5453 | 9.4547 | 167.1547 | 138.6553 | 0 | 30.845 | 0.67656 | 0.79427 | 15.8569 | 46.7019 | 1.6 | 3.0594 | 1.0878 | 0.041656
2015-06-02 23:00 | 73.32 | 43.2133 | 30.1067 | 189.9741 | 22.1488 | 181.3029 | 80.8815 | 9.1185 | -178.7778 | 140.8638 | 0 | 32.41 | 0.67641 | 0.79401 | 12.3985 | 44.8085 | 1.5 | 2.9003 | 1.0884 | 0.039991
2015-06-03 | 52.89 | 45.3 | 7.59 | 45.4722 | 22.1542 | -163.6987 | 80.3915 | 9.6085 | -164.7124 | 137.7488 | 0 | 33.975 | 0.67625 | 0.79375 | 8.9417 | 42.9167 | 1.5 | 2.8411 | 1.0886 | 0.038311
2015-06-03 01:00 | 76.5267 | 57.0633 | 19.4633 | 102.9751 | 22.1597 | -148.7004 | 79.105 | 10.895 | -150.6613 | 130.3034 | 0 | 42.7975 | 0.67609 | 0.79349 | 12.9348 | 55.7323 | 1.1 | 2.8416 | 1.0886 | 0.049751
2015-06-03 02:00 | 100.1633 | 68.8267 | 31.3367 | 140.3583 | 22.1652 | -133.702 | 77.0993 | 12.9007 | -136.6184 | 120.1261 | 0 | 51.62 | 0.67594 | 0.79323 | 16.926 | 68.546 | 1.1 | 3.2421 | 1.087 | 0.0611
2015-06-03 03:00 | 123.8 | 80.59 | 43.21 | 161.6281 | 22.1707 | -118.7037 | 74.4938 | 15.5062 | -122.5474 | 108.3783 | 0 | 60.4425 | 0.67578 | 0.79297 | 20.9154 | 81.3579 | 1.2 | 3.7424 | 1.085 | 0.072386
2015-06-03 04:00 | 140.8833 | 109.2833 | 31.6 | 99.2923 | 22.1761 | -103.7053 | 71.4427 | 18.5573 | -108.3768 | 95.7222 | 0 | 81.9625 | 0.67563 | 0.79271 | 23.7961 | 105.7586 | 1.1 | 4.405 | 1.0824 | 0.093866
2015-06-03 05:00 | 157.9667 | 137.9767 | 19.99 | 53.6602 | 22.1816 | -88.707 | 68.1283 | 21.8717 | -94.0031 | 82.5212 | 6.9843 | 103.4825 | 0.67547 | 0.79245 | 26.6754 | 137.1422 | 1.3 | 5.5857 | 1.0777 | 0.12119
2015-06-03 06:00 | 175.05 | 166.67 | 8.38 | 19.6492 | 22.187 | -73.7087 | 64.7555 | 25.2445 | -79.3024 | 68.9831 | 7.047 | 125.0025 | 0.67531 | 0.79219 | 29.5534 | 161.6029 | 2.2 | 7.2501 | 1.071 | 0.14192
2015-06-03 07:00 | 273.09 | 180.2867 | 92.8033 | 194.7859 | 22.1924 | -58.7103 | 61.547 | 28.453 | -64.1521 | 55.2369 | 111.0638 | 135.215 | 0.67516 | 0.79193 | 46.0946 | 292.3734 | 2 | 11.1367 | 1.0555 | 0.25304
2015-06-03 08:00 | 371.13 | 193.9033 | 177.2267 | 341.4764 | 22.1978 | -43.712 | 58.7347 | 31.2653 | -48.4626 | 41.3775 | 256.2339 | 145.4275 | 0.675 | 0.79167 | 62.6282 | 464.2896 | 1.5 | 16.009 | 1.036 | 0.39441
2015-06-03 09:00 | 469.17 | 207.52 | 261.65 | 474.6239 | 22.2032 | -28.7136 | 56.5452 | 33.4548 | -32.2177 | 27.5098 | 420.9589 | 155.64 | 0.67484 | 0.79141 | 79.1541 | 655.753 | 1.3 | 21.7923 | 1.0128 | 0.54462
2015-06-03 10:00 | 465.3167 | 200.1567 | 265.16 | 464.3155 | 22.2086 | -13.7153 | 55.1746 | 34.8254 | -15.5097 | 13.9354 | 450.6497 | 150.1175 | 0.67469 | 0.79115 | 78.4858 | 679.253 | 1 | 22.2267 | 1.0111 | 0.56317
2015-06-03 11:00 | 461.4633 | 192.7933 | 268.67 | 465.5882 | 22.214 | 1.283 | 54.7563 | 35.2437 | 1.4544 | 5.3846 | 463.5337 | 144.595 | 0.67453 | 0.79089 | 77.8179 | 685.9465 | 1.3 | 22.7358 | 1.0091 | 0.56757
2015-06-03 12:00 | 457.61 | 185.43 | 272.18 | 478.5066 | 22.2194 | 16.2813 | 55.3326 | 34.6674 | 18.3945 | 16.2005 | 459.5057 | 139.0725 | 0.67438 | 0.79063 | 77.1502 | 675.7284 | 2.3 | 23.4165 | 1.0063 | 0.55761
2015-06-03 13:00 | 433.6367 | 178.77 | 254.8667 | 466.0079 | 22.2247 | 31.2797 | 56.8444 | 33.1556 | 35.0376 | 29.8777 | 404.0712 | 134.0775 | 0.67422 | 0.79036 | 73.0915 | 611.2402 | 1.6 | 20.7013 | 1.0172 | 0.50984
2015-06-03 14:00 | 409.6633 | 172.11 | 237.5533 | 463.1896 | 22.2301 | 46.278 | 59.1452 | 30.8548 | 51.1943 | 43.7518 | 334.5814 | 129.0825 | 0.67406 | 0.7901 | 69.0347 | 532.6986 | 1.5 | 18.1468 | 1.0274 | 0.44879
2015-06-03 15:00 | 385.69 | 165.45 | 220.24 | 469.6091 | 22.2354 | 61.2763 | 62.0315 | 27.9685 | 66.7917 | 57.5942 | 251.6696 | 124.0875 | 0.67391 | 0.78984 | 64.9797 | 440.7368 | 1.6 | 15.373 | 1.0385 | 0.37532
2015-06-03 16:00 | 322.8667 | 148.22 | 174.6467 | 417.5397 | 22.2407 | 76.2746 | 65.2742 | 24.7258 | 81.8607 | 71.3063 | 133.8253 | 111.165 | 0.67375 | 0.78958 | 54.3829 | 299.3731 | 1.7 | 11.0554 | 1.0558 | 0.25918
2015-06-03 17:00 | 260.0433 | 130.99 | 129.0533 | 354.3525 | 22.246 | 91.2729 | 68.642 | 21.358 | 96.4988 | 84.7898 | 32.1789 | 98.2425 | 0.67359 | 0.78932 | 43.7909 | 174.2123 | 1.3 | 6.7441 | 1.073 | 0.15329
2015-06-03 18:00 | 197.22 | 113.76 | 83.46 | 268.8495 | 22.2513 | 106.2712 | 71.9146 | 18.0854 | 110.8305 | 97.905 | 0 | 85.32 | 0.67344 | 0.78906 | 33.2038 | 118.5238 | 1 | 4.7039 | 1.0812 | 0.10508
2015-06-03 19:00 | 167.6067 | 96.6767 | 70.93 | 272.1157 | 22.2566 | 121.2695 | 74.8907 | 15.1093 | 124.9772 | 110.4235 | 0 | 72.5075 | 0.67328 | 0.7888 | 28.2116 | 100.7191 | 0.6 | 3.7475 | 1.085 | 0.089611
2015-06-03 20:00 | 137.9933 | 79.5933 | 58.4 | 267.5547 | 22.2619 | 136.2678 | 77.3924 | 12.6076 | 139.0373 | 121.9421 | 0 | 59.695 | 0.67313 | 0.78854 | 23.2217 | 82.9167 | 1 | 3.5911 | 1.0856 | 0.073814
2015-06-03 21:00 | 108.38 | 62.51 | 45.87 | 246.3973 | 22.2672 | 151.2661 | 79.2711 | 10.7289 | 153.0761 | 131.7265 | 0 | 46.8825 | 0.67297 | 0.78828 | 18.2341 | 65.1166 | 1.2 | 3.2349 | 1.0871 | 0.058044
2015-06-03 22:00 | 104.34 | 62.3733 | 41.9667 | 252.018 | 22.2724 | 166.2644 | 80.4143 | 9.5857 | 167.1243 | 138.5212 | 0 | 46.78 | 0.67281 | 0.78802 | 17.5503 | 64.3303 | 0.6 | 2.6103 | 1.0896 | 0.057475
2015-06-03 23:00 | 100.3 | 62.2367 | 38.0633 | 236.8665 | 22.2776 | 181.2627 | 80.7527 | 9.2473 | -178.8161 | 140.7362 | 0 | 46.6775 | 0.67266 | 0.78776 | 16.8669 | 63.5444 | 0.1 | 2.0858 | 1.0917 | 0.056882
2015-06-04 | 96.26 | 62.1 | 34.16 | 202.0314 | 22.2829 | -163.739 | 80.2655 | 9.7345 | -164.7585 | 137.6456 | 0 | 46.575 | 0.6725 | 0.7875 | 16.1837 | 62.7587 | -0.2 | 1.7612 | 1.093 | 0.056246
2015-06-04 01:00 | 117.7333 | 85.7 | 32.0333 | 167.6105 | 22.2881 | -148.7407 | 78.982 | 11.018 | -150.7146 | 130.2302 | 0 | 64.275 | 0.67234 | 0.78724 | 19.7893 | 84.0643 | -0.1 | 2.527 | 1.0899 | 0.075129
2015-06-04 02:00 | 139.2067 | 109.3 | 29.9067 | 132.7394 | 22.2933 | -133.7424 | 76.9793 | 13.0207 | -136.6782 | 120.0789 | 0 | 81.975 | 0.67219 | 0.78698 | 23.3932 | 105.3682 | -0.2 | 3.0928 | 1.0876 | 0.093973
2015-06-04 03:00 | 160.68 | 132.9 | 27.78 | 103.1501 | 22.2985 | -118.7441 | 74.3764 | 15.6236 | -122.6127 | 108.3516 | 0 | 99.675 | 0.67203 | 0.78672 | 26.9955 | 126.6705 | -0.2 | 3.7585 | 1.085 | 0.1127
2015-06-04 04:00 | 189.74 | 155.4167 | 34.3233 | 107.2063 | 22.3037 | -103.7458 | 71.3273 | 18.6727 | -108.4464 | 95.7116 | 0 | 116.5625 | 0.67188 | 0.78646 | 31.8704 | 148.4329 | -0.2 | 4.4385 | 1.0822 | 0.13173
2015-06-04 05:00 | 218.8 | 177.9333 | 40.8667 | 109.158 | 22.3089 | -88.7475 | 68.014 | 21.986 | -94.0757 | 82.5238 | 14.203 | 133.45 | 0.67172 | 0.7862 | 36.743 | 184.3961 | -0.1 | 5.6624 | 1.0774 | 0.1629
2015-06-04 06:00 | 247.86 | 200.45 | 47.41 | 110.6973 | 22.314 | -73.7493 | 64.6412 | 25.3588 | -79.3764 | 68.9971 | 39.6756 | 150.3375 | 0.67156 | 0.78594 | 41.6134 | 231.6265 | -0.3 | 6.9383 | 1.0722 | 0.20366
2015-06-04 07:00 | 293.9167 | 220.6267 | 73.29 | 153.2598 | 22.3192 | -58.751 | 61.4316 | 28.5684 | -64.2255 | 55.2617 | 87.3318 | 165.47 | 0.67141 | 0.78568 | 49.3344 | 302.1362 | -0.2 | 9.2418 | 1.063 | 0.26337
2015-06-04 08:00 | 339.9733 | 240.8033 | 99.17 | 190.4359 | 22.3243 | -43.7527 | 58.6172 | 31.3828 | -48.533 | 41.4136 | 142.8182 | 180.6025 | 0.67125 | 0.78542 | 57.0518 | 380.4724 | 0 | 11.8898 | 1.0524 | 0.32835
2015-06-04 09:00 | 386.03 | 260.98 | 125.05 | 226.1187 | 22.3294 | -28.7544 | 56.425 | 33.575 | -32.2823 | 27.5604 | 200.4596 | 195.735 | 0.67109 | 0.78516 | 64.7656 | 460.9602 | -0.2 | 14.205 | 1.0432 | 0.39431
2015-06-04 10:00 | 381.8867 | 266.2633 | 115.6233 | 201.8419 | 22.3346 | -13.7562 | 55.0514 | 34.9486 | -15.5657 | 14.0138 | 195.8346 | 199.6975 | 0.67094 | 0.7849 | 64.0555 | 459.5877 | -0.4 | 13.9621 | 1.0442 | 0.3935
2015-06-04 11:00 | 377.7433 | 271.5467 | 106.1967 | 183.4621 | 22.3397 | 1.2421 | 54.6304 | 35.3696 | 1.4089 | 5.4987 | 182.6179 | 203.66 | 0.67078 | 0.78464 | 63.3458 | 449.6236 | -0.4 | 13.6507 | 1.0454 | 0.38543
2015-06-04 12:00 | 373.6 | 276.83 | 96.77 | 169.5796 | 22.3448 | 16.2404 | 55.2047 | 34.7953 | 18.3602 | 16.1992 | 162.8469 | 207.6225 | 0.67063 | 0.78438 | 62.6364 | 433.1058 | 0.7 | 14.2346 | 1.0431 | 0.37044
2015-06-04 13:00 | 357.3133 | 253.93 | 103.3833 | 188.3803 | 22.3498 | 31.2386 | 56.7152 | 33.2848 | 35.0136 | 29.8499 | 163.3883 | 190.4475 | 0.67047 | 0.78411 | 59.8919 | 413.7276 | 0.6 | 13.529 | 1.0459 | 0.35482
2015-06-04 14:00 | 341.0267 | 231.03 | 109.9967 | 213.6656 | 22.3549 | 46.2369 | 59.0154 | 30.9846 | 51.1784 | 43.7103 | 154.4466 | 173.2725 | 0.67031 | 0.78385 | 57.1486 | 384.8677 | 1.1 | 13.1271 | 1.0475 | 0.33058
2015-06-04 15:00 | 324.74 | 208.13 | 116.61 | 247.5861 | 22.36 | 61.2351 | 61.9016 | 28.0984 | 66.7812 | 57.5422 | 132.874 | 156.0975 | 0.67016 | 0.78359 | 54.4066 | 343.3782 | 0.8 | 11.5306 | 1.0539 | 0.29674
2015-06-04 16:00 | 280.6967 | 187.9167 | 92.78 | 220.7298 | 22.365 | 76.2334 | 65.1444 | 24.8556 | 81.8529 | 71.2447 | 70.9704 | 140.9375 | 0.67 | 0.78333 | 47.0167 | 258.9246 | 0.8 | 8.8914 | 1.0644 | 0.226
2015-06-04 17:00 | 236.6533 | 167.7033 | 68.95 | 188.2335 | 22.3701 | 91.2316 | 68.5124 | 21.4876 | 96.4912 | 84.7185 | 17.3268 | 125.7775 | 0.66984 | 0.78307 | 39.6302 | 182.7345 | 1 | 6.7105 | 1.0732 | 0.1608
2015-06-04 18:00 | 192.61 | 147.49 | 45.12 | 144.3484 | 22.3751 | 106.2299 | 71.7854 | 18.2146 | 110.821 | 97.8231 | 0 | 110.6175 | 0.66969 | 0.78281 | 32.2471 | 142.8646 | 0.9 | 5.3645 | 1.0785 | 0.12635
2015-06-04 19:00 | 163.4733 | 121.32 | 42.1533 | 160.3834 | 22.3801 | 121.2281 | 74.762 | 15.238 | 124.9639 | 110.3297 | 0 | 90.99 | 0.66953 | 0.78255 | 27.3626 | 118.3526 | 0.7 | 4.3985 | 1.0824 | 0.10505
2015-06-04 20:00 | 134.3367 | 95.15 | 39.1867 | 177.7585 | 22.3851 | 136.2264 | 77.2646 | 12.7354 | 139.0186 | 121.8349 | 0 | 71.3625 | 0.66938 | 0.78229 | 22.4804 | 93.8429 | 0.4 | 3.3326 | 1.0867 | 0.083621
2015-06-04 21:00 | 105.2 | 68.98 | 36.22 | 192.3214 | 22.3901 | 151.2246 | 79.1446 | 10.8554 | 153.051 | 131.606 | 0 | 51.735 | 0.66922 | 0.78203 | 17.6005 | 69.3355 | 0.3 | 2.4667 | 1.0901 | 0.06198
2015-06-04 22:00 | 93.7167 | 67.5067 | 26.21 | 155.3955 | 22.3951 | 166.2228 | 80.2897 | 9.7103 | 167.0921 | 138.3928 | 0 | 50.63 | 0.66906 | 0.78177 | 15.6756 | 66.3056 | 0.2 | 2.272 | 1.0909 | 0.059313
2015-06-04 23:00 | 82.2333 | 66.0333 | 16.2 | 99.5084 | 22.4001 | 181.2211 | 80.6305 | 9.3695 | -178.8558 | 140.6151 | 0 | 49.525 | 0.66891 | 0.78151 | 13.7516 | 63.2766 | 0 | 1.9774 | 1.0921 | 0.056665
2015-06-05 | 70.75 | 64.56 | 6.19 | 36.1699 | 22.405 | -163.7807 | 80.1461 | 9.8539 | -164.8055 | 137.5488 | 0 | 48.42 | 0.66875 | 0.78125 | 11.8285 | 60.2485 | -0.1 | 1.7828 | 1.0929 | 0.053992
2015-06-05 01:00 | 94.8967 | 73.3333 | 21.5633 | 111.6627 | 22.41 | -148.7825 | 78.8656 | 11.1344 | -150.7685 | 130.1626 | 0 | 55 | 0.66859 | 0.78099 | 15.8618 | 70.8618 | -0.3 | 1.9144 | 1.0923 | 0.063472
2015-06-05 02:00 | 119.0433 | 82.1067 | 36.9367 | 162.5506 | 22.4149 | -133.7842 | 76.8658 | 13.1342 | -136.7382 | 120.0365 | 0 | 61.58 | 0.66844 | 0.78073 | 19.8933 | 81.4733 | -0.1 | 2.446 | 1.0902 | 0.072835
2015-06-05 03:00 | 143.19 | 90.88 | 52.31 | 192.8992 | 22.4198 | -118.786 | 74.2656 | 15.7344 | -122.6779 | 108.3289 | 0 | 68.16 | 0.66828 | 0.78047 | 23.9228 | 92.0828 | 0 | 2.8776 | 1.0885 | 0.08219
2015-06-05 04:00 | 190.3633 | 119.79 | 70.5733 | 219.1991 | 22.4247 | -103.7878 | 71.2185 | 18.7815 | -108.5158 | 95.7044 | 0 | 89.8425 | 0.66813 | 0.78021 | 31.7966 | 121.6391 | 0.2 | 4.0012 | 1.084 | 0.10812
2015-06-05 05:00 | 237.5367 | 148.7 | 88.8367 | 236.1904 | 22.4296 | -88.7896 | 67.9063 | 22.0937 | -94.1481 | 82.5294 | 30.7091 | 111.525 | 0.66797 | 0.77995 | 39.6668 | 181.9008 | 0.4 | 6.0844 | 1.0757 | 0.16044
2015-06-05 06:00 | 284.71 | 177.61 | 107.1 | 249.08 | 22.4345 | -73.7913 | 64.5336 | 25.4664 | -79.4503 | 69.0137 | 89.2067 | 133.2075 | 0.66781 | 0.77969 | 47.5332 | 269.9474 | 0.3 | 8.7359 | 1.0651 | 0.23576
2015-06-05 07:00 | 334.15 | 195.54 | 138.61 | 288.847 | 22.4394 | -58.7931 | 61.3229 | 28.6771 | -64.2989 | 55.2887 | 164.4817 | 146.655 | 0.66766 | 0.77943 | 55.7743 | 366.911 | 0.6 | 12.066 | 1.0517 | 0.31643
2015-06-05 08:00 | 383.59 | 213.47 | 170.12 | 325.6492 | 22.4443 | -43.7949 | 58.5064 | 31.4936 | -48.6037 | 41.4514 | 244.0797 | 160.1025 | 0.6675 | 0.77917 | 64.0116 | 468.1938 | 1.7 | 16.3311 | 1.0347 | 0.39723
2015-06-05 09:00 | 433.03 | 231.4 | 201.63 | 363.5078 | 22.4491 | -28.7967 | 56.3114 | 33.6886 | -32.3476 | 27.6121 | 322.1065 | 173.55 | 0.66734 | 0.77891 | 72.245 | 567.9015 | 1.3 | 19.0469 | 1.0238 | 0.47677
2015-06-05 10:00 | 429.5167 | 234.5067 | 195.01 | 339.4383 | 22.454 | -13.7985 | 54.9348 | 35.0652 | -15.6229 | 14.0918 | 329.2235 | 175.88 | 0.66719 | 0.77865 | 71.642 | 576.7456 | 1.4 | 19.4233 | 1.0223 | 0.48348
2015-06-05 11:00 | 426.0033 | 237.6133 | 188.39 | 324.505 | 22.4588 | 1.1997 | 54.5111 | 35.4889 | 1.3617 | 5.607 | 322.9524 | 178.21 | 0.66703 | 0.77839 | 71.0394 | 572.2018 | 2 | 19.8813 | 1.0205 | 0.47881
2015-06-05 12:00 | 422.49 | 240.72 | 181.77 | 317.5648 | 22.4636 | 16.1979 | 55.0831 | 34.9169 | 18.3236 | 16.1959 | 304.9619 | 180.54 | 0.66688 | 0.77812 | 70.437 | 555.9389 | 1.6 | 18.9731 | 1.0241 | 0.46686
2015-06-05 13:00 | 392.5367 | 235.02 | 157.5167 | 286.0851 | 22.4685 | 31.1961 | 56.5922 | 33.4078 | 34.9869 | 29.8208 | 248.2032 | 176.265 | 0.66672 | 0.77786 | 65.4279 | 489.8961 | 1.1 | 16.4093 | 1.0344 | 0.41552
2015-06-05 14:00 | 362.5833 | 229.32 | 133.2633 | 257.934 | 22.4733 | 46.1943 | 58.8917 | 31.1083 | 51.1596 | 43.668 | 186.5773 | 171.99 | 0.66656 | 0.7776 | 60.4211 | 418.9884 | 1.9 | 14.9934 | 1.04 | 0.35732
2015-06-05 15:00 | 332.63 | 223.62 | 109.01 | 230.5168 | 22.478 | 61.1925 | 61.7777 | 28.2223 | 66.7677 | 57.4899 | 123.8909 | 167.715 | 0.66641 | 0.77734 | 55.4167 | 347.0226 | 1.9 | 12.7445 | 1.049 | 0.29851
2015-06-05 16:00 | 284.4967 | 193.0933 | 91.4033 | 216.4453 | 22.4828 | 76.1907 | 65.0206 | 24.9794 | 81.8421 | 71.1833 | 69.8127 | 144.82 | 0.66625 | 0.77708 | 47.3865 | 262.0191 | 1.8 | 9.9881 | 1.06 | 0.22776
2015-06-05 17:00 | 236.3633 | 162.5667 | 73.7967 | 200.3674 | 22.4876 | 91.1889 | 68.3888 | 21.6112 | 96.4807 | 84.6478 | 18.6899 | 121.925 | 0.66609 | 0.77682 | 39.36 | 179.9749 | 2.4 | 8.0242 | 1.0679 | 0.1576
2015-06-05 18:00 | 188.23 | 132.04 | 56.19 | 178.5972 | 22.4923 | 106.1871 | 71.6622 | 18.3378 | 110.8086 | 97.7425 | 0 | 99.03 | 0.66594 | 0.77656 | 31.3374 | 130.3674 | 1.6 | 5.674 | 1.0773 | 0.11517
2015-06-05 19:00 | 157.1467 | 111.9567 | 45.19 | 170.5983 | 22.4971 | 121.1853 | 74.6395 | 15.3605 | 124.9479 | 110.2379 | 0 | 83.9675 | 0.66578 | 0.7763 | 26.1563 | 110.1238 | 1.1 | 4.5414 | 1.0818 | 0.097691
2015-06-05 20:00 | 126.0633 | 91.8733 | 34.19 | 153.6508 | 22.5018 | 136.1834 | 77.1431 | 12.8569 | 138.9976 | 121.7308 | 0 | 68.905 | 0.66563 | 0.77604 | 20.9777 | 89.8827 | 0.6 | 3.4088 | 1.0864 | 0.080069
2015-06-05 21:00 | 94.98 | 71.79 | 23.19 | 121.8033 | 22.5065 | 151.1816 | 79.0245 | 10.9755 | 153.0239 | 131.4898 | 0 | 53.8425 | 0.66547 | 0.77578 | 15.8016 | 69.6441 | 0.4 | 2.5764 | 1.0897 | 0.06223
2015-06-05 22:00 | 86.6333 | 66.9433 | 19.69 | 115.3495 | 22.5112 | 166.1798 | 80.1716 | 9.8284 | 167.0582 | 138.27 | 0 | 50.2075 | 0.66531 | 0.77552 | 14.4096 | 64.6171 | 0.2 | 2.2193 | 1.0911 | 0.057814
2015-06-05 23:00 | 78.2867 | 62.0967 | 16.19 | 98.2449 | 22.5159 | 181.178 | 80.5148 | 9.4852 | -178.8967 | 140.5006 | 0 | 46.5725 | 0.66516 | 0.77526 | 13.0182 | 59.5907 | 0.3 | 2.1622 | 1.0914 | 0.053328
2015-06-06 | 69.94 | 57.25 | 12.69 | 73.3202 | 22.5206 | -163.8238 | 80.0333 | 9.9667 | -164.8534 | 137.4584 | 0 | 42.9375 | 0.665 | 0.775 | 11.6275 | 54.565 | 1.2 | 2.9052 | 1.0884 | 0.048698
2015-06-06 01:00 | 87.3033 | 70.8833 | 16.42 | 84.2092 | 22.5253 | -148.8257 | 78.7558 | 11.2442 | -150.8229 | 130.1006 | 0 | 53.1625 | 0.66484 | 0.77474 | 14.5108 | 67.6733 | 1 | 3.1148 | 1.0875 | 0.06035
2015-06-06 02:00 | 104.6667 | 84.5167 | 20.15 | 87.9736 | 22.53 | -133.8275 | 76.7591 | 13.2409 | -136.7985 | 119.9989 | 0 | 63.3875 | 0.66469 | 0.77448 | 17.3927 | 80.7802 | 1.1 | 3.6244 | 1.0855 | 0.071903
2015-06-06 03:00 | 122.03 | 98.15 | 23.88 | 87.4961 | 22.5346 | -118.8293 | 74.1615 | 15.8385 | -122.7431 | 108.3104 | 0 | 73.6125 | 0.66453 | 0.77422 | 20.2732 | 93.8857 | 0.6 | 3.5339 | 1.0859 | 0.083597
2015-06-06 04:00 | 151.4467 | 124.2733 | 27.1733 | 83.9598 | 22.5393 | -103.8312 | 71.1164 | 18.8836 | -108.585 | 95.7008 | 0 | 93.205 | 0.66438 | 0.77396 | 25.1543 | 118.3593 | 0.5 | 4.1987 | 1.0832 | 0.10513
2015-06-06 05:00 | 180.8633 | 150.3967 | 30.4667 | 80.6516 | 22.5439 | -88.833 | 67.8052 | 22.1948 | -94.2201 | 82.5379 | 10.4743 | 112.7975 | 0.66422 | 0.7737 | 30.0332 | 153.305 | 0.6 | 5.3908 | 1.0784 | 0.13557
2015-06-06 06:00 | 210.28 | 176.52 | 33.76 | 78.2255 | 22.5485 | -73.8348 | 64.4326 | 25.5674 | -79.5238 | 69.0328 | 27.9917 | 132.39 | 0.66406 | 0.77344 | 34.9098 | 195.2915 | 0.7 | 6.8029 | 1.0728 | 0.1718
2015-06-06 07:00 | 286.4967 | 199.7533 | 86.7433 | 180.1765 | 22.5531 | -58.8367 | 61.2208 | 28.7792 | -64.3722 | 55.3176 | 102.5252 | 149.815 | 0.66391 | 0.77318 | 47.5517 | 299.8919 | 1 | 10.3716 | 1.0585 | 0.2603
2015-06-06 08:00 | 362.7133 | 222.9867 | 139.7267 | 266.6787 | 22.5577 | -43.8385 | 58.4023 | 31.5977 | -48.6745 | 41.4908 | 199.759 | 167.24 | 0.66375 | 0.77292 | 60.1877 | 427.1868 | 0.5 | 13.8496 | 1.0446 | 0.36592
2015-06-06 09:00 | 438.93 | 246.22 | 192.71 | 346.4574 | 22.5623 | -28.8404 | 56.2045 | 33.7955 | -32.4134 | 27.6646 | 306.8505 | 184.665 | 0.66359 | 0.77266 | 72.8178 | 564.3333 | 0.5 | 18.1354 | 1.0275 | 0.47546
2015-06-06 10:00 | 450.3633 | 234.64 | 215.7233 | 374.4691 | 22.5669 | -13.8422 | 54.8249 | 35.1751 | -15.6813 | 14.1694 | 363.0763 | 175.98 | 0.66344 | 0.7724 | 74.697 | 613.7533 | 0.3 | 19.4798 | 1.0221 | 0.51439
2015-06-06 11:00 | 461.7967 | 223.06 | 238.7367 | 410.0961 | 22.5714 | 1.1559 | 54.3982 | 35.6018 | 1.3128 | 5.7092 | 408.0619 | 167.295 | 0.66328 | 0.77214 | 76.5753 | 651.9321 | 0.3 | 20.6729 | 1.0173 | 0.54384
2015-06-06 12:00 | 473.23 | 211.48 | 261.75 | 455.9841 | 22.576 | 16.1541 | 54.968 | 35.032 | 18.2848 | 16.1903 | 437.9002 | 158.61 | 0.66313 | 0.77187 | 78.4527 | 674.9629 | 0.2 | 21.2926 | 1.0148 | 0.56168
2015-06-06 13:00 | 442.2767 | 179.0433 | 263.2333 | 476.62 | 22.5805 | 31.1522 | 56.4756 | 33.5244 | 34.9576 | 29.7903 | 413.6346 | 134.2825 | 0.66297 | 0.77161 | 73.3039 | 621.221 | 0.5 | 19.9132 | 1.0203 | 0.51977
2015-06-06 14:00 | 411.3233 | 146.6067 | 264.7167 | 510.631 | 22.585 | 46.1503 | 58.7743 | 31.2257 | 51.1378 | 43.6248 | 369.6318 | 109.955 | 0.66281 | 0.77135 | 68.1576 | 547.7444 | 0.2 | 17.317 | 1.0307 | 0.46295
2015-06-06 15:00 | 380.37 | 114.17 | 266.2 | 560.7701 | 22.5895 | 61.1485 | 61.6599 | 28.3401 | 66.7511 | 57.4372 | 301.8197 | 85.6275 | 0.66266 | 0.77109 | 63.0136 | 450.4608 | 0.8 | 14.8769 | 1.0405 | 0.38433
2015-06-06 16:00 | 333.83 | 104.7533 | 229.0767 | 540.0773 | 22.5941 | 76.1466 | 64.9028 | 25.0972 | 81.8282 | 71.122 | 174.7445 | 78.565 | 0.6625 | 0.77083 | 55.2906 | 308.6001 | 0.5 | 10.1438 | 1.0594 | 0.26809
2015-06-06 17:00 | 287.29 | 95.3367 | 191.9533 | 518.4943 | 22.5985 | 91.1448 | 68.2712 | 21.7288 | 96.4671 | 84.5778 | 48.9949 | 71.5025 | 0.66234 | 0.77057 | 47.5712 | 168.0686 | 0.2 | 5.4521 | 1.0782 | 0.14859
2015-06-06 18:00 | 240.75 | 85.92 | 154.83 | 489.1055 | 22.603 | 106.1429 | 71.5451 | 18.4549 | 110.7934 | 97.6631 | 0 | 64.44 | 0.66219 | 0.77031 | 39.8554 | 104.2954 | -0.2 | 3.0592 | 1.0878 | 0.093028
2015-06-06 19:00 | 208.89 | 72.9933 | 135.8967 | 509.2645 | 22.6075 | 121.141 | 74.5232 | 15.4768 | 124.9293 | 110.1483 | 0 | 54.745 | 0.66203 | 0.77005 | 34.5729 | 89.3179 | -0.2 | 2.5912 | 1.0896 | 0.079806
2015-06-06 20:00 | 177.03 | 60.0667 | 116.9633 | 521.0449 | 22.6119 | 136.1392 | 77.0278 | 12.9722 | 138.9743 | 121.6299 | 0 | 45.05 | 0.66187 | 0.76979 | 29.2929 | 74.3429 | -0.2 | 2.1232 | 1.0915 | 0.06654
2015-06-06 21:00 | 145.17 | 47.14 | 98.03 | 509.6782 | 22.6164 | 151.1373 | 78.9108 | 11.0892 | 152.9949 | 131.378 | 0 | 35.355 | 0.66172 | 0.76953 | 24.0154 | 59.3704 | -0.2 | 1.6553 | 1.0934 | 0.05323
2015-06-06 22:00 | 135.8167 | 46.1333 | 89.6833 | 519.5462 | 22.6208 | 166.1354 | 80.0599 | 9.9401 | 167.0227 | 138.153 | 0 | 34.6 | 0.66156 | 0.76927 | 22.4628 | 57.0628 | -0.6 | 1.1832 | 1.0953 | 0.051249
2015-06-06 23:00 | 126.4633 | 45.1267 | 81.3367 | 488.0091 | 22.6253 | 181.1335 | 80.4057 | 9.5943 | -178.9389 | 140.3926 | 0 | 33.845 | 0.66141 | 0.76901 | 20.9109 | 54.7559 | -0.2 | 1.5111 | 1.094 | 0.049118
2015-06-07 | 117.11 | 44.12 | 72.99 | 417.3206 | 22.6297 | -163.8684 | 79.9271 | 10.0729 | -164.9021 | 137.3743 | 0 | 33.09 | 0.66125 | 0.76875 | 19.3597 | 52.4497 | -0.6 | 1.0391 | 1.0958 | 0.047131
2015-06-07 01:00 | 143.92 | 48.4533 | 95.4667 | 485.2059 | 22.6341 | -148.8702 | 78.6527 | 11.3473 | -150.8778 | 130.0443 | 0 | 36.34 | 0.66109 | 0.76849 | 23.7862 | 60.1262 | 0 | 1.8789 | 1.0925 | 0.053863
2015-06-07 02:00 | 170.73 | 52.7867 | 117.9433 | 511.1397 | 22.6384 | -133.8721 | 76.659 | 13.341 | -136.8588 | 119.9661 | 0 | 39.59 | 0.66094 | 0.76823 | 28.2105 | 67.8005 | 0.7 | 2.8188 | 1.0887 | 0.060529
2015-06-07 03:00 | 197.54 | 57.12 | 140.42 | 511.4326 | 22.6428 | -118.874 | 74.0641 | 15.9359 | -122.8082 | 108.2958 | 0 | 42.84 | 0.66078 | 0.76797 | 32.6327 | 75.4727 | 1.1 | 3.4585 | 1.0862 | 0.06722
2015-06-07 04:00 | 237.5467 | 83.1 | 154.4467 | 474.895 | 22.6472 | -103.8759 | 71.0209 | 18.9791 | -108.6539 | 95.7006 | 0 | 62.325 | 0.66063 | 0.76771 | 39.2323 | 101.5573 | 1.1 | 4.2737 | 1.0829 | 0.090181
2015-06-07 05:00 | 277.5533 | 109.08 | 168.4733 | 444.1918 | 22.6515 | -88.8778 | 67.7109 | 22.2891 | -94.2918 | 82.5493 | 57.5997 | 81.81 | 0.66047 | 0.76745 | 45.8288 | 185.2386 | 1.6 | 7.3887 | 1.0704 | 0.1626
2015-06-07 06:00 | 317.56 | 135.06 | 182.5 | 421.4225 | 22.6559 | -73.8797 | 64.3383 | 25.6617 | -79.597 | 69.0543 | 150.6516 | 101.295 | 0.66031 | 0.76719 | 52.4222 | 304.3688 | 2.1 | 11.6115 | 1.0536 | 0.26295
2015-06-07 07:00 | 349.3733 | 179.35 | 170.0233 | 352.093 | 22.6602 | -58.8816 | 61.1255 | 28.8745 | -64.4453 | 55.3486 | 200.1939 | 134.5125 | 0.66016 | 0.76693 | 57.6602 | 392.3666 | 2.9 | 15.1615 | 1.0394 | 0.3344
2015-06-07 08:00 | 381.1867 | 223.64 | 157.5467 | 299.8612 | 22.6645 | -43.8835 | 58.3049 | 31.6951 | -48.7455 | 41.5316 | 224.4733 | 167.73 | 0.66 | 0.76667 | 62.8958 | 455.0991 | 2.1 | 16.3218 | 1.0347 | 0.38614
2015-06-07 09:00 | 413 | 267.93 | 145.07 | 260.1301 | 22.6688 | -28.8854 | 56.1043 | 33.8957 | -32.4798 | 27.718 | 230.2795 | 200.9475 | 0.65984 | 0.76641 | 68.1289 | 499.3559 | 2.7 | 18.3049 | 1.0268 | 0.42044
2015-06-07 10:00 | 425.6 | 253.22 | 172.38 | 298.4674 | 22.6731 | -13.8873 | 54.7216 | 35.2784 | -15.7407 | 14.2463 | 289.2886 | 189.915 | 0.65969 | 0.76615 | 70.1907 | 549.3944 | 1.6 | 18.7686 | 1.0249 | 0.46173
2015-06-07 11:00 | 438.2 | 238.51 | 199.69 | 342.1373 | 22.6774 | 1.1108 | 54.292 | 35.708 | 1.2622 | 5.8055 | 340.3825 | 178.8825 | 0.65953 | 0.76589 | 72.2516 | 591.5166 | 2.4 | 20.8849 | 1.0165 | 0.49303
2015-06-07 12:00 | 450.8 | 223.8 | 227 | 394.3818 | 22.6817 | 16.1089 | 54.8594 | 35.1406 | 18.2439 | 16.1825 | 378.756 | 167.85 | 0.65938 | 0.76562 | 74.3116 | 620.9175 | 1.7 | 21.1037 | 1.0156 | 0.51709
2015-06-07 13:00 | 449.25 | 174.7533 | 274.4967 | 495.5753 | 22.686 | 31.107 | 56.3654 | 33.6346 | 34.9257 | 29.7584 | 430.2217 | 131.065 | 0.65922 | 0.76536 | 74.0385 | 635.3252 | 1.7 | 21.5539 | 1.0138 | 0.52815
2015-06-07 14:00 | 447.7 | 125.7067 | 321.9933 | 619.135 | 22.6902 | 46.1051 | 58.6631 | 31.3369 | 51.1132 | 43.5809 | 448.5024 | 94.28 | 0.65906 | 0.7651 | 73.7656 | 616.5479 | 2.1 | 21.3671 | 1.0145 | 0.51292
2015-06-07 15:00 | 446.15 | 76.66 | 369.49 | 775.5584 | 22.6945 | 61.1032 | 61.5483 | 28.4517 | 66.7315 | 57.3842 | 418.028 | 57.495 | 0.65891 | 0.76484 | 73.4928 | 549.0157 | 2.9 | 20.0567 | 1.0198 | 0.45909
2015-06-07 16:00 | 393.1333 | 67.14 | 325.9933 | 765.3877 | 22.6987 | 76.1013 | 64.7911 | 25.2089 | 81.8112 | 71.0608 | 248.4172 | 50.355 | 0.65875 | 0.76458 | 64.7441 | 363.5163 | 1.9 | 13.2599 | 1.047 | 0.31208
2015-06-07 17:00 | 340.1167 | 57.62 | 282.4967 | 759.3616 | 22.7029 | 91.0993 | 68.1598 | 21.8402 | 96.4506 | 84.5085 | 72.6694 | 43.215 | 0.65859 | 0.76432 | 55.9997 | 171.8841 | 1.8 | 7.1714 | 1.0713 | 0.151
2015-06-07 18:00 | 287.1 | 48.1 | 239 | 750.6444 | 22.7071 | 106.0974 | 71.4342 | 18.5658 | 110.7753 | 97.5852 | 0 | 36.075 | 0.65844 | 0.76406 | 47.2594 | 83.3344 | 1.5 | 4.1042 | 1.0836 | 0.074046
2015-06-07 19:00 | 236.41 | 48.5967 | 187.8133 | 698.9689 | 22.7113 | 121.0955 | 74.413 | 15.587 | 124.9082 | 110.0608 | 0 | 36.4475 | 0.65828 | 0.7638 | 38.9061 | 75.3536 | 1.9 | 4.2548 | 1.083 | 0.066917
2015-06-07 20:00 | 185.72 | 49.0933 | 136.6267 | 603.6594 | 22.7155 | 136.0936 | 76.9189 | 13.0811 | 138.9487 | 121.5321 | 0 | 36.82 | 0.65813 | 0.76354 | 30.5567 | 67.3767 | 0.9 | 3.0055 | 1.088 | 0.06011
2015-06-07 21:00 | 135.03 | 49.59 | 85.44 | 440.0172 | 22.7196 | 151.0916 | 78.8035 | 11.1965 | 152.9639 | 131.2707 | 0 | 37.1925 | 0.65797 | 0.76328 | 22.2114 | 59.4039 | 0.5 | 2.3564 | 1.0906 | 0.053123
2015-06-07 22:00 | 133.8833 | 46.29 | 87.5933 | 502.1815 | 22.7238 | 166.0897 | 79.9548 | 10.0452 | 166.9857 | 138.0418 | 0 | 34.7175 | 0.65781 | 0.76302 | 22.0175 | 56.735 | 0.4 | 2.173 | 1.0913 | 0.050771
2015-06-07 23:00 | 132.7367 | 42.99 | 89.7467 | 532.8294 | 22.7279 | 181.0878 | 80.3032 | 9.6968 | -178.9822 | 140.2911 | 0 | 32.2425 | 0.65766 | 0.76276 | 21.8238 | 54.0663 | 0.4 | 2.0896 | 1.0916 | 0.048397
2015-06-08 | 131.59 | 39.69 | 91.9 | 520.3512 | 22.7321 | -163.9142 | 79.8275 | 10.1725 | -164.9515 | 137.2966 | 0 | 29.7675 | 0.6575 | 0.7625 | 21.6301 | 51.3976 | 0.5 | 2.1062 | 1.0916 | 0.046006
2015-06-08 01:00 | 164.11 | 50.9267 | 113.1833 | 570.4686 | 22.7362 | -148.9161 | 78.5563 | 11.4437 | -150.933 | 129.9935 | 0 | 38.195 | 0.65734 | 0.76224 | 26.9692 | 65.1642 | 0.5 | 2.5364 | 1.0899 | 0.058236
2015-06-08 02:00 | 196.63 | 62.1633 | 134.4667 | 578.7721 | 22.7403 | -133.918 | 76.5657 | 13.4343 | -136.9192 | 119.9381 | 0 | 46.6225 | 0.65719 | 0.76198 | 32.3057 | 78.9282 | 0.3 | 2.7665 | 1.0889 | 0.070477
2015-06-08 03:00 | 229.15 | 73.4 | 155.75 | 564.1395 | 22.7444 | -118.92 | 73.9734 | 16.0266 | -122.8731 | 108.2853 | 0 | 55.05 | 0.65703 | 0.76172 | 37.6397 | 92.6897 | 0.4 | 3.2966 | 1.0868 | 0.082604
2015-06-08 04:00 | 268.9967 | 102.44 | 166.5567 | 509.8359 | 22.7485 | -103.9219 | 70.9322 | 19.0678 | -108.7224 | 95.7037 | 0 | 76.83 | 0.65688 | 0.76146 | 44.1743 | 121.0043 | 0.7 | 4.4814 | 1.0821 | 0.10737
2015-06-08 05:00 | 308.8433 | 131.48 | 177.3633 | 465.8931 | 22.7526 | -88.9238 | 67.6232 | 22.3768 | -94.363 | 82.5636 | 60.2988 | 98.61 | 0.65672 | 0.7612 | 50.7058 | 209.6146 | 0.5 | 7.0505 | 1.0718 | 0.18422
2015-06-08 06:00 | 348.69 | 160.52 | 188.17 | 433.138 | 22.7566 | -73.9258 | 64.2507 | 25.7493 | -79.6697 | 69.0781 | 154.6713 | 120.39 | 0.65656 | 0.76094 | 57.2342 | 332.2955 | 0.8 | 11.1842 | 1.0553 | 0.28754
2015-06-08 07:00 | 413.3633 | 147.3333 | 266.03 | 549.3685 | 22.7607 | -58.9277 | 61.0369 | 28.9631 | -64.5181 | 55.3814 | 312.1025 | 110.5 | 0.65641 | 0.76068 | 67.8336 | 490.4361 | 1.7 | 17.0261 | 1.0319 | 0.41498
2015-06-08 08:00 | 478.0367 | 134.1467 | 343.89 | 652.8596 | 22.7647 | -43.9297 | 58.2143 | 31.7857 | -48.8164 | 41.5737 | 488.4059 | 100.61 | 0.65625 | 0.76042 | 78.4279 | 667.4438 | 1.7 | 22.5576 | 1.0098 | 0.55265
2015-06-08 09:00 | 542.71 | 120.96 | 421.75 | 754.4243 | 22.7688 | -28.9316 | 56.0109 | 33.9891 | -32.5467 | 27.772 | 667.5211 | 90.72 | 0.65609 | 0.76016 | 89.0172 | 847.2583 | 2.1 | 28.5768 | 0.98569 | 0.68481
2015-06-08 10:00 | 537.9433 | 138.8833 | 399.06 | 689.311 | 22.7728 | -13.9336 | 54.625 | 35.375 | -15.801 | 14.3222 | 667.8872 | 104.1625 | 0.65594 | 0.7599 | 88.2143 | 860.264 | 1.6 | 28.4832 | 0.98607 | 0.69559
2015-06-08 11:00 | 533.1767 | 156.8067 | 376.37 | 643.2958 | 22.7768 | 1.0645 | 54.1924 | 35.8076 | 1.2102 | 5.8956 | 639.8932 | 117.605 | 0.65578 | 0.75964 | 87.4118 | 844.91 | 2 | 28.4034 | 0.98639 | 0.68339
2015-06-08 12:00 | 528.41 | 174.73 | 353.68 | 612.9207 | 22.7808 | 16.0625 | 54.7574 | 35.2426 | 18.201 | 16.1723 | 588.6664 | 131.0475 | 0.65563 | 0.75938 | 86.6097 | 806.3236 | 1.7 | 26.8976 | 0.99241 | 0.65617
2015-06-08 13:00 | 490.89 | 161.9967 | 328.8933 | 592.1705 | 22.7848 | 31.0605 | 56.2615 | 33.7385 | 34.8913 | 29.7252 | 514.2487 | 121.4975 | 0.65547 | 0.75911 | 80.4408 | 716.187 | 1.9 | 24.2808 | 1.0029 | 0.58896
2015-06-08 14:00 | 453.37 | 149.2633 | 304.1067 | 582.9902 | 22.7888 | 46.0586 | 58.5582 | 31.4418 | 51.0859 | 43.5362 | 422.6324 | 111.9475 | 0.65531 | 0.75885 | 74.2748 | 608.8546 | 2.4 | 21.4267 | 1.0143 | 0.5064
2015-06-08 15:00 | 415.85 | 136.53 | 279.32 | 584.3092 | 22.7927 | 61.0566 | 61.4429 | 28.5571 | 66.7091 | 57.331 | 315.4012 | 102.3975 | 0.65516 | 0.75859 | 68.1117 | 485.9104 | 3.3 | 18.4847 | 1.0261 | 0.40883
2015-06-08 16:00 | 366.2067 | 117.5767 | 248.63 | 581.4763 | 22.7967 | 76.0546 | 64.6857 | 25.3143 | 81.7914 | 71 | 189.3103 | 88.1825 | 0.655 | 0.75833 | 59.9663 | 337.4591 | 2.5 | 13.0456 | 1.0478 | 0.28995
2015-06-08 17:00 | 316.5633 | 98.6233 | 217.94 | 583.1594 | 22.8006 | 91.0527 | 68.0546 | 21.9454 | 96.4312 | 84.4401 | 56.5005 | 73.9675 | 0.65484 | 0.75807 | 51.8249 | 182.2928 | 2.3 | 7.9967 | 1.068 | 0.15965
2015-06-08 18:00 | 266.92 | 79.67 | 187.25 | 584.9282 | 22.8045 | 106.0507 | 71.3295 | 18.6705 | 110.7546 | 97.5088 | 0 | 59.7525 | 0.65469 | 0.75781 | 43.6873 | 103.4398 | 2.1 | 5.3325 | 1.0787 | 0.091493
2015-06-08 19:00 | 230.1167 | 67.1033 | 163.0133 | 602.7584 | 22.8084 | 121.0487 | 74.3092 | 15.6908 | 124.8845 | 109.9757 | 0 | 50.3275 | 0.65453 | 0.75755 | 37.6546 | 87.9821 | 2.2 | 4.9494 | 1.0802 | 0.077932
2015-06-08 20:00 | 193.3133 | 54.5367 | 138.7767 | 608.4728 | 22.8123 | 136.0468 | 76.8163 | 13.1837 | 138.921 | 121.4377 | 0 | 40.9025 | 0.65438 | 0.75729 | 31.6249 | 72.5274 | 1.5 | 3.7665 | 1.0849 | 0.064524
2015-06-08 21:00 | 156.51 | 41.97 | 114.54 | 584.6867 | 22.8162 | 151.0448 | 78.7027 | 11.2973 | 152.9311 | 131.168 | 0 | 31.4775 | 0.65422 | 0.75703 | 25.5979 | 57.0754 | 1.9 | 3.6836 | 1.0853 | 0.050792
2015-06-08 22:00 | 152.55 | 40.6233 | 111.9267 | 635.5165 | 22.8201 | 166.0428 | 79.8562 | 10.1438 | 166.9473 | 137.9365 | 0 | 30.4675 | 0.65406 | 0.75677 | 24.9443 | 55.4118 | 1.9 | 3.6316 | 1.0855 | 0.049321
2015-06-08 23:00 | 148.59 | 39.2767 | 109.3133 | 642.7056 | 22.824 | 181.0408 | 80.2074 | 9.7926 | -179.0265 | 140.1963 | 0 | 29.4575 | 0.65391 | 0.75651 | 24.291 | 53.7485 | 1.5 | 3.1796 | 1.0873 | 0.047921
2015-06-09 | 144.63 | 37.93 | 106.7 | 598.7456 | 22.8278 | -163.9611 | 79.7347 | 10.2653 | -165.0017 | 137.2253 | 0 | 28.4475 | 0.65375 | 0.75625 | 23.638 | 52.0855 | 1.5 | 3.1277 | 1.0875 | 0.046447
2015-06-09 01:00 | 164.0567 | 50.8033 | 113.2533 | 566.4432 | 22.8317 | -148.9631 | 78.4667 | 11.5333 | -150.9885 | 129.9484 | 0 | 38.1025 | 0.65359 | 0.75599 | 26.8066 | 64.9091 | 1.1 | 3.1284 | 1.0875 | 0.057882
2015-06-09 02:00 | 183.4833 | 63.6767 | 119.8067 | 512.4297 | 22.8355 | -133.9651 | 76.479 | 13.521 | -136.9796 | 119.9148 | 0 | 47.7575 | 0.65344 | 0.75573 | 29.9737 | 77.7312 | 1.4 | 3.8291 | 1.0847 | 0.069137
2015-06-09 03:00 | 202.91 | 76.55 | 126.36 | 455.3633 | 22.8393 | -118.9671 | 73.8894 | 16.1106 | -122.9376 | 108.2788 | 0 | 57.4125 | 0.65328 | 0.75547 | 33.1393 | 90.5518 | 2.2 | 5.0297 | 1.0799 | 0.080184
2015-06-09 04:00 | 242.43 | 95.2333 | 147.1967 | 448.7167 | 22.8432 | -103.9691 | 70.8502 | 19.1498 | -108.7904 | 95.7102 | 0 | 71.425 | 0.65313 | 0.75521 | 39.5843 | 111.0093 | 1.9 | 5.369 | 1.0785 | 0.098175
2015-06-09 05:00 | 281.95 | 113.9167 | 168.0333 | 439.8771 | 22.847 | -88.9711 | 67.5423 | 22.4577 | -94.4335 | 82.5806 | 56.802 | 85.4375 | 0.65297 | 0.75495 | 46.0261 | 188.2656 | 2 | 7.8833 | 1.0685 | 0.16495
2015-06-09 06:00 | 321.47 | 132.6 | 188.87 | 433.4817 | 22.8507 | -73.9731 | 64.1699 | 25.8301 | -79.7418 | 69.1042 | 154.6095 | 99.45 | 0.65281 | 0.75469 | 52.4649 | 306.5244 | 2.2 | 11.7789 | 1.0529 | 0.26464
2015-06-09 07:00 | 367.79 | 161.4067 | 206.3833 | 425.0975 | 22.8545 | -58.9751 | 60.955 | 29.045 | -64.5904 | 55.4159 | 241.2916 | 121.055 | 0.65266 | 0.75443 | 60.0101 | 422.3567 | 2.4 | 15.5986 | 1.0376 | 0.35936
2015-06-09 08:00 | 414.11 | 190.2133 | 223.8967 | 424.0561 | 22.8583 | -43.9771 | 58.1304 | 31.8696 | -48.8872 | 41.6171 | 317.0243 | 142.66 | 0.6525 | 0.75417 | 67.5517 | 527.236 | 2.9 | 19.3761 | 1.0225 | 0.44206
2015-06-09 09:00 | 460.43 | 219.02 | 241.41 | 430.8666 | 22.862 | -28.9791 | 55.9242 | 34.0758 | -32.6138 | 27.8265 | 381.0433 | 164.265 | 0.65234 | 0.75391 | 75.0897 | 620.398 | 1 | 20.3874 | 1.0185 | 0.51811
2015-06-09 10:00 | 417.94 | 236.9733 | 180.9667 | 311.9018 | 22.8658 | -13.9811 | 54.5351 | 35.4649 | -15.8622 | 14.397 | 302.1069 | 177.73 | 0.65219 | 0.75365 | 68.1438 | 547.9807 | 1.7 | 18.8244 | 1.0247 | 0.46044
2015-06-09 11:00 | 375.45 | 254.9267 | 120.5233 | 205.538 | 22.8695 | 1.0169 | 54.0995 | 35.9005 | 1.1568 | 5.9797 | 204.4197 | 191.195 | 0.65203 | 0.75339 | 61.2013 | 456.816 | 2.2 | 16.4755 | 1.0341 | 0.38736
2015-06-09 12:00 | 332.96 | 272.88 | 60.08 | 103.8726 | 22.8732 | 16.0149 | 54.6619 | 35.3381 | 18.1561 | 16.1598 | 99.7685 | 204.66 | 0.65188 | 0.75313 | 54.2621 | 358.6906 | 2.9 | 14.1091 | 1.0436 | 0.30694
2015-06-09 13:00 | 367.73 | 227.62 | 140.11 | 251.6273 | 22.8769 | 31.0129 | 56.1641 | 33.8359 | 34.8545 | 29.6907 | 218.5917 | 170.715 | 0.65172 | 0.75286 | 59.9141 | 449.2208 | 3.2 | 17.2381 | 1.031 | 0.3798
2015-06-09 14:00 | 402.5 | 182.36 | 220.14 | 420.8379 | 22.8806 | 46.0109 | 58.4596 | 31.5404 | 51.0558 | 43.4908 | 305.3115 | 136.77 | 0.65156 | 0.7526 | 65.5635 | 507.645 | 4.1 | 19.9639 | 1.0201 | 0.42465
2015-06-09 15:00 | 437.27 | 137.1 | 300.17 | 625.9365 | 22.8843 | 61.0089 | 61.3438 | 28.6562 | 66.6837 | 57.2776 | 338.3621 | 102.825 | 0.65141 | 0.75234 | 71.2101 | 512.3972 | 4.2 | 20.2124 | 1.0192 | 0.42821
2015-06-09 16:00 | 361.87 | 126.4633 | 235.4067 | 548.5426 | 22.888 | 76.0069 | 64.5864 | 25.4136 | 81.7686 | 70.9395 | 179.1359 | 94.8475 | 0.65125 | 0.75208 | 58.917 | 332.9003 | 1.7 | 12.1031 | 1.0516 | 0.28706
2015-06-09 17:00 | 286.47 | 115.8267 | 170.6433 | 454.6547 | 22.8916 | 91.0049 | 67.9556 | 22.0444 | 96.409 | 84.3725 | 44.5834 | 86.87 | 0.65109 | 0.75182 | 46.6297 | 178.0831 | 1.6 | 7.1651 | 1.0713 | 0.15645
2015-06-09 18:00 | 211.07 | 105.19 | 105.88 | 329.0735 | 22.8953 | 106.0029 | 71.2311 | 18.7689 | 110.7312 | 97.4339 | 0 | 78.8925 | 0.65094 | 0.75156 | 34.3483 | 113.2408 | 1.5 | 5.0388 | 1.0798 | 0.10027
2015-06-09 19:00 | 169.44 | 86.39 | 83.05 | 305.2374 | 22.8989 | 121.0009 | 74.2117 | 15.7883 | 124.8585 | 109.8929 | 0 | 64.7925 | 0.65078 | 0.7513 | 27.5671 | 92.3596 | 1.6 | 4.4862 | 1.0821 | 0.081949
2015-06-09 20:00 | 127.81 | 67.59 | 60.22 | 262.1602 | 22.9025 | 135.9988 | 76.7202 | 13.2798 | 138.8911 | 121.3467 | 0 | 50.6925 | 0.65063 | 0.75104 | 20.7891 | 71.4816 | 1.4 | 3.6338 | 1.0855 | 0.063624
2015-06-09 21:00 | 86.18 | 48.79 | 37.39 | 189.3039 | 22.9062 | 150.9968 | 78.6084 | 11.3916 | 152.8965 | 131.0699 | 0 | 36.5925 | 0.65047 | 0.75078 | 14.0143 | 50.6068 | 1.5 | 3.0815 | 1.0877 | 0.045136
2015-06-09 22:00 | 91.4067 | 48.7133 | 42.6933 | 240.2569 | 22.9098 | 165.9948 | 79.7643 | 10.2357 | 166.9074 | 137.8371 | 0 | 36.535 | 0.65031 | 0.75052 | 14.8607 | 51.3957 | 1.7 | 3.3061 | 1.0868 | 0.045802
2015-06-09 23:00 | 96.6333 | 48.6367 | 47.9967 | 279.6739 | 22.9133 | 180.9928 | 80.1182 | 9.8818 | -179.0718 | 140.1082 | 0 | 36.4775 | 0.65016 | 0.75026 | 15.7067 | 52.1842 | 1.7 | 3.3308 | 1.0867 | 0.0465
2015-06-10 | 101.86 | 48.56 | 53.3 | 296.6314 | 22.9169 | -164.0093 | 79.6486 | 10.3514 | -165.0523 | 137.1604 | 0 | 36.42 | 0.65 | 0.75 | 16.5523 | 52.9723 | 1.5 | 3.1554 | 1.0874 | 0.047233
2015-06-10 01:00 | 125.8 | 66.7833 | 59.0167 | 293.0972 | 22.9205 | -149.0113 | 78.3838 | 11.6162 | -151.0442 | 129.9089 | 0 | 50.0875 | 0.64875 | 0.74792 | 20.4032 | 70.4907 | 1.5 | 3.7028 | 1.0852 | 0.062726
2015-06-10 02:00 | 149.74 | 85.0067 | 64.7333 | 275.2781 | 22.924 | -134.0133 | 76.3992 | 13.6008 | -137.0398 | 119.8962 | 0 | 63.755 | 0.6475 | 0.74583 | 24.2392 | 87.9942 | 1.3 | 4.0498 | 1.0838 | 0.078202
2015-06-10 03:00 | 173.68 | 103.23 | 70.45 | 252.7015 | 22.9276 | -119.0153 | 73.8122 | 16.1878 | -123.0018 | 108.2763 | 0 | 77.4225 | 0.64625 | 0.74375 | 28.0602 | 105.4827 | 1.5 | 4.7963 | 1.0808 | 0.093486
2015-06-10 04:00 | 191.91 | 124.06 | 67.85 | 206.0558 | 22.9311 | -104.0174 | 70.7749 | 19.2251 | -108.8578 | 95.72 | 0 | 93.045 | 0.645 | 0.74167 | 30.9455 | 123.9905 | 1.9 | 5.7747 | 1.0769 | 0.10949
2015-06-10 05:00 | 210.14 | 144.89 | 65.25 | 170.2782 | 22.9346 | -89.0194 | 67.4682 | 22.5318 | -94.5034 | 82.6003 | 21.9301 | 108.6675 | 0.64375 | 0.73958 | 33.8194 | 164.417 | 2 | 7.138 | 1.0714 | 0.14445
2015-06-10 06:00 | 228.37 | 165.72 | 62.65 | 143.4071 | 22.9381 | -74.0215 | 64.0958 | 25.9042 | -79.8133 | 69.1325 | 51.0827 | 124.29 | 0.6425 | 0.7375 | 36.6819 | 212.0546 | 2.1 | 8.7267 | 1.0651 | 0.1852
2015-06-10 07:00 | 253.6233 | 202.2067 | 51.4167 | 105.6561 | 22.9416 | -59.0235 | 60.8799 | 29.1201 | -64.6623 | 55.4522 | 59.9169 | 151.655 | 0.64125 | 0.73542 | 40.659 | 252.2309 | 2 | 9.8822 | 1.0605 | 0.21934
2015-06-10 08:00 | 278.8767 | 238.6933 | 40.1833 | 75.9422 | 22.9451 | -44.0255 | 58.0533 | 31.9467 | -48.9578 | 41.6616 | 56.7352 | 179.02 | 0.64 | 0.73333 | 44.6203 | 280.3754 | 2.1 | 10.8617 | 1.0566 | 0.24291
2015-06-10 09:00 | 304.13 | 275.18 | 28.95 | 51.5635 | 22.9486 | -29.0276 | 55.8443 | 34.1557 | -32.6811 | 27.8814 | 45.5779 | 206.385 | 0.63875 | 0.73125 | 48.5658 | 300.5286 | 2.2 | 11.5915 | 1.0536 | 0.25965
2015-06-10 10:00 | 289.99 | 262.77 | 27.22 | 46.8193 | 22.9521 | -14.0296 | 54.452 | 35.548 | -15.9242 | 14.4706 | 45.334 | 197.0775 | 0.6375 | 0.72917 | 46.2172 | 288.6287 | 1.9 | 10.9196 | 1.0563 | 0.25001
2015-06-10 11:00 | 275.85 | 250.36 | 25.49 | 43.38 | 22.9555 | 0.96834 | 54.0133 | 35.9867 | 1.102 | 6.0575 | 43.1378 | 187.77 | 0.63625 | 0.72708 | 43.8774 | 274.7852 | 2.2 | 10.787 | 1.0569 | 0.23813
2015-06-10 12:00 | 261.71 | 237.95 | 23.76 | 40.9891 | 22.9589 | 15.9663 | 54.573 | 35.427 | 18.1093 | 16.1449 | 39.3726 | 178.4625 | 0.635 | 0.725 | 41.5465 | 259.3816 | 2.4 | 10.5057 | 1.058 | 0.22502
2015-06-10 13:00 | 242.7433 | 214.3 | 28.4433 | 50.9616 | 22.9624 | 30.9642 | 56.0733 | 33.9267 | 34.8155 | 29.6548 | 44.2868 | 160.725 | 0.63375 | 0.72292 | 38.4596 | 243.4714 | 2.6 | 10.2085 | 1.0592 | 0.21146
2015-06-10 14:00 | 223.7767 | 190.65 | 33.1267 | 63.1623 | 22.9658 | 45.9622 | 58.3675 | 31.6325 | 51.0231 | 43.4447 | 45.8582 | 142.9875 | 0.6325 | 0.72083 | 35.3847 | 224.2304 | 2.3 | 9.3072 | 1.0628 | 0.19541
2015-06-10 15:00 | 204.81 | 167 | 37.81 | 78.6113 | 22.9692 | 60.9601 | 61.251 | 28.749 | 66.6556 | 57.224 | 42.5567 | 125.25 | 0.63125 | 0.71875 | 32.3216 | 200.1282 | 2.5 | 8.754 | 1.065 | 0.17477
2015-06-10 16:00 | 164.0967 | 138.63 | 25.4667 | 59.1403 | 22.9726 | 75.9581 | 64.4934 | 25.5066 | 81.743 | 70.8793 | 19.3719 | 103.9725 | 0.63 | 0.71667 | 25.8452 | 149.1896 | 2.4 | 7.0622 | 1.0718 | 0.13111
2015-06-10 17:00 | 123.3833 | 110.26 | 13.1233 | 34.8261 | 22.976 | 90.956 | 67.8629 | 22.1371 | 96.384 | 84.306 | 3.4553 | 82.695 | 0.62875 | 0.71458 | 19.3943 | 105.5446 | 2 | 5.2983 | 1.0788 | 0.093367
2015-06-10 18:00 | 82.67 | 81.89 | 0.78 | 2.4128 | 22.9793 | 105.954 | 71.139 | 18.861 | 110.7053 | 97.3607 | 0 | 61.4175 | 0.6275 | 0.7125 | 12.9689 | 74.3864 | 2.2 | 4.5246 | 1.0819 | 0.065993
2015-06-10 19:00 | 74.8067 | 69.61 | 5.1967 | 18.9928 | 22.9827 | 120.9519 | 74.1206 | 15.8794 | 124.8301 | 109.8126 | 0 | 52.2075 | 0.62625 | 0.71042 | 11.7119 | 63.9194 | 2 | 3.9975 | 1.084 | 0.056817
2015-06-10 20:00 | 66.9433 | 57.33 | 9.6133 | 41.5749 | 22.986 | 135.9499 | 76.6305 | 13.3695 | 138.8592 | 121.2591 | 0 | 42.9975 | 0.625 | 0.70833 | 10.4599 | 53.4574 | 2.3 | 3.9705 | 1.0841 | 0.047522
2015-06-10 21:00 | 59.08 | 45.05 | 14.03 | 70.4977 | 22.9893 | 150.9478 | 78.5207 | 11.4793 | 152.8602 | 130.9765 | 0 | 33.7875 | 0.62375 | 0.70625 | 9.2128 | 43.0003 | 1.8 | 3.1438 | 1.0874 | 0.038343
2015-06-10 22:00 | 74.2333 | 53.37 | 20.8633 | 116.4486 | 22.9927 | 165.9457 | 79.679 | 10.321 | 166.8662 | 137.7437 | 0 | 40.0275 | 0.6225 | 0.70417 | 11.5526 | 51.5801 | 1.7 | 3.3119 | 1.0868 | 0.045965
2015-06-10 23:00 | 89.3867 | 61.69 | 27.6967 | 160.0647 | 22.996 | 180.9437 | 80.0357 | 9.9643 | -179.118 | 140.0267 | 0 | 46.2675 | 0.62125 | 0.70208 | 13.8829 | 60.1504 | 1.6 | 3.4797 | 1.0861 | 0.053569
2015-06-11 | 104.54 | 70.01 | 34.53 | 190.7248 | 22.9993 | -164.0584 | 79.5693 | 10.4307 | -165.1035 | 137.102 | 0 | 52.5075 | 0.62 | 0.7 | 16.2037 | 68.7112 | 1.4 | 3.5472 | 1.0858 | 0.061178
2015-06-11 01:00 | 133.6733 | 79.1467 | 54.5267 | 269.0595 | 23.0026 | -149.0605 | 78.3076 | 11.6924 | -151.1001 | 129.875 | 0 | 59.36 | 0.61875 | 0.69792 | 20.6776 | 80.0376 | 1.5 | 4.0012 | 1.084 | 0.071144
2015-06-11 02:00 | 162.8067 | 88.2833 | 74.5233 | 315.2482 | 23.0058 | -134.0625 | 76.3261 | 13.6739 | -137.0999 | 119.8823 | 0 | 66.2125 | 0.6175 | 0.69583 | 25.1333 | 91.3458 | 2 | 4.8546 | 1.0806 | 0.080939
2015-06-11 03:00 | 191.94 | 97.42 | 94.52 | 337.6098 | 23.0091 | -119.0646 | 73.7417 | 16.2583 | -123.0655 | 108.2776 | 0 | 73.065 | 0.61625 | 0.69375 | 29.5708 | 102.6358 | 2.3 | 5.5074 | 1.078 | 0.090723
2015-06-11 04:00 | 207.75 | 135.3933 | 72.3567 | 218.9917 | 23.0123 | -104.0667 | 70.7064 | 19.2936 | -108.9245 | 95.733 | 0 | 101.545 | 0.615 | 0.69167 | 31.9416 | 133.4866 | 2.3 | 6.4715 | 1.0741 | 0.11757
2015-06-11 05:00 | 223.56 | 173.3667 | 50.1933 | 130.6156 | 23.0156 | -89.0688 | 67.4008 | 22.5992 | -94.5726 | 82.6227 | 16.7713 | 130.025 | 0.61375 | 0.68958 | 34.3025 | 181.0988 | 2.6 | 8.2593 | 1.067 | 0.15845
2015-06-11 06:00 | 239.37 | 211.34 | 28.03 | 64.0064 | 23.0188 | -74.0708 | 64.0285 | 25.9715 | -79.884 | 69.163 | 22.7678 | 158.505 | 0.6125 | 0.6875 | 36.6535 | 217.9263 | 2.8 | 9.6102 | 1.0616 | 0.1897
2015-06-11 07:00 | 269.83 | 238.52 | 31.31 | 64.2015 | 23.022 | -59.0729 | 60.8116 | 29.1884 | -64.7335 | 55.49 | 36.3734 | 178.89 | 0.61125 | 0.68542 | 41.2334 | 256.4967 | 3.7 | 11.7155 | 1.0531 | 0.2215
2015-06-11 08:00 | 300.29 | 265.7 | 34.59 | 65.243 | 23.0252 | -44.075 | 57.983 | 32.017 | -49.028 | 41.7071 | 48.7075 | 199.275 | 0.61 | 0.68333 | 45.7942 | 293.7768 | 2.6 | 11.7805 | 1.0529 | 0.25364
2015-06-11 09:00 | 330.75 | 292.88 | 37.87 | 67.3246 | 23.0284 | -29.0771 | 55.7712 | 34.2288 | -32.7485 | 27.9365 | 59.479 | 219.66 | 0.60875 | 0.68125 | 50.336 | 329.4751 | 2.5 | 12.7961 | 1.0488 | 0.28336
2015-06-11 10:00 | 285.4033 | 257.1367 | 28.2667 | 48.5292 | 23.0316 | -14.0792 | 54.3757 | 35.6243 | -15.9867 | 14.5426 | 46.9744 | 192.8525 | 0.6075 | 0.67917 | 43.3456 | 283.1725 | 2.3 | 11.1491 | 1.0554 | 0.24507
2015-06-11 11:00 | 240.0567 | 221.3933 | 18.6633 | 31.7016 | 23.0348 | 0.91874 | 53.9338 | 36.0662 | 1.046 | 6.1291 | 31.5203 | 166.045 | 0.60625 | 0.67708 | 36.3836 | 233.9489 | 2.5 | 9.8109 | 1.0608 | 0.20349
2015-06-11 12:00 | 194.71 | 185.65 | 9.06 | 15.5982 | 23.0379 | 15.9167 | 54.4907 | 35.5093 | 18.0607 | 16.1275 | 14.9844 | 139.2375 | 0.605 | 0.675 | 29.4499 | 183.6718 | 2.4 | 8.1397 | 1.0674 | 0.16077
2015-06-11 13:00 | 201.4233 | 194.1067 | 7.3167 | 13.0806 | 23.0411 | 30.9146 | 55.9889 | 34.0111 | 34.7741 | 29.6176 | 11.3715 | 145.58 | 0.60375 | 0.67292 | 30.4023 | 187.3539 | 2.3 | 8.1548 | 1.0674 | 0.16398
2015-06-11 14:00 | 208.1367 | 202.5633 | 5.5733 | 10.6009 | 23.0442 | 45.9125 | 58.2818 | 31.7182 | 50.9879 | 43.398 | 7.7026 | 151.9225 | 0.6025 | 0.67083 | 31.3506 | 190.9757 | 2.2 | 8.168 | 1.0673 | 0.16714
2015-06-11 15:00 | 214.85 | 211.02 | 3.83 | 7.9412 | 23.0473 | 60.9104 | 61.1645 | 28.8355 | 66.6247 | 57.1704 | 4.3052 | 158.265 | 0.60125 | 0.66875 | 32.2946 | 194.8649 | 4.3 | 10.3895 | 1.0584 | 0.16913
2015-06-11 16:00 | 149.6033 | 147.0467 | 2.5567 | 5.9185 | 23.0504 | 75.9083 | 64.4068 | 25.5932 | 81.7146 | 70.8197 | 1.9445 | 110.285 | 0.6 | 0.66667 | 22.4405 | 134.67 | 4.3 | 8.5084 | 1.066 | 0.11771
2015-06-11 17:00 | 84.3567 | 83.0733 | 1.2833 | 3.3931 | 23.0535 | 90.9062 | 67.7765 | 22.2235 | 96.3564 | 84.2405 | 0.34051 | 62.305 | 0.59875 | 0.66458 | 12.6271 | 75.2726 | 4.6 | 6.9523 | 1.0722 | 0.066179
2015-06-11 18:00 | 19.11 | 19.1 | 0.01 | 0.030799 | 23.0566 | 105.9041 | 71.0532 | 18.9468 | 110.6768 | 97.2892 | 0 | 14.325 | 0.5975 | 0.6625 | 2.8546 | 17.1796 | 3.7 | 4.2369 | 1.0831 | 0.015257
2015-06-11 19:00 | 15.85 | 14.6667 | 1.1833 | 4.3025 | 23.0597 | 120.902 | 74.0359 | 15.9641 | 124.7994 | 109.7348 | 0 | 11 | 0.59625 | 0.66042 | 2.3626 | 13.3626 | 2.6 | 3.0176 | 1.0879 | 0.011921
2015-06-11 20:00 | 12.59 | 10.2333 | 2.3567 | 10.1301 | 23.0627 | 135.8999 | 76.5474 | 13.4526 | 138.8253 | 121.1752 | 0 | 7.675 | 0.595 | 0.65833 | 1.8728 | 9.5478 | 2.1 | 2.3984 | 1.0904 | 0.008537
2015-06-11 21:00 | 9.33 | 5.8 | 3.53 | 17.6147 | 23.0658 | 150.8978 | 78.4396 | 11.5604 | 152.8223 | 130.888 | 0 | 4.35 | 0.59375 | 0.65625 | 1.3849 | 5.7349 | 2.5 | 2.6792 | 1.0893 | 0.0051225
2015-06-11 22:00 | 19.2067 | 13.4367 | 5.77 | 31.9644 | 23.0688 | 165.8957 | 79.6003 | 10.3997 | 166.8238 | 137.6563 | 0 | 10.0775 | 0.5925 | 0.65417 | 2.845 | 12.9225 | 3.1 | 3.5038 | 1.086 | 0.011508
2015-06-11 23:00 | 29.0833 | 21.0733 | 8.01 | 45.9459 | 23.0719 | 180.8936 | 79.96 | 10.04 | -179.1651 | 139.9519 | 0 | 15.805 | 0.59125 | 0.65208 | 4.2989 | 20.1039 | 2.9 | 3.5282 | 1.0859 | 0.017901
2015-06-12 | 38.96 | 28.71 | 10.25 | 56.2286 | 23.0749 | -164.1085 | 79.4967 | 10.5033 | -165.1552 | 137.05 | 0 | 21.5325 | 0.59 | 0.65 | 5.7466 | 27.2791 | 2.3 | 3.1525 | 1.0874 | 0.024324
2015-06-12 01:00 | 59.3833 | 36.5367 | 22.8467 | 112.0806 | 23.0779 | -149.1106 | 78.2383 | 11.7617 | -151.156 | 129.8467 | 0 | 27.4025 | 0.58875 | 0.64792 | 8.7405 | 36.143 | 1.5 | 2.6295 | 1.0895 | 0.032289
2015-06-12 02:00 | 79.8067 | 44.3633 | 35.4433 | 149.2227 | 23.0809 | -134.1127 | 76.2598 | 13.7402 | -137.1596 | 119.8732 | 0 | 33.2725 | 0.5875 | 0.64583 | 11.7216 | 44.9941 | 1.8 | 3.2061 | 1.0872 | 0.040112
2015-06-12 03:00 | 100.23 | 52.19 | 48.04 | 170.9396 | 23.0838 | -119.1148 | 73.678 | 16.322 | -123.1286 | 108.2828 | 0 | 39.1425 | 0.58625 | 0.64375 | 14.69 | 53.8325 | 2.3 | 3.9823 | 1.0841 | 0.047854
2015-06-12 04:00 | 84.2133 | 50.1133 | 34.1 | 102.8891 | 23.0868 | -104.1169 | 70.6447 | 19.3553 | -108.9905 | 95.7492 | 0 | 37.585 | 0.585 | 0.64167 | 12.3162 | 49.9012 | 2.8 | 4.3594 | 1.0826 | 0.044297
2015-06-12 05:00 | 68.1967 | 48.0367 | 20.16 | 52.3283 | 23.0898 | -89.1191 | 67.3401 | 22.6599 | -94.6408 | 82.6477 | 6.6964 | 36.0275 | 0.58375 | 0.63958 | 9.9525 | 52.6764 | 2 | 3.6461 | 1.0854 | 0.046884
2015-06-12 06:00 | 52.18 | 45.96 | 6.22 | 14.1726 | 23.0927 | -74.1212 | 63.9679 | 26.0321 | -79.9538 | 69.1954 | 5.0339 | 34.47 | 0.5825 | 0.6375 | 7.5987 | 47.1026 | 2.3 | 3.772 | 1.0849 | 0.041904
2015-06-12 07:00 | 42.99 | 38.66 | 4.33 | 8.8617 | 23.0956 | -59.1233 | 60.7501 | 29.2499 | -64.8039 | 55.5294 | 5.0156 | 28.995 | 0.58125 | 0.63542 | 6.247 | 40.2576 | 2.3 | 3.558 | 1.0858 | 0.035842
2015-06-12 08:00 | 33.8 | 31.36 | 2.44 | 4.5941 | 23.0986 | -44.1254 | 57.9195 | 32.0805 | -49.0978 | 41.7536 | 3.4273 | 23.52 | 0.58 | 0.63333 | 4.901 | 31.8483 | 2.8 | 3.7953 | 1.0848 | 0.028331
2015-06-12 09:00 | 24.61 | 24.06 | 0.55 | 0.97612 | 23.1015 | -29.1275 | 55.7049 | 34.2951 | -32.8159 | 27.9917 | 0.86193 | 18.045 | 0.57875 | 0.63125 | 3.5608 | 22.4677 | 2.7 | 3.4021 | 1.0864 | 0.020015
2015-06-12 10:00 | 77.2667 | 68.97 | 8.2967 | 14.22 | 23.1044 | -14.1296 | 54.3063 | 35.6937 | -16.0498 | 14.6131 | 13.76 | 51.7275 | 0.5775 | 0.62917 | 11.1554 | 76.6428 | 2.8 | 5.1951 | 1.0792 | 0.067826
2015-06-12 11:00 | 129.9233 | 113.88 | 16.0433 | 27.2039 | 23.1073 | 0.86823 | 53.8611 | 36.1389 | 0.98884 | 6.1945 | 27.045 | 85.41 | 0.57625 | 0.62708 | 18.7171 | 131.1721 | 3.9 | 7.9991 | 1.068 | 0.11488
2015-06-12 12:00 | 182.58 | 158.79 | 23.79 | 40.8828 | 23.1101 | 15.8661 | 54.4152 | 35.5848 | 18.0105 | 16.1076 | 39.2779 | 119.0925 | 0.575 | 0.625 | 26.2459 | 184.6162 | 1.4 | 7.1693 | 1.0713 | 0.16218
2015-06-12 13:00 | 201.7733 | 164.6633 | 37.11 | 66.2115 | 23.113 | 30.864 | 55.9112 | 34.0888 | 34.7306 | 29.5791 | 57.5825 | 123.4975 | 0.57375 | 0.62292 | 28.9419 | 210.0218 | 1 | 7.5632 | 1.0697 | 0.18423
2015-06-12 14:00 | 220.9667 | 170.5367 | 50.43 | 95.7076 | 23.1158 | 45.8619 | 58.2026 | 31.7974 | 50.9502 | 43.3506 | 69.5954 | 127.9025 | 0.5725 | 0.62083 | 31.6259 | 229.1237 | 1.2 | 8.3601 | 1.0666 | 0.20039
2015-06-12 15:00 | 240.16 | 176.41 | 63.75 | 131.8458 | 23.1187 | 60.8597 | 61.0845 | 28.9155 | 66.5912 | 57.1167 | 71.583 | 132.3075 | 0.57125 | 0.61875 | 34.2978 | 238.1883 | 1.2 | 8.6434 | 1.0654 | 0.20809
2015-06-12 16:00 | 188.1667 | 144.47 | 43.6967 | 100.8597 | 23.1215 | 75.8576 | 64.3265 | 25.6735 | 81.6836 | 70.7606 | 33.235 | 108.3525 | 0.57 | 0.61667 | 26.8137 | 168.4012 | 0.8 | 6.0625 | 1.0757 | 0.14855
2015-06-12 17:00 | 136.1733 | 112.53 | 23.6433 | 62.299 | 23.1243 | 90.8555 | 67.6964 | 22.3036 | 96.3261 | 84.1761 | 6.3215 | 84.3975 | 0.56875 | 0.61458 | 19.3621 | 110.0812 | 1.7 | 5.14 | 1.0794 | 0.097437
2015-06-12 18:00 | 84.18 | 80.59 | 3.59 | 11.0123 | 23.1271 | 105.8533 | 70.9739 | 19.0261 | 110.6458 | 97.2195 | 0 | 60.4425 | 0.5675 | 0.6125 | 11.943 | 72.3855 | 2.1 | 4.362 | 1.0826 | 0.064256
2015-06-12 19:00 | 71.3967 | 69.0033 | 2.3933 | 8.6606 | 23.1299 | 120.8512 | 73.9577 | 16.0423 | 124.7665 | 109.6597 | 0 | 51.7525 | 0.56625 | 0.61042 | 10.1071 | 61.8596 | 3 | 4.9331 | 1.0803 | 0.054796
2015-06-12 20:00 | 58.6133 | 57.4167 | 1.1967 | 5.1153 | 23.1327 | 135.8491 | 76.4708 | 13.5292 | 138.7894 | 121.0948 | 0 | 43.0625 | 0.565 | 0.60833 | 8.2791 | 51.3416 | 3.9 | 5.5044 | 1.078 | 0.045383
2015-06-12 21:00 | 45.83 | 45.83 | 0 | 0 | 23.1355 | 150.8469 | 78.3651 | 11.6349 | 152.7828 | 130.8043 | 0 | 34.3725 | 0.56375 | 0.60625 | 6.4592 | 40.8317 | 4 | 5.276 | 1.0789 | 0.036124
2015-06-12 22:00 | 38.3167 | 38.3167 | 0 | 0 | 23.1382 | 165.8448 | 79.5284 | 10.4716 | 166.7802 | 137.575 | 0 | 28.7375 | 0.5625 | 0.60417 | 5.3883 | 34.1258 | 3.7 | 4.7664 | 1.0809 | 0.030248
2015-06-12 23:00 | 30.8033 | 30.8033 | 0 | 0 | 23.141 | 180.8427 | 79.8911 | 10.1089 | -179.2129 | 139.8839 | 0 | 23.1025 | 0.56125 | 0.60208 | 4.3221 | 27.4246 | 3.5 | 4.357 | 1.0826 | 0.024345
2015-06-13 | 23.29 | 23.29 | 0 | 0 | 23.1437 | -164.1595 | 79.431 | 10.569 | -165.2072 | 137.0044 | 0 | 17.4675 | 0.56 | 0.6 | 3.2606 | 20.7281 | 3.5 | 4.1478 | 1.0834 | 0.018415
2015-06-13 01:00 | 29.45 | 29.42 | 0.03 | 0.14641 | 23.1464 | -149.1616 | 78.1758 | 11.8242 | -151.2118 | 129.8239 | 0 | 22.065 | 0.55875 | 0.59792 | 4.1138 | 26.1788 | 3.5 | 4.3181 | 1.0827 | 0.023242
2015-06-13 02:00 | 35.61 | 35.55 | 0.06 | 0.25154 | 23.1491 | -134.1638 | 76.2003 | 13.7997 | -137.219 | 119.8686 | 0 | 26.6625 | 0.5575 | 0.59583 | 4.9631 | 31.6256 | 3.4 | 4.3883 | 1.0824 | 0.028071
2015-06-13 03:00 | 41.77 | 41.68 | 0.09 | 0.31916 | 23.1518 | -119.1659 | 73.6211 | 16.3789 | -123.191 | 108.2918 | 0 | 31.26 | 0.55625 | 0.59375 | 5.8086 | 37.0686 | 3.5 | 4.6584 | 1.0814 | 0.03287
2015-06-13 04:00 | 65.49 | 65.43 | 0.06 | 0.18054 | 23.1545 | -104.1681 | 70.5898 | 19.4102 | -109.0556 | 95.7685 | 0 | 49.0725 | 0.555 | 0.59167 | 9.0867 | 58.1592 | 3.5 | 5.3175 | 1.0787 | 0.051445
2015-06-13 05:00 | 89.21 | 89.18 | 0.03 | 0.077695 | 23.1572 | -89.1702 | 67.2863 | 22.7137 | -94.7081 | 82.6752 | 0.0099056 | 66.885 | 0.55375 | 0.58958 | 12.35 | 79.2449 | 3.2 | 5.6764 | 1.0773 | 0.070003
2015-06-13 06:00 | 112.93 | 112.93 | 0 | 0 | 23.1598 | -74.1724 | 63.9141 | 26.0859 | -80.0227 | 69.2298 | 0 | 84.6975 | 0.5525 | 0.5875 | 15.5985 | 100.296 | 3 | 6.1342 | 1.0755 | 0.088449
2015-06-13 07:00 | 175.6367 | 155.6733 | 19.9633 | 40.787 | 23.1625 | -59.1745 | 60.6953 | 29.3047 | -64.8736 | 55.5701 | 23.0609 | 116.755 | 0.55125 | 0.58542 | 24.2049 | 164.0208 | 3.1 | 8.2256 | 1.0671 | 0.14352
2015-06-13 08:00 | 238.3433 | 198.4167 | 39.9267 | 75.0574 | 23.1651 | -44.1767 | 57.8628 | 32.1372 | -49.167 | 41.8008 | 55.9528 | 148.8125 | 0.55 | 0.58333 | 32.7722 | 237.5375 | 3.2 | 10.623 | 1.0575 | 0.20598
2015-06-13 09:00 | 301.05 | 241.16 | 59.89 | 106.1294 | 23.1678 | -29.1788 | 55.6455 | 34.3545 | -32.8831 | 28.0469 | 93.6658 | 180.87 | 0.54875 | 0.58125 | 41.3003 | 315.8361 | 2.3 | 12.1699 | 1.0513 | 0.27228
2015-06-13 10:00 | 297.99 | 231.6767 | 66.3133 | 113.4842 | 23.1704 | -14.181 | 54.2436 | 35.7564 | -16.1133 | 14.6818 | 109.7787 | 173.7575 | 0.5475 | 0.57917 | 40.7874 | 324.3236 | 2.1 | 12.2351 | 1.0511 | 0.27952
2015-06-13 11:00 | 294.93 | 222.1933 | 72.7367 | 123.142 | 23.173 | 0.81689 | 53.7952 | 36.2048 | 0.93069 | 6.2535 | 122.4092 | 166.645 | 0.54625 | 0.57708 | 40.2764 | 329.3306 | 2.4 | 12.6916 | 1.0492 | 0.28335
2015-06-13 12:00 | 291.87 | 212.71 | 79.16 | 135.8076 | 23.1756 | 15.8147 | 54.3464 | 35.6536 | 17.9586 | 16.0851 | 130.4909 | 159.5325 | 0.545 | 0.575 | 39.7673 | 329.7907 | 2.5 | 12.806 | 1.0488 | 0.28362
2015-06-13 13:00 | 307.2267 | 199.2533 | 107.9733 | 192.293 | 23.1781 | 30.8126 | 55.8401 | 34.1599 | 34.6851 | 29.5393 | 167.2984 | 149.44 | 0.54375 | 0.57292 | 41.7636 | 358.502 | 2.2 | 13.4032 | 1.0464 | 0.30761
2015-06-13 14:00 | 322.5833 | 185.7967 | 136.7867 | 259.068 | 23.1807 | 45.8104 | 58.1299 | 31.8701 | 50.9101 | 43.3027 | 188.5342 | 139.3475 | 0.5425 | 0.57083 | 43.7504 | 371.6321 | 2.6 | 14.2135 | 1.0431 | 0.31789
2015-06-13 15:00 | 337.94 | 172.34 | 165.6 | 341.695 | 23.1833 | 60.8083 | 61.0109 | 28.9891 | 66.5551 | 57.0631 | 185.7847 | 129.255 | 0.54125 | 0.56875 | 45.7275 | 360.7672 | 2.6 | 13.874 | 1.0445 | 0.30899
2015-06-13 16:00 | 290.1333 | 152.6967 | 137.4367 | 316.3803 | 23.1858 | 75.8061 | 64.2527 | 25.7473 | 81.6499 | 70.702 | 104.5577 | 114.5225 | 0.54 | 0.56667 | 39.168 | 258.2482 | 2.8 | 10.8703 | 1.0565 | 0.22373
2015-06-13 17:00 | 242.3267 | 133.0533 | 109.2733 | 287.0307 | 23.1883 | 90.8039 | 67.6228 | 22.3772 | 96.2933 | 84.113 | 29.4401 | 99.79 | 0.53875 | 0.56458 | 32.6384 | 161.8684 | 2.9 | 7.9584 | 1.0682 | 0.14178
2015-06-13 18:00 | 194.52 | 113.41 | 81.11 | 247.8898 | 23.1908 | 105.8018 | 70.901 | 19.099 | 110.6124 | 97.1517 | 0 | 85.0575 | 0.5375 | 0.5625 | 26.1386 | 111.1961 | 3.2 | 6.6749 | 1.0733 | 0.097864
2015-06-13 19:00 | 140.2233 | 85.1733 | 55.05 | 198.3436 | 23.1934 | 120.7996 | 73.886 | 16.114 | 124.7315 | 109.5873 | 0 | 63.88 | 0.53625 | 0.56042 | 18.7987 | 82.6787 | 2.9 | 5.4837 | 1.0781 | 0.073089
2015-06-13 20:00 | 85.9267 | 56.9367 | 28.99 | 123.2944 | 23.1958 | 135.7974 | 76.4008 | 13.5992 | 138.7517 | 121.0182 | 0 | 42.7025 | 0.535 | 0.55833 | 11.4927 | 54.1952 | 2.7 | 4.3936 | 1.0824 | 0.048103
2015-06-13 21:00 | 31.63 | 28.7 | 2.93 | 14.4454 | 23.1983 | 150.7953 | 78.2973 | 11.7027 | 152.7418 | 130.7255 | 0 | 21.525 | 0.53375 | 0.55625 | 4.2206 | 25.7456 | 3.1 | 3.9046 | 1.0844 | 0.022893
2015-06-13 22:00 | 31.6867 | 29.1533 | 2.5333 | 13.8535 | 23.2008 | 165.7931 | 79.4633 | 10.5367 | 166.7356 | 137.4998 | 0 | 21.865 | 0.5325 | 0.55417 | 4.2183 | 26.0833 | 3.3 | 4.1151 | 1.0835 | 0.023175
2015-06-13 23:00 | 31.7433 | 29.6067 | 2.1367 | 12.0997 | 23.2033 | 180.7909 | 79.8289 | 10.1711 | -179.2614 | 139.8226 | 0 | 22.205 | 0.53125 | 0.55208 | 4.2159 | 26.4209 | 3.3 | 4.1257 | 1.0835 | 0.023474
2015-06-14 | 31.8 | 30.06 | 1.74 | 9.4345 | 23.2057 | -164.2112 | 79.3721 | 10.6279 | -165.2594 | 136.9653 | 0 | 22.545 | 0.53 | 0.55 | 4.2135 | 26.7585 | 3.1 | 3.9362 | 1.0843 | 0.023791
2015-06-14 01:00 | 38.94 | 36.2667 | 2.6733 | 12.9861 | 23.2081 | -149.2134 | 78.1201 | 11.8799 | -151.2676 | 129.8067 | 0 | 27.2 | 0.52875 | 0.54792 | 5.1474 | 32.3474 | 3.3 | 4.3109 | 1.0828 | 0.02872
2015-06-14 02:00 | 46.08 | 42.4733 | 3.6067 | 15.0642 | 23.2106 | -134.2156 | 76.1477 | 13.8523 | -137.2779 | 119.8687 | 0 | 31.855 | 0.5275 | 0.54583 | 6.0768 | 37.9318 | 3.3 | 4.4854 | 1.0821 | 0.033656
2015-06-14 03:00 | 53.22 | 48.68 | 4.54 | 16.0523 | 23.213 | -119.2178 | 73.5711 | 16.4289 | -123.2527 | 108.3046 | 0 | 36.51 | 0.52625 | 0.54375 | 7.0018 | 43.5118 | 3.5 | 4.8597 | 1.0806 | 0.038554
2015-06-14 04:00 | 107.63 | 65.92 | 41.71 | 125.2093 | 23.2154 | -104.2199 | 70.5416 | 19.4584 | -109.1198 | 95.7909 | 0 | 49.44 | 0.525 | 0.54167 | 14.1264 | 63.5664 | 3.6 | 5.5865 | 1.0777 | 0.056172
2015-06-14 05:00 | 162.04 | 83.16 | 78.88 | 203.8848 | 23.2178 | -89.2221 | 67.2392 | 22.7608 | -94.7743 | 82.7052 | 25.8883 | 62.37 | 0.52375 | 0.53958 | 21.2171 | 109.4754 | 3.9 | 7.3211 | 1.0707 | 0.096118
2015-06-14 06:00 | 216.45 | 100.4 | 116.05 | 263.4781 | 23.2201 | -74.2243 | 63.8671 | 26.1329 | -80.0906 | 69.2661 | 93.2785 | 75.3 | 0.5225 | 0.5375 | 28.2738 | 196.8523 | 4 | 10.1516 | 1.0594 | 0.17101
2015-06-14 07:00 | 300.0767 | 136.9267 | 163.15 | 332.8354 | 23.2225 | -59.2265 | 60.6474 | 29.3526 | -64.9423 | 55.6122 | 187.9824 | 102.695 | 0.52125 | 0.53542 | 39.1037 | 329.7812 | 3.7 | 14.0057 | 1.044 | 0.28231
2015-06-14 08:00 | 383.7033 | 173.4533 | 210.25 | 394.6989 | 23.2249 | -44.2287 | 57.813 | 32.187 | -49.2356 | 41.8488 | 294.0145 | 130.09 | 0.52 | 0.53333 | 49.8814 | 473.9859 | 3.3 | 18.1121 | 1.0276 | 0.39938
2015-06-14 09:00 | 467.33 | 209.98 | 257.35 | 455.4319 | 23.2272 | -29.2308 | 55.593 | 34.407 | -32.9502 | 28.102 | 401.7411 | 157.485 | 0.51875 | 0.53125 | 60.6069 | 619.833 | 2.7 | 22.0698 | 1.0117 | 0.51422
2015-06-14 10:00 | 465.9 | 208.4267 | 257.4733 | 440.028 | 23.2295 | -14.233 | 54.1879 | 35.8121 | -16.1771 | 14.7487 | 425.5299 | 156.32 | 0.5175 | 0.52917 | 60.2758 | 642.1257 | 2.9 | 22.9664 | 1.0081 | 0.53083
2015-06-14 11:00 | 464.47 | 206.8733 | 257.5967 | 435.4937 | 23.2319 | 0.7648 | 53.7361 | 36.2639 | 0.87163 | 6.3062 | 432.8586 | 155.155 | 0.51625 | 0.52708 | 59.9457 | 647.9592 | 3.3 | 23.5487 | 1.0058 | 0.53441
2015-06-14 12:00 | 463.04 | 205.32 | 257.72 | 441.4804 | 23.2342 | 15.7626 | 54.2843 | 35.7157 | 17.9053 | 16.0601 | 424.2504 | 153.99 | 0.515 | 0.525 | 59.6164 | 637.8568 | 3.5 | 23.433 | 1.0063 | 0.52632
2015-06-14 13:00 | 423.49 | 209.03 | 214.46 | 381.3067 | 23.2365 | 30.7604 | 55.7757 | 34.2243 | 34.6376 | 29.4983 | 331.8782 | 156.7725 | 0.51375 | 0.52292 | 54.392 | 543.0427 | 3.7 | 20.6701 | 1.0173 | 0.45301
2015-06-14 14:00 | 383.94 | 212.74 | 171.2 | 323.645 | 23.2387 | 45.7582 | 58.0638 | 31.9362 | 50.8676 | 43.2543 | 235.717 | 159.555 | 0.5125 | 0.52083 | 49.1923 | 444.4643 | 4 | 17.8895 | 1.0284 | 0.37483
2015-06-14 15:00 | 344.39 | 216.45 | 127.94 | 263.4319 | 23.241 | 60.7561 | 60.9439 | 29.0561 | 66.5165 | 57.0096 | 143.4384 | 162.3375 | 0.51125 | 0.51875 | 44.0173 | 349.7932 | 3.5 | 14.431 | 1.0423 | 0.29896
2015-06-14 16:00 | 304.4667 | 182.22 | 122.2467 | 280.7283 | 23.2433 | 75.7539 | 64.1853 | 25.8147 | 81.6137 | 70.6442 | 93.0429 | 136.665 | 0.51 | 0.51667 | 38.8195 | 268.5274 | 3.8 | 12.1915 | 1.0512 | 0.23147
2015-06-14 17:00 | 264.5433 | 147.99 | 116.5533 | 305.2842 | 23.2455 | 90.7517 | 67.5556 | 22.4444 | 96.258 | 84.0511 | 31.6403 | 110.9925 | 0.50875 | 0.51458 | 33.6466 | 176.2794 | 3.4 | 8.9087 | 1.0644 | 0.15385
2015-06-14 18:00 | 224.62 | 113.76 | 110.86 | 337.6821 | 23.2477 | 105.7495 | 70.8346 | 19.1654 | 110.5768 | 97.0859 | 0 | 85.32 | 0.5075 | 0.5125 | 28.4987 | 113.8187 | 3.2 | 6.7568 | 1.073 | 0.10014
2015-06-14 19:00 | 181.9033 | 98.78 | 83.1233 | 298.3171 | 23.25 | 120.7473 | 73.8209 | 16.1791 | 124.6943 | 109.5176 | 0 | 74.085 | 0.50625 | 0.51042 | 23.0221 | 97.1071 | 3.3 | 6.3346 | 1.0747 | 0.085573
2015-06-14 20:00 | 139.1867 | 83.8 | 55.3867 | 234.4874 | 23.2522 | 135.7451 | 76.3374 | 13.6626 | 138.7123 | 120.9454 | 0 | 62.85 | 0.505 | 0.50833 | 17.5723 | 80.4223 | 2.8 | 5.3132 | 1.0787 | 0.071139
2015-06-14 21:00 | 96.47 | 68.82 | 27.65 | 135.6209 | 23.2544 | 150.7429 | 78.2362 | 11.7638 | 152.6994 | 130.6517 | 0 | 51.615 | 0.50375 | 0.50625 | 12.1492 | 63.7642 | 2.6 | 4.5926 | 1.0816 | 0.056555
2015-06-14 22:00 | 78.6367 | 59.5633 | 19.0733 | 103.7343 | 23.2566 | 165.7407 | 79.4049 | 10.5951 | 166.6899 | 137.4308 | 0 | 44.6725 | 0.5025 | 0.50417 | 9.8787 | 54.5512 | 2.8 | 4.5047 | 1.082 | 0.048399
2015-06-14 23:00 | 60.8033 | 50.3067 | 10.4967 | 59.1234 | 23.2587 | 180.7385 | 79.7736 | 10.2264 | -179.3106 | 139.7681 | 0 | 37.73 | 0.50125 | 0.50208 | 7.6194 | 45.3494 | 2.7 | 4.1172 | 1.0835 | 0.040293
2015-06-15 | 42.97 | 41.05 | 1.92 | 10.3603 | 23.2609 | -164.2637 | 79.32 | 10.68 | -165.3119 | 136.9326 | 0 | 30.7875 | 0.5 | 0.5 | 5.3712 | 36.1587 | 2.5 | 3.63 | 1.0855 | 0.032185
2015-06-15 01:00 | 65.6267 | 55.1767 | 10.45 | 50.5577 | 23.263 | -149.2659 | 78.0713 | 11.9287 | -151.3231 | 129.7951 | 0 | 41.3825 | 0.49875 | 0.49792 | 8.1828 | 49.5653 | 3 | 4.5489 | 1.0818 | 0.043968
2015-06-15 02:00 | 88.2833 | 69.3033 | 18.98 | 79.0185 | 23.2652 | -134.2681 | 76.1018 | 13.8982 | -137.3363 | 119.8733 | 0 | 51.9775 | 0.4975 | 0.49583 | 10.9802 | 62.9577 | 3.1 | 5.0674 | 1.0797 | 0.055741
2015-06-15 03:00 | 110.94 | 83.43 | 27.51 | 97.0198 | 23.2673 | -119.2703 | 73.5278 | 16.4722 | -123.3136 | 108.3212 | 0 | 62.5725 | 0.49625 | 0.49375 | 13.7635 | 76.336 | 3.2 | 5.5855 | 1.0777 | 0.067457
2015-06-15 04:00 | 135.08 | 103.5833 | 31.4967 | 94.357 | 23.2694 | -104.2725 | 70.5002 | 19.4998 | -109.1829 | 95.8163 | 0 | 77.6875 | 0.495 | 0.49167 | 16.7161 | 94.4036 | 3.1 | 6.0501 | 1.0758 | 0.083279
2015-06-15 05:00 | 159.22 | 123.7367 | 35.4833 | 91.5619 | 23.2715 | -89.2747 | 67.1989 | 22.8011 | -94.8394 | 82.7375 | 11.5749 | 92.8025 | 0.49375 | 0.48958 | 19.6537 | 124.0311 | 3.2 | 7.076 | 1.0717 | 0.109
2015-06-15 06:00 | 183.36 | 143.89 | 39.47 | 89.4841 | 23.2736 | -74.2769 | 63.8269 | 26.1731 | -80.1572 | 69.3042 | 31.6242 | 107.9175 | 0.4925 | 0.4875 | 22.5762 | 162.1179 | 3.4 | 8.4662 | 1.0661 | 0.14173
2015-06-15 07:00 | 209.4667 | 169.12 | 40.3467 | 82.2047 | 23.2757 | -59.2791 | 60.6063 | 29.3937 | -65.01 | 55.6555 | 46.3772 | 126.84 | 0.49125 | 0.48542 | 25.7251 | 198.9423 | 3.5 | 9.7169 | 1.0611 | 0.17311
2015-06-15 08:00 | 235.5733 | 194.35 | 41.2233 | 77.2958 | 23.2778 | -44.2813 | 57.77 | 32.23 | -49.3034 | 41.8973 | 57.5345 | 145.7625 | 0.49 | 0.48333 | 28.8577 | 232.1548 | 3.3 | 10.5548 | 1.0578 | 0.20137
2015-06-15 09:00 | 261.68 | 219.58 | 42.1 | 74.4177 | 23.2798 | -29.2835 | 55.5473 | 34.4527 | -33.0169 | 28.1569 | 65.611 | 164.685 | 0.48875 | 0.48125 | 31.974 | 262.27 | 2.8 | 10.9959 | 1.056 | 0.22711
2015-06-15 10:00 | 274.75 | 229.88 | 44.87 | 76.5933 | 23.2819 | -14.2857 | 54.139 | 35.861 | -16.2412 | 14.8135 | 74.0476 | 172.41 | 0.4875 | 0.47917 | 33.4852 | 279.9428 | 2.8 | 11.5482 | 1.0538 | 0.2419
2015-06-15 11:00 | 287.82 | 240.18 | 47.64 | 80.4404 | 23.2839 | 0.71206 | 53.6839 | 36.3161 | 0.81174 | 6.3525 | 79.9465 | 180.135 | 0.48625 | 0.47708 | 34.9881 | 295.0696 | 2.9 | 12.1209 | 1.0515 | 0.25442
2015-06-15 12:00 | 300.89 | 250.48 | 50.41 | 86.2379 | 23.2859 | 15.7098 | 54.2291 | 35.7709 | 17.8505 | 16.0324 | 82.8837 | 187.86 | 0.485 | 0.475 | 36.4829 | 307.2266 | 3.2 | 12.8008 | 1.0488 | 0.26422
2015-06-15 13:00 | 292.4267 | 229.6833 | 62.7433 | 111.3918 | 23.2879 | 30.7076 | 55.7179 | 34.2821 | 34.5881 | 29.456 | 96.9925 | 172.2625 | 0.48375 | 0.47292 | 35.3653 | 304.6204 | 2.8 | 12.3194 | 1.0507 | 0.26246
2015-06-15 14:00 | 283.9633 | 208.8867 | 75.0767 | 141.6927 | 23.2899 | 45.7054 | 58.0043 | 31.9957 | 50.823 | 43.2055 | 103.2803 | 156.665 | 0.4825 | 0.47083 | 34.2531 | 294.1984 | 2.1 | 11.2937 | 1.0548 | 0.25447
2015-06-15 15:00 | 275.5 | 188.09 | 87.41 | 179.6381 | 23.2919 | 60.7032 | 60.8833 | 29.1167 | 66.4755 | 56.9562 | 97.953 | 141.0675 | 0.48125 | 0.46875 | 33.1461 | 272.1666 | 2.6 | 11.1052 | 1.0556 | 0.23558
2015-06-15 16:00 | 252.1867 | 155.83 | 96.3567 | 220.7893 | 23.2939 | 75.701 | 64.1244 | 25.8756 | 81.575 | 70.5871 | 73.3846 | 116.8725 | 0.48 | 0.46667 | 30.2624 | 220.5195 | 2.5 | 9.3912 | 1.0624 | 0.19212
2015-06-15 17:00 | 228.8733 | 123.57 | 105.3033 | 275.1123 | 23.2958 | 90.6988 | 67.4949 | 22.5051 | 96.2203 | 83.9905 | 28.8023 | 92.6775 | 0.47875 | 0.46458 | 27.3933 | 148.8731 | 2.9 | 7.5523 | 1.0698 | 0.1306
2015-06-15 18:00 | 205.56 | 91.31 | 114.25 | 346.9649 | 23.2978 | 105.6966 | 70.7747 | 19.2253 | 110.5389 | 97.0221 | 0 | 68.4825 | 0.4775 | 0.4625 | 24.5387 | 93.0212 | 3.1 | 6.0069 | 1.076 | 0.082072
2015-06-15 19:00 | 171.16 | 82.66 | 88.5 | 316.4984 | 23.2997 | 120.6943 | 73.7623 | 16.2377 | 124.6552 | 109.4509 | 0 | 61.995 | 0.47625 | 0.46042 | 20.3787 | 82.3737 | 3.2 | 5.7742 | 1.0769 | 0.072741
2015-06-15 20:00 | 136.76 | 74.01 | 62.75 | 264.5839 | 23.3017 | 135.6921 | 76.2807 | 13.7193 | 138.6711 | 120.8765 | 0 | 55.5075 | 0.475 | 0.45833 | 16.2402 | 71.7477 | 3.3 | 5.5421 | 1.0778 | 0.063412
2015-06-15 21:00 | 102.36 | 65.36 | 37 | 180.6588 | 23.3036 | 150.6899 | 78.1819 | 11.8181 | 152.6557 | 130.5829 | 0 | 49.02 | 0.47375 | 0.45625 | 12.1233 | 61.1433 | 3.2 | 5.1107 | 1.0796 | 0.054126
2015-06-15 22:00 | 88.1033 | 62.9733 | 25.13 | 136.0201 | 23.3055 | 165.6877 | 79.3533 | 10.6467 | 166.6432 | 137.368 | 0 | 47.23 | 0.4725 | 0.45417 | 10.4072 | 57.6372 | 2.9 | 4.7012 | 1.0812 | 0.0511
2015-06-15 23:00 | 73.8467 | 60.5867 | 13.26 | 74.3394 | 23.3074 | 180.6855 | 79.7251 | 10.2749 | -179.3602 | 139.7204 | 0 | 45.44 | 0.47125 | 0.45208 | 8.7001 | 54.1401 | 2.3 | 3.9919 | 1.084 | 0.048125
2015-06-16 | 59.59 | 58.2 | 1.39 | 7.4691 | 23.3092 | -164.3167 | 79.2748 | 10.7252 | -165.3644 | 136.9063 | 0 | 43.65 | 0.47 | 0.45 | 7.0018 | 50.6518 | 1.9 | 3.4829 | 1.0861 | 0.045109
2015-06-16 01:00 | 72.58 | 69.34 | 3.24 | 15.6211 | 23.3111 | -149.319 | 78.0293 | 11.9707 | -151.3784 | 129.789 | 0 | 52.005 | 0.46875 | 0.44792 | 8.5055 | 60.5105 | 1.6 | 3.491 | 1.086 | 0.053888
2015-06-16 02:00 | 85.57 | 80.48 | 5.09 | 21.1328 | 23.313 | -134.3212 | 76.0628 | 13.9372 | -137.394 | 119.8825 | 0 | 60.36 | 0.4675 | 0.44583 | 10.001 | 70.361 | 1.7 | 3.8988 | 1.0844 | 0.062566
2015-06-16 03:00 | 98.56 | 91.62 | 6.94 | 24.4228 | 23.3148 | -119.3234 | 73.4913 | 16.5087 | -123.3736 | 108.3414 | 0 | 68.715 | 0.46625 | 0.44375 | 11.4884 | 80.2034 | 1.4 | 3.9064 | 1.0844 | 0.071316
2015-06-16 04:00 | 120.1167 | 113.6833 | 6.4333 | 19.24 | 23.3166 | -104.3256 | 70.4656 | 19.5344 | -109.2449 | 95.8446 | 0 | 85.2625 | 0.465 | 0.44167 | 13.9636 | 99.2261 | 1.9 | 5.0008 | 1.08 | 0.087874
2015-06-16 05:00 | 141.6733 | 135.7467 | 5.9267 | 15.272 | 23.3184 | -89.3279 | 67.1653 | 22.8347 | -94.9032 | 82.7721 | 1.9215 | 101.81 | 0.46375 | 0.43958 | 16.4253 | 120.1567 | 2.5 | 6.2549 | 1.075 | 0.10592
2015-06-16 06:00 | 163.23 | 157.81 | 5.42 | 12.2733 | 23.3202 | -74.3301 | 63.7935 | 26.2065 | -80.2226 | 69.3441 | 4.3295 | 118.3575 | 0.4625 | 0.4375 | 18.8735 | 141.5605 | 2 | 6.4238 | 1.0743 | 0.1247
2015-06-16 07:00 | 195.9667 | 187.6367 | 8.33 | 16.954 | 23.322 | -59.3323 | 60.572 | 29.428 | -65.0765 | 55.7 | 9.554 | 140.7275 | 0.46125 | 0.43542 | 22.5974 | 172.8789 | 3.1 | 8.5025 | 1.066 | 0.15112
2015-06-16 08:00 | 228.7033 | 217.4633 | 11.24 | 21.0545 | 23.3238 | -44.3346 | 57.7339 | 32.2661 | -49.3704 | 41.9464 | 15.6597 | 163.0975 | 0.46 | 0.43333 | 26.3009 | 205.0581 | 2.4 | 8.8081 | 1.0648 | 0.17904
2015-06-16 09:00 | 261.44 | 247.29 | 14.15 | 24.9875 | 23.3256 | -29.3368 | 55.5085 | 34.4915 | -33.0831 | 28.2114 | 22.0192 | 185.4675 | 0.45875 | 0.43125 | 29.9839 | 237.4706 | 2.4 | 9.821 | 1.0607 | 0.20655
2015-06-16 10:00 | 268.7767 | 253.3067 | 15.47 | 26.3806 | 23.3274 | -14.339 | 54.097 | 35.903 | -16.3053 | 14.8761 | 25.4964 | 189.98 | 0.4575 | 0.42917 | 30.7413 | 246.2178 | 3.4 | 11.0943 | 1.0556 | 0.21313
2015-06-16 11:00 | 276.1133 | 259.3233 | 16.79 | 28.3195 | 23.3291 | 0.65875 | 53.6385 | 36.3615 | 0.75116 | 6.3924 | 28.1434 | 194.4925 | 0.45625 | 0.42708 | 31.4942 | 254.1301 | 3.8 | 11.7416 | 1.053 | 0.21944
2015-06-16 12:00 | 283.45 | 265.34 | 18.11 | 30.945 | 23.3308 | 15.6565 | 54.1806 | 35.8194 | 17.7945 | 16.0022 | 29.7459 | 199.005 | 0.455 | 0.425 | 32.2424 | 260.9933 | 3.6 | 11.756 | 1.053 | 0.22535
2015-06-16 13:00 | 274.4167 | 235.83 | 38.5867 | 68.4157 | 23.3326 | 30.6543 | 55.6669 | 34.3331 | 34.5369 | 29.4126 | 59.5974 | 176.8725 | 0.45375 | 0.42292 | 31.1291 | 267.599 | 4 | 12.3625 | 1.0506 | 0.23052
2015-06-16 14:00 | 265.3833 | 206.32 | 59.0633 | 111.3063 | 23.3343 | 45.6521 | 57.9515 | 32.0485 | 50.7762 | 43.1562 | 81.197 | 154.74 | 0.4525 | 0.42083 | 30.0215 | 265.9585 | 4.2 | 12.5112 | 1.05 | 0.22898
2015-06-16 15:00 | 256.35 | 176.81 | 79.54 | 163.1884 | 23.336 | 60.6498 | 60.8294 | 29.1706 | 66.4321 | 56.9031 | 89.1102 | 132.6075 | 0.45125 | 0.41875 | 28.9195 | 250.6372 | 6.4 | 14.2324 | 1.0431 | 0.21437
2015-06-16 16:00 | 220.9533 | 152.8667 | 68.0867 | 155.7075 | 23.3376 | 75.6476 | 64.07 | 25.93 | 81.5339 | 70.5308 | 51.8974 | 114.65 | 0.45 | 0.41667 | 24.8573 | 191.4047 | 6.5 | 12.4814 | 1.0501 | 0.16481
2015-06-16 17:00 | 185.5567 | 128.9233 | 56.6333 | 147.6219 | 23.3393 | 90.6453 | 67.4408 | 22.5592 | 96.1803 | 83.9314 | 15.6064 | 96.6925 | 0.44875 | 0.41458 | 20.8171 | 133.116 | 4.8 | 8.9599 | 1.0642 | 0.11616
2015-06-16 18:00 | 150.16 | 104.98 | 45.18 | 136.8416 | 23.341 | 105.6431 | 70.7214 | 19.2786 | 110.4988 | 96.9604 | 0 | 78.735 | 0.4475 | 0.4125 | 16.7992 | 95.5341 | 5 | 7.9854 | 1.0681 | 0.08367
2015-06-16 19:00 | 127.1033 | 89.1933 | 37.91 | 135.1551 | 23.3426 | 120.6409 | 73.7104 | 16.2896 | 124.6141 | 109.3871 | 0 | 66.895 | 0.44625 | 0.41042 | 14.18 | 81.075 | 4.3 | 6.8336 | 1.0727 | 0.071312
2015-06-16 20:00 | 104.0467 | 73.4067 | 30.64 | 128.7325 | 23.3443 | 135.6386 | 76.2307 | 13.7693 | 138.6283 | 120.8115 | 0 | 55.055 | 0.445 | 0.40833 | 11.5752 | 66.6302 | 4.1 | 6.1822 | 1.0753 | 0.058749
2015-06-16 21:00 | 80.99 | 57.62 | 23.37 | 113.6567 | 23.3459 | 150.6364 | 78.1342 | 11.8658 | 152.6106 | 130.5193 | 0 | 43.215 | 0.44375 | 0.40625 | 8.9848 | 52.1998 | 4.4 | 6.0312 | 1.0759 | 0.046052
2015-06-16 22:00 | 106.4567 | 48.3 | 58.1567 | 313.4792 | 23.3475 | 165.6342 | 79.3085 | 10.6915 | 166.5957 | 137.3114 | 0 | 36.225 | 0.4425 | 0.40417 | 11.7768 | 48.0018 | 3.5 | 5.0001 | 1.08 | 0.04251
2015-06-16 23:00 | 131.9233 | 38.98 | 92.9433 | 518.9875 | 23.3491 | 180.6319 | 79.6835 | 10.3165 | -179.4103 | 139.6795 | 0 | 29.235 | 0.44125 | 0.40208 | 14.5528 | 43.7878 | 3.2 | 4.5684 | 1.0817 | 0.03884
2015-06-17 | 157.39 | 29.66 | 127.73 | 683.9386 | 23.3507 | -164.3703 | 79.2364 | 10.7636 | -165.417 | 136.8865 | 0 | 22.245 | 0.44 | 0.4 | 17.3129 | 39.5579 | 3.2 | 4.4362 | 1.0823 | 0.035106
2015-06-17 01:00 | 187.7133 | 40.01 | 147.7033 | 710.0753 | 23.3523 | -149.3726 | 77.9942 | 12.0058 | -151.4333 | 129.7884 | 0 | 30.0075 | 0.43875 | 0.39792 | 20.5898 | 50.5973 | 3.2 | 4.7812 | 1.0809 | 0.044845
2015-06-17 02:00 | 218.0367 | 50.36 | 167.6767 | 694.5952 | 23.3539 | -134.3748 | 76.0307 | 13.9693 | -137.451 | 119.8962 | 0 | 37.77 | 0.4375 | 0.39583 | 23.8478 | 61.6178 | 4.3 | 6.2256 | 1.0751 | 0.054321
2015-06-17 03:00 | 248.36 | 60.71 | 187.65 | 659.2151 | 23.3554 | -119.3771 | 73.4617 | 16.5383 | -123.4325 | 108.3652 | 0 | 45.5325 | 0.43625 | 0.39375 | 27.0868 | 72.6193 | 3.8 | 6.0694 | 1.0757 | 0.064057
2015-06-17 04:00 | 295.16 | 71.5867 | 223.5733 | 667.7229 | 23.357 | -104.3793 | 70.4378 | 19.5622 | -109.3056 | 95.8758 | 0 | 53.69 | 0.435 | 0.39167 | 32.0986 | 85.7886 | 3.9 | 6.5809 | 1.0737 | 0.07553
2015-06-17 05:00 | 341.96 | 82.4633 | 259.4967 | 667.9387 | 23.3585 | -89.3815 | 67.1386 | 22.8614 | -94.9657 | 82.809 | 83.611 | 61.8475 | 0.43375 | 0.38958 | 37.0813 | 182.5398 | 3.7 | 9.4044 | 1.0624 | 0.15902
2015-06-17 06:00 | 388.76 | 93.34 | 295.42 | 668.3343 | 23.36 | -74.3838 | 63.7669 | 26.2331 | -80.2867 | 69.3856 | 235.3055 | 70.005 | 0.4325 | 0.3875 | 42.0347 | 347.3452 | 4.6 | 15.4545 | 1.0382 | 0.2957
2015-06-17 07:00 | 418.53 | 110.5533 | 307.9767 | 626.2914 | 23.3615 | -59.386 | 60.5446 | 29.4554 | -65.1418 | 55.7456 | 352.52 | 82.915 | 0.43125 | 0.38542 | 45.1228 | 480.5578 | 4.3 | 19.3174 | 1.0227 | 0.40301
2015-06-17 08:00 | 448.3 | 127.7667 | 320.5333 | 599.9295 | 23.363 | -44.3883 | 57.7046 | 32.2954 | -49.4364 | 41.9959 | 445.8629 | 95.825 | 0.43 | 0.38333 | 48.1922 | 589.8802 | 4.6 | 23.0338 | 1.0079 | 0.48751
2015-06-17 09:00 | 478.07 | 144.98 | 333.09 | 587.7266 | 23.3645 | -29.3905 | 55.4766 | 34.5234 | -33.1488 | 28.2654 | 517.6481 | 108.735 | 0.42875 | 0.38125 | 51.2431 | 677.6262 | 4.2 | 25.3758 | 0.9985 | 0.55482
2015-06-17 10:00 | 461.51 | 157.3267 | 304.1833 | 518.2781 | 23.366 | -14.3928 | 54.0619 | 35.9381 | -16.3694 | 14.9366 | 500.7664 | 117.995 | 0.4275 | 0.37917 | 49.3239 | 668.0852 | 4.7 | 25.5777 | 0.99769 | 0.54656
2015-06-17 11:00 | 444.95 | 169.6733 | 275.2767 | 463.8833 | 23.3674 | 0.60497 | 53.6001 | 36.3999 | 0.68997 | 6.4259 | 460.9689 | 127.255 | 0.42625 | 0.37708 | 47.415 | 635.6389 | 4.9 | 24.7637 | 1.0009 | 0.52172
2015-06-17 12:00 | 428.39 | 182.02 | 246.37 | 420.555 | 23.3689 | 15.6027 | 54.139 | 35.861 | 17.7372 | 15.9694 | 404.3252 | 136.515 | 0.425 | 0.375 | 45.5164 | 586.3566 | 5.4 | 23.7236 | 1.0051 | 0.48327
2015-06-17 13:00 | 395.1033 | 171.7433 | 223.36 | 395.5792 | 23.3703 | 30.6005 | 55.6227 | 34.3773 | 34.484 | 29.368 | 344.7425 | 128.8075 | 0.42375 | 0.37292 | 41.8563 | 515.4062 | 5.5 | 21.6064 | 1.0136 | 0.42837
2015-06-17 14:00 | 361.8167 | 161.4667 | 200.35 | 377.0793 | 23.3717 | 45.5982 | 57.9053 | 32.0947 | 50.7273 | 43.1066 | 275.2992 | 121.1 | 0.4225 | 0.37083 | 38.2169 | 434.6161 | 6 | 19.5818 | 1.0217 | 0.36411
2015-06-17 15:00 | 328.53 | 151.19 | 177.34 | 363.3023 | 23.3731 | 60.596 | 60.782 | 29.218 | 66.3865 | 56.8502 | 198.6643 | 113.3925 | 0.42125 | 0.36875 | 34.5983 | 346.6551 | 5.5 | 16.333 | 1.0347 | 0.29411
2015-06-17 16:00 | 284.9367 | 131.73 | 153.2067 | 349.7687 | 23.3745 | 75.5937 | 64.0222 | 25.9778 | 81.4905 | 70.4754 | 116.897 | 98.7975 | 0.42 | 0.36667 | 29.9184 | 245.6128 | 5.6 | 13.2754 | 1.0469 | 0.21085
2015-06-17 17:00 | 241.3433 | 112.27 | 129.0733 | 335.7749 | 23.3759 | 90.5915 | 67.3932 | 22.6068 | 96.138 | 83.8738 | 35.8333 | 84.2025 | 0.41875 | 0.36458 | 25.2656 | 145.3014 | 5.3 | 9.8407 | 1.0606 | 0.12637
2015-06-17 18:00 | 197.75 | 92.81 | 104.94 | 317.1041 | 23.3773 | 105.5892 | 70.6746 | 19.3254 | 110.4566 | 96.901 | 0 | 69.6075 | 0.4175 | 0.3625 | 20.6402 | 90.2477 | 4.6 | 7.4202 | 1.0703 | 0.079207
2015-06-17 19:00 | 168.0633 | 79.8667 | 88.1967 | 313.5867 | 23.3787 | 120.587 | 73.6651 | 16.3349 | 124.5712 | 109.3263 | 0 | 59.9 | 0.41625 | 0.36042 | 17.4891 | 77.3891 | 4 | 6.4184 | 1.0743 | 0.068176
2015-06-17 20:00 | 138.3767 | 66.9233 | 71.4533 | 299.2847 | 23.38 | 135.5847 | 76.1874 | 13.8126 | 138.584 | 120.7505 | 0 | 50.1925 | 0.415 | 0.35833 | 14.3566 | 64.5491 | 3.9 | 5.9172 | 1.0763 | 0.05697
2015-06-17 21:00 | 108.69 | 53.98 | 54.71 | 265.175 | 23.3814 | 150.5824 | 78.0934 | 11.9066 | 152.5645 | 130.4608 | 0 | 40.485 | 0.41375 | 0.35625 | 11.2426 | 51.7276 | 3.2 | 4.8165 | 1.0807 | 0.045841
2015-06-17 22:00 | 96.1033 | 56.8 | 39.3033 | 211.1146 | 23.3827 | 165.5802 | 79.2706 | 10.7294 | 166.5474 | 137.2611 | 0 | 42.6 | 0.4125 | 0.35417 | 9.9107 | 52.5107 | 3.7 | 5.341 | 1.0786 | 0.046445
2015-06-17 23:00 | 83.5167 | 59.62 | 23.8967 | 132.9937 | 23.384 | 180.5779 | 79.6487 | 10.3513 | -179.4608 | 139.6454 | 0 | 44.715 | 0.41125 | 0.35208 | 8.5866 | 53.3016 | 2.9 | 4.5657 | 1.0817 | 0.04728
2015-06-18 | 70.93 | 62.44 | 8.49 | 45.3293 | 23.3853 | -164.4243 | 79.205 | 10.795 | -165.4696 | 136.8731 | 0 | 46.83 | 0.41 | 0.35 | 7.2703 | 54.1003 | 2.9 | 4.5906 | 1.0816 | 0.047984
2015-06-18 01:00 | 85.82 | 79.57 | 6.25 | 29.977 | 23.3866 | -149.4266 | 77.9659 | 12.0341 | -151.4878 | 129.7933 | 0 | 59.6775 | 0.40875 | 0.34792 | 8.7697 | 68.4472 | 2.6 | 4.739 | 1.081 | 0.060675
2015-06-18 02:00 | 100.71 | 96.7 | 4.01 | 16.5819 | 23.3879 | -134.4288 | 76.0054 | 13.9946 | -137.5072 | 119.9144 | 0 | 72.525 | 0.4075 | 0.34583 | 10.2598 | 82.7848 | 3.3 | 5.887 | 1.0765 | 0.073073
2015-06-18 03:00 | 115.6 | 113.83 | 1.77 | 6.2097 | 23.3891 | -119.4311 | 73.4388 | 16.5612 | -123.4904 | 108.3926 | 0 | 85.3725 | 0.40625 | 0.34375 | 11.7406 | 97.1131 | 3 | 6.0348 | 1.0759 | 0.085674
2015-06-18 04:00 | 143.31 | 137.11 | 6.2 | 18.4978 | 23.3904 | -104.4334 | 70.4168 | 19.5832 | -109.3651 | 95.9099 | 0 | 102.8325 | 0.405 | 0.34167 | 14.5101 | 117.3426 | 3.4 | 7.067 | 1.0717 | 0.10312
2015-06-18 05:00 | 171.02 | 160.39 | 10.63 | 27.3388 | 23.3916 | -89.4356 | 67.1186 | 22.8814 | -95.0268 | 82.848 | 3.4037 | 120.2925 | 0.40375 | 0.33958 | 17.2623 | 140.9586 | 3.3 | 7.705 | 1.0692 | 0.12358
2015-06-18 06:00 | 198.73 | 183.67 | 15.06 | 34.0466 | 23.3929 | -74.4379 | 63.747 | 26.253 | -80.3492 | 69.4286 | 11.9631 | 137.7525 | 0.4025 | 0.3375 | 19.9972 | 169.7128 | 2.7 | 8.0035 | 1.068 | 0.14863
2015-06-18 07:00 | 232.1233 | 194.59 | 37.5333 | 76.2778 | 23.3941 | -59.4401 | 60.5239 | 29.4761 | -65.2058 | 55.7921 | 42.8832 | 145.9425 | 0.40125 | 0.33542 | 23.2849 | 212.1106 | 3.3 | 9.9285 | 1.0603 | 0.18442
2015-06-18 08:00 | 265.5167 | 205.51 | 60.0067 | 112.2425 | 23.3953 | -44.4424 | 57.6821 | 32.3179 | -49.5012 | 42.0458 | 83.3524 | 154.1325 | 0.4 | 0.33333 | 26.5517 | 264.0366 | 2.5 | 10.7511 | 1.057 | 0.22885
2015-06-18 09:00 | 298.91 | 216.43 | 82.48 | 145.4409 | 23.3965 | -29.4447 | 55.4515 | 34.5485 | -33.2138 | 28.3189 | 128.0347 | 162.3225 | 0.39875 | 0.33125 | 29.7976 | 320.1548 | 2.5 | 12.5048 | 1.05 | 0.27565
2015-06-18 10:00 | 299.2533 | 220.86 | 78.3933 | 133.4787 | 23.3977 | -14.4469 | 54.0337 | 35.9663 | -16.4333 | 14.9947 | 128.9337 | 165.645 | 0.3975 | 0.32917 | 29.7383 | 324.317 | 2.6 | 12.7349 | 1.0491 | 0.27899
2015-06-18 11:00 | 299.5967 | 225.29 | 74.3067 | 125.1246 | 23.3989 | 0.5508 | 53.5685 | 36.4315 | 0.6283 | 6.4529 | 124.3319 | 168.9675 | 0.39625 | 0.32708 | 29.6788 | 322.9782 | 2.8 | 12.8931 | 1.0484 | 0.27767
2015-06-18 12:00 | 299.94 | 229.72 | 70.22 | 119.7654 | 23.4 | 15.5485 | 54.1042 | 35.8958 | 17.6789 | 15.9341 | 115.1638 | 172.29 | 0.395 | 0.325 | 29.6191 | 317.0729 | 4.3 | 14.2085 | 1.0432 | 0.27122
2015-06-18 13:00 | 308.3867 | 236.41 | 71.9767 | 127.3517 | 23.4012 | 30.5463 | 55.5852 | 34.4148 | 34.4295 | 29.3223 | 111.0352 | 177.3075 | 0.39375 | 0.32292 | 30.3568 | 318.6995 | 3.4 | 13.3594 | 1.0466 | 0.2735
2015-06-18 14:00 | 316.8333 | 243.1 | 73.7333 | 138.6215 | 23.4023 | 45.544 | 57.8658 | 32.1342 | 50.6765 | 43.0568 | 101.2876 | 182.325 | 0.3925 | 0.32083 | 31.0893 | 314.7018 | 3.8 | 13.6344 | 1.0455 | 0.26979
2015-06-18 15:00 | 325.28 | 249.79 | 75.49 | 154.4542 | 23.4034 | 60.5417 | 60.7413 | 29.2587 | 66.3388 | 56.7978 | 84.5784 | 187.3425 | 0.39125 | 0.31875 | 31.8164 | 303.7374 | 3.1 | 12.5918 | 1.0496 | 0.26143
2015-06-18 16:00 | 279.0833 | 212.85 | 66.2333 | 150.987 | 23.4045 | 75.5395 | 63.981 | 26.019 | 81.4449 | 70.4209 | 50.5969 | 159.6375 | 0.39 | 0.31667 | 27.2106 | 237.445 | 3 | 10.4202 | 1.0583 | 0.20606
2015-06-18 17:00 | 232.8867 | 175.91 | 56.9767 | 147.9666 | 23.4056 | 90.5372 | 67.3523 | 22.6477 | 96.0936 | 83.8178 | 15.9346 | 131.9325 | 0.38875 | 0.31458 | 22.6337 | 170.5007 | 3 | 8.3281 | 1.0667 | 0.14913
2015-06-18 18:00 | 186.69 | 138.97 | 47.72 | 143.9115 | 23.4067 | 105.5349 | 70.6345 | 19.3655 | 110.4124 | 96.8438 | 0 | 104.2275 | 0.3875 | 0.3125 | 18.0856 | 122.3131 | 3 | 6.8223 | 1.0727 | 0.10759
2015-06-18 19:00 | 157.9333 | 117.8567 | 40.0767 | 142.1673 | 23.4078 | 120.5327 | 73.6265 | 16.3735 | 124.5265 | 109.2686 | 0 | 88.3925 | 0.38625 | 0.31042 | 15.2504 | 103.6429 | 2.9 | 6.1388 | 1.0754 | 0.091399
2015-06-18 20:00 | 129.1767 | 96.7433 | 32.4333 | 135.4964 | 23.4089 | 135.5304 | 76.1508 | 13.8492 | 138.5382 | 120.6936 | 0 | 72.5575 | 0.385 | 0.30833 | 12.4333 | 84.9908 | 2.7 | 5.356 | 1.0786 | 0.075169
2015-06-18 21:00 | 100.42 | 75.63 | 24.79 | 119.8177 | 23.4099 | 150.5281 | 78.0594 | 11.9406 | 152.5171 | 130.4076 | 0 | 56.7225 | 0.38375 | 0.30625 | 9.634 | 66.3565 | 2.5 | 4.5736 | 1.0817 | 0.058858
2015-06-18 22:00 | 91.1067 | 71.98 | 19.1267 | 102.444 | 23.411 | 165.5259 | 79.2395 | 10.7605 | 166.4984 | 137.2171 | 0 | 53.985 | 0.3825 | 0.30417 | 8.7121 | 62.6971 | 2.7 | 4.6593 | 1.0814 | 0.055595
2015-06-18 23:00 | 81.7933 | 68.33 | 13.4633 | 74.7293 | 23.412 | 180.5236 | 79.6208 | 10.3792 | -179.5115 | 139.6181 | 0 | 51.2475 | 0.38125 | 0.30208 | 7.7959 | 59.0434 | 2.9 | 4.7451 | 1.081 | 0.052338
2015-06-19 | 72.48 | 64.68 | 7.8 | 41.5518 | 23.413 | -164.4787 | 79.1804 | 10.8196 | -165.522 | 136.8661 | 0 | 48.51 | 0.38 | 0.3 | 6.8856 | 55.3956 | 2.5 | 4.2311 | 1.0831 | 0.049198
2015-06-19 01:00 | 98.5033 | 83.28 | 15.2233 | 72.8885 | 23.414 | -149.4809 | 77.9446 | 12.0554 | -151.5417 | 129.8036 | 0 | 62.46 | 0.37875 | 0.29792 | 9.327 | 71.787 | 2.7 | 4.9433 | 1.0802 | 0.063588
2015-06-19 02:00 | 124.5267 | 101.88 | 22.6467 | 93.5258 | 23.415 | -134.4832 | 75.9869 | 14.0131 | -137.5626 | 119.937 | 0 | 76.41 | 0.3775 | 0.29583 | 11.7522 | 88.1622 | 3.2 | 5.9551 | 1.0762 | 0.0778
2015-06-19 03:00 | 150.55 | 120.48 | 30.07 | 105.3951 | 23.416 | -119.4855 | 73.4228 | 16.5772 | -123.5471 | 108.4236 | 0 | 90.36 | 0.37625 | 0.29375 | 14.1611 | 104.5211 | 2.6 | 5.8663 | 1.0765 | 0.092267
2015-06-19 04:00 | 210.6033 | 128.0133 | 82.59 | 246.2361 | 23.4169 | -104.4878 | 70.4025 | 19.5975 | -109.4232 | 95.9467 | 0 | 96.01 | 0.375 | 0.29167 | 19.7441 | 115.7541 | 2.8 | 6.4173 | 1.0743 | 0.10197
2015-06-19 05:00 | 270.6567 | 135.5467 | 135.11 | 347.2923 | 23.4179 | -89.49 | 67.1053 | 22.8947 | -95.0863 | 82.8891 | 42.9912 | 101.66 | 0.37375 | 0.28958 | 25.2895 | 169.9406 | 3.5 | 8.8106 | 1.0648 | 0.14838
2015-06-19 06:00 | 330.71 | 143.08 | 187.63 | 423.9839 | 23.4189 | -74.4923 | 63.7339 | 26.2661 | -80.4103 | 69.4731 | 148.6685 | 107.31 | 0.3725 | 0.2875 | 30.7974 | 286.7758 | 3.7 | 12.6617 | 1.0494 | 0.24676
2015-06-19 07:00 | 368.64 | 169.37 | 199.27 | 404.7964 | 23.4198 | -59.4946 | 60.51 | 29.49 | -65.2683 | 55.8395 | 227.2985 | 127.0275 | 0.37125 | 0.28542 | 34.2144 | 388.5404 | 4.5 | 16.6419 | 1.0334 | 0.32925
2015-06-19 08:00 | 406.57 | 195.66 | 210.91 | 394.3375 | 23.4207 | -44.4968 | 57.6665 | 32.3335 | -49.5649 | 42.0959 | 292.608 | 146.745 | 0.37 | 0.28333 | 37.6077 | 476.9607 | 4.1 | 19.005 | 1.024 | 0.40049
2015-06-19 09:00 | 444.5 | 221.95 | 222.55 | 392.2526 | 23.4216 | -29.4991 | 55.4334 | 34.5666 | -33.278 | 28.3718 | 345.1364 | 166.4625 | 0.36875 | 0.28125 | 40.9773 | 552.5762 | 4 | 21.268 | 1.0149 | 0.45988
2015-06-19 10:00 | 446.8 | 225.19 | 221.61 | 377.1376 | 23.4225 | -14.5014 | 54.0124 | 35.9876 | -16.4971 | 15.0504 | 364.201 | 168.8925 | 0.3675 | 0.27917 | 41.0498 | 574.1433 | 4.6 | 22.542 | 1.0098 | 0.47543
2015-06-19 11:00 | 449.1 | 228.43 | 220.67 | 371.3684 | 23.4234 | 0.49634 | 53.5438 | 36.4562 | 0.56625 | 6.4735 | 369.0006 | 171.3225 | 0.36625 | 0.27708 | 41.1207 | 581.4439 | 6.1 | 24.2701 | 1.0029 | 0.47818
2015-06-19 12:00 | 451.4 | 231.67 | 219.73 | 374.5137 | 23.4243 | 15.4941 | 54.0763 | 35.9237 | 17.6196 | 15.8961 | 360.1923 | 173.7525 | 0.365 | 0.275 | 41.1902 | 575.1351 | 5 | 22.973 | 1.0081 | 0.47543
2015-06-19 13:00 | 416.69 | 217.13 | 199.56 | 352.8153 | 23.4251 | 30.4918 | 55.5545 | 34.4455 | 34.3735 | 29.2756 | 307.7528 | 162.8475 | 0.36375 | 0.27292 | 37.8927 | 508.4931 | 5.3 | 21.1904 | 1.0152 | 0.42332
2015-06-19 14:00 | 381.98 | 202.59 | 179.39 | 336.9535 | 23.426 | 45.4895 | 57.8331 | 32.1669 | 50.6238 | 43.0067 | 246.4051 | 151.9425 | 0.3625 | 0.27083 | 34.6169 | 432.9646 | 5.8 | 19.3301 | 1.0227 | 0.36308
2015-06-19 15:00 | 347.27 | 188.05 | 159.22 | 325.4224 | 23.4268 | 60.4872 | 60.7073 | 29.2927 | 66.2889 | 56.7457 | 178.4472 | 141.0375 | 0.36125 | 0.26875 | 31.3628 | 350.8475 | 6 | 16.964 | 1.0321 | 0.29694
2015-06-19 16:00 | 300.1533 | 185.3 | 114.8533 | 261.4991 | 23.4276 | 75.485 | 63.9464 | 26.0536 | 81.3971 | 70.3675 | 87.86 | 138.975 | 0.36 | 0.26667 | 27.0138 | 253.8488 | 5.5 | 13.4328 | 1.0463 | 0.21779
2015-06-19 17:00 | 253.0367 | 182.55 | 70.4867 | 182.789 | 23.4284 | 90.4827 | 67.3179 | 22.6821 | 96.047 | 83.7635 | 19.857 | 136.9125 | 0.35875 | 0.26458 | 22.6942 | 179.4637 | 5.6 | 11.2082 | 1.0552 | 0.15528
2015-06-19 18:00 | 205.92 | 179.8 | 26.12 | 78.6407 | 23.4292 | 105.4804 | 70.6011 | 19.3989 | 110.3663 | 96.789 | 0 | 134.85 | 0.3575 | 0.2625 | 18.4041 | 153.2541 | 4.5 | 9.2892 | 1.0628 | 0.13357
2015-06-19 19:00 | 173.3733 | 152.33 | 21.0433 | 74.5075 | 23.43 | 120.4781 | 73.5946 | 16.4054 | 124.4801 | 109.214 | 0 | 114.2475 | 0.35625 | 0.26042 | 15.4411 | 129.6886 | 4 | 8.0528 | 1.0678 | 0.11355
2015-06-19 20:00 | 140.8267 | 124.86 | 15.9667 | 66.5633 | 23.4308 | 135.4759 | 76.121 | 13.879 | 138.491 | 120.6408 | 0 | 93.645 | 0.355 | 0.25833 | 12.4984 | 106.1434 | 3.7 | 7.017 | 1.0719 | 0.093298
2015-06-19 21:00 | 108.28 | 97.39 | 10.89 | 52.5168 | 23.4316 | 150.4736 | 78.0322 | 11.9678 | 152.4688 | 130.3596 | 0 | 73.0425 | 0.35375 | 0.25625 | 9.576 | 82.6185 | 3.7 | 6.2818 | 1.0749 | 0.07282
2015-06-19 22:00 | 100.1233 | 88.39 | 11.7333 | 62.7053 | 23.4323 | 165.4713 | 79.2153 | 10.7847 | 166.4488 | 137.1794 | 0 | 66.2925 | 0.3525 | 0.25417 | 8.8234 | 75.1159 | 3.3 | 5.6474 | 1.0774 | 0.066363
2015-06-19 23:00 | 91.9667 | 79.39 | 12.5767 | 69.6685 | 23.4331 | 180.469 | 79.5999 | 10.4001 | -179.5625 | 139.5977 | 0 | 59.5425 | 0.35125 | 0.25208 | 8.0758 | 67.6183 | 2.3 | 4.4131 | 1.0823 | 0.060013
2015-06-20 | 83.81 | 70.39 | 13.42 | 71.3752 | 23.4338 | -164.5333 | 79.1627 | 10.8373 | -165.5742 | 136.8656 | 0 | 52.7925 | 0.35 | 0.25 | 7.3334 | 60.1259 | 2.4 | 4.2789 | 1.0829 | 0.05339
2015-06-20 01:00 | 113.3067 | 82.4433 | 30.8633 | 147.5969 | 23.4345 | -149.5355 | 77.9301 | 12.0699 | -151.5951 | 129.8194 | 0 | 61.8325 | 0.34946 | 0.24911 | 9.8992 | 71.7317 | 2.2 | 4.4416 | 1.0822 | 0.063657
2015-06-20 02:00 | 142.8033 | 94.4967 | 48.3067 | 199.3338 | 23.4352 | -134.5378 | 75.9753 | 14.0247 | -137.617 | 119.964 | 0 | 70.8725 | 0.34893 | 0.24821 | 12.457 | 83.3295 | 2.4 | 5.004 | 1.08 | 0.073796
2015-06-20 03:00 | 172.3 | 106.55 | 65.75 | 230.3283 | 23.4359 | -119.5401 | 73.4135 | 16.5865 | -123.6025 | 108.458 | 0 | 79.9125 | 0.34839 | 0.24732 | 15.007 | 94.9195 | 2.3 | 5.2662 | 1.0789 | 0.083978
2015-06-20 04:00 | 203.3333 | 127.13 | 76.2033 | 227.1113 | 23.4366 | -104.5424 | 70.395 | 19.605 | -109.4798 | 95.9862 | 0 | 95.3475 | 0.34786 | 0.24643 | 17.6827 | 113.0302 | 2.6 | 6.1322 | 1.0755 | 0.09968
2015-06-20 05:00 | 234.3667 | 147.71 | 86.6567 | 222.686 | 23.4373 | -89.5446 | 67.0988 | 22.9012 | -95.1442 | 82.9323 | 27.3998 | 110.7825 | 0.34732 | 0.24554 | 20.3501 | 158.5324 | 3.3 | 8.2541 | 1.067 | 0.1387
2015-06-20 06:00 | 265.4 | 168.29 | 97.11 | 219.3883 | 23.4379 | -74.5469 | 63.7276 | 26.2724 | -80.4697 | 69.5191 | 76.763 | 126.2175 | 0.34679 | 0.24464 | 23.0092 | 225.9897 | 3.8 | 10.8622 | 1.0566 | 0.19579
2015-06-20 07:00 | 273.4867 | 201.46 | 72.0267 | 146.2826 | 23.4386 | -59.5492 | 60.5029 | 29.4971 | -65.3293 | 55.8877 | 82.0377 | 151.095 | 0.34625 | 0.24375 | 23.6737 | 256.8064 | 3.4 | 11.4252 | 1.0543 | 0.22202
2015-06-20 08:00 | 281.5733 | 234.63 | 46.9433 | 87.7485 | 23.4392 | -44.5515 | 57.6577 | 32.3423 | -49.6273 | 42.1461 | 65.0599 | 175.9725 | 0.34571 | 0.24286 | 24.336 | 265.3684 | 4 | 12.2928 | 1.0508 | 0.22866
2015-06-20 09:00 | 289.66 | 267.8 | 21.86 | 38.5181 | 23.4398 | -29.5538 | 55.4221 | 34.5779 | -33.3413 | 28.4239 | 33.8747 | 200.85 | 0.34518 | 0.24196 | 24.9961 | 259.7208 | 3.9 | 12.0163 | 1.0519 | 0.22403
2015-06-20 10:00 | 320.7733 | 275.14 | 45.6333 | 77.6323 | 23.4404 | -14.556 | 53.998 | 36.002 | -16.5605 | 15.1035 | 74.9507 | 206.355 | 0.34464 | 0.24107 | 27.6381 | 308.9437 | 3.6 | 13.2545 | 1.047 | 0.26524
2015-06-20 11:00 | 351.8867 | 282.48 | 69.4067 | 116.7564 | 23.441 | 0.44167 | 53.5261 | 36.4739 | 0.50393 | 6.4876 | 116.0088 | 211.86 | 0.34411 | 0.24018 | 30.2717 | 358.1405 | 3 | 14.1919 | 1.0432 | 0.30637
2015-06-20 12:00 | 383 | 289.82 | 93.18 | 158.7381 | 23.4416 | 15.4394 | 54.0553 | 35.9447 | 17.5594 | 15.8556 | 152.6987 | 217.365 | 0.34357 | 0.23929 | 32.897 | 402.9606 | 3.3 | 15.8925 | 1.0364 | 0.34247
2015-06-20 13:00 | 401.54 | 254.9367 | 146.6033 | 259.0325 | 23.4422 | 30.4371 | 55.5307 | 34.4693 | 34.3161 | 29.2279 | 226.0536 | 191.2025 | 0.34304 | 0.23839 | 34.4356 | 451.6917 | 3.3 | 17.4154 | 1.0303 | 0.38162
2015-06-20 14:00 | 420.08 | 220.0533 | 200.0267 | 375.4451 | 23.4427 | 45.4348 | 57.8071 | 32.1929 | 50.5694 | 42.9565 | 274.7773 | 165.04 | 0.3425 | 0.2375 | 35.9693 | 475.7867 | 4.2 | 19.0683 | 1.0237 | 0.3994
2015-06-20 15:00 | 438.62 | 185.17 | 253.45 | 517.5745 | 23.4433 | 60.4325 | 60.6799 | 29.3201 | 66.2371 | 56.6942 | 284.204 | 138.8775 | 0.34196 | 0.23661 | 37.4981 | 460.5796 | 4.4 | 18.7931 | 1.0248 | 0.38705
2015-06-20 16:00 | 380.8933 | 161.25 | 219.6433 | 499.5884 | 23.4438 | 75.4303 | 63.9185 | 26.0815 | 81.3473 | 70.3152 | 168.2841 | 120.9375 | 0.34143 | 0.23571 | 32.512 | 321.7336 | 4.3 | 14.3542 | 1.0426 | 0.27506
2015-06-20 17:00 | 323.1667 | 137.33 | 185.8367 | 481.3629 | 23.4444 | 90.428 | 67.2902 | 22.7098 | 95.9985 | 83.7108 | 52.7316 | 102.9975 | 0.34089 | 0.23482 | 27.5413 | 183.2704 | 4.3 | 10.0272 | 1.0599 | 0.15928
2015-06-20 18:00 | 265.44 | 113.41 | 152.03 | 457.1176 | 23.4449 | 105.4257 | 70.5743 | 19.4257 | 110.3183 | 96.7366 | 0 | 85.0575 | 0.34036 | 0.23393 | 22.5861 | 107.6436 | 4.4 | 7.7639 | 1.0689 | 0.094353
2015-06-20 19:00 | 225.5 | 97.85 | 127.65 | 451.2929 | 23.4454 | 120.4234 | 73.5694 | 16.4306 | 124.4321 | 109.1627 | 0 | 73.3875 | 0.33982 | 0.23304 | 19.1574 | 92.5449 | 4.2 | 7.092 | 1.0716 | 0.081323
2015-06-20 20:00 | 185.56 | 82.29 | 103.27 | 429.8227 | 23.4459 | 135.4211 | 76.098 | 13.902 | 138.4425 | 120.5923 | 0 | 61.7175 | 0.33929 | 0.23214 | 15.7395 | 77.457 | 3.1 | 5.5205 | 1.0779 | 0.068464
2015-06-20 21:00 | 145.62 | 66.73 | 78.89 | 379.8086 | 23.4463 | 150.4189 | 78.0118 | 11.9882 | 152.4195 | 130.317 | 0 | 50.0475 | 0.33875 | 0.23125 | 12.3322 | 62.3797 | 2.7 | 4.6494 | 1.0814 | 0.055315
2015-06-20 22:00 | 143.43 | 59.36 | 84.07 | 448.5741 | 23.4468 | 165.4166 | 79.198 | 10.802 | 166.3986 | 137.1482 | 0 | 44.52 | 0.33821 | 0.23036 | 12.1275 | 56.6475 | 2.7 | 4.4702 | 1.0821 | 0.050265
2015-06-20 23:00 | 141.24 | 51.99 | 89.25 | 493.7391 | 23.4473 | 180.4143 | 79.5858 | 10.4142 | -179.6136 | 139.5841 | 0 | 38.9925 | 0.33768 | 0.22946 | 11.9234 | 50.9159 | 2.3 | 3.8911 | 1.0844 | 0.045276
2015-06-21 | 139.05 | 44.62 | 94.43 | 501.7384 | 23.4477 | -164.588 | 79.1519 | 10.8481 | -165.6261 | 136.8714 | 0 | 33.465 | 0.33714 | 0.22857 | 11.7199 | 45.1849 | 2.3 | 3.712 | 1.0852 | 0.040207
2015-06-21 01:00 | 163.3267 | 51.5267 | 111.8 | 534.325 | 23.4481 | -149.5903 | 77.9224 | 12.0776 | -151.6477 | 129.8405 | 0 | 38.645 | 0.33661 | 0.22768 | 13.7442 | 52.3892 | 2.3 | 3.9372 | 1.0843 | 0.046579
2015-06-21 02:00 | 187.6033 | 58.4333 | 129.17 | 532.831 | 23.4485 | -134.5926 | 75.9705 | 14.0295 | -137.6703 | 119.9953 | 0 | 43.825 | 0.33607 | 0.22679 | 15.762 | 59.587 | 2.6 | 4.4621 | 1.0822 | 0.052875
2015-06-21 03:00 | 211.88 | 65.34 | 146.54 | 513.2688 | 23.4489 | -119.5948 | 73.4111 | 16.5889 | -123.6566 | 108.4958 | 0 | 49.005 | 0.33554 | 0.22589 | 17.7733 | 66.7783 | 2.7 | 4.7868 | 1.0809 | 0.059186
2015-06-21 04:00 | 257.4433 | 84.7633 | 172.68 | 514.6248 | 23.4493 | -104.5971 | 70.3943 | 19.6057 | -109.5348 | 96.0283 | 0 | 63.5725 | 0.335 | 0.225 | 21.5609 | 85.1334 | 3 | 5.6604 | 1.0774 | 0.07521
2015-06-21 05:00 | 303.0067 | 104.1867 | 198.82 | 510.9226 | 23.4497 | -89.5994 | 67.0991 | 22.9009 | -95.2004 | 82.9774 | 62.466 | 78.14 | 0.33446 | 0.22411 | 25.3362 | 165.9422 | 3.2 | 8.3857 | 1.0665 | 0.14512
2015-06-21 06:00 | 348.57 | 123.61 | 224.96 | 508.2304 | 23.4501 | -74.6017 | 63.7279 | 26.2721 | -80.5273 | 69.5664 | 177.4345 | 92.7075 | 0.33393 | 0.22321 | 29.0994 | 299.2414 | 3.4 | 12.7513 | 1.049 | 0.2574
2015-06-21 07:00 | 408.1933 | 128.3433 | 279.85 | 568.3555 | 23.4504 | -59.604 | 60.5025 | 29.4975 | -65.3886 | 55.9367 | 318.3408 | 96.2575 | 0.33339 | 0.22232 | 34.0222 | 448.6205 | 3.8 | 17.8194 | 1.0287 | 0.37843
2015-06-21 08:00 | 467.8167 | 133.0767 | 334.74 | 625.6764 | 23.4508 | -44.6063 | 57.6557 | 32.3443 | -49.6883 | 42.1964 | 463.5304 | 99.8075 | 0.33286 | 0.22143 | 38.929 | 602.2669 | 4.3 | 23.1208 | 1.0075 | 0.49757
2015-06-21 09:00 | 527.44 | 137.81 | 389.63 | 686.4648 | 23.4511 | -29.6085 | 55.4177 | 34.5823 | -33.4037 | 28.4752 | 603.4188 | 103.3575 | 0.33232 | 0.22054 | 43.8199 | 750.5962 | 3.7 | 27.1561 | 0.99138 | 0.61018
2015-06-21 10:00 | 524.1033 | 130.3167 | 393.7867 | 669.7979 | 23.4514 | -14.6108 | 53.9906 | 36.0094 | -16.6234 | 15.1542 | 646.5063 | 97.7375 | 0.33179 | 0.21964 | 43.4725 | 787.7163 | 3.5 | 28.1161 | 0.98754 | 0.63788
2015-06-21 11:00 | 520.7667 | 122.8233 | 397.9433 | 669.2524 | 23.4517 | 0.38689 | 53.5153 | 36.4847 | 0.44145 | 6.4952 | 664.9566 | 92.1175 | 0.33125 | 0.21875 | 43.126 | 800.2001 | 3.5 | 28.5063 | 0.98597 | 0.64696
2015-06-21 12:00 | 517.43 | 115.33 | 402.1 | 684.7704 | 23.452 | 15.3846 | 54.0411 | 35.9589 | 17.4984 | 15.8126 | 658.8575 | 86.4975 | 0.33071 | 0.21786 | 42.7804 | 788.1354 | 3.5 | 28.1292 | 0.98748 | 0.63818
2015-06-21 13:00 | 498.7133 | 107.9033 | 390.81 | 690.2214 | 23.4523 | 30.3823 | 55.5137 | 34.4863 | 34.2575 | 29.1793 | 602.631 | 80.9275 | 0.33018 | 0.21696 | 41.1661 | 724.7246 | 3.2 | 25.8476 | 0.99661 | 0.59226
2015-06-21 14:00 | 479.9967 | 100.4767 | 379.52 | 711.9704 | 23.4526 | 45.38 | 57.7878 | 32.2122 | 50.5133 | 42.9063 | 521.4958 | 75.3575 | 0.32964 | 0.21607 | 39.5569 | 636.4102 | 4.2 | 24.0878 | 1.0036 | 0.52376
2015-06-21 15:00 | 461.28 | 93.05 | 368.23 | 751.4868 | 23.4529 | 60.3778 | 60.6593 | 29.3407 | 66.1834 | 56.6432 | 413.2053 | 69.7875 | 0.32911 | 0.21518 | 37.9526 | 520.9455 | 4 | 20.2795 | 1.0189 | 0.43524
2015-06-21 16:00 | 403.0733 | 83.1133 | 319.96 | 727.2129 | 23.4531 | 75.3755 | 63.8973 | 26.1027 | 81.2955 | 70.2641 | 245.5692 | 62.335 | 0.32857 | 0.21429 | 33.1096 | 341.0138 | 3.5 | 14.1567 | 1.0434 | 0.29176
2015-06-21 17:00 | 344.8667 | 73.1767 | 271.69 | 703.1282 | 23.4534 | 90.3732 | 67.2692 | 22.7308 | 95.948 | 83.66 | 77.645 | 54.8825 | 0.32804 | 0.21339 | 28.2821 | 160.8097 | 3.4 | 8.4253 | 1.0663 | 0.14061
2015-06-21 18:00 | 286.66 | 63.24 | 223.42 | 671.1038 | 23.4536 | 105.3709 | 70.5542 | 19.4458 | 110.2686 | 96.6867 | 0 | 47.43 | 0.3275 | 0.2125 | 23.4703 | 70.9003 | 3.2 | 5.4156 | 1.0783 | 0.062693
2015-06-21 19:00 | 244.63 | 56.8333 | 187.7967 | 663.2113 | 23.4538 | 120.3686 | 73.5509 | 16.4491 | 124.3826 | 109.1147 | 0 | 42.625 | 0.32696 | 0.21161 | 19.9963 | 62.6213 | 3.4 | 5.3569 | 1.0786 | 0.055384
2015-06-21 20:00 | 202.6 | 50.4267 | 152.1733 | 632.6407 | 23.454 | 135.3663 | 76.0818 | 13.9182 | 138.3928 | 120.548 | 0 | 37.82 | 0.32643 | 0.21071 | 16.5336 | 54.3536 | 3.4 | 5.0986 | 1.0796 | 0.048118
2015-06-21 21:00 | 160.57 | 44.02 | 116.55 | 560.4964 | 23.4542 | 150.3641 | 77.9983 | 12.0017 | 152.3694 | 130.2796 | 0 | 33.015 | 0.32589 | 0.20982 | 13.0822 | 46.0972 | 2.3 | 3.7405 | 1.085 | 0.041014
2015-06-21 22:00 | 154.7733 | 43.17 | 111.6033 | 594.9154 | 23.4544 | 165.3618 | 79.1875 | 10.8125 | 166.3479 | 137.1233 | 0 | 32.3775 | 0.32536 | 0.20893 | 12.5892 | 44.9667 | 2.5 | 3.9052 | 1.0844 | 0.039984
2015-06-21 23:00 | 148.9767 | 42.32 | 106.6567 | 589.6319 | 23.4545 | 180.3595 | 79.5786 | 10.4214 | -179.6647 | 139.5773 | 0 | 31.74 | 0.32482 | 0.20804 | 12.0977 | 43.8377 | 2.4 | 3.7699 | 1.0849 | 0.039
2015-06-22 | 143.18 | 41.47 | 101.71 | 540.2275 | 23.4547 | -164.6428 | 79.148 | 10.852 | -165.6776 | 136.8836 | 0 | 31.1025 | 0.32429 | 0.20714 | 11.6078 | 42.7103 | 2.8 | 4.1347 | 1.0835 | 0.037945
2015-06-22 01:00 | 164.6133 | 57.3267 | 107.2867 | 512.7218 | 23.4548 | -149.6451 | 77.9216 | 12.0784 | -151.6996 | 129.867 | 0 | 42.995 | 0.32375 | 0.20625 | 13.3234 | 56.3184 | 2.7 | 4.4599 | 1.0822 | 0.049975
2015-06-22 02:00 | 186.0467 | 73.1833 | 112.8633 | 465.6306 | 23.4549 | -134.6474 | 75.9725 | 14.0275 | -137.7225 | 120.0308 | 0 | 54.8875 | 0.32321 | 0.20536 | 15.0332 | 69.9207 | 3.1 | 5.285 | 1.0789 | 0.061856
2015-06-22 03:00 | 207.48 | 89.04 | 118.44 | 414.9507 | 23.4551 | -119.6496 | 73.4154 | 16.5846 | -123.7093 | 108.5369 | 0 | 66.78 | 0.32268 | 0.20446 | 16.7373 | 83.5173 | 2.9 | 5.5099 | 1.078 | 0.073823
2015-06-22 04:00 | 236.2433 | 122.4033 | 113.84 | 339.3679 | 23.4552 | -104.6519 | 70.4003 | 19.5997 | -109.5881 | 96.0729 | 0 | 91.8025 | 0.32214 | 0.20357 | 19.026 | 110.8285 | 2.9 | 6.3634 | 1.0745 | 0.097654
2015-06-22 05:00 | 265.0067 | 155.7667 | 109.24 | 280.8027 | 23.4553 | -89.6542 | 67.106 | 22.894 | -95.2547 | 83.0244 | 34.1028 | 116.825 | 0.32161 | 0.20268 | 21.307 | 172.2348 | 3.5 | 8.8823 | 1.0645 | 0.15034
2015-06-22 06:00 | 293.77 | 189.13 | 104.64 | 236.4624 | 23.4553 | -74.6565 | 63.735 | 26.265 | -80.5831 | 69.6149 | 82.3665 | 141.8475 | 0.32107 | 0.20179 | 23.5803 | 247.7943 | 3.5 | 11.2436 | 1.055 | 0.21437
2015-06-22 07:00 | 305.5567 | 219.5133 | 86.0433 | 174.7824 | 23.4554 | -59.6588 | 60.5089 | 29.4911 | -65.4462 | 55.9863 | 97.7717 | 164.635 | 0.32054 | 0.20089 | 24.4855 | 286.8922 | 3.7 | 12.6654 | 1.0493 | 0.24686
2015-06-22 08:00 | 317.3433 | 249.8967 | 67.4467 | 126.0842 | 23.4555 | -44.6611 | 57.6606 | 32.3394 | -49.7478 | 42.2467 | 93.3347 | 187.4225 | 0.32 | 0.2 | 25.3875 | 306.1446 | 4.1 | 13.667 | 1.0453 | 0.26242
2015-06-22 09:00 | 329.13 | 280.28 | 48.85 | 86.0711 | 23.4555 | -29.6633 | 55.4202 | 34.5798 | -33.4649 | 28.5256 | 75.6224 | 210.21 | 0.31946 | 0.19911 | 26.2863 | 312.1187 | 4 | 13.7537 | 1.045 | 0.26745
2015-06-22 10:00 | 316.9567 | 270.61 | 46.3467 | 78.8307 | 23.4555 | -14.6656 | 53.99 | 36.01 | -16.6857 | 15.2022 | 76.0722 | 202.9575 | 0.31893 | 0.19821 | 25.2716 | 304.3013 | 4.2 | 13.7094 | 1.0452 | 0.2608
2015-06-22 11:00 | 304.7833 | 260.94 | 43.8433 | 73.728 | 23.4556 | 0.33209 | 53.5114 | 36.4886 | 0.37893 | 6.4964 | 73.2546 | 195.705 | 0.31839 | 0.19732 | 24.2602 | 293.2198 | 4.1 | 13.2631 | 1.0469 | 0.25173
2015-06-22 12:00 | 292.61 | 251.27 | 41.34 | 70.3892 | 23.4556 | 15.3298 | 54.0339 | 35.9661 | 17.4368 | 15.767 | 67.7407 | 188.4525 | 0.31786 | 0.19643 | 23.252 | 279.4453 | 4.9 | 13.6327 | 1.0455 | 0.23956
2015-06-22 13:00 | 300.08 | 240.79 | 59.29 | 104.6869 | 23.4556 | 30.3275 | 55.5035 | 34.4965 | 34.1976 | 29.1298 | 91.4459 | 180.5925 | 0.31732 | 0.19554 | 23.8055 | 295.8439 | 4.3 | 13.5451 | 1.0458 | 0.25371
2015-06-22 14:00 | 307.55 | 230.31 | 77.24 | 144.8505 | 23.4556 | 45.3252 | 57.7754 | 32.2246 | 50.4556 | 42.856 | 106.1849 | 172.7325 | 0.31679 | 0.19464 | 24.3569 | 303.2743 | 4.3 | 13.7773 | 1.0449 | 0.25985
2015-06-22 15:00 | 315.02 | 219.83 | 95.19 | 194.1808 | 23.4555 | 60.323 | 60.6454 | 29.3546 | 66.1279 | 56.593 | 106.9127 | 164.8725 | 0.31625 | 0.19375 | 24.9063 | 296.6915 | 4.2 | 13.4716 | 1.0461 | 0.25451
2015-06-22 16:00 | 276.9167 | 189.5267 | 87.39 | 198.5195 | 23.4555 | 75.3207 | 63.8828 | 26.1172 | 81.2419 | 70.2142 | 67.1997 | 142.145 | 0.31571 | 0.19286 | 21.8566 | 231.2013 | 4.2 | 11.425 | 1.0543 | 0.19988
2015-06-22 17:00 | 238.8133 | 159.2233 | 79.59 | 205.8546 | 23.4554 | 90.3184 | 67.2549 | 22.7451 | 95.8957 | 83.6111 | 22.9069 | 119.4175 | 0.31518 | 0.19196 | 18.8172 | 161.1416 | 3.5 | 8.5357 | 1.0659 | 0.14084
2015-06-22 18:00 | 200.71 | 128.92 | 71.79 | 215.499 | 23.4554 | 105.3161 | 70.5409 | 19.4591 | 110.2172 | 96.6393 | 0 | 96.69 | 0.31464 | 0.19107 | 15.788 | 112.478 | 3.6 | 7.1149 | 1.0715 | 0.09883
2015-06-22 19:00 | 170.1033 | 109.8 | 60.3033 | 212.8167 | 23.4553 | 120.3138 | 73.5393 | 16.4607 | 124.3316 | 109.0701 | 0 | 82.35 | 0.31411 | 0.19018 | 13.3577 | 95.7077 | 3 | 5.9909 | 1.076 | 0.084448
2015-06-22 20:00 | 139.4967 | 90.68 | 48.8167 | 202.8145 | 23.4552 | 135.3116 | 76.0724 | 13.9276 | 138.3419 | 120.508 | 0 | 68.01 | 0.31357 | 0.18929 | 10.9355 | 78.9455 | 2.8 | 5.267 | 1.0789 | 0.069845
2015-06-22 21:00 | 108.89 | 71.56 | 37.33 | 179.4243 | 23.4551 | 150.3093 | 77.9916 | 12.0084 | 152.3185 | 130.2477 | 0 | 53.67 | 0.31304 | 0.18839 | 8.5216 | 62.1916 | 2.8 | 4.7435 | 1.081 | 0.055129
2015-06-22 22:00 | 122.36 | 60.2333 | 62.1267 | 331.0661 | 23.455 | 165.307 | 79.184 | 10.816 | 166.2969 | 137.1048 | 0 | 45.175 | 0.3125 | 0.1875 | 9.5594 | 54.7344 | 2.7 | 4.4104 | 1.0824 | 0.048579
2015-06-22 23:00 | 135.83 | 48.9067 | 86.9233 | 480.5266 | 23.4549 | 180.3047 | 79.5783 | 10.4217 | -179.7158 | 139.5774 | 0 | 36.68 | 0.31196 | 0.18661 | 10.5935 | 47.2735 | 2.5 | 3.9773 | 1.0841 | 0.042024
2015-06-23 | 149.3 | 37.58 | 111.72 | 593.5563 | 23.4547 | -164.6976 | 79.151 | 10.849 | -165.7287 | 136.9021 | 0 | 28.185 | 0.31143 | 0.18571 | 11.6241 | 39.8091 | 2.1 | 3.344 | 1.0866 | 0.035471
2015-06-23 01:00 | 168.78 | 55.9733 | 112.8067 | 539.3689 | 23.4546 | -149.6998 | 77.9277 | 12.0723 | -151.7506 | 129.8988 | 0 | 41.98 | 0.31089 | 0.18482 | 13.1181 | 55.0981 | 2 | 3.7218 | 1.0851 | 0.049026
2015-06-23 02:00 | 188.26 | 74.3667 | 113.8933 | 470.1693 | 23.4544 | -134.7021 | 75.9813 | 14.0187 | -137.7735 | 120.0706 | 0 | 55.775 | 0.31036 | 0.18393 | 14.607 | 70.382 | 1.6 | 3.7994 | 1.0848 | 0.062607
2015-06-23 03:00 | 207.74 | 92.76 | 114.98 | 403.0897 | 23.4543 | -119.7044 | 73.4264 | 16.5736 | -123.7604 | 108.5814 | 0 | 69.57 | 0.30982 | 0.18304 | 16.0906 | 85.6606 | 1.1 | 3.7769 | 1.0849 | 0.076205
2015-06-23 04:00 | 241.9867 | 125.9867 | 116 | 346.0223 | 23.4541 | -104.7067 | 70.413 | 19.587 | -109.6397 | 96.1201 | 0 | 94.49 | 0.30929 | 0.18214 | 18.7108 | 113.2008 | 1 | 4.5375 | 1.0818 | 0.10042
2015-06-23 05:00 | 276.2333 | 159.2133 | 117.02 | 300.9708 | 23.4539 | -89.709 | 67.1196 | 22.8804 | -95.3072 | 83.0731 | 36.2979 | 119.41 | 0.30875 | 0.18125 | 21.3218 | 177.0296 | 2.9 | 8.4322 | 1.0663 | 0.15478
2015-06-23 06:00 | 310.48 | 192.44 | 118.04 | 266.8735 | 23.4537 | -74.7112 | 63.7488 | 26.2512 | -80.637 | 69.6646 | 92.7425 | 144.33 | 0.30821 | 0.18036 | 23.9236 | 260.9961 | 2.6 | 10.7561 | 1.057 | 0.22621
2015-06-23 07:00 | 370.9433 | 190.17 | 180.7733 | 367.3592 | 23.4535 | -59.7135 | 60.522 | 29.478 | -65.5019 | 56.0365 | 205.2306 | 142.6275 | 0.30768 | 0.17946 | 28.5328 | 376.391 | 3.5 | 15.2622 | 1.039 | 0.32066
2015-06-23 08:00 | 431.4067 | 187.9 | 243.5067 | 455.355 | 23.4532 | -44.7158 | 57.6722 | 32.3278 | -49.8057 | 42.2969 | 336.8113 | 140.925 | 0.30714 | 0.17857 | 33.1259 | 510.8621 | 2.2 | 18.1644 | 1.0273 | 0.43036
2015-06-23 09:00 | 491.87 | 185.63 | 306.24 | 539.7061 | 23.453 | -29.7181 | 55.4295 | 34.5705 | -33.5249 | 28.575 | 473.9652 | 139.2225 | 0.30661 | 0.17768 | 37.7027 | 650.8904 | 1.9 | 22.2403 | 1.011 | 0.53962
2015-06-23 10:00 | 496.09 | 195.0233 | 301.0667 | 512.1604 | 23.4527 | -14.7204 | 53.9964 | 36.0036 | -16.7474 | 15.2475 | 494.1319 | 146.2675 | 0.30607 | 0.17679 | 37.9597 | 678.3591 | 1.5 | 22.6987 | 1.0092 | 0.56137
2015-06-23 11:00 | 500.31 | 204.4167 | 295.8933 | 497.6167 | 23.4525 | 0.27736 | 53.5144 | 36.4856 | 0.31648 | 6.491 | 494.4268 | 153.3125 | 0.30554 | 0.17589 | 38.2156 | 685.9549 | 1.5 | 22.9361 | 1.0083 | 0.56713
2015-06-23 12:00 | 504.53 | 213.81 | 290.72 | 495.0022 | 23.4522 | 15.2751 | 54.0336 | 35.9664 | 17.3746 | 15.7191 | 476.4898 | 160.3575 | 0.305 | 0.175 | 38.4704 | 675.3177 | 1.8 | 22.9037 | 1.0084 | 0.5584
2015-06-23 13:00 | 470.9 | 195.66 | 275.24 | 485.9437 | 23.4519 | 30.2728 | 55.5002 | 34.4998 | 34.1367 | 29.0796 | 424.6883 | 146.745 | 0.30446 | 0.17411 | 35.8431 | 607.2764 | 2.1 | 21.0774 | 1.0157 | 0.50578
2015-06-23 14:00 | 437.27 | 177.51 | 259.76 | 487.0601 | 23.4516 | 45.2705 | 57.7698 | 32.2302 | 50.3965 | 42.8058 | 357.337 | 133.1325 | 0.30393 | 0.17321 | 33.2247 | 523.6942 | 2.4 | 18.7654 | 1.0249 | 0.44014
2015-06-23 15:00 | 403.64 | 159.36 | 244.28 | 498.2034 | 23.4513 | 60.2683 | 60.6383 | 29.3617 | 66.0707 | 56.5434 | 274.6621 | 119.52 | 0.30339 | 0.17232 | 30.6154 | 424.7975 | 2.5 | 15.7749 | 1.0369 | 0.36119
2015-06-23 16:00 | 351.34 | 139.9033 | 211.4367 | 480.177 | 23.4509 | 75.266 | 63.875 | 26.125 | 81.1864 | 70.1657 | 162.9246 | 104.9275 | 0.30286 | 0.17143 | 26.6015 | 294.4535 | 1.9 | 11.1017 | 1.0556 | 0.25487
2015-06-23 17:00 | 299.04 | 120.4467 | 178.5933 | 461.7747 | 23.4506 | 90.2637 | 67.2473 | 22.7527 | 95.8417 | 83.5641 | 51.7611 | 90.335 | 0.30232 | 0.17054 | 22.6015 | 164.6977 | 1.9 | 7.0468 | 1.0718 | 0.14475
2015-06-23 18:00 | 246.74 | 100.99 | 145.75 | 437.3695 | 23.4503 | 105.2614 | 70.5343 | 19.4657 | 110.1641 | 96.5946 | 0 | 75.7425 | 0.30179 | 0.16964 | 18.6157 | 94.3582 | 2.1 | 5.0487 | 1.0798 | 0.083549
2015-06-23 19:00 | 209.84 | 87.3733 | 122.4667 | 432.0727 | 23.4499 | 120.2592 | 73.5344 | 16.4656 | 124.2792 | 109.0289 | 0 | 65.53 | 0.30125 | 0.16875 | 15.8036 | 81.3336 | 2.4 | 4.9417 | 1.0802 | 0.072045
2015-06-23 20:00 | 172.94 | 73.7567 | 99.1833 | 411.9937 | 23.4495 | 135.2569 | 76.0698 | 13.9302 | 138.29 | 120.4724 | 0 | 55.3175 | 0.30071 | 0.16786 | 13.0014 | 68.3189 | 2.8 | 4.935 | 1.0803 | 0.060518
2015-06-23 21:00 | 136.04 | 60.14 | 75.9 | 364.8148 | 23.4491 | 150.2546 | 77.9919 | 12.0081 | 152.2668 | 130.2213 | 0 | 45.105 | 0.30018 | 0.16696 | 10.2091 | 55.3141 | 2.7 | 4.4286 | 1.0823 | 0.04909
2015-06-23 22:00 | 142.2767 | 52.9367 | 89.34 | 476.2279 | 23.4487 | 165.2523 | 79.1873 | 10.8127 | 166.2456 | 137.0927 | 0 | 39.7025 | 0.29964 | 0.16607 | 10.658 | 50.3605 | 3.2 | 4.7738 | 1.0809 | 0.044637
2015-06-23 23:00 | 148.5133 | 45.7333 | 102.78 | 568.5417 | 23.4483 | 180.2501 | 79.5849 | 10.4151 | -179.7668 | 139.5843 | 0 | 34.3 | 0.29911 | 0.16518 | 11.1053 | 45.4053 | 2.6 | 4.0189 | 1.0839 | 0.040357
2015-06-24 | 154.75 | 38.53 | 116.22 | 618.0196 | 23.4479 | -164.7522 | 79.1609 | 10.8391 | -165.7792 | 136.927 | 0 | 28.8975 | 0.29857 | 0.16429 | 11.551 | 40.4485 | 3.2 | 4.464 | 1.0821 | 0.035892
2015-06-24 01:00 | 165.84 | 56.2367 | 109.6033 | 524.6054 | 23.4475 | -149.7545 | 77.9406 | 12.0594 | -151.8006 | 129.9359 | 0 | 42.1775 | 0.29804 | 0.16339 | 12.3566 | 54.5341 | 3.1 | 4.8042 | 1.0808 | 0.04833
2015-06-24 02:00 | 176.93 | 73.9433 | 102.9867 | 425.6089 | 23.447 | -134.7568 | 75.9969 | 14.0031 | -137.8232 | 120.1146 | 0 | 55.4575 | 0.2975 | 0.1625 | 13.1592 | 68.6167 | 3.4 | 5.5443 | 1.0778 | 0.060644
2015-06-24 03:00 | 188.02 | 91.65 | 96.37 | 338.2007 | 23.4466 | -119.759 | 73.4442 | 16.5558 | -123.81 | 108.629 | 0 | 68.7375 | 0.29696 | 0.16161 | 13.9588 | 82.6963 | 3.3 | 5.8843 | 1.0765 | 0.072996
2015-06-24 04:00 | 217.88 | 110.37 | 107.51 | 321.0022 | 23.4461 | -104.7613 | 70.4323 | 19.5677 | -109.6895 | 96.1696 | 0 | 82.7775 | 0.29643 | 0.16071 | 16.1465 | 98.924 | 3.9 | 6.9914 | 1.072 | 0.086961
2015-06-24 05:00 | 247.74 | 129.09 | 118.65 | 305.4194 | 23.4456 | -89.7636 | 67.1399 | 22.8601 | -95.3578 | 83.1236 | 36.5672 | 96.8175 | 0.29589 | 0.15982 | 18.3261 | 151.7108 | 4.7 | 9.441 | 1.0622 | 0.13215
2015-06-24 06:00 | 277.6 | 147.81 | 129.79 | 293.6515 | 23.4451 | -74.7658 | 63.7693 | 26.2307 | -80.6889 | 69.7154 | 101.8039 | 110.8575 | 0.29536 | 0.15893 | 20.4978 | 233.1592 | 4.9 | 12.1862 | 1.0513 | 0.20099
2015-06-24 07:00 | 296.3467 | 191.78 | 104.5667 | 212.6258 | 23.4446 | -59.7681 | 60.5419 | 29.4581 | -65.5557 | 56.0872 | 118.6305 | 143.835 | 0.29482 | 0.15804 | 21.8423 | 284.3078 | 5.5 | 14.3846 | 1.0425 | 0.24303
2015-06-24 08:00 | 315.0933 | 235.75 | 79.3433 | 148.4465 | 23.4441 | -44.7704 | 57.6906 | 32.3094 | -49.8619 | 42.3469 | 109.7138 | 176.8125 | 0.29429 | 0.15714 | 23.1819 | 309.7081 | 4.6 | 14.2784 | 1.0429 | 0.26485
2015-06-24 09:00 | 333.84 | 279.72 | 54.12 | 95.4181 | 23.4435 | -29.7727 | 55.4456 | 34.5544 | -33.5836 | 28.6234 | 83.7568 | 209.79 | 0.29375 | 0.15625 | 24.5164 | 318.0632 | 4.4 | 14.3395 | 1.0426 | 0.27193
2015-06-24 10:00 | 335.7567 | 292.0467 | 43.71 | 74.3811 | 23.443 | -14.7749 | 54.0096 | 35.9904 | -16.8083 | 15.29 | 71.7482 | 219.035 | 0.29321 | 0.15536 | 24.6122 | 315.3954 | 4.4 | 14.2561 | 1.043 | 0.26974
2015-06-24 11:00 | 337.6733 | 304.3733 | 33.3 | 56.0152 | 23.4424 | 0.2228 | 53.5243 | 36.4757 | 0.25421 | 6.4792 | 55.6574 | 228.28 | 0.29268 | 0.15446 | 24.7074 | 308.6449 | 4.6 | 14.2452 | 1.043 | 0.26398
2015-06-24 12:00 | 339.59 | 316.7 | 22.89 | 38.9805 | 23.4419 | 15.2205 | 54.0402 | 35.9598 | 17.312 | 15.6688 | 37.5319 | 237.525 | 0.29214 | 0.15357 | 24.8022 | 299.8591 | 5.1 | 14.4706 | 1.0421 | 0.25624
2015-06-24 13:00 | 312.3167 | 290.5167 | 21.8 | 38.492 | 23.4413 | 30.2183 | 55.5038 | 34.4962 | 34.0747 | 29.0286 | 33.6565 | 217.8875 | 0.29161 | 0.15268 | 22.7684 | 274.3125 | 4.5 | 13.0723 | 1.0477 | 0.23567
2015-06-24 14:00 | 285.0433 | 264.3333 | 20.71 | 38.8333 | 23.4407 | 45.216 | 57.771 | 32.229 | 50.3359 | 42.7558 | 28.5135 | 198.25 | 0.29107 | 0.15179 | 20.742 | 247.5055 | 4.6 | 12.3345 | 1.0507 | 0.21324
2015-06-24 15:00 | 257.77 | 238.15 | 19.62 | 40.0141 | 23.4401 | 60.2137 | 60.6379 | 29.3621 | 66.0119 | 56.4947 | 22.0884 | 178.6125 | 0.29054 | 0.15089 | 18.7228 | 219.4237 | 4.4 | 11.257 | 1.055 | 0.18982
2015-06-24 16:00 | 221.1633 | 204.2633 | 16.9 | 38.3788 | 23.4395 | 75.2115 | 63.874 | 26.126 | 81.1293 | 70.1186 | 13.0517 | 153.1975 | 0.29 | 0.15 | 16.0343 | 182.2835 | 4.8 | 10.4964 | 1.058 | 0.15814
2015-06-24 17:00 | 184.5567 | 170.3767 | 14.18 | 36.6628 | 23.4389 | 90.2092 | 67.2465 | 22.7535 | 95.786 | 83.5191 | 4.1382 | 127.7825 | 0.28946 | 0.14911 | 13.3556 | 145.2763 | 5.3 | 9.8399 | 1.0606 | 0.12635
2015-06-24 18:00 | 147.95 | 136.49 | 11.46 | 34.3897 | 23.4382 | 105.2069 | 70.5345 | 19.4655 | 110.1096 | 96.5526 | 0 | 102.3675 | 0.28893 | 0.14821 | 10.6867 | 113.0542 | 5.6 | 9.1329 | 1.0635 | 0.098588
2015-06-24 19:00 | 124.8467 | 115.2533 | 9.5933 | 33.8499 | 23.4376 | 120.2047 | 73.5363 | 16.4637 | 124.2255 | 108.9912 | 0 | 86.44 | 0.28839 | 0.14732 | 9.0012 | 95.4412 | 4.6 | 7.5825 | 1.0697 | 0.083714
2015-06-24 20:00 | 101.7433 | 94.0167 | 7.7267 | 32.1051 | 23.4369 | 135.2024 | 76.074 | 13.926 | 138.237 | 120.4412 | 0 | 70.5125 | 0.28786 | 0.14643 | 7.3219 | 77.8344 | 4 | 6.4323 | 1.0743 | 0.068564
2015-06-24 21:00 | 78.64 | 72.78 | 5.86 | 28.1826 | 23.4362 | 150.2001 | 77.9989 | 12.0011 | 152.2146 | 130.2003 | 0 | 54.585 | 0.28732 | 0.14554 | 5.6487 | 60.2337 | 4.3 | 6.1823 | 1.0753 | 0.053109
2015-06-24 22:00 | 95.8433 | 58.9533 | 36.89 | 196.8265 | 23.4356 | 165.1979 | 79.1975 | 10.8025 | 166.194 | 137.0871 | 0 | 44.215 | 0.28679 | 0.14464 | 6.8716 | 51.0866 | 4 | 5.5965 | 1.0776 | 0.045142
2015-06-24 23:00 | 113.0467 | 45.1267 | 67.92 | 376.1913 | 23.4349 | 180.1956 | 79.5984 | 10.4016 | -179.8175 | 139.598 | 0 | 33.845 | 0.28625 | 0.14375 | 8.0899 | 41.9349 | 3.5 | 4.8105 | 1.0808 | 0.037164
2015-06-25 | 130.25 | 31.3 | 98.95 | 526.9874 | 23.4341 | -164.8067 | 79.1776 | 10.8224 | -165.8291 | 136.9581 | 0 | 23.475 | 0.28571 | 0.14286 | 9.3036 | 32.7786 | 3.4 | 4.4243 | 1.0823 | 0.029091
2015-06-25 01:00 | 125.43 | 38.2867 | 87.1433 | 417.7765 | 23.4334 | -149.8089 | 77.9604 | 12.0396 | -151.8497 | 129.9781 | 0 | 28.715 | 0.28518 | 0.14196 | 8.9425 | 37.6575 | 3.8 | 4.9768 | 1.0801 | 0.033352
2015-06-25 02:00 | 120.61 | 45.2733 | 75.3367 | 311.8289 | 23.4327 | -134.8112 | 76.0192 | 13.9808 | -137.8715 | 120.1626 | 0 | 33.955 | 0.28464 | 0.14107 | 8.5827 | 42.5377 | 3.9 | 5.2293 | 1.0791 | 0.037639
2015-06-25 03:00 | 115.79 | 52.26 | 63.53 | 223.2732 | 23.4319 | -119.8134 | 73.4687 | 16.5313 | -123.8578 | 108.6798 | 0 | 39.195 | 0.28411 | 0.14018 | 8.2242 | 47.4192 | 4.3 | 5.7818 | 1.0769 | 0.041873
2015-06-25 04:00 | 152.77 | 72.0267 | 80.7433 | 241.3913 | 23.4312 | -104.8157 | 70.4584 | 19.5416 | -109.7374 | 96.2215 | 0 | 54.02 | 0.28357 | 0.13929 | 10.8303 | 64.8503 | 4.4 | 6.4266 | 1.0743 | 0.057128
2015-06-25 05:00 | 189.75 | 91.7933 | 97.9567 | 252.4338 | 23.4304 | -89.818 | 67.1668 | 22.8332 | -95.4062 | 83.1757 | 29.9953 | 68.845 | 0.28304 | 0.13839 | 13.4265 | 112.2668 | 3.9 | 7.4083 | 1.0704 | 0.098537
2015-06-25 06:00 | 226.73 | 111.56 | 115.17 | 260.8241 | 23.4296 | -74.8202 | 63.7964 | 26.2036 | -80.7386 | 69.7673 | 90.2018 | 83.67 | 0.2825 | 0.1375 | 16.0128 | 189.8846 | 4.6 | 10.5339 | 1.0579 | 0.16472
2015-06-25 07:00 | 257.5867 | 158.4467 | 99.14 | 201.7566 | 23.4288 | -59.8225 | 60.5684 | 29.4316 | -65.6075 | 56.1383 | 112.4168 | 118.835 | 0.28196 | 0.13661 | 18.1576 | 249.4094 | 4.5 | 12.294 | 1.0508 | 0.21491
2015-06-25 08:00 | 288.4433 | 205.3333 | 83.11 | 155.6017 | 23.428 | -44.8247 | 57.7157 | 32.2843 | -49.9162 | 42.3968 | 114.9108 | 154 | 0.28143 | 0.13571 | 20.294 | 289.2049 | 4.7 | 13.7377 | 1.045 | 0.24783
2015-06-25 09:00 | 319.3 | 252.22 | 67.08 | 118.3366 | 23.4272 | -29.827 | 55.4686 | 34.5314 | -33.6408 | 28.6707 | 103.8275 | 189.165 | 0.28089 | 0.13482 | 22.4223 | 315.4148 | 4.3 | 14.1567 | 1.0434 | 0.26986
2015-06-25 10:00 | 325.9433 | 269.7367 | 56.2067 | 95.6929 | 23.4264 | -14.8292 | 54.0297 | 35.9703 | -16.8683 | 15.3299 | 92.2881 | 202.3025 | 0.28036 | 0.13393 | 22.8451 | 317.4357 | 4.5 | 14.4199 | 1.0423 | 0.27131
2015-06-25 11:00 | 332.5867 | 287.2533 | 45.3333 | 76.2873 | 23.4255 | 0.1685 | 53.5412 | 36.4588 | 0.19223 | 6.4608 | 75.8028 | 215.44 | 0.27982 | 0.13304 | 23.2662 | 314.509 | 4.9 | 14.7284 | 1.0411 | 0.26849
2015-06-25 12:00 | 339.23 | 304.77 | 34.46 | 58.7027 | 23.4247 | 15.1662 | 54.0537 | 35.9463 | 17.2491 | 15.6161 | 56.5358 | 228.5775 | 0.27929 | 0.13214 | 23.6855 | 308.7988 | 4.9 | 14.55 | 1.0418 | 0.2638
2015-06-25 13:00 | 314.8567 | 284.6433 | 30.2133 | 53.3615 | 23.4238 | 30.164 | 55.5143 | 34.4857 | 34.012 | 28.977 | 46.6814 | 213.4825 | 0.27875 | 0.13125 | 21.9416 | 282.1055 | 5.9 | 14.7158 | 1.0411 | 0.24084
2015-06-25 14:00 | 290.4833 | 264.5167 | 25.9667 | 48.701 | 23.4229 | 45.1617 | 57.779 | 32.221 | 50.2742 | 42.706 | 35.7876 | 198.3875 | 0.27821 | 0.13036 | 20.2042 | 254.3793 | 5.5 | 13.4494 | 1.0462 | 0.21823
2015-06-25 15:00 | 266.11 | 244.39 | 21.72 | 44.3058 | 23.422 | 60.1595 | 60.6443 | 29.3557 | 65.9516 | 56.4468 | 24.4883 | 183.2925 | 0.27768 | 0.12946 | 18.4733 | 226.254 | 4.9 | 11.9704 | 1.0521 | 0.1952
2015-06-25 16:00 | 228.18 | 209.4767 | 18.7033 | 42.4827 | 23.4211 | 75.1572 | 63.8797 | 26.1203 | 81.0706 | 70.073 | 14.4791 | 157.1075 | 0.27714 | 0.12857 | 15.8096 | 187.3962 | 4.6 | 10.4561 | 1.0582 | 0.1626
2015-06-25 17:00 | 190.25 | 174.5633 | 15.6867 | 40.5683 | 23.4202 | 90.155 | 67.2524 | 22.7476 | 95.7288 | 83.4763 | 4.6091 | 130.9225 | 0.27661 | 0.12768 | 13.1561 | 148.6878 | 4.3 | 8.9465 | 1.0642 | 0.12975
2015-06-25 18:00 | 152.32 | 139.65 | 12.67 | 38.0337 | 23.4193 | 105.1527 | 70.5414 | 19.4586 | 110.0536 | 96.5134 | 0 | 104.7375 | 0.27607 | 0.12679 | 10.5128 | 115.2503 | 4.3 | 7.9016 | 1.0684 | 0.10097
2015-06-25 19:00 | 128.5233 | 117.8767 | 10.6467 | 37.5859 | 23.4184 | 120.1505 | 73.545 | 16.455 | 124.1707 | 108.957 | 0 | 88.4075 | 0.27554 | 0.12589 | 8.8532 | 97.2607 | 4.1 | 7.1394 | 1.0714 | 0.085452
2015-06-25 20:00 | 104.7267 | 96.1033 | 8.6233 | 35.8588 | 23.4174 | 135.1482 | 76.0851 | 13.9149 | 138.1832 | 120.4144 | 0 | 72.0775 | 0.275 | 0.125 | 7.2 | 79.2775 | 4.1 | 6.5774 | 1.0737 | 0.069798
2015-06-25 21:00 | 80.93 | 74.33 | 6.6 | 31.7779 | 23.4165 | 150.146 | 78.0129 | 11.9871 | 152.1618 | 130.1848 | 0 | 55.7475 | 0.27446 | 0.12411 | 5.5531 | 61.3006 | 4.1 | 6.0156 | 1.0759 | 0.054084
2015-06-25 22:00 | 102.4067 | 62.7667 | 39.64 | 211.8309 | 23.4155 | 165.1437 | 79.2146 | 10.7854 | 166.1423 | 137.088 | 0 | 47.075 | 0.27393 | 0.12321 | 7.013 | 54.088 | 3.9 | 5.5903 | 1.0776 | 0.047796
2015-06-25 23:00 | 123.8833 | 51.2033 | 72.68 | 403.3379 | 23.4145 | 180.1415 | 79.6188 | 10.3812 | -179.868 | 139.6186 | 0 | 38.4025 | 0.27339 | 0.12232 | 8.4672 | 46.8697 | 3.8 | 5.2647 | 1.0789 | 0.041467
2015-06-26 | 145.36 | 39.64 | 105.72 | 564.2586 | 23.4135 | -164.8608 | 79.2012 | 10.7988 | -165.8783 | 136.9955 | 0 | 29.73 | 0.27286 | 0.12143 | 9.9156 | 39.6456 | 4 | 5.2389 | 1.079 | 0.035079
2015-06-26 01:00 | 170.89 | 55.0733 | 115.8167 | 556.4492 | 23.4125 | -149.863 | 77.9869 | 12.0131 | -151.8976 | 130.0256 | 0 | 41.305 | 0.27232 | 0.12054 | 11.6343 | 52.9393 | 4.1 | 5.7544 | 1.077 | 0.046752
2015-06-26 02:00 | 196.42 | 70.5067 | 125.9133 | 522.2387 | 23.4115 | -134.8653 | 76.0483 | 13.9517 | -137.9183 | 120.2148 | 0 | 52.88 | 0.27179 | 0.11964 | 13.346 | 66.226 | 4.2 | 6.2696 | 1.0749 | 0.058374
2015-06-26 03:00 | 221.95 | 85.94 | 136.01 | 478.879 | 23.4104 | -119.8675 | 73.4999 | 16.5001 | -123.9039 | 108.7336 | 0 | 64.455 | 0.27125 | 0.11875 | 15.051 | 79.506 | 4.3 | 6.7846 | 1.0729 | 0.069945
2015-06-26 04:00 | 271.6467 | 103.1467 | 168.5 | 504.5607 | 23.4094 | -104.8698 | 70.4911 | 19.5089 | -109.7832 | 96.2757 | 0 | 77.36 | 0.27071 | 0.11786 | 18.3847 | 95.7447 | 4.2 | 7.192 | 1.0712 | 0.084103
2015-06-26 05:00 | 321.3433 | 120.3533 | 200.99 | 518.6716 | 23.4083 | -89.872 | 67.2004 | 22.7996 | -95.4525 | 83.2295 | 61.148 | 90.265 | 0.27018 | 0.11696 | 21.705 | 173.118 | 4 | 9.4099 | 1.0624 | 0.15081
2015-06-26 06:00 | 371.04 | 137.56 | 233.48 | 529.3927 | 23.4073 | -74.8743 | 63.8301 | 26.1699 | -80.7862 | 69.8201 | 182.6242 | 103.17 | 0.26964 | 0.11607 | 25.0121 | 310.8063 | 3.9 | 13.6127 | 1.0455 | 0.26647
2015-06-26 07:00 | 399.51 | 185.3533 | 214.1567 | 436.2713 | 23.4062 | -59.8765 | 60.6016 | 29.3984 | -65.6571 | 56.1897 | 242.7607 | 139.015 | 0.26911 | 0.11518 | 26.8777 | 408.6534 | 4.3 | 17.0704 | 1.0317 | 0.34572
2015-06-26 08:00 | 427.98 | 233.1467 | 194.8333 | 365.0958 | 23.4051 | -44.8787 | 57.7476 | 32.2524 | -49.9687 | 42.4463 | 269.4081 | 174.86 | 0.26857 | 0.11429 | 28.7358 | 473.0039 | 4.6 | 19.3814 | 1.0225 | 0.39658
2015-06-26 09:00 | 456.45 | 280.94 | 175.51 | 309.8532 | 23.404 | -29.881 | 55.4984 | 34.5016 | -33.6965 | 28.7169 | 271.7427 | 210.705 | 0.26804 | 0.11339 | 30.5862 | 513.0339 | 4.8 | 20.8323 | 1.0167 | 0.4277
2015-06-26 10:00 | 463.2867 | 283.8933 | 179.3933 | 305.6189 | 23.4029 | -14.8832 | 54.0567 | 35.9433 | -16.9272 | 15.3669 | 294.6926 | 212.92 | 0.2675 | 0.1125 | 30.9823 | 538.5949 | 4.7 | 21.5311 | 1.0139 | 0.44778
2015-06-26 11:00 | 470.1233 | 286.8467 | 183.2767 | 308.5929 | 23.4017 | 0.11454 | 53.565 | 36.435 | 0.13066 | 6.436 | 306.6481 | 215.135 | 0.26696 | 0.11161 | 31.3765 | 553.1596 | 5.2 | 22.4862 | 1.0101 | 0.45815
2015-06-26 12:00 | 476.96 | 289.8 | 187.16 | 318.9842 | 23.4006 | 15.1123 | 54.0742 | 35.9258 | 17.186 | 15.5612 | 307.2916 | 217.35 | 0.26643 | 0.11071 | 31.7689 | 556.4105 | 5.3 | 22.6878 | 1.0092 | 0.46048
2015-06-26 13:00 | 432.06 | 264.79 | 167.27 | 295.5556 | 23.3994 | 30.1101 | 55.5316 | 34.4684 | 33.9485 | 28.9248 | 258.6865 | 198.5925 | 0.26589 | 0.10982 | 28.7204 | 485.9994 | 5 | 20.1875 | 1.0193 | 0.40619
2015-06-26 14:00 | 387.16 | 239.78 | 147.38 | 276.5279 | 23.3983 | 45.1078 | 57.7939 | 32.2061 | 50.2113 | 42.6565 | 203.3667 | 179.835 | 0.26536 | 0.10893 | 25.6839 | 408.8857 | 4.4 | 17.1777 | 1.0313 | 0.34578
2015-06-26 15:00 | 342.26 | 214.77 | 127.49 | 260.1686 | 23.3971 | 60.1056 | 60.6576 | 29.3424 | 65.8899 | 56.3999 | 143.9754 | 161.0775 | 0.26482 | 0.10804 | 22.6594 | 327.7124 | 4.8 | 15.041 | 1.0398 | 0.27943
2015-06-26 16:00 | 298.1633 | 188.5533 | 109.61 | 249.0787 | 23.3959 | 75.1034 | 63.8922 | 26.1078 | 81.0103 | 70.0289 | 85.0717 | 141.415 | 0.26429 | 0.10714 | 19.7001 | 246.1868 | 4.7 | 12.3933 | 1.0504 | 0.21205
2015-06-26 17:00 | 254.0667 | 162.3367 | 91.73 | 237.3541 | 23.3947 | 90.1011 | 67.265 | 22.735 | 95.67 | 83.4356 | 27.1343 | 121.7525 | 0.26375 | 0.10625 | 16.7525 | 165.6393 | 3.8 | 8.9762 | 1.0641 | 0.14453
2015-06-26 18:00 | 209.97 | 136.12 | 73.85 | 221.8385 | 23.3935 | 105.0989 | 70.5551 | 19.4449 | 109.9963 | 96.477 | 0 | 102.09 | 0.26321 | 0.10536 | 13.8168 | 115.9068 | 3.5 | 7.1221 | 1.0715 | 0.10184
2015-06-26 19:00 | 177.7333 | 115.7033 | 62.03 | 219.1851 | 23.3923 | 120.0966 | 73.5605 | 16.4395 | 124.1147 | 108.9265 | 0 | 86.7775 | 0.26268 | 0.10446 | 11.6717 | 98.4492 | 3.7 | 6.7765 | 1.0729 | 0.086613
2015-06-26 20:00 | 145.4967 | 95.2867 | 50.21 | 209.055 | 23.391 | 135.0944 | 76.1031 | 13.8969 | 138.1286 | 120.3922 | 0 | 71.465 | 0.26214 | 0.10357 | 9.5352 | 81.0002 | 3.4 | 5.9313 | 1.0763 | 0.071486
2015-06-26 21:00 | 113.26 | 74.87 | 38.39 | 185.1585 | 23.3898 | 150.0922 | 78.0337 | 11.9663 | 152.1085 | 130.1749 | 0 | 56.1525 | 0.26161 | 0.10268 | 7.4074 | 63.5599 | 3.2 | 5.1862 | 1.0793 | 0.05625
2015-06-26 22:00 | 92.1167 | 65.05 | 27.0667 | 144.9596 | 23.3885 | 165.09 | 79.2386 | 10.7614 | 166.0905 | 137.0953 | 0 | 48.7875 | 0.26107 | 0.10179 | 6.0123 | 54.7998 | 3.4 | 5.1125 | 1.0796 | 0.04851
2015-06-26 23:00 | 70.9733 | 55.23 | 15.7433 | 87.5953 | 23.3872 | 180.0877 | 79.6461 | 10.3539 | -179.9182 | 139.646 | 0 | 41.4225 | 0.26054 | 0.10089 | 4.6228 | 46.0453 | 3.4 | 4.8389 | 1.0806 | 0.040802
2015-06-27 | 49.83 | 45.41 | 4.42 | 23.6567 | 23.386 | -164.9145 | 79.2316 | 10.7684 | -165.9268 | 137.0392 | 0 | 34.0575 | 0.26 | 0.1 | 3.2389 | 37.2964 | 3.4 | 4.5655 | 1.0817 | 0.033083
2015-06-27 01:00 | 67.6767 | 58.42 | 9.2567 | 44.5963 | 23.3847 | -149.9167 | 78.0202 | 11.9798 | -151.9444 | 130.0782 | 0 | 43.815 | 0.25978 | 0.09963 | 4.3952 | 48.2102 | 3.2 | 4.7066 | 1.0812 | 0.042741
2015-06-27 02:00 | 85.5233 | 71.43 | 14.0933 | 58.6011 | 23.3833 | -134.919 | 76.0842 | 13.9158 | -137.9636 | 120.2708 | 0 | 53.5725 | 0.25956 | 0.099259 | 5.5495 | 59.122 | 3.3 | 5.1476 | 1.0794 | 0.05233
2015-06-27 03:00 | 103.37 | 84.44 | 18.93 | 66.7998 | 23.382 | -119.9212 | 73.5377 | 16.4623 | -123.9482 | 108.7905 | 0 | 63.33 | 0.25933 | 0.098889 | 6.7018 | 70.0318 | 3.2 | 5.3885 | 1.0784 | 0.061931
2015-06-27 04:00 | 129.0833 | 115.2 | 13.8833 | 41.6532 | 23.3807 | -104.9234 | 70.5304 | 19.4696 | -109.827 | 96.332 | 0 | 86.4 | 0.25911 | 0.098519 | 8.3617 | 94.7617 | 3.1 | 6.0613 | 1.0758 | 0.083591
2015-06-27 05:00 | 154.7967 | 145.96 | 8.8367 | 22.8418 | 23.3794 | -89.9256 | 67.2405 | 22.7595 | -95.4966 | 83.2847 | 2.671 | 109.47 | 0.25889 | 0.098148 | 10.0188 | 122.1598 | 3.4 | 7.2175 | 1.0711 | 0.1073
2015-06-27 06:00 | 180.51 | 176.72 | 3.79 | 8.6058 | 23.378 | -74.9279 | 63.8705 | 26.1295 | -80.8315 | 69.8738 | 2.9612 | 132.54 | 0.25867 | 0.097778 | 11.673 | 147.1741 | 3.5 | 8.0992 | 1.0676 | 0.12884
2015-06-27 07:00 | 219.55 | 210.0533 | 9.4967 | 19.3701 | 23.3766 | -59.9301 | 60.6414 | 29.3586 | -65.7045 | 56.2415 | 10.7639 | 157.54 | 0.25844 | 0.097407 | 14.1854 | 182.4892 | 3.2 | 8.9028 | 1.0644 | 0.15928
2015-06-27 08:00 | 258.59 | 243.3867 | 15.2033 | 28.5198 | 23.3752 | -44.9323 | 57.7862 | 32.2138 | -50.0191 | 42.4954 | 21.0285 | 182.54 | 0.25822 | 0.097037 | 16.6934 | 220.2619 | 3.6 | 10.4832 | 1.0581 | 0.1911
2015-06-27 09:00 | 297.63 | 276.72 | 20.91 | 36.9497 | 23.3739 | -29.9345 | 55.5349 | 34.4651 | -33.7506 | 28.7618 | 32.3912 | 207.54 | 0.258 | 0.096667 | 19.1971 | 259.1283 | 3.3 | 11.3978 | 1.0544 | 0.22405
2015-06-27 10:00 | 324.44 | 292.9467 | 31.4933 | 53.6966 | 23.3724 | -14.9368 | 54.0906 | 35.9094 | -16.985 | 15.4011 | 51.7683 | 219.71 | 0.25778 | 0.096296 | 20.9084 | 292.3867 | 3.5 | 12.6371 | 1.0495 | 0.25161
2015-06-27 11:00 | 351.25 | 309.1733 | 42.0767 | 70.8982 | 23.371 | 0.061025 | 53.5956 | 36.4044 | 0.069601 | 6.4046 | 70.4557 | 231.88 | 0.25756 | 0.095926 | 22.6166 | 324.9523 | 3.7 | 13.8548 | 1.0446 | 0.27834
2015-06-27 12:00 | 378.06 | 325.4 | 52.66 | 89.8097 | 23.3696 | 15.0588 | 54.1015 | 35.8985 | 17.1227 | 15.5042 | 86.5416 | 244.05 | 0.25733 | 0.095556 | 24.3219 | 354.9134 | 4.1 | 15.191 | 1.0392 | 0.30245
2015-06-27 13:00 | 354.7833 | 303.0567 | 51.7267 | 91.4541 | 23.3682 | 30.0566 | 55.5559 | 34.4441 | 33.8843 | 28.8722 | 80.0863 | 227.2925 | 0.25711 | 0.095185 | 22.8047 | 330.1835 | 4 | 14.3182 | 1.0427 | 0.28232
2015-06-27 14:00 | 331.5067 | 280.7133 | 50.7933 | 95.3605 | 23.3667 | 45.0544 | 57.8156 | 32.1844 | 50.1473 | 42.6074 | 70.1863 | 210.535 | 0.25689 | 0.094815 | 21.2901 | 302.0114 | 4.3 | 13.7379 | 1.045 | 0.25881
2015-06-27 15:00 | 308.23 | 258.37 | 49.86 | 101.8125 | 23.3653 | 60.0522 | 60.6776 | 29.3224 | 65.8269 | 56.3541 | 56.4101 | 193.7775 | 0.25667 | 0.094444 | 19.7781 | 269.9657 | 4.2 | 12.6364 | 1.0495 | 0.23232
2015-06-27 16:00 | 266.57 | 233.1767 | 33.3933 | 75.9354 | 23.3638 | 75.0499 | 63.9114 | 26.0886 | 80.9487 | 69.9865 | 25.9882 | 174.8825 | 0.25644 | 0.094074 | 17.0901 | 217.9608 | 4.2 | 11.0113 | 1.056 | 0.18873
2015-06-27 17:00 | 224.91 | 207.9833 | 16.9267 | 43.8338 | 23.3623 | 90.0477 | 67.2845 | 22.7155 | 95.6099 | 83.3972 | 5.0403 | 155.9875 | 0.25622 | 0.093704 | 14.4067 | 175.4345 | 4.3 | 9.7823 | 1.0609 | 0.15261
2015-06-27 18:00 | 183.25 | 182.79 | 0.46 | 1.3832 | 23.3608 | 105.0455 | 70.5756 | 19.4244 | 109.9378 | 96.4435 | 0 | 137.0925 | 0.256 | 0.093333 | 11.728 | 148.8205 | 4 | 8.6506 | 1.0654 | 0.13001
2015-06-27 19:00 | 153.95 | 153.6167 | 0.33333 | 1.1794 | 23.3593 | 120.0433 | 73.5828 | 16.4172 | 124.0578 | 108.8996 | 0 | 115.2125 | 0.25578 | 0.092963 | 9.8442 | 125.0567 | 3.5 | 7.408 | 1.0704 | 0.10976
2015-06-27 20:00 | 124.65 | 124.4433 | 0.20667 | 0.86199 | 23.3578 | 135.0411 | 76.1279 | 13.8721 | 138.0732 | 120.3746 | 0 | 93.3325 | 0.25556 | 0.092593 | 7.9637 | 101.2963 | 3.4 | 6.5655 | 1.0737 | 0.089188
2015-06-27 21:00 | 95.35 | 95.27 | 0.08 | 0.38673 | 23.3562 | 150.0389 | 78.0614 | 11.9386 | 152.0549 | 130.1705 | 0 | 71.4525 | 0.25533 | 0.092222 | 6.0865 | 77.539 | 3.1 | 5.5231 | 1.0779 | 0.068536
2015-06-27 22:00 | 82.8733 | 82.74 | 0.13333 | 0.71612 | 23.3547 | 165.0367 | 79.2695 | 10.7305 | 166.0388 | 137.1092 | 0 | 62.055 | 0.25511 | 0.091852 | 5.2855 | 67.3405 | 3 | 5.1044 | 1.0796 | 0.059614
2015-06-27 23:00 | 70.3967 | 70.21 | 0.18667 | 1.042 | 23.3531 | 180.0345 | 79.6802 | 10.3198 | -179.9678 | 139.6802 | 0 | 52.6575 | 0.25489 | 0.091481 | 4.4858 | 57.1433 | 3.1 | 4.8857 | 1.0805 | 0.050628
2015-06-28 | 57.92 | 57.68 | 0.24 | 1.2889 | 23.3515 | -164.9677 | 79.2689 | 10.7311 | -165.9743 | 137.0891 | 0 | 43.26 | 0.25467 | 0.091111 | 3.6876 | 46.9476 | 2.8 | 4.2671 | 1.0829 | 0.04169
2015-06-28 01:00 | 73.4367 | 72.1433 | 1.2933 | 6.2516 | 23.35 | -149.97 | 78.0604 | 11.9396 | -151.9899 | 130.1358 | 0 | 54.1075 | 0.25444 | 0.090741 | 4.6714 | 58.7789 | 2.2 | 4.0368 | 1.0839 | 0.05224
2015-06-28 02:00 | 88.9533 | 86.6067 | 2.3467 | 9.7869 | 23.3484 | -134.9722 | 76.1267 | 13.8733 | -138.0073 | 120.3308 | 0 | 64.955 | 0.25422 | 0.09037 | 5.6535 | 70.6085 | 2.3 | 4.5065 | 1.082 | 0.062645
2015-06-28 03:00 | 104.47 | 101.07 | 3.4 | 12.0295 | 23.3468 | -119.9744 | 73.5822 | 16.4178 | -123.9905 | 108.8502 | 0 | 75.8025 | 0.254 | 0.09 | 6.6338 | 82.4363 | 2.1 | 4.6761 | 1.0813 | 0.073093
2015-06-28 04:00 | 115.5367 | 107.3967 | 8.14 | 24.4773 | 23.3451 | -104.9766 | 70.5762 | 19.4238 | -109.8686 | 96.3905 | 0 | 80.5475 | 0.25378 | 0.08963 | 7.3302 | 87.8777 | 2.7 | 5.4462 | 1.0782 | 0.077696
2015-06-28 05:00 | 126.6033 | 113.7233 | 12.88 | 33.3582 | 23.3435 | -89.9788 | 67.2872 | 22.7128 | -95.5384 | 83.3413 | 3.8681 | 85.2925 | 0.25356 | 0.089259 | 8.0252 | 97.1858 | 2.7 | 5.7371 | 1.0771 | 0.085833
2015-06-28 06:00 | 137.67 | 120.05 | 17.62 | 40.0758 | 23.3419 | -74.981 | 63.9173 | 26.0827 | -80.8744 | 69.9282 | 13.7539 | 90.0375 | 0.25333 | 0.088889 | 8.7191 | 112.5105 | 3.4 | 6.916 | 1.0723 | 0.098932
2015-06-28 07:00 | 189.5433 | 170.41 | 19.1333 | 39.0821 | 23.3402 | -59.9832 | 60.6878 | 29.3122 | -65.7496 | 56.2934 | 21.6882 | 127.8075 | 0.25311 | 0.088519 | 11.9939 | 161.4896 | 3.5 | 8.5465 | 1.0658 | 0.14114
2015-06-28 08:00 | 241.4167 | 220.77 | 20.6467 | 38.7794 | 23.3385 | -44.9854 | 57.8314 | 32.1686 | -50.0675 | 42.5441 | 28.571 | 165.5775 | 0.25289 | 0.088148 | 15.2629 | 209.4114 | 3.4 | 9.9441 | 1.0602 | 0.18206
2015-06-28 09:00 | 293.29 | 271.13 | 22.16 | 39.2018 | 23.3369 | -29.9876 | 55.5782 | 34.4218 | -33.803 | 28.8054 | 34.351 | 203.3475 | 0.25267 | 0.087778 | 18.5262 | 256.2246 | 3.6 | 11.607 | 1.0536 | 0.22136
2015-06-28 10:00 | 291.1767 | 262.08 | 29.0967 | 49.6589 | 23.3352 | -14.9898 | 54.1313 | 35.8687 | -17.0417 | 15.4325 | 47.8684 | 196.56 | 0.25244 | 0.087407 | 18.3765 | 262.8049 | 4.3 | 12.5127 | 1.0499 | 0.22626
2015-06-28 11:00 | 289.0633 | 253.03 | 36.0333 | 60.7693 | 23.3335 | 0.008041 | 53.6332 | 36.3668 | 0.0091692 | 6.3668 | 60.3945 | 189.7725 | 0.25222 | 0.087037 | 18.227 | 268.3941 | 4.5 | 12.8873 | 1.0485 | 0.23075
2015-06-28 12:00 | 286.95 | 243.98 | 42.97 | 73.3443 | 23.3318 | 15.0058 | 54.1357 | 35.8643 | 17.0595 | 15.445 | 70.6956 | 182.985 | 0.252 | 0.086667 | 18.0778 | 271.7584 | 3.1 | 11.5925 | 1.0536 | 0.23479
2015-06-28 13:00 | 271.4433 | 239.8333 | 31.61 | 55.9316 | 23.33 | 30.0037 | 55.587 | 34.413 | 33.8196 | 28.8192 | 49.0042 | 179.875 | 0.25178 | 0.086296 | 17.0858 | 245.9651 | 3.1 | 10.7864 | 1.0569 | 0.21316
2015-06-28 14:00 | 255.9367 | 235.6867 | 20.25 | 38.048 | 23.3283 | 45.0015 | 57.8442 | 32.1558 | 50.0824 | 42.5588 | 28.0255 | 176.765 | 0.25156 | 0.085926 | 16.0956 | 220.8861 | 2.9 | 9.8027 | 1.0608 | 0.19214
2015-06-28 15:00 | 240.43 | 231.54 | 8.89 | 18.1683 | 23.3265 | 59.9993 | 60.7044 | 29.2956 | 65.7627 | 56.3094 | 10.0781 | 173.655 | 0.25133 | 0.085556 | 15.107 | 198.8401 | 2.5 | 8.7138 | 1.0651 | 0.17367
2015-06-28 16:00 | 211.2933 | 203.6133 | 7.68 | 17.4803 | 23.3248 | 74.9971 | 63.9375 | 26.0625 | 80.8857 | 69.9459 | 5.9941 | 152.71 | 0.25111 | 0.085185 | 13.2645 | 171.9687 | 2.6 | 7.974 | 1.0681 | 0.15062
2015-06-28 17:00 | 182.1567 | 175.6867 | 6.47 | 16.7732 | 23.323 | 89.9949 | 67.3107 | 22.6893 | 95.5485 | 83.3611 | 1.9392 | 131.765 | 0.25089 | 0.084815 | 11.4253 | 145.1295 | 2.3 | 6.8353 | 1.0727 | 0.12765
2015-06-28 18:00 | 153.02 | 147.76 | 5.26 | 15.838 | 23.3212 | 104.9927 | 70.6029 | 19.3971 | 109.8781 | 96.413 | 0 | 110.82 | 0.25067 | 0.084444 | 9.5893 | 120.4093 | 2.3 | 6.0628 | 1.0757 | 0.10621
2015-06-28 19:00 | 128.9033 | 124.49 | 4.4133 | 15.6423 | 23.3194 | 119.9905 | 73.612 | 16.388 | 123.9998 | 108.8764 | 0 | 93.3675 | 0.25044 | 0.084074 | 8.0708 | 101.4383 | 2.3 | 5.4699 | 1.0781 | 0.089677
2015-06-28 20:00 | 104.7867 | 101.22 | 3.5667 | 14.9096 | 23.3176 | 134.9883 | 76.1595 | 13.8405 | 138.0172 | 120.3616 | 0 | 75.915 | 0.25022 | 0.083704 | 6.555 | 82.47 | 2.1 | 4.6772 | 1.0813 | 0.073123
2015-06-28 21:00 | 80.67 | 77.95 | 2.72 | 13.1864 | 23.3158 | 149.9861 | 78.096 | 11.904 | 152.001 | 130.1718 | 0 | 58.4625 | 0.25 | 0.083333 | 5.0419 | 63.5044 | 1.8 | 3.7845 | 1.0849 | 0.056493
2015-06-28 22:00 | 76.2767 | 74.1167 | 2.16 | 11.6416 | 23.314 | 164.984 | 79.3073 | 10.6927 | 165.9872 | 137.1295 | 0 | 55.5875 | 0.24978 | 0.082963 | 4.7631 | 60.3506 | 1.7 | 3.586 | 1.0857 | 0.053726
2015-06-28 23:00 | 71.8833 | 70.2833 | 1.6 | 8.9667 | 23.3121 | 179.9818 | 79.7212 | 10.2788 | 179.983 | 139.7212 | 0 | 52.7125 | 0.24956 | 0.082593 | 4.4847 | 57.1972 | 1.8 | 3.5874 | 1.0857 | 0.050919
2015-06-29 | 67.49 | 66.45 | 1.04 | 5.6082 | 23.3103 | -165.0204 | 79.313 | 10.687 | -166.0209 | 137.1451 | 0 | 49.8375 | 0.24933 | 0.082222 | 4.2069 | 54.0444 | 2 | 3.6889 | 1.0852 | 0.048094
2015-06-29 01:00 | 90.3833 | 80.2233 | 10.16 | 49.301 | 23.3084 | -150.0226 | 78.1072 | 11.8928 | -152.0341 | 130.1985 | 0 | 60.1675 | 0.24911 | 0.081852 | 5.6289 | 65.7964 | 1.9 | 3.9561 | 1.0842 | 0.058495
2015-06-29 02:00 | 113.2767 | 93.9967 | 19.28 | 80.6893 | 23.3065 | -135.0248 | 76.1759 | 13.8241 | -138.0493 | 120.3947 | 0 | 70.4975 | 0.24889 | 0.081481 | 7.0483 | 77.5458 | 1.9 | 4.3233 | 1.0827 | 0.068847
2015-06-29 03:00 | 136.17 | 107.77 | 28.4 | 100.7863 | 23.3046 | -120.0269 | 73.6333 | 16.3667 | -124.0308 | 108.9129 | 0 | 80.8275 | 0.24867 | 0.081111 | 8.4652 | 89.2927 | 1.9 | 4.6904 | 1.0812 | 0.079168
2015-06-29 04:00 | 164.9533 | 134.2133 | 30.74 | 92.677 | 23.3027 | -105.0291 | 70.6286 | 19.3714 | -109.908 | 96.4509 | 0 | 100.66 | 0.24844 | 0.080741 | 10.2454 | 110.9054 | 2.1 | 5.5658 | 1.0777 | 0.098012
2015-06-29 05:00 | 193.7367 | 160.6567 | 33.08 | 85.8651 | 23.3008 | -90.0313 | 67.3404 | 22.6596 | -95.5778 | 83.3992 | 9.8702 | 120.4925 | 0.24822 | 0.08037 | 12.0224 | 142.3852 | 1.6 | 6.0495 | 1.0758 | 0.12561
2015-06-29 06:00 | 222.52 | 187.1 | 35.42 | 80.7146 | 23.2989 | -75.0335 | 63.9707 | 26.0293 | -80.9148 | 69.9834 | 27.628 | 140.325 | 0.248 | 0.08 | 13.7962 | 181.7492 | 1.6 | 7.2797 | 1.0709 | 0.1596
2015-06-29 07:00 | 254.0867 | 228.1667 | 25.92 | 53.032 | 23.2969 | -60.0356 | 60.7408 | 29.2592 | -65.7924 | 56.3455 | 29.3895 | 171.125 | 0.24778 | 0.07963 | 15.7393 | 216.2537 | 1.9 | 8.6579 | 1.0654 | 0.18892
2015-06-29 08:00 | 285.6533 | 269.2333 | 16.42 | 30.8852 | 23.295 | -45.0378 | 57.8832 | 32.1168 | -50.1137 | 42.5922 | 22.7373 | 201.925 | 0.24756 | 0.079259 | 17.6788 | 242.3411 | 2 | 9.5732 | 1.0617 | 0.21098
2015-06-29 09:00 | 317.22 | 310.3 | 6.92 | 12.2573 | 23.293 | -30.04 | 55.6282 | 34.3718 | -33.8535 | 28.8478 | 10.7362 | 232.725 | 0.24733 | 0.078889 | 19.6148 | 263.076 | 2.4 | 10.6211 | 1.0575 | 0.22813
2015-06-29 10:00 | 314.7233 | 303.1133 | 11.61 | 19.8374 | 23.291 | -15.0422 | 54.1788 | 35.8212 | -17.0969 | 15.4611 | 19.1195 | 227.335 | 0.24711 | 0.078519 | 19.4429 | 265.8974 | 1.7 | 10.0093 | 1.06 | 0.23111
2015-06-29 11:00 | 312.2267 | 295.9267 | 16.3 | 27.5185 | 23.2891 | -0.04432 | 53.6776 | 36.3224 | -0.050527 | 6.3225 | 27.3512 | 221.945 | 0.24689 | 0.078148 | 19.2713 | 268.5675 | 1.7 | 10.0927 | 1.0596 | 0.23336
2015-06-29 12:00 | 309.73 | 288.74 | 20.99 | 35.8629 | 23.2871 | 14.9535 | 54.1769 | 35.8231 | 16.9964 | 15.3839 | 34.5779 | 216.555 | 0.24667 | 0.077778 | 19.1 | 270.2329 | 2 | 10.4448 | 1.0582 | 0.23449
2015-06-29 13:00 | 285.7833 | 261.5567 | 24.2267 | 42.9089 | 23.285 | 29.9513 | 55.625 | 34.375 | 33.7545 | 28.766 | 37.6136 | 196.1675 | 0.24644 | 0.077407 | 17.6074 | 251.3886 | 1.9 | 9.7559 | 1.061 | 0.21871
2015-06-29 14:00 | 261.8367 | 234.3733 | 27.4633 | 51.652 | 23.283 | 44.9492 | 57.8796 | 32.1204 | 50.0166 | 42.5108 | 38.0752 | 175.78 | 0.24622 | 0.077037 | 16.1175 | 229.9727 | 2.6 | 9.7866 | 1.0609 | 0.20005
2015-06-29 15:00 | 237.89 | 207.19 | 30.7 | 62.8065 | 23.281 | 59.947 | 60.7381 | 29.2619 | 65.6973 | 56.2659 | 34.8789 | 155.3925 | 0.246 | 0.076667 | 14.6302 | 204.9016 | 2.5 | 8.9032 | 1.0644 | 0.17884
2015-06-29 16:00 | 209.9533 | 184.8633 | 25.09 | 57.1739 | 23.2789 | 74.9449 | 63.9703 | 26.0297 | 80.8216 | 69.907 | 19.6418 | 138.6475 | 0.24578 | 0.076296 | 12.9005 | 171.1898 | 2.6 | 7.9497 | 1.0682 | 0.14995
2015-06-29 17:00 | 182.0167 | 162.5367 | 19.48 | 50.5709 | 23.2769 | 89.9427 | 67.3437 | 22.6563 | 95.4859 | 83.3273 | 5.8762 | 121.9025 | 0.24556 | 0.075926 | 11.1738 | 138.9525 | 2.3 | 6.6423 | 1.0734 | 0.12231
2015-06-29 18:00 | 154.08 | 140.21 | 13.87 | 41.8336 | 23.2748 | 104.9405 | 70.637 | 19.363 | 109.8173 | 96.3856 | 0 | 105.1575 | 0.24533 | 0.075556 | 9.4502 | 114.6077 | 2.4 | 5.9815 | 1.0761 | 0.10113
2015-06-29 19:00 | 129.7967 | 118.1633 | 11.6333 | 41.3205 | 23.2727 | 119.9384 | 73.6479 | 16.3521 | 123.9411 | 108.857 | 0 | 88.6225 | 0.24511 | 0.075185 | 7.9537 | 96.5762 | 2.3 | 5.318 | 1.0787 | 0.085427
2015-06-29 20:00 | 105.5133 | 96.1167 | 9.3967 | 39.3878 | 23.2706 | 134.9362 | 76.198 | 13.802 | 137.9606 | 120.3532 | 0 | 72.0875 | 0.24489 | 0.074815 | 6.4598 | 78.5473 | 2.2 | 4.6546 | 1.0814 | 0.06965
2015-06-29 21:00 | 81.23 | 74.07 | 7.16 | 34.8309 | 23.2685 | 149.9341 | 78.1374 | 11.8626 | 151.9468 | 130.1786 | 0 | 55.5525 | 0.24467 | 0.074444 | 4.9686 | 60.5211 | 2.3 | 4.1913 | 1.0832 | 0.053758
2015-06-29 22:00 | 80.81 | 70.18 | 10.63 | 57.529 | 23.2664 | 164.9319 | 79.3519 | 10.6481 | 165.9357 | 137.1563 | 0 | 52.635 | 0.24444 | 0.074074 | 4.9384 | 57.5734 | 1.8 | 3.5992 | 1.0856 | 0.051252
2015-06-29 23:00 | 80.39 | 66.29 | 14.1 | 79.3845 | 23.2643 | 179.9298 | 79.769 | 10.231 | 179.9344 | 139.769 | 0 | 49.7175 | 0.24422 | 0.073704 | 4.9083 | 54.6258 | 1.6 | 3.3071 | 1.0868 | 0.04868
2015-06-30 | 79.97 | 62.4 | 17.57 | 95.1933 | 23.2621 | -165.0724 | 79.3638 | 10.6362 | -166.0666 | 137.2073 | 0 | 46.8 | 0.244 | 0.073333 | 4.8782 | 51.6782 | 1.9 | 3.5149 | 1.0859 | 0.046018
2015-06-30 01:00 | 95.45 | 82.1867 | 13.2633 | 64.6468 | 23.26 | -150.0745 | 78.1608 | 11.8392 | -152.0768 | 130.2661 | 0 | 61.64 | 0.24378 | 0.072963 | 5.8171 | 67.4571 | 2.1 | 4.208 | 1.0832 | 0.059915
2015-06-30 02:00 | 110.93 | 101.9733 | 8.9567 | 37.6339 | 23.2578 | -135.0767 | 76.2318 | 13.7682 | -138.0895 | 120.4623 | 0 | 76.48 | 0.24356 | 0.072593 | 6.7544 | 83.2344 | 2.3 | 4.9011 | 1.0804 | 0.073739
2015-06-30 03:00 | 126.41 | 121.76 | 4.65 | 16.5587 | 23.2557 | -120.0788 | 73.6909 | 16.3091 | -124.0691 | 108.9783 | 0 | 91.32 | 0.24333 | 0.072222 | 7.6899 | 99.0099 | 2.4 | 5.4941 | 1.078 | 0.087523
2015-06-30 04:00 | 153.5 | 148.7367 | 4.7633 | 14.403 | 23.2535 | -105.081 | 70.6876 | 19.3124 | -109.9451 | 96.5134 | 0 | 111.5525 | 0.24311 | 0.071852 | 9.3294 | 120.8819 | 3.3 | 7.0776 | 1.0717 | 0.10623
2015-06-30 05:00 | 180.59 | 175.7133 | 4.8767 | 12.6899 | 23.2513 | -90.0831 | 67.4001 | 22.5999 | -95.6147 | 83.4585 | 1.4457 | 131.785 | 0.24289 | 0.071481 | 10.9658 | 144.1965 | 3 | 7.5061 | 1.07 | 0.12652
2015-06-30 06:00 | 207.68 | 202.69 | 4.99 | 11.3955 | 23.2491 | -75.0853 | 64.0306 | 25.9694 | -80.9528 | 70.0393 | 3.8902 | 152.0175 | 0.24267 | 0.071111 | 12.5993 | 168.5069 | 4.3 | 9.5658 | 1.0617 | 0.14671
2015-06-30 07:00 | 269.4533 | 253.9967 | 15.4567 | 31.6829 | 23.2468 | -60.0874 | 60.8003 | 29.1997 | -65.8326 | 56.3976 | 17.5341 | 190.4975 | 0.24244 | 0.070741 | 16.3319 | 224.3635 | 4.4 | 11.4114 | 1.0544 | 0.19398
2015-06-30 08:00 | 331.2267 | 305.3033 | 25.9233 | 48.8399 | 23.2446 | -45.0896 | 57.9417 | 32.0583 | -50.1576 | 42.6399 | 35.9279 | 228.9775 | 0.24222 | 0.07037 | 20.0576 | 284.963 | 5.6 | 14.5051 | 1.042 | 0.24348
2015-06-30 09:00 | 393 | 356.61 | 36.39 | 64.5507 | 23.2423 | -30.0917 | 55.6849 | 34.3151 | -33.9021 | 28.8887 | 56.5179 | 267.4575 | 0.242 | 0.07 | 23.7765 | 347.7519 | 4.8 | 15.6672 | 1.0373 | 0.2958
2015-06-30 10:00 | 377.8 | 331.1467 | 46.6533 | 79.8188 | 23.2401 | -15.0938 | 54.233 | 35.767 | -17.1508 | 15.4869 | 76.9207 | 248.36 | 0.24178 | 0.06963 | 22.8359 | 348.1166 | 5.7 | 16.5786 | 1.0337 | 0.29507
2015-06-30 11:00 | 362.6 | 305.6833 | 56.9167 | 96.2069 | 23.2378 | -0.095969 | 53.7289 | 36.2711 | -0.10938 | 6.2718 | 95.6311 | 229.2625 | 0.24156 | 0.069259 | 21.897 | 346.7906 | 4.6 | 15.4372 | 1.0383 | 0.29525
2015-06-30 12:00 | 347.4 | 280.22 | 67.18 | 114.9151 | 23.2355 | 14.9019 | 54.2249 | 35.7751 | 16.9336 | 15.3209 | 110.8311 | 210.165 | 0.24133 | 0.068889 | 20.9598 | 341.9559 | 4 | 14.6861 | 1.0413 | 0.29197
2015-06-30 13:00 | 343.0767 | 253.92 | 89.1567 | 158.0903 | 23.2332 | 29.8998 | 55.6699 | 34.3301 | 33.6891 | 28.7126 | 138.6517 | 190.44 | 0.24111 | 0.068519 | 20.6799 | 349.7716 | 3.7 | 14.6304 | 1.0415 | 0.29871
2015-06-30 14:00 | 338.7533 | 227.62 | 111.1333 | 209.2612 | 23.2309 | 44.8976 | 57.9219 | 32.0781 | 49.9501 | 42.4635 | 154.3735 | 170.715 | 0.24089 | 0.068148 | 20.4005 | 345.489 | 3.9 | 14.6965 | 1.0412 | 0.29498
2015-06-30 15:00 | 334.43 | 201.32 | 133.11 | 272.6623 | 23.2286 | 59.8955 | 60.7786 | 29.2214 | 65.631 | 56.2238 | 151.5867 | 150.99 | 0.24067 | 0.067778 | 20.1215 | 322.6983 | 3.7 | 13.7843 | 1.0449 | 0.27648
2015-06-30 16:00 | 290.67 | 186.9433 | 103.7267 | 236.7029 | 23.2263 | 74.8934 | 64.01 | 25.99 | 80.7563 | 69.87 | 81.4617 | 140.2075 | 0.24044 | 0.067407 | 17.4725 | 239.1417 | 4 | 11.4732 | 1.0541 | 0.20671
2015-06-30 17:00 | 246.91 | 172.5667 | 74.3433 | 193.32 | 23.2239 | 89.8912 | 67.3835 | 22.6165 | 95.4222 | 83.2961 | 22.5679 | 129.425 | 0.24022 | 0.067037 | 14.8283 | 166.8213 | 3.4 | 8.6132 | 1.0655 | 0.14576
2015-06-30 18:00 | 203.15 | 158.19 | 44.96 | 135.8806 | 23.2216 | 104.8891 | 70.6779 | 19.3221 | 109.7555 | 96.3612 | 0 | 118.6425 | 0.24 | 0.066667 | 12.189 | 130.8315 | 3.4 | 7.4885 | 1.07 | 0.1148
2015-06-30 19:00 | 171.0633 | 133.4233 | 37.64 | 134.035 | 23.2192 | 119.887 | 73.6907 | 16.3093 | 123.8815 | 108.8415 | 0 | 100.0675 | 0.23978 | 0.066296 | 10.2543 | 110.3218 | 3.6 | 7.0476 | 1.0718 | 0.09696
2015-06-30 20:00 | 138.9767 | 108.6567 | 30.32 | 127.5022 | 23.2168 | 134.8849 | 76.2433 | 13.7567 | 137.9036 | 120.3495 | 0 | 81.4925 | 0.23956 | 0.065926 | 8.3232 | 89.8157 | 3 | 5.8067 | 1.0768 | 0.079303
2015-06-30 21:00 | 106.89 | 83.89 | 23 | 112.3375 | 23.2144 | 149.8827 | 78.1857 | 11.8143 | 151.8926 | 130.1911 | 0 | 62.9175 | 0.23933 | 0.065556 | 6.3956 | 69.3131 | 3.6 | 5.766 | 1.0769 | 0.06121
2015-06-30 22:00 | 110.9233 | 75.6833 | 35.24 | 191.6326 | 23.212 | 164.8806 | 79.4034 | 10.5966 | 165.8846 | 137.1896 | 0 | 56.7625 | 0.23911 | 0.065185 | 6.6308 | 63.3933 | 3.1 | 5.081 | 1.0797 | 0.056124
2015-06-30 23:00 | 114.9567 | 67.4767 | 47.48 | 268.7374 | 23.2096 | 179.8785 | 79.8237 | 10.1763 | 179.8866 | 139.8235 | 0 | 50.6075 | 0.23889 | 0.064815 | 6.8655 | 57.473 | 2.5 | 4.296 | 1.0828 | 0.051031
2015-07-01 | 118.99 | 59.27 | 59.72 | 325.302 | 23.2072 | -165.1236 | 79.4215 | 10.5785 | -166.1111 | 137.2756 | 0 | 44.4525 | 0.23867 | 0.064444 | 7.0997 | 51.5522 | 2.3 | 3.911 | 1.0844 | 0.045839
2015-07-01 01:00 | 161.1733 | 54.1133 | 107.06 | 524.4529 | 23.2048 | -150.1257 | 78.221 | 11.779 | -152.1181 | 130.3386 | 0 | 40.585 | 0.23844 | 0.064074 | 9.6077 | 50.1927 | 2.5 | 4.0685 | 1.0837 | 0.044604
2015-07-01 02:00 | 203.3567 | 48.9567 | 154.4 | 651.6538 | 23.2023 | -135.1278 | 76.2943 | 13.7057 | -138.1279 | 120.5336 | 0 | 36.7175 | 0.23822 | 0.063704 | 12.111 | 48.8285 | 4.2 | 5.7259 | 1.0771 | 0.043126
2015-07-01 03:00 | 245.54 | 43.8 | 201.74 | 721.1602 | 23.1999 | -120.13 | 73.7551 | 16.2449 | -124.1052 | 109.0464 | 0 | 32.85 | 0.238 | 0.063333 | 14.6096 | 47.4596 | 3.6 | 5.0831 | 1.0797 | 0.042017
2015-07-01 04:00 | 296.39 | 51.4633 | 244.9267 | 743.0081 | 23.1974 | -105.1321 | 70.753 | 19.247 | -109.9798 | 96.5777 | 0 | 38.5975 | 0.23778 | 0.062963 | 17.6187 | 56.2162 | 3.1 | 4.8568 | 1.0806 | 0.049812
2015-07-01 05:00 | 347.24 | 59.1267 | 288.1133 | 751.8056 | 23.1949 | -90.1342 | 67.4662 | 22.5338 | -95.6491 | 83.5189 | 84.8604 | 44.345 | 0.23756 | 0.062593 | 20.6222 | 149.8276 | 3.2 | 7.8821 | 1.0685 | 0.13127
2015-07-01 06:00 | 398.09 | 66.79 | 331.3 | 758.384 | 23.1924 | -75.1363 | 64.0969 | 25.9031 | -80.9881 | 70.0957 | 258.1921 | 50.0925 | 0.23733 | 0.062222 | 23.62 | 331.9046 | 4.4 | 14.772 | 1.0409 | 0.2833
2015-07-01 07:00 | 441.3867 | 90.04 | 351.3467 | 721.6728 | 23.1899 | -60.1384 | 60.8662 | 29.1338 | -65.8703 | 56.4497 | 398.8458 | 67.53 | 0.23711 | 0.061852 | 26.1644 | 492.5403 | 4.3 | 19.6919 | 1.0212 | 0.41246
2015-07-01 08:00 | 484.6833 | 113.29 | 371.3933 | 700.9796 | 23.1874 | -45.1405 | 58.0067 | 31.9933 | -50.1991 | 42.6869 | 515.2691 | 84.9675 | 0.23689 | 0.061481 | 28.704 | 628.9406 | 5.9 | 25.5544 | 0.99778 | 0.51459
2015-07-01 09:00 | 527.98 | 136.54 | 391.44 | 695.4858 | 23.1849 | -30.1426 | 55.7483 | 34.2517 | -33.9487 | 28.9283 | 608.707 | 102.405 | 0.23667 | 0.061111 | 31.2388 | 742.3508 | 5.9 | 29.0985 | 0.98361 | 0.59875
2015-07-01 10:00 | 526.96 | 135.38 | 391.58 | 670.9435 | 23.1823 | -15.1447 | 54.294 | 35.706 | -17.2031 | 15.5099 | 646.5106 | 101.535 | 0.23644 | 0.060741 | 31.1492 | 779.1948 | 6.7 | 31.0498 | 0.9758 | 0.62348
2015-07-01 11:00 | 525.94 | 134.22 | 391.72 | 663.0452 | 23.1798 | -0.14682 | 53.787 | 36.213 | -0.16728 | 6.2146 | 659.1487 | 100.665 | 0.23622 | 0.06037 | 31.0597 | 790.8734 | 6.7 | 31.4148 | 0.97434 | 0.63188
2015-07-01 12:00 | 524.92 | 133.06 | 391.86 | 671.1903 | 23.1772 | 14.8511 | 54.2797 | 35.7203 | 16.871 | 15.2562 | 647.5368 | 99.795 | 0.236 | 0.06 | 30.9703 | 778.3021 | 5.7 | 30.0219 | 0.97991 | 0.62539
2015-07-01 13:00 | 492.66 | 122.3733 | 370.2867 | 657.4524 | 23.1746 | 29.849 | 55.7216 | 34.2784 | 33.6234 | 28.6591 | 576.907 | 91.78 | 0.23578 | 0.05963 | 29.0396 | 697.7266 | 5.2 | 27.004 | 0.99198 | 0.56755
2015-07-01 14:00 | 460.4 | 111.6867 | 348.7133 | 657.5176 | 23.172 | 44.8469 | 57.971 | 32.029 | 49.883 | 42.417 | 485.4158 | 83.765 | 0.23556 | 0.059259 | 27.1124 | 596.2932 | 5.8 | 24.4342 | 1.0023 | 0.49007
2015-07-01 15:00 | 428.14 | 101 | 327.14 | 671.1032 | 23.1694 | 59.8448 | 60.8258 | 29.1742 | 65.5639 | 56.183 | 373.4969 | 75.75 | 0.23533 | 0.058889 | 25.1889 | 474.4358 | 5.2 | 20.0261 | 1.0199 | 0.39678
2015-07-01 16:00 | 358.0067 | 102.7233 | 255.2833 | 583.5234 | 23.1668 | 74.8427 | 64.0564 | 25.9436 | 80.69 | 69.8349 | 201.1556 | 77.0425 | 0.23511 | 0.058519 | 21.0428 | 299.2409 | 4.6 | 13.9513 | 1.0442 | 0.25622
2015-07-01 17:00 | 287.8733 | 104.4467 | 183.4267 | 477.9095 | 23.1642 | 89.8406 | 67.4301 | 22.5699 | 95.3575 | 83.2673 | 56.0286 | 78.335 | 0.23489 | 0.058148 | 16.9046 | 151.2682 | 4 | 8.7271 | 1.0651 | 0.13211
2015-07-01 18:00 | 217.74 | 106.17 | 111.57 | 337.9953 | 23.1615 | 104.8385 | 70.7256 | 19.2744 | 109.6929 | 96.34 | 0 | 79.6275 | 0.23467 | 0.057778 | 12.7741 | 92.4016 | 3.7 | 6.5875 | 1.0736 | 0.08135
2015-07-01 19:00 | 180.2967 | 94.6267 | 85.67 | 305.9736 | 23.1589 | 119.8364 | 73.7403 | 16.2597 | 123.8213 | 108.8298 | 0 | 70.97 | 0.23444 | 0.057407 | 10.5674 | 81.5374 | 3.5 | 6.048 | 1.0758 | 0.071929
2015-07-01 20:00 | 142.8533 | 83.0833 | 59.77 | 252.2836 | 23.1562 | 134.8343 | 76.2954 | 13.7046 | 137.8462 | 120.3505 | 0 | 62.3125 | 0.23422 | 0.057037 | 8.3649 | 70.6774 | 4.2 | 6.4087 | 1.0744 | 0.062265
2015-07-01 21:00 | 105.41 | 71.54 | 33.87 | 166.1934 | 23.1536 | 149.8323 | 78.2408 | 11.7592 | 151.8383 | 130.2093 | 0 | 53.655 | 0.234 | 0.056667 | 6.1665 | 59.8215 | 4.1 | 5.9694 | 1.0761 | 0.052788
2015-07-01 22:00 | 93.1967 | 68.47 | 24.7267 | 135.197 | 23.1509 | 164.8302 | 79.4616 | 10.5384 | 165.8337 | 137.2295 | 0 | 51.3525 | 0.23378 | 0.056296 | 5.4468 | 56.7993 | 3.3 | 5.075 | 1.0797 | 0.050288
2015-07-01 23:00 | 80.9833 | 65.4 | 15.5833 | 88.7319 | 23.1482 | 179.8281 | 79.8851 | 10.1149 | 179.8394 | 139.8848 | 0 | 49.05 | 0.23356 | 0.055926 | 4.7285 | 53.7785 | 3.1 | 4.7806 | 1.0809 | 0.047665
2015-07-02 | 68.77 | 62.33 | 6.44 | 35.2917 | 23.1455 | -165.174 | 79.4858 | 10.5142 | -166.1544 | 137.3499 | 0 | 46.7475 | 0.23333 | 0.055556 | 4.0116 | 50.7591 | 3.1 | 4.6862 | 1.0813 | 0.045004
2015-07-02 01:00 | 89.51 | 77.43 | 12.08 | 59.5094 | 23.1428 | -150.1761 | 78.288 | 11.712 | -152.1578 | 130.4159 | 0 | 58.0725 | 0.23311 | 0.055185 | 5.2164 | 63.2889 | 3.2 | 5.1778 | 1.0793 | 0.056012
2015-07-02 02:00 | 110.25 | 92.53 | 17.72 | 75.1596 | 23.14 | -135.1781 | 76.3633 | 13.6367 | -138.1644 | 120.6086 | 0 | 69.3975 | 0.23289 | 0.054815 | 6.419 | 75.8165 | 2.9 | 5.2693 | 1.0789 | 0.067076
2015-07-02 03:00 | 130.99 | 107.63 | 23.36 | 83.86 | 23.1373 | -120.1802 | 73.8258 | 16.1742 | -124.1391 | 109.1171 | 0 | 80.7225 | 0.23267 | 0.054444 | 7.6193 | 88.3418 | 3.3 | 6.0607 | 1.0758 | 0.077928
2015-07-02 04:00 | 157.07 | 137.2233 | 19.8467 | 60.4237 | 23.1345 | -105.1823 | 70.8248 | 19.1752 | -110.0121 | 96.6438 | 0 | 102.9175 | 0.23244 | 0.054074 | 9.1275 | 112.045 | 3 | 6.5014 | 1.074 | 0.098675
2015-07-02 05:00 | 183.15 | 166.8167 | 16.3333 | 42.7508 | 23.1318 | -90.1844 | 67.5387 | 22.4613 | -95.6808 | 83.5804 | 4.7799 | 125.1125 | 0.23222 | 0.053704 | 10.6329 | 140.5253 | 3.8 | 8.1914 | 1.0672 | 0.12298
2015-07-02 06:00 | 209.23 | 196.41 | 12.82 | 29.4234 | 23.129 | -75.1864 | 64.1696 | 25.8304 | -81.0207 | 70.1526 | 9.9897 | 147.3075 | 0.232 | 0.053333 | 12.1353 | 169.4325 | 3.4 | 8.6948 | 1.0652 | 0.148
2015-07-02 07:00 | 232.42 | 217.7 | 14.72 | 30.3039 | 23.1262 | -60.1885 | 60.9386 | 29.0614 | -65.9054 | 56.5018 | 16.7251 | 163.275 | 0.23178 | 0.052963 | 13.4674 | 193.4675 | 3.2 | 9.2459 | 1.063 | 0.16864
2015-07-02 08:00 | 255.61 | 238.99 | 16.62 | 31.432 | 23.1234 | -45.1906 | 58.0782 | 31.9218 | -50.2382 | 42.7332 | 23.0874 | 179.2425 | 0.23156 | 0.052593 | 14.797 | 217.1269 | 3.7 | 10.4852 | 1.0581 | 0.18838
2015-07-02 09:00 | 278.8 | 260.28 | 18.52 | 32.9643 | 23.1206 | -30.1926 | 55.8183 | 34.1817 | -33.9931 | 28.9664 | 28.8406 | 195.21 | 0.23133 | 0.052222 | 16.1239 | 240.1745 | 3.1 | 10.6055 | 1.0576 | 0.20828
2015-07-02 10:00 | 270.0933 | 243.4 | 26.6933 | 45.8124 | 23.1177 | -15.1947 | 54.3618 | 35.6382 | -17.2537 | 15.53 | 44.1398 | 182.55 | 0.23111 | 0.051852 | 15.6054 | 242.2952 | 3.5 | 11.0717 | 1.0557 | 0.20975
2015-07-02 11:00 | 261.3867 | 226.52 | 34.8667 | 59.1085 | 23.1149 | -0.19677 | 53.8518 | 36.1482 | -0.22412 | 6.151 | 58.7682 | 169.89 | 0.23089 | 0.051481 | 15.0878 | 243.7461 | 3.4 | 11.0171 | 1.0559 | 0.21105
2015-07-02 12:00 | 252.68 | 209.64 | 43.04 | 73.8309 | 23.1121 | 14.8012 | 54.3414 | 35.6586 | 16.809 | 15.1898 | 71.2515 | 157.23 | 0.23067 | 0.051111 | 14.5712 | 243.0527 | 3.2 | 10.7954 | 1.0568 | 0.21063
2015-07-02 13:00 | 254.8867 | 217.1033 | 37.7833 | 67.186 | 23.1092 | 29.7991 | 55.7802 | 34.2198 | 33.5577 | 28.6057 | 58.985 | 162.8275 | 0.23044 | 0.050741 | 14.6843 | 236.4968 | 3.5 | 10.8905 | 1.0564 | 0.20487
2015-07-02 14:00 | 257.0933 | 224.5667 | 32.5267 | 61.4267 | 23.1063 | 44.797 | 58.0269 | 31.9731 | 49.8154 | 42.3713 | 45.3816 | 168.425 | 0.23022 | 0.05037 | 14.7971 | 228.6037 | 4.2 | 11.3439 | 1.0546 | 0.19769
2015-07-02 15:00 | 259.3 | 232.03 | 27.27 | 56.0371 | 23.1034 | 59.795 | 60.8799 | 29.1201 | 65.4959 | 56.1438 | 31.2189 | 174.0225 | 0.23 | 0.05 | 14.9098 | 220.1512 | 3.5 | 10.3797 | 1.0585 | 0.19108
2015-07-02 16:00 | 234.5767 | 200.0833 | 34.4933 | 78.9953 | 23.1006 | 74.7929 | 64.1096 | 25.8904 | 80.6229 | 69.8019 | 27.2744 | 150.0625 | 0.22978 | 0.04963 | 13.4751 | 190.812 | 5 | 10.9629 | 1.0561 | 0.16525
2015-07-02 17:00 | 209.8533 | 168.1367 | 41.7167 | 108.9349 | 23.0976 | 89.7909 | 67.4834 | 22.5166 | 95.292 | 83.2412 | 12.8205 | 126.1025 | 0.22956 | 0.049259 | 12.0432 | 150.9663 | 3.5 | 8.2177 | 1.0671 | 0.1321
2015-07-02 18:00 | 185.13 | 136.19 | 48.94 | 148.6653 | 23.0947 | 104.7888 | 70.78 | 19.22 | 109.6295 | 96.322 | 0 | 102.1425 | 0.22933 | 0.048889 | 10.6141 | 112.7566 | 3.8 | 7.3236 | 1.0707 | 0.098998
2015-07-02 19:00 | 150.62 | 116.58 | 34.04 | 121.9868 | 23.0918 | 119.7868 | 73.7967 | 16.2033 | 123.7605 | 108.822 | 0 | 87.435 | 0.22911 | 0.048519 | 8.6272 | 96.0622 | 3.7 | 6.7019 | 1.0732 | 0.084536
2015-07-02 20:00 | 116.11 | 96.97 | 19.14 | 81.1305 | 23.0889 | 134.7847 | 76.3544 | 13.6456 | 137.7885 | 120.3562 | 0 | 72.7275 | 0.22889 | 0.048148 | 6.6441 | 79.3716 | 3.7 | 6.1804 | 1.0753 | 0.069984
2015-07-02 21:00 | 81.6 | 77.36 | 4.24 | 20.9134 | 23.0859 | 149.7827 | 78.3027 | 11.6973 | 151.7841 | 130.2331 | 0 | 58.02 | 0.22867 | 0.047778 | 4.6648 | 62.6848 | 4 | 5.9589 | 1.0762 | 0.055317
2015-07-02 22:00 | 82.7933 | 75.1267 | 7.6667 | 42.1763 | 23.0829 | 164.7807 | 79.5267 | 10.4733 | 165.7833 | 137.2758 | 0 | 56.345 | 0.22844 | 0.047407 | 4.7284 | 61.0734 | 3.9 | 5.8085 | 1.0768 | 0.053925
2015-07-02 23:00 | 83.9867 | 72.8933 | 11.0933 | 63.59 | 23.08 | 179.7786 | 79.9533 | 10.0467 | 179.7932 | 139.9528 | 0 | 54.67 | 0.22822 | 0.047037 | 4.7919 | 59.4619 | 4 | 5.8582 | 1.0766 | 0.052492
2015-07-03 | 85.18 | 70.66 | 14.52 | 80.1061 | 23.077 | -165.2234 | 79.5569 | 10.4431 | -166.1965 | 137.4302 | 0 | 52.995 | 0.228 | 0.046667 | 4.8553 | 57.8503 | 3.8 | 5.6078 | 1.0776 | 0.051117
2015-07-03 01:00 | 90.4533 | 78.89 | 11.5633 | 57.3191 | 23.074 | -150.2255 | 78.3615 | 11.6385 | -152.1958 | 130.498 | 0 | 59.1675 | 0.22778 | 0.046296 | 5.1508 | 64.3183 | 3.9 | 5.9099 | 1.0764 | 0.056768
2015-07-03 02:00 | 95.7267 | 87.12 | 8.6067 | 36.7049 | 23.071 | -135.2275 | 76.4388 | 13.5612 | -138.1988 | 120.6871 | 0 | 65.34 | 0.22756 | 0.045926 | 5.4458 | 70.7858 | 3.7 | 5.9121 | 1.0764 | 0.062476
2015-07-03 03:00 | 101 | 95.35 | 5.65 | 20.3775 | 23.0679 | -120.2295 | 73.9029 | 16.0971 | -124.1707 | 109.1904 | 0 | 71.5125 | 0.22733 | 0.045556 | 5.7402 | 77.2527 | 3.9 | 6.3141 | 1.0747 | 0.068082
2015-07-03 04:00 | 116.8367 | 113.0133 | 3.8233 | 11.6861 | 23.0649 | -105.2316 | 70.903 | 19.097 | -110.0418 | 96.7117 | 0 | 84.76 | 0.22711 | 0.045185 | 6.6337 | 91.3937 | 3.1 | 5.9561 | 1.0762 | 0.080652
2015-07-03 05:00 | 132.6733 | 130.6767 | 1.9967 | 5.2435 | 23.0618 | -90.2336 | 67.6175 | 22.3825 | -95.7099 | 83.643 | 0.58058 | 98.0075 | 0.22689 | 0.044815 | 7.5255 | 106.1136 | 3.7 | 7.0161 | 1.0719 | 0.093273
2015-07-03 06:00 | 148.51 | 148.34 | 0.17 | 0.39129 | 23.0588 | -75.2356 | 64.2487 | 25.7513 | -81.0506 | 70.21 | 0.13248 | 111.255 | 0.22667 | 0.044444 | 8.4156 | 119.803 | 3.9 | 7.6438 | 1.0694 | 0.10506
2015-07-03 07:00 | 216.11 | 212.6133 | 3.4967 | 7.2164 | 23.0557 | -60.2377 | 61.0174 | 28.9826 | -65.9378 | 56.5537 | 3.9774 | 159.46 | 0.22644 | 0.044074 | 12.2342 | 175.6716 | 3.9 | 9.3897 | 1.0624 | 0.15305
2015-07-03 08:00 | 283.71 | 276.8867 | 6.8233 | 12.9326 | 23.0526 | -45.2397 | 58.1562 | 31.8438 | -50.2747 | 42.7788 | 9.4923 | 207.665 | 0.22622 | 0.043704 | 16.0454 | 233.2027 | 3.3 | 10.5876 | 1.0576 | 0.20225
2015-07-03 09:00 | 351.31 | 341.16 | 10.15 | 18.1019 | 23.0495 | -30.2417 | 55.8948 | 34.1052 | -34.0354 | 29.0031 | 15.8318 | 255.87 | 0.226 | 0.043333 | 19.849 | 291.5508 | 3.5 | 12.611 | 1.0496 | 0.25092
2015-07-03 10:00 | 331.4333 | 324.35 | 7.0833 | 12.1788 | 23.0464 | -15.2437 | 54.4362 | 35.5638 | -17.3027 | 15.5475 | 11.7332 | 243.2625 | 0.22578 | 0.042963 | 18.7076 | 273.7033 | 4.3 | 12.8532 | 1.0486 | 0.23534
2015-07-03 11:00 | 311.5567 | 307.54 | 4.0167 | 6.821 | 23.0433 | -0.24575 | 53.9235 | 36.0765 | -0.2798 | 6.081 | 6.7826 | 230.655 | 0.22556 | 0.042593 | 17.5683 | 255.006 | 3.8 | 11.7689 | 1.0529 | 0.22017
2015-07-03 12:00 | 291.68 | 290.73 | 0.95 | 1.6324 | 23.0402 | 14.7522 | 54.4099 | 35.5901 | 16.7475 | 15.1219 | 1.5758 | 218.0475 | 0.22533 | 0.042222 | 16.4313 | 236.0546 | 4.1 | 11.4767 | 1.0541 | 0.20404
2015-07-03 13:00 | 272.45 | 271.0333 | 1.4167 | 2.5233 | 23.037 | 29.7502 | 55.8456 | 34.1544 | 33.492 | 28.5524 | 2.2165 | 203.275 | 0.22511 | 0.041852 | 15.3329 | 220.8243 | 3.8 | 10.7008 | 1.0572 | 0.19143
2015-07-03 14:00 | 253.22 | 251.3367 | 1.8833 | 3.5629 | 23.0339 | 44.7482 | 58.0897 | 31.9103 | 49.7474 | 42.3267 | 2.6341 | 188.5025 | 0.22489 | 0.041481 | 14.2366 | 205.3732 | 3.9 | 10.3179 | 1.0587 | 0.1783
2015-07-03 15:00 | 233.99 | 231.64 | 2.35 | 4.8382 | 23.0307 | 59.7462 | 60.9408 | 29.0592 | 65.4272 | 56.106 | 2.6981 | 173.73 | 0.22467 | 0.041111 | 13.1424 | 189.5705 | 4 | 9.9241 | 1.0603 | 0.16482
2015-07-03 16:00 | 212.5633 | 206.5033 | 6.06 | 13.9084 | 23.0275 | 74.7442 | 64.1696 | 25.8304 | 80.5549 | 69.771 | 4.8091 | 154.8775 | 0.22444 | 0.040741 | 11.9272 | 171.6138 | 3.9 | 9.2629 | 1.0629 | 0.14958
2015-07-03 17:00 | 191.1367 | 181.3667 | 9.77 | 25.5772 | 23.0244 | 89.7422 | 67.5436 | 22.4564 | 95.2255 | 83.2177 | 3.0206 | 136.025 | 0.22422 | 0.04037 | 10.7143 | 149.7599 | 3.5 | 8.18 | 1.0673 | 0.13107
2015-07-03 18:00 | 169.71 | 156.23 | 13.48 | 41.0742 | 23.0212 | 104.7402 | 70.8413 | 19.1587 | 109.5654 | 96.3072 | 0 | 117.1725 | 0.224 | 0.04 | 9.5038 | 126.6763 | 3.5 | 7.4586 | 1.0702 | 0.11116
2015-07-03 19:00 | 140.7167 | 123.5567 | 17.16 | 61.7294 | 23.0179 | 119.7382 | 73.8599 | 16.1401 | 123.6992 | 108.8182 | 0 | 92.6675 | 0.22378 | 0.03963 | 7.8723 | 100.5398 | 3.5 | 6.6419 | 1.0734 | 0.088497
2015-07-03 20:00 | 111.7233 | 90.8833 | 20.84 | 88.7561 | 23.0147 | 134.7361 | 76.4201 | 13.5799 | 137.7305 | 120.3668 | 0 | 68.1625 | 0.22356 | 0.039259 | 6.2441 | 74.4066 | 3.3 | 5.6252 | 1.0775 | 0.065742
2015-07-03 21:00 | 82.73 | 58.21 | 24.52 | 121.6477 | 23.0115 | 149.7341 | 78.3715 | 11.6285 | 151.7299 | 130.2626 | 0 | 43.6575 | 0.22333 | 0.038889 | 4.6191 | 48.2766 | 4.1 | 5.6086 | 1.0776 | 0.042657
2015-07-03 22:00 | 85.3933 | 60.2467 | 25.1467 | 139.2833 | 23.0082 | 164.7321 | 79.5986 | 10.4014 | 165.7335 | 137.3286 | 0 | 45.185 | 0.22311 | 0.038519 | 4.7631 | 49.9481 | 4 | 5.5609 | 1.0778 | 0.044142
2015-07-03 23:00 | 88.0567 | 62.2833 | 25.7733 | 148.8384 | 23.005 | 179.7302 | 80.0282 | 9.9718 | 179.7478 | 140.0275 | 0 | 46.7125 | 0.22289 | 0.038148 | 4.9067 | 51.6192 | 4 | 5.6131 | 1.0775 | 0.04561
2015-07-04 | 90.72 | 64.32 | 26.4 | 146.7275 | 23.0017 | -165.2718 | 79.6346 | 10.3654 | -166.2372 | 137.5164 | 0 | 48.24 | 0.22267 | 0.037778 | 5.0501 | 53.2901 | 3.8 | 5.4653 | 1.0781 | 0.047112
2015-07-04 01:00 | 125.9933 | 73.31 | 52.6833 | 262.935 | 22.9984 | -150.2738 | 78.4416 | 11.5584 | -152.2321 | 130.5848 | 0 | 54.9825 | 0.22244 | 0.037407 | 7.0066 | 61.9891 | 3.7 | 5.6372 | 1.0775 | 0.054768
2015-07-04 02:00 | 161.2667 | 82.3 | 78.9667 | 338.781 | 22.9951 | -135.2758 | 76.5209 | 13.4791 | -138.2312 | 120.769 | 0 | 61.725 | 0.22222 | 0.037037 | 8.9593 | 70.6843 | 3.9 | 6.1089 | 1.0756 | 0.062341
2015-07-04 03:00 | 196.54 | 91.29 | 105.25 | 381.5262 | 22.9918 | -120.2778 | 73.9864 | 16.0136 | -124.1999 | 109.2661 | 0 | 68.4675 | 0.222 | 0.036667 | 10.908 | 79.3755 | 2.7 | 5.1805 | 1.0793 | 0.070248
2015-07-04 04:00 | 246.95 | 107.2167 | 139.7333 | 428.9269 | 22.9885 | -105.2798 | 70.9875 | 19.0125 | -110.0689 | 96.7811 | 0 | 80.4125 | 0.22178 | 0.036296 | 13.692 | 94.1045 | 4.1 | 7.0408 | 1.0718 | 0.082709
2015-07-04 05:00 | 297.36 | 123.1433 | 174.2167 | 459.1747 | 22.9852 | -90.2818 | 67.7027 | 22.2973 | -95.7362 | 83.7065 | 50.3353 | 92.3575 | 0.22156 | 0.035926 | 16.4704 | 159.1632 | 3.7 | 8.6739 | 1.0653 | 0.13904
2015-07-04 06:00 | 347.77 | 139.07 | 208.7 | 481.8492 | 22.9819 | -75.2838 | 64.3341 | 25.6659 | -81.0777 | 70.2677 | 162.6848 | 104.3025 | 0.22133 | 0.035556 | 19.2433 | 286.2306 | 4.4 | 13.3447 | 1.0466 | 0.24565
2015-07-04 07:00 | 394.71 | 154.4967 | 240.2133 | 497.0864 | 22.9785 | -60.2858 | 61.1026 | 28.8974 | -65.9673 | 56.6054 | 273.5971 | 115.8725 | 0.22111 | 0.035185 | 21.8187 | 411.2883 | 4.6 | 17.4528 | 1.0302 | 0.34744
2015-07-04 08:00 | 441.65 | 169.9233 | 271.7267 | 516.2445 | 22.9751 | -45.2877 | 58.2406 | 31.7594 | -50.3086 | 42.8237 | 378.6391 | 127.4425 | 0.22089 | 0.034815 | 24.3889 | 530.4705 | 5.4 | 21.9772 | 1.0121 | 0.44025
2015-07-04 09:00 | 488.59 | 185.35 | 303.24 | 541.972 | 22.9718 | -30.2897 | 55.9779 | 34.0221 | -34.0753 | 29.0383 | 473.8435 | 139.0125 | 0.22067 | 0.034444 | 26.9539 | 639.8099 | 6.3 | 26.2941 | 0.99482 | 0.52193
2015-07-04 10:00 | 479.37 | 204.35 | 275.02 | 473.7982 | 22.9684 | -15.2917 | 54.5172 | 35.4828 | -17.3498 | 15.5621 | 456.4288 | 153.2625 | 0.22044 | 0.034074 | 26.4186 | 636.1099 | 4.2 | 24.0784 | 1.0037 | 0.52353
2015-07-04 11:00 | 470.15 | 223.35 | 246.8 | 419.9002 | 22.965 | -0.29367 | 54.0019 | 35.9981 | -0.33422 | 6.0047 | 417.5964 | 167.5125 | 0.22022 | 0.033704 | 25.8844 | 610.9933 | 5.2 | 24.2935 | 1.0028 | 0.50243
2015-07-04 12:00 | 460.93 | 242.35 | 218.58 | 376.2701 | 22.9616 | 14.7044 | 54.4853 | 35.5147 | 16.6866 | 15.0527 | 363.3593 | 181.7625 | 0.22 | 0.033333 | 25.3512 | 570.4729 | 5.8 | 23.6273 | 1.0055 | 0.47036
2015-07-04 13:00 | 418.5267 | 229.5133 | 189.0133 | 337.2941 | 22.9581 | 29.7024 | 55.9178 | 34.0822 | 33.4265 | 28.4995 | 296.4213 | 172.135 | 0.21978 | 0.032963 | 22.9957 | 491.552 | 4.5 | 19.861 | 1.0206 | 0.41136
2015-07-04 14:00 | 376.1233 | 216.6767 | 159.4467 | 302.2341 | 22.9547 | 44.7004 | 58.1593 | 31.8407 | 49.6791 | 42.283 | 223.6019 | 162.5075 | 0.21956 | 0.032593 | 20.645 | 406.7544 | 4.6 | 17.3111 | 1.0308 | 0.3438
2015-07-04 15:00 | 333.72 | 203.84 | 129.88 | 267.9704 | 22.9513 | 59.6985 | 61.0085 | 28.9915 | 65.358 | 56.07 | 149.5756 | 152.88 | 0.21933 | 0.032222 | 18.299 | 320.7546 | 3.9 | 13.9236 | 1.0443 | 0.27467
2015-07-04 16:00 | 288.7767 | 167.8767 | 120.9 | 278.1488 | 22.9478 | 74.6965 | 64.2364 | 25.7636 | 80.4861 | 69.7423 | 96.307 | 125.9075 | 0.21911 | 0.031852 | 15.8185 | 238.033 | 4 | 11.4385 | 1.0542 | 0.20578
2015-07-04 17:00 | 243.8333 | 131.9133 | 111.92 | 293.8293 | 22.9443 | 89.6945 | 67.6105 | 22.3895 | 95.1584 | 83.197 | 34.8059 | 98.935 | 0.21889 | 0.031481 | 13.3431 | 147.084 | 4.3 | 8.8964 | 1.0644 | 0.12838
2015-07-04 18:00 | 198.89 | 95.95 | 102.94 | 314.7386 | 22.9409 | 104.6926 | 70.9093 | 19.0907 | 109.5006 | 96.2958 | 0 | 71.9625 | 0.21867 | 0.031111 | 10.8727 | 82.8352 | 4.7 | 7.2886 | 1.0708 | 0.072737
2015-07-04 19:00 | 154.0367 | 82.1767 | 71.86 | 259.5961 | 22.9374 | 119.6906 | 73.9298 | 16.0702 | 123.6376 | 108.8184 | 0 | 61.6325 | 0.21844 | 0.030741 | 8.4121 | 70.0446 | 4.2 | 6.3889 | 1.0744 | 0.061712
2015-07-04 20:00 | 109.1833 | 68.4033 | 40.78 | 174.5942 | 22.9339 | 134.6887 | 76.4926 | 13.5074 | 137.6724 | 120.3821 | 0 | 51.3025 | 0.21822 | 0.03037 | 5.9566 | 57.2591 | 4 | 5.7893 | 1.0768 | 0.05056
2015-07-04 21:00 | 64.33 | 54.63 | 9.7 | 48.4335 | 22.9304 | 149.6867 | 78.447 | 11.553 | 151.676 | 130.2979 | 0 | 40.9725 | 0.218 | 0.03 | 3.506 | 44.4785 | 3.8 | 5.19 | 1.0792 | 0.039362
2015-07-04 22:00 | 66.63 | 58.54 | 8.09 | 45.1467 | 22.9268 | 164.6847 | 79.6772 | 10.3228 | 165.6842 | 137.3879 | 0 | 43.905 | 0.21778 | 0.02963 | 3.6276 | 47.5326 | 3.7 | 5.1854 | 1.0793 | 0.042066
2015-07-04 23:00 | 68.93 | 62.45 | 6.48 | 37.7271 | 22.9233 | 179.6828 | 80.1098 | 9.8902 | 179.7034 | 140.1088 | 0 | 46.8375 | 0.21756 | 0.029259 | 3.749 | 50.5865 | 3.7 | 5.2808 | 1.0789 | 0.044753
2015-07-05 | 71.23 | 66.36 | 4.87 | 27.2864 | 22.9198 | -165.3191 | 79.7189 | 10.2811 | -166.2766 | 137.6086 | 0 | 49.77 | 0.21733 | 0.028889 | 3.8702 | 53.6402 | 3.8 | 5.4763 | 1.0781 | 0.04742
2015-07-05 01:00 | 94.22 | 84.9367 | 9.2833 | 46.6771 | 22.9162 | -150.3211 | 78.5283 | 11.4717 | -152.2667 | 130.6762 | 0 | 63.7025 | 0.21711 | 0.028519 | 5.1141 | 68.8166 | 3.7 | 5.8505 | 1.0766 | 0.060752
2015-07-05 02:00 | 117.21 | 103.5133 | 13.6967 | 59.1423 | 22.9126 | -135.323 | 76.6094 | 13.3906 | -138.2615 | 120.8544 | 0 | 77.635 | 0.21689 | 0.028148 | 6.3554 | 83.9904 | 3.8 | 6.4247 | 1.0743 | 0.073989
2015-07-05 03:00 | 140.2 | 122.09 | 18.11 | 66.0087 | 22.909 | -120.325 | 74.0763 | 15.9237 | -124.2267 | 109.3442 | 0 | 91.5675 | 0.21667 | 0.027778 | 7.5942 | 99.1617 | 3.1 | 6.1988 | 1.0752 | 0.087428
2015-07-05 04:00 | 165.7967 | 152.82 | 12.9767 | 40.0175 | 22.9054 | -105.3269 | 71.0783 | 18.9217 | -110.0933 | 96.8522 | 0 | 114.615 | 0.21644 | 0.027407 | 8.9714 | 123.5864 | 3.3 | 7.1621 | 1.0714 | 0.10857
2015-07-05 05:00 | 191.3933 | 183.55 | 7.8433 | 20.7531 | 22.9018 | -90.3289 | 67.7941 | 22.2059 | -95.7596 | 83.7709 | 2.2518 | 137.6625 | 0.21622 | 0.027037 | 10.3459 | 150.2602 | 2.9 | 7.5956 | 1.0696 | 0.13179
2015-07-05 06:00 | 216.99 | 214.28 | 2.71 | 6.2778 | 22.8982 | -75.3308 | 64.4257 | 25.5743 | -81.1018 | 70.3257 | 2.1136 | 160.71 | 0.216 | 0.026667 | 11.7175 | 174.541 | 2.7 | 8.1544 | 1.0674 | 0.15277
2015-07-05 07:00 | 251.0133 | 246.2667 | 4.7467 | 9.851 | 22.8946 | -60.3327 | 61.1941 | 28.8059 | -65.994 | 56.6569 | 5.4146 | 184.7 | 0.21578 | 0.026296 | 13.5408 | 203.6554 | 2.7 | 9.0642 | 1.0637 | 0.17764
2015-07-05 08:00 | 285.0367 | 278.2533 | 6.7833 | 12.9205 | 22.8909 | -45.3347 | 58.3315 | 31.6685 | -50.3398 | 42.8677 | 9.4698 | 208.69 | 0.21556 | 0.025926 | 15.3603 | 233.5201 | 2.8 | 10.0975 | 1.0596 | 0.2029
2015-07-05 09:00 | 319.06 | 310.24 | 8.82 | 15.8003 | 22.8873 | -30.3366 | 56.0675 | 33.9325 | -34.1129 | 29.072 | 13.8097 | 232.68 | 0.21533 | 0.025556 | 17.1761 | 263.6657 | 2.4 | 10.6396 | 1.0574 | 0.22863
2015-07-05 10:00 | 319 | 311.1767 | 7.8233 | 13.5069 | 22.8836 | -15.3385 | 54.6049 | 35.3951 | -17.3949 | 15.5741 | 13.011 | 233.3825 | 0.21511 | 0.025185 | 17.1551 | 263.5486 | 2.6 | 10.8359 | 1.0567 | 0.22835
2015-07-05 11:00 | 318.94 | 312.1133 | 6.8267 | 11.6385 | 22.88 | -0.34044 | 54.087 | 35.913 | -0.38727 | 5.9219 | 11.5764 | 234.085 | 0.21489 | 0.024815 | 17.1342 | 262.7956 | 3 | 11.2124 | 1.0552 | 0.22738
2015-07-05 12:00 | 318.88 | 313.05 | 5.83 | 10.0561 | 22.8763 | 14.6576 | 54.5673 | 35.4327 | 16.6266 | 14.9823 | 9.7143 | 234.7875 | 0.21467 | 0.024444 | 17.1132 | 261.615 | 3.5 | 11.6755 | 1.0533 | 0.22596
2015-07-05 13:00 | 289.1933 | 285.0233 | 4.17 | 7.4566 | 22.8726 | 29.6557 | 55.9968 | 34.0032 | 33.3612 | 28.447 | 6.5562 | 213.7675 | 0.21444 | 0.024074 | 15.504 | 235.8277 | 3.5 | 10.8696 | 1.0565 | 0.20431
2015-07-05 14:00 | 259.5067 | 256.9967 | 2.51 | 4.768 | 22.8689 | 44.6538 | 58.2356 | 31.7644 | 49.6106 | 42.2406 | 3.5299 | 192.7475 | 0.21422 | 0.023704 | 13.898 | 210.1754 | 3.8 | 10.368 | 1.0585 | 0.18243
2015-07-05 15:00 | 229.82 | 228.97 | 0.85 | 1.7579 | 22.8651 | 59.6519 | 61.0829 | 28.9171 | 65.2883 | 56.0357 | 0.98207 | 171.7275 | 0.214 | 0.023333 | 12.2954 | 185.0049 | 3.9 | 9.6814 | 1.0613 | 0.161
2015-07-05 16:00 | 204.62 | 199.0833 | 5.5367 | 12.7719 | 22.8614 | 74.65 | 64.3099 | 25.6901 | 80.4168 | 69.7159 | 4.4277 | 149.3125 | 0.21378 | 0.022963 | 10.9358 | 164.676 | 3.6 | 8.7461 | 1.065 | 0.14381
2015-07-05 17:00 | 179.42 | 169.1967 | 10.2233 | 26.9239 | 22.8577 | 89.6481 | 67.6841 | 22.3159 | 95.0907 | 83.179 | 3.1977 | 126.8975 | 0.21356 | 0.022593 | 9.579 | 139.6742 | 3.5 | 7.8648 | 1.0685 | 0.12238
2015-07-05 18:00 | 154.22 | 139.31 | 14.91 | 45.7598 | 22.8539 | 104.6462 | 70.984 | 19.016 | 109.4354 | 96.2878 | 0 | 104.4825 | 0.21333 | 0.022222 | 8.2251 | 112.7076 | 3.4 | 6.9221 | 1.0723 | 0.099103
2015-07-05 19:00 | 131.4667 | 117.9367 | 13.53 | 49.1057 | 22.8501 | 119.6442 | 74.0065 | 15.9935 | 123.5755 | 108.8227 | 0 | 88.4525 | 0.21311 | 0.021852 | 7.0043 | 95.4568 | 2.9 | 5.883 | 1.0765 | 0.08426
2015-07-05 20:00 | 108.7133 | 96.5633 | 12.15 | 52.3201 | 22.8463 | 134.6423 | 76.5719 | 13.4281 | 137.6143 | 120.4023 | 0 | 72.4225 | 0.21289 | 0.021481 | 5.786 | 78.2085 | 3.3 | 5.744 | 1.077 | 0.069071
2015-07-05 21:00 | 85.96 | 75.19 | 10.77 | 54.1566 | 22.8426 | 149.6404 | 78.5292 | 11.4708 | 151.6224 | 130.3388 | 0 | 56.3925 | 0.21267 | 0.021111 | 4.5702 | 60.9627 | 3.1 | 5.0051 | 1.08 | 0.053988
2015-07-05 22:00 | 89.7033 | 73.1033 | 16.6 | 93.4012 | 22.8388 | 164.6385 | 79.7626 | 10.2374 | 165.6356 | 137.4537 | 0 | 54.8275 | 0.21244 | 0.020741 | 4.7642 | 59.5917 | 3.3 | 5.1622 | 1.0794 | 0.052743
2015-07-05 23:00 | 93.4467 | 71.0167 | 22.43 | 131.7542 | 22.8349 | 179.6366 | 80.1982 | 9.8018 | 179.6602 | 140.1968 | 0 | 53.2625 | 0.21222 | 0.02037 | 4.9579 | 58.2204 | 3.1 | 4.9194 | 1.0803 | 0.051575
2015-07-06 | 97.19 | 68.93 | 28.26 | 159.738 | 22.8311 | -165.3653 | 79.8099 | 10.1901 | -166.3145 | 137.7065 | 0 | 51.6975 | 0.2 | 0 | 4.8595 | 56.557 | 3.2 | 4.9674 | 1.0801 | 0.050093
2015-07-06 01:00 | 127.6733 | 85.2267 | 42.4467 | 215.1483 | 22.8273 | -150.3672 | 78.6215 | 11.3785 | -152.2994 | 130.7722 | 0 | 63.92 | 0.2 | 0 | 6.3837 | 70.3037 | 3.4 | 5.597 | 1.0776 | 0.062123
2015-07-06 02:00 | 158.1567 | 101.5233 | 56.6333 | 246.2571 | 22.8234 | -135.369 | 76.7043 | 13.2957 | -138.2895 | 120.943 | 0 | 76.1425 | 0.2 | 0 | 7.9078 | 84.0503 | 3.1 | 5.7266 | 1.0771 | 0.074235
2015-07-06 03:00 | 188.64 | 117.82 | 70.82 | 259.6586 | 22.8196 | -120.3709 | 74.1725 | 15.8275 | -124.251 | 109.4245 | 0 | 88.365 | 0.2 | 0 | 9.432 | 97.797 | 3.5 | 6.5562 | 1.0738 | 0.08611
2015-07-06 04:00 | 251.5933 | 116.3867 | 135.2067 | 419.0221 | 22.8157 | -105.3728 | 71.1754 | 18.8246 | -110.115 | 96.9247 | 0 | 87.29 | 0.2 | 0 | 12.5797 | 99.8697 | 3.7 | 6.8209 | 1.0727 | 0.087848
2015-07-06 05:00 | 314.5467 | 114.9533 | 199.5933 | 530.3279 | 22.8118 | -90.3747 | 67.8917 | 22.1083 | -95.7802 | 83.8361 | 56.9426 | 86.215 | 0.2 | 0 | 15.7273 | 158.8849 | 3.7 | 8.6652 | 1.0653 | 0.1388
2015-07-06 06:00 | 377.5 | 113.52 | 263.98 | 613.7067 | 22.8079 | -75.3766 | 64.5235 | 25.4765 | -81.123 | 70.384 | 206.0306 | 85.14 | 0.2 | 0 | 18.875 | 310.0456 | 4 | 13.6889 | 1.0452 | 0.26574
2015-07-06 07:00 | 439.4633 | 92.26 | 347.2033 | 722.8142 | 22.804 | -60.3785 | 61.2918 | 28.7082 | -66.0178 | 56.7081 | 396.7561 | 69.195 | 0.2 | 0 | 21.9732 | 487.9243 | 4 | 19.2476 | 1.023 | 0.4093
2015-07-06 08:00 | 501.4267 | 71 | 430.4267 | 822.1151 | 22.8001 | -45.3804 | 58.4286 | 31.5714 | -50.3683 | 42.9109 | 602.1285 | 53.25 | 0.2 | 0 | 25.0713 | 680.4498 | 5.1 | 26.3641 | 0.99454 | 0.55492
2015-07-06 09:00 | 563.39 | 49.74 | 513.65 | 922.4639 | 22.7962 | -30.3822 | 56.1636 | 33.8364 | -34.148 | 29.1042 | 805.9904 | 37.305 | 0.2 | 0 | 28.1695 | 871.4649 | 5.1 | 32.3333 | 0.97067 | 0.69364
2015-07-06 10:00 | 570.2267 | 49.91 | 520.3167 | 900.4048 | 22.7922 | -15.3841 | 54.6992 | 35.3008 | -17.4381 | 15.5834 | 867.3061 | 37.4325 | 0.2 | 0 | 28.5113 | 933.2499 | 6.2 | 35.3641 | 0.95854 | 0.73354
2015-07-06 11:00 | 577.0633 | 50.08 | 526.9833 | 900.4281 | 22.7883 | -0.38597 | 54.1787 | 35.8213 | -0.43886 | 5.8329 | 895.7662 | 37.56 | 0.2 | 0 | 28.8532 | 962.1794 | 5.9 | 35.9681 | 0.95613 | 0.75437
2015-07-06 12:00 | 583.9 | 50.25 | 533.65 | 922.5003 | 22.7843 | 14.6122 | 54.6561 | 35.3439 | 16.5674 | 14.9109 | 891.437 | 37.6875 | 0.2 | 0 | 29.195 | 958.3195 | 5.7 | 35.6475 | 0.95741 | 0.75235
2015-07-06 13:00 | 510.5033 | 100.09 | 410.4133 | 735.5117 | 22.7803 | 29.6103 | 56.0826 | 33.9174 | 33.2962 | 28.395 | 647.0225 | 75.0675 | 0.2 | 0 | 25.5252 | 747.6152 | 5.4 | 28.763 | 0.98495 | 0.60382
2015-07-06 14:00 | 437.1067 | 149.93 | 287.1767 | 546.8013 | 22.7763 | 44.6084 | 58.3187 | 31.6813 | 49.5421 | 42.1995 | 405.0762 | 112.4475 | 0.2 | 0 | 21.8553 | 539.3791 | 6.6 | 23.4556 | 1.0062 | 0.44502
2015-07-06 15:00 | 363.71 | 199.77 | 163.94 | 339.9111 | 22.7723 | 59.6066 | 61.1641 | 28.8359 | 65.2183 | 56.0032 | 190.0599 | 149.8275 | 0.2 | 0 | 18.1855 | 358.0729 | 6.2 | 17.3898 | 1.0304 | 0.30256
2015-07-06 16:00 | 319.01 | 183.4267 | 135.5833 | 313.6754 | 22.7683 | 74.6047 | 64.3901 | 25.6099 | 80.347 | 69.6918 | 108.8673 | 137.57 | 0.2 | 0 | 15.9505 | 262.3878 | 6.1 | 14.2996 | 1.0428 | 0.22437
2015-07-06 17:00 | 274.31 | 167.0833 | 107.2267 | 283.3576 | 22.7643 | 89.6028 | 67.7645 | 22.2355 | 95.0224 | 83.1639 | 33.7277 | 125.3125 | 0.2 | 0 | 13.7155 | 172.7557 | 6.6 | 11.9986 | 1.052 | 0.14903
2015-07-06 18:00 | 229.61 | 150.74 | 78.87 | 243.0607 | 22.7603 | 104.601 | 71.0655 | 18.9345 | 109.3697 | 96.2832 | 0 | 113.055 | 0.2 | 0 | 11.4805 | 124.5355 | 7.5 | 11.3917 | 1.0544 | 0.10768
2015-07-06 19:00 | 204.34 | 114.6367 | 89.7033 | 327.2322 | 22.7562 | 119.5991 | 74.09 | 15.91 | 123.5133 | 108.831 | 0 | 85.9775 | 0.2 | 0 | 10.217 | 96.1945 | 6.8 | 9.8061 | 1.0608 | 0.083673
2015-07-06 20:00 | 179.07 | 78.5333 | 100.5367 | 435.6697 | 22.7522 | 134.5973 | 76.658 | 13.342 | 137.5562 | 120.4273 | 0 | 58.9 | 0.2 | 0 | 8.9535 | 67.8535 | 6.1 | 8.2204 | 1.0671 | 0.059374
2015-07-06 21:00 | 153.8 | 42.43 | 111.37 | 564.3398 | 22.7481 | 149.5954 | 78.6182 | 11.3818 | 151.5692 | 130.3854 | 0 | 31.8225 | 0.2 | 0 | 7.69 | 39.5125 | 6.6 | 7.8348 | 1.0687 | 0.034625
2015-07-06 22:00 | 146.48 | 41.1 | 105.38 | 598.2505 | 22.744 | 164.5936 | 79.8546 | 10.1454 | 165.5877 | 137.5259 | 0 | 30.825 | 0.2 | 0 | 7.324 | 38.149 | 6.2 | 7.3922 | 1.0704 | 0.033485
2015-07-06 23:00 | 139.16 | 39.77 | 99.39 | 589.4733 | 22.7399 | 179.5917 | 80.2931 | 9.7069 | 179.618 | 140.2914 | 0 | 29.8275 | 0.2 | 0 | 6.958 | 36.7855 | 5.8 | 6.9495 | 1.0722 | 0.032342
2015-07-07 | 131.84 | 38.44 | 93.4 | 532.9852 | 22.7358 | -165.4101 | 79.9074 | 10.0926 | -166.3508 | 137.8103 | 0 | 28.83 | 0.2 | 0 | 6.592 | 35.422 | 6.1 | 7.2069 | 1.0712 | 0.031113
2015-07-07 01:00 | 163.06 | 46.58 | 116.48 | 595.5458 | 22.7317 | -150.4119 | 78.7211 | 11.2789 | -152.3301 | 130.8726 | 0 | 34.935 | 0.2 | 0 | 8.153 | 43.088 | 5.6 | 6.9465 | 1.0722 | 0.037884
2015-07-07 02:00 | 194.28 | 54.72 | 139.56 | 611.4186 | 22.7276 | -135.4138 | 76.8056 | 13.1944 | -138.3153 | 121.0349 | 0 | 41.04 | 0.2 | 0 | 9.714 | 50.754 | 5.7 | 7.2861 | 1.0709 | 0.044567
2015-07-07 03:00 | 225.5 | 62.86 | 162.64 | 600.0988 | 22.7235 | -120.4156 | 74.2749 | 15.7251 | -124.2727 | 109.5071 | 0 | 47.145 | 0.2 | 0 | 11.275 | 58.42 | 6 | 7.8256 | 1.0687 | 0.051195
2015-07-07 04:00 | 246.9233 | 102.44 | 144.4833 | 450.152 | 22.7193 | -105.4174 | 71.2787 | 18.7213 | -110.1339 | 96.9986 | 0 | 76.83 | 0.2 | 0 | 12.3462 | 89.1762 | 5.3 | 8.0868 | 1.0677 | 0.078072
2015-07-07 05:00 | 268.3467 | 142.02 | 126.3267 | 337.1587 | 22.7151 | -90.4193 | 67.9955 | 22.0045 | -95.7978 | 83.9021 | 35.8158 | 106.515 | 0.2 | 0 | 13.4173 | 155.7481 | 5.9 | 10.7671 | 1.0569 | 0.13498
2015-07-07 06:00 | 289.77 | 181.6 | 108.17 | 252.438 | 22.711 | -75.4211 | 64.6275 | 25.3725 | -81.1411 | 70.4424 | 84.5048 | 136.2 | 0.2 | 0 | 14.4885 | 235.1933 | 6.2 | 13.5498 | 1.0458 | 0.20169
2015-07-07 07:00 | 293.6733 | 203.54 | 90.1333 | 188.265 | 22.7068 | -60.4229 | 61.3957 | 28.6043 | -66.0386 | 56.7589 | 103.1999 | 152.655 | 0.2 | 0 | 14.6837 | 270.5386 | 6.3 | 14.7543 | 1.041 | 0.23093
2015-07-07 08:00 | 297.5767 | 225.48 | 72.0967 | 138.1107 | 22.7026 | -45.4247 | 58.5321 | 31.4679 | -50.3939 | 42.9531 | 101.0848 | 169.11 | 0.2 | 0 | 14.8788 | 285.0736 | 6.1 | 15.0086 | 1.04 | 0.2431
2015-07-07 09:00 | 301.48 | 247.42 | 54.06 | 97.3462 | 22.6984 | -30.4266 | 56.266 | 33.734 | -34.1806 | 29.1349 | 85.0295 | 185.565 | 0.2 | 0 | 15.074 | 285.6685 | 6.2 | 15.1271 | 1.0395 | 0.2435
2015-07-07 10:00 | 321.3967 | 251.24 | 70.1567 | 121.7082 | 22.6942 | -15.4284 | 54.7999 | 35.2001 | -17.4792 | 15.5902 | 117.2304 | 188.43 | 0.2 | 0 | 16.0698 | 321.7302 | 6.2 | 16.2541 | 1.035 | 0.27305
2015-07-07 11:00 | 341.3133 | 255.06 | 86.2533 | 147.7281 | 22.6899 | -0.43019 | 54.2771 | 35.7229 | -0.48888 | 5.7376 | 146.9881 | 191.295 | 0.2 | 0 | 17.0657 | 355.3487 | 6.4 | 17.5046 | 1.03 | 0.30012
2015-07-07 12:00 | 361.23 | 258.88 | 102.35 | 177.3456 | 22.6857 | 14.568 | 54.7517 | 35.2483 | 16.5092 | 14.8387 | 171.4313 | 194.16 | 0.2 | 0 | 18.0615 | 383.6528 | 6.2 | 18.1891 | 1.0272 | 0.32317
2015-07-07 13:00 | 289.1033 | 215.9133 | 73.19 | 131.4815 | 22.6815 | 29.5662 | 56.1751 | 33.8249 | 33.2317 | 28.3437 | 115.7189 | 161.935 | 0.2 | 0 | 14.4552 | 292.1091 | 5 | 14.1284 | 1.0435 | 0.24995
2015-07-07 14:00 | 216.9767 | 172.9467 | 44.03 | 84.0494 | 22.6772 | 44.5644 | 58.4086 | 31.5914 | 49.4735 | 42.1597 | 62.3038 | 129.71 | 0.2 | 0 | 10.8488 | 202.8627 | 5.3 | 11.6395 | 1.0534 | 0.17524
2015-07-07 15:00 | 144.85 | 129.98 | 14.87 | 30.9175 | 22.6729 | 59.5626 | 61.252 | 28.748 | 65.1479 | 55.9727 | 17.301 | 97.485 | 0.2 | 0 | 7.2425 | 122.0285 | 4.5 | 8.3134 | 1.0667 | 0.10674
2015-07-07 16:00 | 110.18 | 100.2667 | 9.9133 | 23.0076 | 22.6686 | 74.5608 | 64.4771 | 25.5229 | 80.2768 | 69.6701 | 7.9934 | 75.2 | 0.2 | 0 | 5.509 | 88.7024 | 4.3 | 7.072 | 1.0717 | 0.077952
2015-07-07 17:00 | 75.51 | 70.5533 | 4.9567 | 13.1474 | 22.6643 | 89.559 | 67.8516 | 22.1484 | 94.9537 | 83.1518 | 1.5677 | 52.915 | 0.2 | 0 | 3.7755 | 58.2582 | 4.3 | 6.1206 | 1.0755 | 0.051379
2015-07-07 18:00 | 40.84 | 40.84 | 0 | 0 | 22.66 | 104.5572 | 71.1537 | 18.8463 | 109.3037 | 96.282 | 0 | 30.63 | 0.2 | 0 | 2.042 | 32.672 | 3.6 | 4.621 | 1.0815 | 0.028975
2015-07-07 19:00 | 40.1067 | 40.1067 | 0 | 0 | 22.6557 | 119.5554 | 74.1801 | 15.8199 | 123.4509 | 108.8435 | 0 | 30.08 | 0.2 | 0 | 2.0053 | 32.0853 | 3.3 | 4.3027 | 1.0828 | 0.028488
2015-07-07 20:00 | 39.3733 | 39.3733 | 0 | 0 | 22.6514 | 134.5536 | 76.7507 | 13.2493 | 137.4983 | 120.4572 | 0 | 29.53 | 0.2 | 0 | 1.9687 | 31.4987 | 3.3 | 4.2843 | 1.0829 | 0.027969
2015-07-07 21:00 | 38.64 | 38.64 | 0 | 0 | 22.647 | 149.5518 | 78.7139 | 11.2861 | 151.5164 | 130.4378 | 0 | 28.98 | 0.2 | 0 | 1.932 | 30.912 | 5.6 | 6.566 | 1.0737 | 0.027217
2015-07-07 22:00 | 47.0233 | 41.7867 | 5.2367 | 30.018 | 22.6427 | 164.55 | 79.9533 | 10.0467 | 165.5406 | 137.6046 | 0 | 31.34 | 0.2 | 0 | 2.3512 | 33.6912 | 3.9 | 4.9528 | 1.0802 | 0.029842
2015-07-07 23:00 | 55.4067 | 44.9333 | 10.4733 | 62.7668 | 22.6383 | 179.5482 | 80.3946 | 9.6054 | 179.5771 | 140.3925 | 0 | 33.7 | 0.2 | 0 | 2.7703 | 36.4703 | 5.7 | 6.8397 | 1.0726 | 0.032078
2015-07-08 | 63.79 | 48.08 | 15.71 | 90.5728 | 22.6339 | -165.4536 | 80.0114 | 9.9886 | -166.3855 | 137.9198 | 0 | 36.06 | 0.2 | 0 | 3.1895 | 39.2495 | 5 | 6.2265 | 1.0751 | 0.034601
2015-07-08 01:00 | 79.1833 | 61.5067 | 17.6767 | 91.225 | 22.6296 | -150.4554 | 78.8271 | 11.1729 | -152.3589 | 130.9774 | 0 | 46.13 | 0.2 | 0 | 3.9592 | 50.0892 | 4.7 | 6.2653 | 1.0749 | 0.044151
2015-07-08 02:00 | 94.5767 | 74.9333 | 19.6433 | 86.7532 | 22.6252 | -135.4571 | 76.9132 | 13.0868 | -138.3388 | 121.1299 | 0 | 56.2 | 0.2 | 0 | 4.7288 | 60.9288 | 4.7 | 6.604 | 1.0736 | 0.053638
2015-07-08 03:00 | 109.97 | 88.36 | 21.61 | 80.2761 | 22.6207 | -120.4589 | 74.3836 | 15.6164 | -124.2918 | 109.5918 | 0 | 66.27 | 0.2 | 0 | 5.4985 | 71.7685 | 4.9 | 7.1428 | 1.0714 | 0.063054
2015-07-08 04:00 | 141.4033 | 103.41 | 37.9933 | 119.0428 | 22.6163 | -105.4607 | 71.3881 | 18.6119 | -110.15 | 97.0737 | 0 | 77.5575 | 0.2 | 0 | 7.0702 | 84.6277 | 4.9 | 7.5446 | 1.0698 | 0.07424
2015-07-08 05:00 | 172.8367 | 118.46 | 54.3767 | 145.8203 | 22.6119 | -90.4624 | 68.1053 | 21.8947 | -95.8124 | 83.9686 | 15.3217 | 88.845 | 0.2 | 0 | 8.6418 | 112.8086 | 3.5 | 7.0253 | 1.0719 | 0.099154
2015-07-08 06:00 | 204.27 | 133.51 | 70.76 | 165.8057 | 22.6074 | -75.4642 | 64.7376 | 25.2624 | -81.1562 | 70.5009 | 55.3447 | 100.1325 | 0.2 | 0 | 10.2135 | 165.6907 | 3.3 | 8.4778 | 1.0661 | 0.14485
2015-07-08 07:00 | 253.6633 | 178.2233 | 75.44 | 158.1317 | 22.603 | -60.466 | 61.5057 | 28.4943 | -66.0563 | 56.8093 | 86.5657 | 133.6675 | 0.2 | 0 | 12.6832 | 232.9163 | 4.8 | 12.0786 | 1.0517 | 0.20086
2015-07-08 08:00 | 303.0567 | 222.9367 | 80.12 | 153.9623 | 22.5985 | -45.4677 | 58.6418 | 31.3582 | -50.4166 | 42.9945 | 112.611 | 167.2025 | 0.2 | 0 | 15.1528 | 294.9664 | 5.2 | 14.4177 | 1.0423 | 0.25211
2015-07-08 09:00 | 352.45 | 267.65 | 84.8 | 153.1356 | 22.594 | -30.4695 | 56.3748 | 33.6252 | -34.2106 | 29.164 | 133.7224 | 200.7375 | 0.2 | 0 | 17.6225 | 352.0824 | 4.6 | 15.6026 | 1.0376 | 0.29956
2015-07-08 10:00 | 358.6433 | 285.8967 | 72.7467 | 126.5373 | 22.5896 | -15.4713 | 54.9072 | 35.0928 | -17.518 | 15.5944 | 121.8793 | 214.4225 | 0.2 | 0 | 17.9322 | 354.234 | 5.3 | 16.3698 | 1.0345 | 0.3005
2015-07-08 11:00 | 364.8367 | 304.1433 | 60.6933 | 104.2166 | 22.5851 | -0.47302 | 54.3821 | 35.6179 | -0.53726 | 5.636 | 103.7128 | 228.1075 | 0.2 | 0 | 18.2418 | 350.0622 | 5.9 | 16.8394 | 1.0326 | 0.29642
2015-07-08 12:00 | 371.03 | 322.39 | 48.64 | 84.4937 | 22.5805 | 14.5252 | 54.8538 | 35.1462 | 16.4521 | 14.7658 | 81.7034 | 241.7925 | 0.2 | 0 | 18.5515 | 342.0474 | 6.6 | 17.289 | 1.0308 | 0.28913
2015-07-08 13:00 | 343.6967 | 297.5467 | 46.15 | 83.1207 | 22.576 | 29.5235 | 56.2743 | 33.7257 | 33.1677 | 28.2932 | 73.1906 | 223.16 | 0.2 | 0 | 17.1848 | 313.5354 | 7.1 | 16.898 | 1.0324 | 0.26543
2015-07-08 14:00 | 316.3633 | 272.7033 | 43.66 | 83.5723 | 22.5715 | 44.5217 | 58.5051 | 31.4949 | 49.4051 | 42.1215 | 61.9876 | 204.5275 | 0.2 | 0 | 15.8182 | 282.3332 | 6.5 | 15.3229 | 1.0387 | 0.24047
2015-07-08 15:00 | 289.03 | 247.86 | 41.17 | 85.8587 | 22.5669 | 59.52 | 61.3467 | 28.6533 | 65.0774 | 55.9442 | 48.0809 | 185.895 | 0.2 | 0 | 14.4515 | 248.4274 | 7.3 | 15.0634 | 1.0397 | 0.21181
2015-07-08 16:00 | 256.2467 | 210.36 | 45.8867 | 106.8635 | 22.5624 | 74.5182 | 64.5708 | 25.4292 | 80.2062 | 69.6509 | 37.1605 | 157.77 | 0.2 | 0 | 12.8123 | 207.7429 | 7.2 | 13.692 | 1.0452 | 0.17805
2015-07-08 17:00 | 223.4633 | 172.86 | 50.6033 | 134.766 | 22.5578 | 89.5165 | 67.9454 | 22.0546 | 94.8847 | 83.1426 | 16.0909 | 129.645 | 0.2 | 0 | 11.1732 | 156.909 | 6.2 | 11.1034 | 1.0556 | 0.13582
2015-07-08 18:00 | 190.68 | 135.36 | 55.32 | 172.0886 | 22.5532 | 104.5148 | 71.2486 | 18.7514 | 109.2374 | 96.2844 | 0 | 101.52 | 0.2 | 0 | 9.534 | 111.054 | 5.7 | 9.1704 | 1.0633 | 0.09683
2015-07-08 19:00 | 154.0367 | 113.5367 | 40.5 | 149.4538 | 22.5486 | 119.513 | 74.277 | 15.723 | 123.3884 | 108.8601 | 0 | 85.1525 | 0.2 | 0 | 7.7018 | 92.8543 | 5.7 | 8.6017 | 1.0656 | 0.081135
2015-07-08 20:00 | 117.3933 | 91.7133 | 25.68 | 112.8798 | 22.544 | 134.5113 | 76.8502 | 13.1498 | 137.4405 | 120.492 | 0 | 68.785 | 0.2 | 0 | 5.8697 | 74.6547 | 5.3 | 7.633 | 1.0695 | 0.065469
2015-07-08 21:00 | 80.75 | 69.89 | 10.86 | 55.992 | 22.5394 | 149.5096 | 78.8162 | 11.1838 | 151.4641 | 130.4959 | 0 | 52.4175 | 0.2 | 0 | 4.0375 | 56.455 | 5.4 | 7.1642 | 1.0713 | 0.049596
2015-07-08 22:00 | 83.2667 | 65.83 | 17.4367 | 100.9997 | 22.5348 | 164.5078 | 80.0586 | 9.9414 | 165.4945 | 137.6897 | 0 | 49.3725 | 0.2 | 0 | 4.1633 | 53.5358 | 3.9 | 5.573 | 1.0777 | 0.047311
2015-07-08 23:00 | 85.7833 | 61.77 | 24.0133 | 145.5349 | 22.5302 | 179.5061 | 80.5027 | 9.4973 | 179.5375 | 140.5002 | 0 | 46.3275 | 0.2 | 0 | 4.2892 | 50.6167 | 4.8 | 6.3818 | 1.0745 | 0.044597
2015-07-09 | 88.3 | 57.71 | 30.59 | 178.3132 | 22.5255 | -165.4956 | 80.1219 | 9.8781 | -166.4185 | 138.035 | 0 | 43.2825 | 0.2 | 0 | 4.415 | 47.6975 | 4.4 | 5.8905 | 1.0764 | 0.042102
2015-07-09 01:00 | 116.3767 | 73.9967 | 42.38 | 220.9077 | 22.5208 | -150.4973 | 78.9395 | 11.0605 | -152.3856 | 131.0865 | 0 | 55.4975 | 0.2 | 0 | 5.8188 | 61.3163 | 4.2 | 6.1161 | 1.0755 | 0.054077
2015-07-09 02:00 | 144.4533 | 90.2833 | 54.17 | 241.3001 | 22.5162 | -135.499 | 77.027 | 12.973 | -138.3598 | 121.2279 | 0 | 67.7125 | 0.2 | 0 | 7.2227 | 74.9352 | 4.2 | 6.5417 | 1.0738 | 0.065984
2015-07-09 03:00 | 172.53 | 106.57 | 65.96 | 246.7956 | 22.5115 | -120.5008 | 74.4984 | 15.5016 | -124.3082 | 109.6784 | 0 | 79.9275 | 0.2 | 0 | 8.6265 | 88.554 | 4.3 | 7.0673 | 1.0717 | 0.077823
2015-07-09 04:00 | 201.1467 | 131.6767 | 69.47 | 218.978 | 22.5068 | -105.5025 | 71.5035 | 18.4965 | -110.1631 | 97.1502 | 0 | 98.7575 | 0.2 | 0 | 10.0573 | 108.8148 | 5 | 8.4005 | 1.0664 | 0.095153
2015-07-09 05:00 | 229.7633 | 156.7833 | 72.98 | 196.6986 | 22.5021 | -90.5042 | 68.2212 | 21.7788 | -95.824 | 84.0358 | 20.4384 | 117.5875 | 0.2 | 0 | 11.4882 | 149.514 | 4.9 | 9.5723 | 1.0617 | 0.13017
2015-07-09 06:00 | 258.38 | 181.89 | 76.49 | 180.0056 | 22.4974 | -75.5059 | 64.8537 | 25.1463 | -81.1681 | 70.5594 | 59.9112 | 136.4175 | 0.2 | 0 | 12.919 | 209.2477 | 4.7 | 11.239 | 1.055 | 0.18103
2015-07-09 07:00 | 294.42 | 207.58 | 86.84 | 182.7102 | 22.4926 | -60.5076 | 61.6219 | 28.3781 | -66.0709 | 56.8592 | 99.8874 | 155.685 | 0.2 | 0 | 14.721 | 270.2934 | 4.8 | 13.2467 | 1.047 | 0.23206
2015-07-09 08:00 | 330.46 | 233.27 | 97.19 | 187.387 | 22.4879 | -45.5093 | 58.7576 | 31.2424 | -50.4364 | 43.0349 | 136.9684 | 174.9525 | 0.2 | 0 | 16.523 | 328.4439 | 5.7 | 15.9639 | 1.0361 | 0.27906
2015-07-09 09:00 | 366.5 | 258.96 | 107.54 | 194.7893 | 22.4832 | -30.511 | 56.4899 | 33.5101 | -34.2378 | 29.1916 | 170.0499 | 194.22 | 0.2 | 0 | 18.325 | 382.5949 | 4.5 | 16.4561 | 1.0342 | 0.32445
2015-07-09 10:00 | 356.6867 | 263.1867 | 93.5 | 163.097 | 22.4784 | -15.5127 | 55.0208 | 34.9792 | -17.5546 | 15.5961 | 157.0919 | 197.39 | 0.2 | 0 | 17.8343 | 372.3162 | 5.6 | 17.2349 | 1.0311 | 0.31478
2015-07-09 11:00 | 346.8733 | 267.4133 | 79.46 | 136.8129 | 22.4736 | -0.51437 | 54.4936 | 35.5064 | -0.58388 | 5.5282 | 136.1765 | 200.56 | 0.2 | 0 | 17.3437 | 354.0802 | 6.9 | 17.965 | 1.0281 | 0.29852
2015-07-09 12:00 | 337.06 | 271.64 | 65.42 | 113.9502 | 22.4688 | 14.4839 | 54.9626 | 35.0374 | 16.3962 | 14.6924 | 110.2242 | 203.73 | 0.2 | 0 | 16.853 | 330.8072 | 6.3 | 16.6377 | 1.0334 | 0.28034
2015-07-09 13:00 | 316.08 | 252.0567 | 64.0233 | 115.6326 | 22.464 | 29.4822 | 56.3802 | 33.6198 | 33.1044 | 28.2436 | 101.8658 | 189.0425 | 0.2 | 0 | 15.804 | 306.7123 | 6.5 | 16.0848 | 1.0357 | 0.26047
2015-07-09 14:00 | 295.1 | 232.4733 | 62.6267 | 120.2314 | 22.4592 | 44.4806 | 58.6084 | 31.3916 | 49.3369 | 42.0849 | 89.2301 | 174.355 | 0.2 | 0 | 14.755 | 278.3401 | 7.9 | 16.5981 | 1.0336 | 0.23591
2015-07-09 15:00 | 274.12 | 212.89 | 61.23 | 128.108 | 22.4544 | 59.4789 | 61.448 | 28.552 | 65.0069 | 55.9178 | 71.7894 | 159.6675 | 0.2 | 0 | 13.706 | 245.1629 | 7.6 | 15.2613 | 1.039 | 0.20886
2015-07-09 16:00 | 266.7333 | 175.8 | 90.9333 | 212.5541 | 22.4496 | 74.4772 | 64.6712 | 25.3288 | 80.1355 | 69.6343 | 73.971 | 131.85 | 0.2 | 0 | 13.3367 | 219.1577 | 6.8 | 13.6487 | 1.0454 | 0.18787
2015-07-09 17:00 | 259.3467 | 138.71 | 120.6367 | 322.6746 | 22.4447 | 89.4755 | 68.0458 | 21.9542 | 94.8154 | 83.1365 | 38.5612 | 104.0325 | 0.2 | 0 | 12.9673 | 155.561 | 8 | 12.8613 | 1.0486 | 0.13375
2015-07-09 18:00 | 251.96 | 101.62 | 150.34 | 470.1312 | 22.4399 | 104.4739 | 71.3502 | 18.6498 | 109.171 | 96.2904 | 0 | 76.215 | 0.2 | 0 | 12.598 | 88.813 | 5.7 | 8.4754 | 1.0661 | 0.07764
2015-07-09 19:00 | 205.6 | 86.1633 | 119.4367 | 443.5951 | 22.435 | 119.4722 | 74.3805 | 15.6195 | 123.326 | 108.8809 | 0 | 64.6225 | 0.2 | 0 | 10.28 | 74.9025 | 6.2 | 8.5407 | 1.0658 | 0.065464
2015-07-09 20:00 | 159.24 | 70.7067 | 88.5333 | 392.2697 | 22.4302 | 134.4705 | 76.9562 | 13.0438 | 137.3831 | 120.5317 | 0 | 53.03 | 0.2 | 0 | 7.962 | 60.992 | 4.7 | 6.606 | 1.0736 | 0.053693
2015-07-09 21:00 | 112.88 | 55.25 | 57.63 | 300.0158 | 22.4253 | 149.4688 | 78.9252 | 11.0748 | 151.4124 | 130.5596 | 0 | 41.4375 | 0.2 | 0 | 5.644 | 47.0815 | 7.6 | 9.0713 | 1.0637 | 0.041067
2015-07-09 22:00 | 109.1267 | 51.2267 | 57.9 | 339.1585 | 22.4204 | 164.4672 | 80.1705 | 9.8295 | 165.4493 | 137.7812 | 0 | 38.42 | 0.2 | 0 | 5.4563 | 43.8763 | 7 | 8.3711 | 1.0665 | 0.038372
2015-07-09 23:00 | 105.3733 | 47.2033 | 58.17 | 356.8115 | 22.4155 | 179.4655 | 80.6173 | 9.3827 | 179.4992 | 140.6144 | 0 | 35.4025 | 0.2 | 0 | 5.2687 | 40.6712 | 6.7 | 7.971 | 1.0681 | 0.035622
2015-07-10 | 101.62 | 43.18 | 58.44 | 344.6947 | 22.4105 | -165.5361 | 80.2388 | 9.7612 | -166.4498 | 138.1557 | 0 | 32.385 | 0.2 | 0 | 5.081 | 37.466 | 7.1 | 8.2708 | 1.0669 | 0.032778
2015-07-10 01:00 | 109.4967 | 64.3033 | 45.1933 | 238.0967 | 22.4056 | -150.5378 | 79.0583 | 10.9417 | -152.4102 | 131.1998 | 0 | 48.2275 | 0.2 | 0 | 5.4748 | 53.7023 | 6.5 | 8.1782 | 1.0673 | 0.046999
2015-07-10 02:00 | 117.3733 | 85.4267 | 31.9467 | 143.6126 | 22.4007 | -135.5394 | 77.147 | 12.853 | -138.3784 | 121.3288 | 0 | 64.07 | 0.2 | 0 | 5.8687 | 69.9387 | 6.3 | 8.4856 | 1.0661 | 0.061138
2015-07-10 03:00 | 125.25 | 106.55 | 18.7 | 70.5044 | 22.3957 | -120.5411 | 74.6193 | 15.3807 | -124.3219 | 109.7671 | 0 | 79.9125 | 0.2 | 0 | 6.2625 | 86.175 | 6 | 8.693 | 1.0652 | 0.075273
2015-07-10 04:00 | 140.19 | 119.3567 | 20.8333 | 66.0883 | 22.3907 | -105.5427 | 71.625 | 18.375 | -110.1733 | 97.2277 | 0 | 89.5175 | 0.2 | 0 | 7.0095 | 96.527 | 6.9 | 9.9165 | 1.0603 | 0.083928
2015-07-10 05:00 | 155.13 | 132.1633 | 22.9667 | 62.2321 | 22.3858 | -90.5444 | 68.343 | 21.657 | -95.8324 | 84.1035 | 6.3933 | 99.1225 | 0.2 | 0 | 7.7565 | 113.2723 | 5.1 | 8.6398 | 1.0654 | 0.098962
2015-07-10 06:00 | 170.07 | 144.97 | 25.1 | 59.3379 | 22.3808 | -75.546 | 64.9758 | 25.0242 | -81.1768 | 70.6179 | 19.6923 | 108.7275 | 0.2 | 0 | 8.5035 | 136.9233 | 5.2 | 9.4789 | 1.0621 | 0.11925
2015-07-10 07:00 | 224.0467 | 181.1133 | 42.9333 | 90.6893 | 22.3758 | -60.5477 | 61.7441 | 28.2559 | -66.0823 | 56.9086 | 49.5142 | 135.835 | 0.2 | 0 | 11.2023 | 196.5516 | 4.9 | 11.0422 | 1.0558 | 0.17017
2015-07-10 08:00 | 278.0233 | 217.2567 | 60.7667 | 117.574 | 22.3708 | -45.5493 | 58.8796 | 31.1204 | -50.4531 | 43.0742 | 85.8842 | 162.9425 | 0.2 | 0 | 13.9012 | 262.7279 | 7.9 | 16.1102 | 1.0356 | 0.2231
2015-07-10 09:00 | 332 | 253.4 | 78.6 | 142.8269 | 22.3658 | -30.5509 | 56.6113 | 33.3887 | -34.2623 | 29.2176 | 124.6553 | 190.05 | 0.2 | 0 | 16.6 | 331.3053 | 7.8 | 18.1533 | 1.0274 | 0.27911
2015-07-10 10:00 | 332.1433 | 260.38 | 71.7633 | 125.5569 | 22.3607 | -15.5525 | 55.1409 | 34.8591 | -17.5889 | 15.5955 | 120.9344 | 195.285 | 0.2 | 0 | 16.6072 | 332.8265 | 7 | 17.4008 | 1.0304 | 0.28121
2015-07-10 11:00 | 332.2867 | 267.36 | 64.9267 | 112.1136 | 22.3557 | -0.55418 | 54.6117 | 35.3883 | -0.62868 | 5.4142 | 111.6134 | 200.52 | 0.2 | 0 | 16.6143 | 328.7477 | 7.8 | 18.0734 | 1.0277 | 0.27704
2015-07-10 12:00 | 332.43 | 274.34 | 58.09 | 101.4743 | 22.3506 | 14.4442 | 55.078 | 34.922 | 16.3415 | 14.6188 | 98.1892 | 205.755 | 0.2 | 0 | 16.6215 | 320.5657 | 8.5 | 18.5177 | 1.0259 | 0.26968
2015-07-10 13:00 | 363.11 | 218.9767 | 144.1333 | 261.0912 | 22.3456 | 29.4426 | 56.4928 | 33.5072 | 33.0418 | 28.1952 | 230.1108 | 164.2325 | 0.2 | 0 | 18.1555 | 412.4988 | 8.9 | 21.7906 | 1.0128 | 0.34259
2015-07-10 14:00 | 393.79 | 163.6133 | 230.1767 | 443.2903 | 22.3405 | 44.441 | 58.7183 | 31.2817 | 49.2691 | 42.05 | 329.1701 | 122.71 | 0.2 | 0 | 19.6895 | 471.5696 | 8 | 22.7365 | 1.0091 | 0.39019
2015-07-10 15:00 | 424.47 | 108.25 | 316.22 | 663.9097 | 22.3354 | 59.4393 | 61.556 | 28.444 | 64.9364 | 55.8936 | 372.2751 | 81.1875 | 0.2 | 0 | 21.2235 | 474.6861 | 8.8 | 23.6339 | 1.0055 | 0.39137
2015-07-10 16:00 | 311.1 | 94.95 | 216.15 | 507.2472 | 22.3303 | 74.4377 | 64.7782 | 25.2218 | 80.0646 | 69.6204 | 176.6431 | 71.2125 | 0.2 | 0 | 15.555 | 263.4106 | 7.1 | 15.3316 | 1.0387 | 0.22435
2015-07-10 17:00 | 197.73 | 81.65 | 116.08 | 311.9338 | 22.3252 | 89.4361 | 68.1529 | 21.8471 | 94.746 | 83.1335 | 37.2939 | 61.2375 | 0.2 | 0 | 9.8865 | 108.4179 | 6.4 | 9.7881 | 1.0608 | 0.094312
2015-07-10 18:00 | 84.36 | 68.35 | 16.01 | 50.347 | 22.3201 | 104.4345 | 71.4584 | 18.5416 | 109.1045 | 96.3 | 0 | 51.2625 | 0.2 | 0 | 4.218 | 55.4805 | 5.9 | 7.6338 | 1.0695 | 0.048654
2015-07-10 19:00 | 89.4333 | 56.1267 | 33.3067 | 124.5599 | 22.3149 | 119.4329 | 74.4907 | 15.5093 | 123.2637 | 108.9059 | 0 | 42.095 | 0.2 | 0 | 4.4717 | 46.5667 | 5.1 | 6.5552 | 1.0738 | 0.041002
2015-07-10 20:00 | 94.5067 | 43.9033 | 50.6033 | 226.1317 | 22.3098 | 134.4313 | 77.069 | 12.931 | 137.326 | 120.5763 | 0 | 32.9275 | 0.2 | 0 | 4.7253 | 37.6528 | 4.9 | 6.0767 | 1.0757 | 0.033212
2015-07-10 21:00 | 99.58 | 31.68 | 67.9 | 357.1619 | 22.3046 | 149.4297 | 79.0408 | 10.9592 | 151.3615 | 130.6291 | 0 | 23.76 | 0.2 | 0 | 4.979 | 28.739 | 5.2 | 6.0981 | 1.0756 | 0.025348
2015-07-10 22:00 | 105.6533 | 33.9667 | 71.6867 | 424.9881 | 22.2995 | 164.4281 | 80.289 | 9.711 | 165.4052 | 137.8792 | 0 | 25.475 | 0.2 | 0 | 5.2827 | 30.7577 | 5.1 | 6.0612 | 1.0758 | 0.027132
2015-07-10 23:00 | 111.7267 | 36.2533 | 75.4733 | 468.9479 | 22.2943 | 179.4265 | 80.7384 | 9.2616 | 179.4624 | 140.735 | 0 | 27.19 | 0.2 | 0 | 5.5863 | 32.7763 | 4.7 | 5.7243 | 1.0771 | 0.028949
2015-07-11 | 117.8 | 38.54 | 79.26 | 473.4194 | 22.2891 | -165.5751 | 80.3621 | 9.6379 | -166.4792 | 138.282 | 0 | 28.905 | 0.2 | 0 | 5.89 | 34.795 | 4 | 5.0873 | 1.0797 | 0.030804
2015-07-11 01:00 | 130.0433 | 60.3467 | 69.6967 | 371.3814 | 22.2839 | -150.5766 | 79.1832 | 10.8168 | -152.4326 | 131.3173 | 0 | 45.26 | 0.2 | 0 | 6.5022 | 51.7622 | 3.9 | 5.5176 | 1.0779 | 0.045753
2015-07-11 02:00 | 142.2867 | 82.1533 | 60.1333 | 272.9575 | 22.2787 | -135.5782 | 77.2732 | 12.7268 | -138.3945 | 121.4326 | 0 | 61.615 | 0.2 | 0 | 7.1143 | 68.7293 | 3.9 | 6.0478 | 1.0758 | 0.06063
2015-07-11 03:00 | 154.53 | 103.96 | 50.57 | 192.2122 | 22.2735 | -120.5798 | 74.7462 | 15.2538 | -124.3328 | 109.8575 | 0 | 77.97 | 0.2 | 0 | 7.7265 | 85.6965 | 4 | 6.678 | 1.0733 | 0.075421
2015-07-11 04:00 | 192.63 | 128.4133 | 64.2167 | 205.0842 | 22.2682 | -105.5814 | 71.7524 | 18.2476 | -110.1804 | 97.3063 | 0 | 96.31 | 0.2 | 0 | 9.6315 | 105.9415 | 3.7 | 7.0107 | 1.072 | 0.093123
2015-07-11 05:00 | 230.73 | 152.8667 | 77.8633 | 212.1759 | 22.263 | -90.583 | 68.4708 | 21.5292 | -95.8376 | 84.1715 | 21.5466 | 114.65 | 0.2 | 0 | 11.5365 | 147.7331 | 3.8 | 8.4167 | 1.0663 | 0.12918
2015-07-11 06:00 | 268.83 | 177.32 | 91.51 | 217.3759 | 22.2577 | -75.5845 | 65.1038 | 24.8962 | -81.1823 | 70.6763 | 71.9309 | 132.99 | 0.2 | 0 | 13.4415 | 218.3624 | 2.9 | 9.7238 | 1.0611 | 0.19
2015-07-11 07:00 | 287.12 | 222.9867 | 64.1333 | 136.0371 | 22.2525 | -60.5861 | 61.8722 | 28.1278 | -66.0904 | 56.9574 | 74.1759 | 167.24 | 0.2 | 0 | 14.356 | 255.7719 | 2.9 | 10.8929 | 1.0564 | 0.22157
2015-07-11 08:00 | 305.41 | 268.6533 | 36.7567 | 71.3828 | 22.2472 | -45.5877 | 59.0077 | 30.9923 | -50.4667 | 43.1126 | 52.1103 | 201.49 | 0.2 | 0 | 15.2705 | 268.8708 | 3.2 | 11.6022 | 1.0536 | 0.23229
2015-07-11 09:00 | 323.7 | 314.32 | 9.38 | 17.1025 | 22.2419 | -30.5892 | 56.7388 | 33.2612 | -34.284 | 29.2421 | 14.923 | 235.74 | 0.2 | 0 | 16.185 | 266.848 | 3.7 | 12.039 | 1.0518 | 0.23016
2015-07-11 10:00 | 329.4567 | 321.0467 | 8.41 | 14.7609 | 22.2366 | -15.5908 | 55.2673 | 34.7327 | -17.6207 | 15.5925 | 14.2177 | 240.785 | 0.2 | 0 | 16.4728 | 271.4755 | 3.2 | 11.6836 | 1.0533 | 0.23447
2015-07-11 11:00 | 335.2133 | 327.7733 | 7.44 | 12.8866 | 22.2313 | -0.59235 | 54.7361 | 35.2639 | -0.67155 | 5.2941 | 12.8317 | 245.83 | 0.2 | 0 | 16.7607 | 275.4223 | 3.5 | 12.1069 | 1.0516 | 0.23749
2015-07-11 12:00 | 340.97 | 334.5 | 6.47 | 11.3367 | 22.226 | 14.4061 | 55.2 | 34.8 | 16.2882 | 14.5452 | 10.9733 | 250.875 | 0.2 | 0 | 17.0485 | 278.8968 | 3.5 | 12.2155 | 1.0511 | 0.24039
2015-07-11 13:00 | 319.12 | 280.0467 | 39.0733 | 71.0028 | 22.2206 | 29.4045 | 56.6119 | 33.3881 | 32.9801 | 28.1481 | 62.6054 | 210.035 | 0.2 | 0 | 15.956 | 288.5964 | 4 | 13.0186 | 1.0479 | 0.24799
2015-07-11 14:00 | 297.27 | 225.5933 | 71.6767 | 138.5039 | 22.2153 | 44.403 | 58.8349 | 31.1651 | 49.2017 | 42.0169 | 102.9011 | 169.195 | 0.2 | 0 | 14.8635 | 286.9596 | 4.1 | 13.0675 | 1.0477 | 0.24654
2015-07-11 15:00 | 275.42 | 171.14 | 104.28 | 219.7498 | 22.2099 | 59.4014 | 61.6706 | 28.3294 | 64.8661 | 55.8717 | 123.2902 | 128.355 | 0.2 | 0 | 13.771 | 265.4162 | 3.8 | 12.0943 | 1.0516 | 0.22888
2015-07-11 16:00 | 247.9867 | 137.8133 | 110.1733 | 259.6417 | 22.2046 | 74.3999 | 64.8918 | 25.1082 | 79.9937 | 69.6091 | 90.4651 | 103.36 | 0.2 | 0 | 12.3993 | 206.2244 | 3.7 | 10.1445 | 1.0594 | 0.17915
2015-07-11 17:00 | 220.5533 | 104.4867 | 116.0667 | 313.4504 | 22.1992 | 89.3984 | 68.2667 | 21.7333 | 94.6766 | 83.1336 | 37.4745 | 78.365 | 0.2 | 0 | 11.0277 | 126.8672 | 4.1 | 8.0646 | 1.0677 | 0.11108
2015-07-11 18:00 | 193.12 | 71.16 | 121.96 | 385.8368 | 22.1938 | 104.3968 | 71.5732 | 18.4268 | 109.0381 | 96.3133 | 0 | 53.37 | 0.2 | 0 | 9.656 | 63.026 | 5 | 6.9696 | 1.0721 | 0.055409
2015-07-11 19:00 | 175.4833 | 60.76 | 114.7233 | 432.2163 | 22.1884 | 119.3953 | 74.6075 | 15.3925 | 123.2016 | 108.9352 | 0 | 45.57 | 0.2 | 0 | 8.7742 | 54.3442 | 4.9 | 6.5983 | 1.0736 | 0.047842
2015-07-11 20:00 | 157.8467 | 50.36 | 107.4867 | 484.724 | 22.183 | 134.3938 | 77.1883 | 12.8117 | 137.2693 | 120.6258 | 0 | 37.77 | 0.2 | 0 | 7.8923 | 45.6623 | 3.6 | 5.0269 | 1.0799 | 0.040435
2015-07-11 21:00 | 140.21 | 39.96 | 100.25 | 533.1973 | 22.1776 | 149.3922 | 79.1629 | 10.8371 | 151.3113 | 130.7043 | 0 | 29.97 | 0.2 | 0 | 7.0105 | 36.9805 | 3.3 | 4.4556 | 1.0822 | 0.032816
2015-07-11 22:00 | 129.8467 | 47.6367 | 82.21 | 493.6671 | 22.1721 | 164.3907 | 80.4139 | 9.5861 | 165.3622 | 137.9835 | 0 | 35.7275 | 0.2 | 0 | 6.4923 | 42.2198 | 3.6 | 4.9194 | 1.0803 | 0.037401
2015-07-11 23:00 | 119.4833 | 55.3133 | 64.17 | 404.2332 | 22.1667 | 179.3892 | 80.8659 | 9.1341 | 179.4271 | 140.8621 | 0 | 41.485 | 0.2 | 0 | 5.9742 | 47.4592 | 4 | 5.4831 | 1.0781 | 0.041955
2015-07-12 | 109.12 | 62.99 | 46.13 | 279.2548 | 22.1612 | -165.6123 | 80.4918 | 9.5082 | -166.5068 | 138.4137 | 0 | 47.2425 | 0.2 | 0 | 5.456 | 52.6985 | 3.2 | 4.8468 | 1.0806 | 0.046696
2015-07-12 01:00 | 127.7867 | 79.87 | 47.9167 | 258.4234 | 22.1558 | -150.6138 | 79.3144 | 10.6856 | -152.4527 | 131.4387 | 0 | 59.9025 | 0.2 | 0 | 6.3893 | 66.2918 | 3.4 | 5.4716 | 1.0781 | 0.058605
2015-07-12 02:00 | 146.4533 | 96.75 | 49.7033 | 227.9439 | 22.1503 | -135.6154 | 77.4054 | 12.5946 | -138.4079 | 121.5392 | 0 | 72.5625 | 0.2 | 0 | 7.3227 | 79.8852 | 3.3 | 5.7964 | 1.0768 | 0.070538
2015-07-12 03:00 | 165.12 | 113.63 | 51.49 | 197.3889 | 22.1448 | -120.6169 | 74.8792 | 15.1208 | -124.3408 | 109.9497 | 0 | 85.2225 | 0.2 | 0 | 8.256 | 93.4785 | 3.3 | 6.2212 | 1.0751 | 0.08241
2015-07-12 04:00 | 199.0633 | 145.4867 | 53.5767 | 172.3208 | 22.1393 | -105.6184 | 71.8858 | 18.1142 | -110.1845 | 97.3858 | 0 | 109.115 | 0.2 | 0 | 9.9532 | 119.0682 | 4.7 | 8.4209 | 1.0663 | 0.10411
2015-07-12 05:00 | 233.0067 | 177.3433 | 55.6633 | 152.5838 | 22.1338 | -90.6199 | 68.6044 | 21.3956 | -95.8396 | 84.24 | 15.3137 | 133.0075 | 0.2 | 0 | 11.6503 | 159.9715 | 4.9 | 9.8991 | 1.0604 | 0.1391
2015-07-12 06:00 | 266.95 | 209.2 | 57.75 | 137.8757 | 22.1283 | -75.6214 | 65.2376 | 24.7624 | -81.1844 | 70.7345 | 45.4916 | 156.9 | 0.2 | 0 | 13.3475 | 215.7391 | 5.5 | 12.2418 | 1.051 | 0.18593
2015-07-12 07:00 | 344.1067 | 186.18 | 157.9267 | 336.4614 | 22.1228 | -60.6229 | 62.0062 | 27.9938 | -66.0953 | 57.0056 | 183.2222 | 139.635 | 0.2 | 0 | 17.2053 | 340.0626 | 5.6 | 16.227 | 1.0351 | 0.28864
2015-07-12 08:00 | 421.2633 | 163.16 | 258.1033 | 503.2078 | 22.1172 | -45.6244 | 59.1417 | 30.8583 | -50.4771 | 43.1499 | 367.1237 | 122.37 | 0.2 | 0 | 21.0632 | 510.5569 | 6.5 | 22.4549 | 1.0102 | 0.42292
2015-07-12 09:00 | 498.42 | 140.14 | 358.28 | 655.5852 | 22.1117 | -30.6259 | 56.8725 | 33.1275 | -34.3028 | 29.2651 | 571.9108 | 105.105 | 0.2 | 0 | 24.921 | 701.9368 | 6.5 | 28.4355 | 0.98626 | 0.56768
2015-07-12 10:00 | 506.2233 | 142.0467 | 364.1767 | 641.3317 | 22.1061 | -15.6273 | 55.4 | 34.6 | -17.6501 | 15.5874 | 617.7448 | 106.535 | 0.2 | 0 | 25.3112 | 749.5909 | 6.8 | 30.2247 | 0.9791 | 0.60182
2015-07-12 11:00 | 514.0267 | 143.9533 | 370.0733 | 643.0735 | 22.1005 | -0.62883 | 54.867 | 35.133 | -0.71242 | 5.1679 | 640.4595 | 107.965 | 0.2 | 0 | 25.7013 | 774.1258 | 6.6 | 30.7914 | 0.97683 | 0.62008
2015-07-12 12:00 | 521.83 | 145.86 | 375.97 | 660.905 | 22.0949 | 14.3697 | 55.3284 | 34.6716 | 16.2364 | 14.4718 | 639.9351 | 109.395 | 0.2 | 0 | 26.0915 | 775.4216 | 6.7 | 30.9319 | 0.97627 | 0.62076
2015-07-12 13:00 | 478.3667 | 155.0633 | 323.3033 | 589.4598 | 22.0893 | 29.3682 | 56.7376 | 33.2624 | 32.9194 | 28.1023 | 519.9672 | 116.2975 | 0.2 | 0 | 23.9183 | 660.183 | 6.9 | 27.5307 | 0.98988 | 0.53587
2015-07-12 14:00 | 434.9033 | 164.2667 | 270.6367 | 524.8292 | 22.0837 | 44.3667 | 58.958 | 31.042 | 49.1348 | 41.9858 | 390.1112 | 123.2 | 0.2 | 0 | 21.7452 | 535.0563 | 7.6 | 24.3205 | 1.0027 | 0.43994
2015-07-12 15:00 | 391.44 | 173.47 | 217.97 | 461.14 | 22.0781 | 59.3653 | 61.7918 | 28.2082 | 64.796 | 55.8522 | 258.8518 | 130.1025 | 0.2 | 0 | 19.572 | 408.5263 | 6.1 | 18.8664 | 1.0245 | 0.34321
2015-07-12 16:00 | 345.8333 | 139.2433 | 206.59 | 489.0547 | 22.0725 | 74.3638 | 65.0121 | 24.9879 | 79.9229 | 69.6007 | 170.4654 | 104.4325 | 0.2 | 0 | 17.2917 | 292.1896 | 7.4 | 16.5309 | 1.0339 | 0.24771
2015-07-12 17:00 | 300.2267 | 105.0167 | 195.21 | 529.9786 | 22.0668 | 89.3623 | 68.387 | 21.613 | 94.6071 | 83.137 | 63.3306 | 78.7625 | 0.2 | 0 | 15.0113 | 157.1044 | 6.9 | 11.8095 | 1.0528 | 0.13562
2015-07-12 18:00 | 254.62 | 70.79 | 183.83 | 585.2947 | 22.0612 | 104.3609 | 71.6947 | 18.3053 | 108.9717 | 96.3302 | 0 | 53.0925 | 0.2 | 0 | 12.731 | 65.8235 | 6.8 | 8.857 | 1.0646 | 0.057461
2015-07-12 19:00 | 215.3633 | 61.5067 | 153.8567 | 584.2194 | 22.0555 | 119.3594 | 74.7308 | 15.2692 | 123.1397 | 108.9687 | 0 | 46.13 | 0.2 | 0 | 10.7682 | 56.8982 | 6.4 | 8.1781 | 1.0673 | 0.049796
2015-07-12 20:00 | 176.1067 | 52.2233 | 123.8833 | 564.1169 | 22.0498 | 134.3579 | 77.3141 | 12.6859 | 137.2132 | 120.6802 | 0 | 39.1675 | 0.2 | 0 | 8.8053 | 47.9728 | 6.3 | 7.7992 | 1.0688 | 0.042044
2015-07-12 21:00 | 136.85 | 42.94 | 93.91 | 505.4061 | 22.0441 | 149.3565 | 79.2916 | 10.7084 | 151.2619 | 130.7852 | 0 | 32.205 | 0.2 | 0 | 6.8425 | 39.0475 | 5.2 | 6.4202 | 1.0743 | 0.034399
2015-07-12 22:00 | 126.3533 | 43.94 | 82.4133 | 501.7027 | 22.0384 | 164.355 | 80.5453 | 9.4547 | 165.3204 | 138.0941 | 0 | 32.955 | 0.2 | 0 | 6.3177 | 39.2727 | 4.8 | 6.0273 | 1.0759 | 0.034648
2015-07-12 23:00 | 115.8567 | 44.94 | 70.9167 | 453.3227 | 22.0327 | 179.3536 | 80.9998 | 9.0002 | 179.3933 | 140.9955 | 0 | 33.705 | 0.2 | 0 | 5.7928 | 39.4978 | 3.4 | 4.6343 | 1.0815 | 0.035027
2015-07-13 | 105.36 | 45.94 | 59.42 | 364.8753 | 22.027 | -165.6479 | 80.6276 | 9.3724 | -166.5324 | 138.5508 | 0 | 34.455 | 0.2 | 0 | 5.268 | 39.723 | 3.5 | 4.7413 | 1.081 | 0.035212
2015-07-13 01:00 | 134.51 | 53.64 | 80.87 | 441.7598 | 22.0213 | -150.6493 | 79.4518 | 10.5482 | -152.4705 | 131.5642 | 0 | 40.23 | 0.2 | 0 | 6.7255 | 46.9555 | 3.7 | 5.1674 | 1.0793 | 0.041558
2015-07-13 02:00 | 163.66 | 61.34 | 102.32 | 474.3744 | 22.0155 | -135.6507 | 77.5437 | 12.4563 | -138.4188 | 121.6484 | 0 | 46.005 | 0.2 | 0 | 8.183 | 54.188 | 4 | 5.6934 | 1.0772 | 0.047866
2015-07-13 03:00 | 192.81 | 69.04 | 123.77 | 478.772 | 22.0098 | -120.6522 | 75.018 | 14.982 | -124.3458 | 110.0435 | 0 | 51.78 | 0.2 | 0 | 9.6405 | 61.4205 | 3.9 | 5.8194 | 1.0767 | 0.054229
2015-07-13 04:00 | 224.63 | 115.9067 | 108.7233 | 352.3082 | 22.004 | -105.6536 | 72.0249 | 17.9751 | -110.1854 | 97.4663 | 0 | 86.93 | 0.2 | 0 | 11.2315 | 98.1615 | 4.8 | 7.8675 | 1.0685 | 0.086009
2015-07-13 05:00 | 256.45 | 162.7733 | 93.6767 | 258.391 | 21.9983 | -90.655 | 68.7438 | 21.2562 | -95.8383 | 84.3087 | 25.6244 | 122.08 | 0.2 | 0 | 12.8225 | 160.5269 | 4.7 | 9.7165 | 1.0611 | 0.13968
2015-07-13 06:00 | 288.27 | 209.64 | 78.63 | 188.7236 | 21.9925 | -75.6565 | 65.3773 | 24.6227 | -81.1832 | 70.7925 | 62.0883 | 157.23 | 0.2 | 0 | 14.4135 | 233.7318 | 5 | 12.3041 | 1.0508 | 0.20139
2015-07-13 07:00 | 315.96 | 232.83 | 83.13 | 177.9255 | 21.9867 | -60.6579 | 62.1461 | 27.8539 | -66.0968 | 57.0532 | 96.7666 | 174.6225 | 0.2 | 0 | 15.798 | 287.1871 | 5.8 | 14.7746 | 1.0409 | 0.24513
2015-07-13 08:00 | 343.65 | 256.02 | 87.63 | 171.5487 | 21.9809 | -45.6593 | 59.2817 | 30.7183 | -50.4843 | 43.1862 | 125.082 | 192.015 | 0.2 | 0 | 17.1825 | 334.2795 | 5.6 | 16.0462 | 1.0358 | 0.28393
2015-07-13 09:00 | 371.34 | 279.21 | 92.13 | 169.2136 | 21.9751 | -30.6607 | 57.0122 | 32.9878 | -34.3186 | 29.2866 | 147.5853 | 209.4075 | 0.2 | 0 | 18.567 | 375.5598 | 5.6 | 17.3362 | 1.0307 | 0.3174
2015-07-13 10:00 | 373.5233 | 278.0067 | 95.5167 | 168.8028 | 21.9692 | -15.6621 | 55.5388 | 34.4612 | -17.6768 | 15.5801 | 162.6003 | 208.505 | 0.2 | 0 | 18.6762 | 389.7815 | 6 | 18.1807 | 1.0273 | 0.32834
2015-07-13 11:00 | 375.7067 | 276.8033 | 98.9033 | 172.451 | 21.9634 | -0.66353 | 55.0043 | 34.9957 | -0.7512 | 5.0357 | 171.7854 | 207.6025 | 0.2 | 0 | 18.7853 | 398.1732 | 5.5 | 17.9429 | 1.0282 | 0.33572
2015-07-13 12:00 | 377.89 | 275.6 | 102.29 | 180.4268 | 21.9575 | 14.3351 | 55.4633 | 34.5367 | 16.1862 | 14.3988 | 174.7593 | 206.7 | 0.2 | 0 | 18.8945 | 400.3538 | 5.7 | 18.2111 | 1.0272 | 0.33721
2015-07-13 13:00 | 337.65 | 266.7033 | 70.9467 | 129.8099 | 21.9517 | 29.3337 | 56.8698 | 33.1302 | 32.8597 | 28.0581 | 114.5535 | 200.0275 | 0.2 | 0 | 16.8825 | 331.4635 | 5.7 | 16.0582 | 1.0358 | 0.28152
2015-07-13 14:00 | 297.41 | 257.8067 | 39.6033 | 77.0905 | 21.9458 | 44.3323 | 59.0877 | 30.9123 | 49.0686 | 41.9568 | 57.3283 | 193.355 | 0.2 | 0 | 14.8705 | 265.5538 | 6.1 | 14.3986 | 1.0424 | 0.22699
2015-07-13 15:00 | 257.17 | 248.91 | 8.26 | 17.548 | 21.9399 | 59.3309 | 61.9196 | 28.0804 | 64.7262 | 55.8351 | 9.8545 | 186.6825 | 0.2 | 0 | 12.8585 | 209.3955 | 6.2 | 12.7436 | 1.049 | 0.18012
2015-07-13 16:00 | 213.8067 | 205.8067 | 8 | 19.0286 | 21.934 | 74.3295 | 65.1389 | 24.8611 | 79.8523 | 69.5951 | 6.6344 | 154.355 | 0.2 | 0 | 10.6903 | 171.6797 | 5.7 | 11.065 | 1.0557 | 0.14862
2015-07-13 17:00 | 170.4433 | 162.7033 | 7.74 | 21.1316 | 21.9281 | 89.3281 | 68.5139 | 21.4861 | 94.5379 | 83.1436 | 2.5227 | 122.0275 | 0.2 | 0 | 8.5222 | 133.0724 | 6 | 10.1585 | 1.0594 | 0.1156
2015-07-13 18:00 | 127.08 | 119.6 | 7.48 | 23.9774 | 21.9222 | 104.3267 | 71.8226 | 18.1774 | 108.9056 | 96.3509 | 0 | 89.7 | 0.2 | 0 | 6.354 | 96.054 | 4.9 | 7.9017 | 1.0684 | 0.084151
2015-07-13 19:00 | 104.47 | 98.0833 | 6.3867 | 24.4544 | 21.9163 | 119.3253 | 74.8607 | 15.1393 | 123.0783 | 109.0065 | 0 | 73.5625 | 0.2 | 0 | 5.2235 | 78.786 | 5.3 | 7.7621 | 1.069 | 0.069059
2015-07-13 20:00 | 81.86 | 76.5667 | 5.2933 | 24.3538 | 21.9103 | 134.3239 | 77.4465 | 12.5535 | 137.1577 | 120.7396 | 0 | 57.425 | 0.2 | 0 | 4.093 | 61.518 | 5.1 | 7.0224 | 1.0719 | 0.054072
2015-07-13 21:00 | 59.25 | 55.05 | 4.2 | 22.8891 | 21.9044 | 149.3225 | 79.4267 | 10.5733 | 151.2135 | 130.8717 | 0 | 41.2875 | 0.2 | 0 | 2.9625 | 44.25 | 5.3 | 6.6828 | 1.0733 | 0.038944
2015-07-13 22:00 | 55.7567 | 51.3267 | 4.43 | 27.3636 | 21.8984 | 164.3212 | 80.6831 | 9.3169 | 165.2799 | 138.2111 | 0 | 38.495 | 0.2 | 0 | 2.7878 | 41.2828 | 5.2 | 6.4901 | 1.074 | 0.036358
2015-07-13 23:00 | 52.2633 | 47.6033 | 4.66 | 30.2558 | 21.8925 | 179.3198 | 81.14 | 8.86 | 179.3612 | 141.1352 | 0 | 35.7025 | 0.2 | 0 | 2.6132 | 38.3157 | 4.5 | 5.6974 | 1.0772 | 0.033845
2015-07-14 | 48.77 | 43.88 | 4.89 | 30.4858 | 21.8865 | -165.6816 | 80.7697 | 9.2303 | -166.5559 | 138.6932 | 0 | 32.91 | 0.2 | 0 | 2.4385 | 35.3485 | 4.9 | 6.0046 | 1.076 | 0.031188
2015-07-14 01:00 | 71.8033 | 58.9033 | 12.9 | 71.4279 | 21.8805 | -150.6829 | 79.5952 | 10.4048 | -152.4859 | 131.6934 | 0 | 44.1775 | 0.2 | 0 | 3.5902 | 47.7677 | 3.9 | 5.3927 | 1.0784 | 0.042242
2015-07-14 02:00 | 94.8367 | 73.9267 | 20.91 | 98.0606 | 21.8745 | -135.6843 | 77.688 | 12.312 | -138.4269 | 121.7601 | 0 | 55.445 | 0.2 | 0 | 4.7418 | 60.1868 | 4.6 | 6.4808 | 1.0741 | 0.053009
2015-07-14 03:00 | 117.87 | 88.95 | 28.92 | 112.9356 | 21.8685 | -120.6857 | 75.1627 | 14.8373 | -124.348 | 110.1389 | 0 | 66.7125 | 0.2 | 0 | 5.8935 | 72.606 | 4.6 | 6.8689 | 1.0725 | 0.063855
2015-07-14 04:00 | 165.03 | 110.26 | 54.77 | 178.8725 | 21.8624 | -105.687 | 72.1699 | 17.8301 | -110.1832 | 97.5475 | 0 | 82.695 | 0.2 | 0 | 8.2515 | 90.9465 | 4.6 | 7.4421 | 1.0702 | 0.079814
2015-07-14 05:00 | 212.19 | 131.57 | 80.62 | 223.8346 | 21.8564 | -90.6884 | 68.889 | 21.111 | -95.8337 | 84.3776 | 21.9296 | 98.6775 | 0.2 | 0 | 10.6095 | 131.2166 | 5 | 9.1005 | 1.0636 | 0.11444
2015-07-14 06:00 | 259.35 | 152.88 | 106.47 | 256.9671 | 21.8503 | -75.6897 | 65.5227 | 24.4773 | -81.1786 | 70.8502 | 84.2953 | 114.66 | 0.2 | 0 | 12.9675 | 211.9228 | 5.4 | 12.0226 | 1.0519 | 0.1828
2015-07-14 07:00 | 318.1233 | 172.31 | 145.8133 | 313.5981 | 21.8443 | -60.6911 | 62.2918 | 27.7082 | -66.095 | 57.1 | 170.3383 | 129.2325 | 0.2 | 0 | 15.9062 | 315.477 | 6.9 | 16.7587 | 1.033 | 0.26722
2015-07-14 08:00 | 376.8967 | 191.74 | 185.1567 | 364.0326 | 21.8382 | -45.6924 | 59.4276 | 30.5724 | -50.4883 | 43.2213 | 265.2757 | 143.805 | 0.2 | 0 | 18.8448 | 427.9256 | 7.5 | 20.8727 | 1.0165 | 0.35669
2015-07-14 09:00 | 435.67 | 211.17 | 224.5 | 413.9589 | 21.8321 | -30.6937 | 57.158 | 32.842 | -34.3314 | 29.3066 | 360.9774 | 158.3775 | 0.2 | 0 | 21.7835 | 541.1384 | 6.8 | 23.7106 | 1.0052 | 0.44602
2015-07-14 10:00 | 444.4733 | 222.88 | 221.5933 | 393.0641 | 21.8261 | -15.6951 | 55.6839 | 34.3161 | -17.701 | 15.5707 | 378.6386 | 167.16 | 0.2 | 0 | 22.2237 | 568.0223 | 7 | 24.7507 | 1.001 | 0.46624
2015-07-14 11:00 | 453.2767 | 234.59 | 218.6867 | 382.6796 | 21.82 | -0.6964 | 55.1478 | 34.8522 | -0.78783 | 4.8975 | 381.2824 | 175.9425 | 0.2 | 0 | 22.6638 | 579.8888 | 7.6 | 25.7215 | 0.99711 | 0.47414
2015-07-14 12:00 | 462.08 | 246.3 | 215.78 | 381.9789 | 21.8138 | 14.3023 | 55.6046 | 34.3954 | 16.1376 | 14.3265 | 370.0999 | 184.725 | 0.2 | 0 | 23.104 | 577.9289 | 8 | 26.0603 | 0.99576 | 0.47189
2015-07-14 13:00 | 432.05 | 223.6033 | 208.4467 | 382.8123 | 21.8077 | 29.3009 | 57.0085 | 32.9915 | 32.8012 | 28.0156 | 337.9542 | 167.7025 | 0.2 | 0 | 21.6025 | 527.2592 | 7.5 | 23.9769 | 1.0041 | 0.43412
2015-07-14 14:00 | 402.02 | 200.9067 | 201.1133 | 393.0418 | 21.8016 | 44.2996 | 59.2239 | 30.7761 | 49.0031 | 41.9299 | 292.4085 | 150.68 | 0.2 | 0 | 20.101 | 463.1895 | 7.7 | 22.1747 | 1.0113 | 0.38411
2015-07-14 15:00 | 371.99 | 178.21 | 193.78 | 413.494 | 21.7954 | 59.2983 | 62.0539 | 27.9461 | 64.6568 | 55.8206 | 232.295 | 133.6575 | 0.2 | 0 | 18.5995 | 384.552 | 7.7 | 19.7173 | 1.0211 | 0.322
2015-07-14 16:00 | 325.14 | 143.7867 | 181.3533 | 433.5405 | 21.7893 | 74.297 | 65.2722 | 24.7278 | 79.7819 | 69.5924 | 151.1738 | 107.84 | 0.2 | 0 | 16.257 | 275.2708 | 7.4 | 16.0022 | 1.036 | 0.23385
2015-07-14 17:00 | 278.29 | 109.3633 | 168.9267 | 463.9457 | 21.7831 | 89.2957 | 68.6473 | 21.3527 | 94.4688 | 83.1536 | 55.3064 | 82.0225 | 0.2 | 0 | 13.9145 | 151.2434 | 7.3 | 12.0264 | 1.0519 | 0.13046
2015-07-14 18:00 | 231.44 | 74.94 | 156.5 | 505.2797 | 21.7769 | 104.2944 | 71.9571 | 18.0429 | 108.8398 | 96.3754 | 0 | 56.205 | 0.2 | 0 | 11.572 | 67.777 | 7.2 | 9.318 | 1.0627 | 0.059063
2015-07-14 19:00 | 187.7633 | 68.5533 | 119.21 | 460.5039 | 21.7708 | 119.2931 | 74.9971 | 15.0029 | 123.0172 | 109.0486 | 0 | 51.415 | 0.2 | 0 | 9.3882 | 60.8032 | 6 | 7.9001 | 1.0684 | 0.053269
2015-07-14 20:00 | 144.0867 | 62.1667 | 81.92 | 381.049 | 21.7646 | 134.2918 | 77.5853 | 12.4147 | 137.1029 | 120.804 | 0 | 46.625 | 0.2 | 0 | 7.2043 | 53.8293 | 6.6 | 8.2822 | 1.0669 | 0.047092
2015-07-14 21:00 | 100.41 | 55.78 | 44.63 | 246.4872 | 21.7583 | 149.2905 | 79.5682 | 10.4318 | 151.166 | 130.964 | 0 | 41.835 | 0.2 | 0 | 5.0205 | 46.8555 | 7.3 | 8.7642 | 1.0649 | 0.040917
2015-07-14 22:00 | 87.71 | 50.1933 | 37.5167 | 235.3465 | 21.7521 | 164.2892 | 80.8273 | 9.1727 | 165.2407 | 138.3343 | 0 | 37.645 | 0.2 | 0 | 4.3855 | 42.0305 | 6.6 | 7.9135 | 1.0683 | 0.036821
2015-07-14 23:00 | 75.01 | 44.6067 | 30.4033 | 200.6904 | 21.7459 | 179.2879 | 81.2865 | 8.7135 | 179.3308 | 141.2812 | 0 | 33.455 | 0.2 | 0 | 3.7505 | 37.2055 | 6.8 | 7.9627 | 1.0681 | 0.032588
2015-07-15 | 62.31 | 39.02 | 23.29 | 147.5468 | 21.7397 | -165.7134 | 80.918 | 9.082 | -166.5774 | 138.8409 | 0 | 29.265 | 0.2 | 0 | 3.1155 | 32.3805 | 5.6 | 6.6119 | 1.0736 | 0.028505
2015-07-15 01:00 | 73.2467 | 54.6533 | 18.5933 | 104.4361 | 21.7334 | -150.7147 | 79.7446 | 10.2554 | -152.4989 | 131.8265 | 0 | 40.99 | 0.2 | 0 | 3.6623 | 44.6523 | 6.7 | 8.0954 | 1.0676 | 0.039091
2015-07-15 02:00 | 84.1833 | 70.2867 | 13.8967 | 65.9627 | 21.7271 | -135.716 | 77.8381 | 12.1619 | -138.4323 | 121.8743 | 0 | 52.715 | 0.2 | 0 | 4.2092 | 56.9242 | 5.3 | 7.0789 | 1.0717 | 0.050024
2015-07-15 03:00 | 95.12 | 85.92 | 9.2 | 36.2868 | 21.7209 | -120.7173 | 75.3132 | 14.6868 | -124.3471 | 110.2357 | 0 | 64.44 | 0.2 | 0 | 4.756 | 69.196 | 5.1 | 7.2624 | 1.071 | 0.060767
2015-07-15 04:00 | 132.21 | 112.3633 | 19.8467 | 65.3513 | 21.7146 | -105.7185 | 72.3205 | 17.6795 | -110.1777 | 97.6295 | 0 | 84.2725 | 0.2 | 0 | 6.6105 | 90.883 | 5.9 | 8.7401 | 1.065 | 0.079371
2015-07-15 05:00 | 169.3 | 138.8067 | 30.4933 | 85.2435 | 21.7083 | -90.7198 | 69.0397 | 20.9603 | -95.8257 | 84.4466 | 8.2493 | 104.105 | 0.2 | 0 | 8.465 | 120.8193 | 7 | 10.7756 | 1.0569 | 0.10471
2015-07-15 06:00 | 206.39 | 165.25 | 41.14 | 99.8707 | 21.702 | -75.7211 | 65.6737 | 24.3263 | -81.1706 | 70.9075 | 32.667 | 123.9375 | 0.2 | 0 | 10.3195 | 166.924 | 5.7 | 10.9164 | 1.0563 | 0.14459
2015-07-15 07:00 | 221.1067 | 192.7767 | 28.33 | 61.2371 | 21.6957 | -60.7223 | 62.4432 | 27.5568 | -66.0897 | 57.1461 | 33.221 | 144.5825 | 0.2 | 0 | 11.0553 | 188.8588 | 6.5 | 12.4018 | 1.0504 | 0.16267
2015-07-15 08:00 | 235.8233 | 220.3033 | 15.52 | 30.651 | 21.6893 | -45.7236 | 59.5793 | 30.4207 | -50.489 | 43.2553 | 22.3234 | 165.2275 | 0.2 | 0 | 11.7912 | 199.342 | 6.4 | 12.6294 | 1.0495 | 0.17155
2015-07-15 09:00 | 250.54 | 247.83 | 2.71 | 5.0176 | 21.683 | -30.7249 | 57.3097 | 32.6903 | -34.3412 | 29.3252 | 4.3746 | 185.8725 | 0.2 | 0 | 12.527 | 202.7741 | 6.6 | 12.9367 | 1.0483 | 0.1743
2015-07-15 10:00 | 214.3667 | 211.8767 | 2.49 | 4.4339 | 21.6766 | -15.7261 | 55.835 | 34.165 | -17.7224 | 15.5595 | 4.2714 | 158.9075 | 0.2 | 0 | 10.7183 | 173.8973 | 7 | 12.4343 | 1.0503 | 0.14976
2015-07-15 11:00 | 178.1933 | 175.9233 | 2.27 | 3.9873 | 21.6703 | -0.72736 | 55.2976 | 34.7024 | -0.82221 | 4.7534 | 3.9735 | 131.9425 | 0.2 | 0 | 8.9097 | 144.8257 | 7.6 | 12.1258 | 1.0515 | 0.12487
2015-07-15 12:00 | 142.02 | 139.97 | 2.05 | 3.6427 | 21.6639 | 14.2714 | 55.7523 | 34.2477 | 16.0907 | 14.2552 | 3.5305 | 104.9775 | 0.2 | 0 | 7.101 | 115.609 | 7.2 | 10.8128 | 1.0567 | 0.10018
2015-07-15 13:00 | 158.5033 | 141.7867 | 16.7167 | 30.8205 | 21.6575 | 29.2701 | 57.1537 | 32.8463 | 32.7439 | 27.975 | 27.2192 | 106.34 | 0.2 | 0 | 7.9252 | 141.4844 | 6.8 | 11.2214 | 1.0551 | 0.12241
2015-07-15 14:00 | 174.9867 | 143.6033 | 31.3833 | 61.5911 | 21.6511 | 44.2689 | 59.3666 | 30.6334 | 48.9385 | 41.9053 | 45.8391 | 107.7025 | 0.2 | 0 | 8.7493 | 162.291 | 7.1 | 12.1716 | 1.0513 | 0.13991
2015-07-15 15:00 | 191.47 | 145.42 | 46.05 | 98.7205 | 21.6447 | 59.2677 | 62.1947 | 27.8053 | 64.588 | 55.8088 | 55.4767 | 109.065 | 0.2 | 0 | 9.5735 | 174.1152 | 6.2 | 11.6411 | 1.0534 | 0.1504
2015-07-15 16:00 | 199.5133 | 124.1033 | 75.41 | 181.2348 | 21.6383 | 74.2664 | 65.412 | 24.588 | 79.7119 | 69.5928 | 63.1948 | 93.0775 | 0.2 | 0 | 9.9757 | 166.248 | 6.1 | 11.2953 | 1.0548 | 0.1438
2015-07-15 17:00 | 207.5567 | 102.7867 | 104.77 | 289.5527 | 21.6319 | 89.2652 | 68.7871 | 21.2129 | 94.4 | 83.1669 | 34.4503 | 77.09 | 0.2 | 0 | 10.3778 | 121.9181 | 6.3 | 10.1099 | 1.0596 | 0.10593
2015-07-15 18:00 | 215.6 | 81.47 | 134.13 | 436.3518 | 21.6255 | 104.264 | 72.098 | 17.902 | 108.7743 | 96.4037 | 0 | 61.1025 | 0.2 | 0 | 10.78 | 71.8825 | 5.9 | 8.1463 | 1.0674 | 0.062917
2015-07-15 19:00 | 161.7833 | 66.26 | 95.5233 | 372.4688 | 21.619 | 119.2628 | 75.1399 | 14.8601 | 122.9567 | 109.095 | 0 | 49.695 | 0.2 | 0 | 8.0892 | 57.7842 | 6 | 7.8058 | 1.0688 | 0.050642
2015-07-15 20:00 | 107.9667 | 51.05 | 56.9167 | 267.8321 | 21.6126 | 134.2615 | 77.7306 | 12.2694 | 137.0488 | 120.8733 | 0 | 38.2875 | 0.2 | 0 | 5.3983 | 43.6858 | 5.8 | 7.1652 | 1.0713 | 0.038378
2015-07-15 21:00 | 54.15 | 35.84 | 18.31 | 102.5629 | 21.6061 | 149.2603 | 79.7162 | 10.2838 | 151.1196 | 131.0618 | 0 | 26.88 | 0.2 | 0 | 2.7075 | 29.5875 | 3.8 | 4.7246 | 1.0811 | 0.026229
2015-07-15 22:00 | 40.4933 | 28.2867 | 12.2067 | 77.8403 | 21.5996 | 164.2591 | 80.9778 | 9.0222 | 165.2029 | 138.4638 | 0 | 21.215 | 0.2 | 0 | 2.0247 | 23.2397 | 2.4 | 3.1262 | 1.0875 | 0.020724
2015-07-15 23:00 | 26.8367 | 20.7333 | 6.1033 | 41.0008 | 21.5931 | 179.2579 | 81.4392 | 8.5608 | 179.3022 | 141.4334 | 0 | 15.55 | 0.2 | 0 | 1.3418 | 16.8918 | 1.8 | 2.3279 | 1.0907 | 0.015107
2015-07-16 | 13.18 | 13.18 | 0 | 0 | 21.5866 | -165.7433 | 81.0723 | 8.9277 | -166.5968 | 138.9937 | 0 | 9.885 | 0.2 | 0 | 0.659 | 10.544 | 1.7 | 2.0295 | 1.0919 | 0.0094405
2015-07-16 01:00 | 16.9667 | 16.49 | 0.47667 | 2.7181 | 21.5801 | -150.7445 | 79.9001 | 10.0999 | -152.5095 | 131.9631 | 0 | 12.3675 | 0.2 | 0 | 0.84833 | 13.2158 | 1.6 | 2.013 | 1.0919 | 0.011833
2015-07-16 02:00 | 20.7533 | 19.8 | 0.95333 | 4.5831 | 21.5736 | -135.7457 | 77.9941 | 12.0059 | -138.435 | 121.9908 | 0 | 14.85 | 0.2 | 0 | 1.0377 | 15.8877 | 1.7 | 2.1965 | 1.0912 | 0.014216
2015-07-16 03:00 | 24.54 | 23.11 | 1.43 | 5.6995 | 21.5671 | -120.7469 | 75.4694 | 14.5306 | -124.3432 | 110.3339 | 0 | 17.3325 | 0.2 | 0 | 1.227 | 18.5595 | 2.1 | 2.68 | 1.0893 | 0.016578
2015-07-16 04:00 | 38.0533 | 32.7033 | 5.35 | 17.7686 | 21.5605 | -105.7481 | 72.4768 | 17.5232 | -110.169 | 97.712 | 0 | 24.5275 | 0.2 | 0 | 1.9027 | 26.4302 | 2.5 | 3.3259 | 1.0867 | 0.023552
2015-07-16 05:00 | 51.5667 | 42.2967 | 9.27 | 26.1001 | 21.554 | -90.7493 | 69.1961 | 20.8039 | -95.8143 | 84.5157 | 2.4945 | 31.7225 | 0.2 | 0 | 2.5783 | 36.7953 | 2.6 | 3.7499 | 1.085 | 0.032737
2015-07-16 06:00 | 65.08 | 51.89 | 13.19 | 32.2147 | 21.5474 | -75.7505 | 65.8303 | 24.1697 | -81.159 | 70.9645 | 10.5069 | 38.9175 | 0.2 | 0 | 3.254 | 52.6784 | 2.6 | 4.2462 | 1.083 | 0.046782
2015-07-16 07:00 | 149.19 | 127.18 | 22.01 | 47.8273 | 21.5408 | -60.7517 | 62.6002 | 27.3998 | -66.081 | 57.1914 | 25.9145 | 95.385 | 0.2 | 0 | 7.4595 | 128.759 | 3.2 | 7.2237 | 1.0711 | 0.11309
2015-07-16 08:00 | 233.3 | 202.47 | 30.83 | 61.1738 | 21.5342 | -45.7528 | 59.7367 | 30.2633 | -50.4863 | 43.2883 | 44.5292 | 151.8525 | 0.2 | 0 | 11.665 | 208.0467 | 2.7 | 9.2015 | 1.0632 | 0.18138
2015-07-16 09:00 | 317.41 | 277.76 | 39.65 | 73.7289 | 21.5277 | -30.754 | 57.4673 | 32.5327 | -34.3478 | 29.3423 | 64.2701 | 208.32 | 0.2 | 0 | 15.8705 | 288.4606 | 3.7 | 12.7144 | 1.0491 | 0.24816
2015-07-16 10:00 | 356.7467 | 260.5067 | 96.24 | 172.0703 | 21.521 | -15.7552 | 55.9922 | 34.0078 | -17.7411 | 15.5464 | 165.7748 | 195.38 | 0.2 | 0 | 17.8373 | 378.9922 | 3.6 | 15.4435 | 1.0382 | 0.32265
2015-07-16 11:00 | 396.0833 | 243.2533 | 152.83 | 269.5059 | 21.5144 | -0.75635 | 55.4535 | 34.5465 | -0.8543 | 4.6034 | 268.6365 | 182.44 | 0.2 | 0 | 19.8042 | 470.8806 | 3.3 | 18.015 | 1.0279 | 0.39691
2015-07-16 12:00 | 435.42 | 226 | 209.42 | 373.5982 | 21.5078 | 14.2425 | 55.9062 | 34.0938 | 16.0456 | 14.1852 | 362.2067 | 169.5 | 0.2 | 0 | 21.771 | 553.4777 | 3.5 | 20.7962 | 1.0168 | 0.46148
2015-07-16 13:00 | 406.4733 | 189.6933 | 216.78 | 401.3222 | 21.5012 | 29.2413 | 57.3052 | 32.6948 | 32.6879 | 27.9364 | 354.5554 | 142.27 | 0.2 | 0 | 20.3237 | 517.1491 | 4.4 | 20.5609 | 1.0178 | 0.43159
2015-07-16 14:00 | 377.5267 | 153.3867 | 224.14 | 441.8271 | 21.4945 | 44.2402 | 59.5157 | 30.4843 | 48.8747 | 41.8832 | 328.9435 | 115.04 | 0.2 | 0 | 18.8763 | 462.8598 | 4.1 | 18.5644 | 1.0257 | 0.38932
2015-07-16 15:00 | 348.58 | 117.08 | 231.5 | 498.7142 | 21.4879 | 59.239 | 62.3419 | 27.6581 | 64.5199 | 55.7997 | 280.3213 | 87.81 | 0.2 | 0 | 17.429 | 385.5603 | 4.6 | 16.6488 | 1.0334 | 0.32672
2015-07-16 16:00 | 307.1367 | 106.57 | 200.5667 | 484.7327 | 21.4812 | 74.2379 | 65.5583 | 24.4417 | 79.6423 | 69.5962 | 168.9946 | 79.9275 | 0.2 | 0 | 15.3568 | 264.279 | 4.8 | 13.0587 | 1.0478 | 0.22706
2015-07-16 17:00 | 265.6933 | 96.06 | 169.6333 | 471.9219 | 21.4745 | 89.2367 | 68.9334 | 21.0666 | 94.3317 | 83.1837 | 56.0109 | 72.045 | 0.2 | 0 | 13.2847 | 141.3406 | 4.7 | 9.1169 | 1.0635 | 0.12326
2015-07-16 18:00 | 224.25 | 85.55 | 138.7 | 454.842 | 21.4678 | 104.2356 | 72.2454 | 17.7546 | 108.7093 | 96.4358 | 0 | 64.1625 | 0.2 | 0 | 11.2125 | 75.375 | 4.4 | 6.7555 | 1.073 | 0.066318
2015-07-16 19:00 | 188.95 | 71.2633 | 117.6867 | 463.4399 | 21.4611 | 119.2344 | 75.2891 | 14.7109 | 122.8968 | 109.1458 | 0 | 53.4475 | 0.2 | 0 | 9.4475 | 62.895 | 4.5 | 6.4655 | 1.0741 | 0.055397
2015-07-16 20:00 | 153.65 | 56.9767 | 96.6733 | 460.5205 | 21.4544 | 134.2333 | 77.8822 | 12.1178 | 136.9955 | 120.9475 | 0 | 42.7325 | 0.2 | 0 | 7.6825 | 50.415 | 3.9 | 5.4755 | 1.0781 | 0.044569
2015-07-16 21:00 | 118.35 | 42.69 | 75.66 | 430.1921 | 21.4477 | 149.2322 | 79.8704 | 10.1296 | 151.0743 | 131.1653 | 0 | 32.0175 | 0.2 | 0 | 5.9175 | 37.935 | 3.8 | 4.9855 | 1.0801 | 0.033597
2015-07-16 22:00 | 110.84 | 39.54 | 71.3 | 462.6433 | 21.4409 | 164.231 | 81.1346 | 8.8654 | 165.1665 | 138.5995 | 0 | 29.655 | 0.2 | 0 | 5.542 | 35.197 | 3.8 | 4.8999 | 1.0804 | 0.031182
2015-07-16 23:00 | 103.33 | 36.39 | 66.94 | 458.1259 | 21.4342 | 179.2299 | 81.598 | 8.402 | 179.2754 | 141.5917 | 0 | 27.2925 | 0.2 | 0 | 5.1665 | 32.459 | 3.4 | 4.4143 | 1.0823 | 0.028808
2015-07-17 | 95.82 | 33.24 | 62.58 | 410.5715 | 21.4275 | -165.7712 | 81.2327 | 8.7673 | -166.614 | 139.1516 | 0 | 24.93 | 0.2 | 0 | 4.791 | 29.721 | 4.2 | 5.1288 | 1.0795 | 0.026308
2015-07-17 01:00 | 94.8633 | 40.8333 | 54.03 | 313.0488 | 21.4207 | -150.7723 | 80.0614 | 9.9386 | -152.5175 | 132.1033 | 0 | 30.625 | 0.2 | 0 | 4.7432 | 35.3682 | 4.2 | 5.3053 | 1.0788 | 0.031287
2015-07-17 02:00 | 93.9067 | 48.4267 | 45.48 | 221.5833 | 21.4139 | -135.7734 | 78.1559 | 11.8441 | -138.4347 | 122.1096 | 0 | 36.32 | 0.2 | 0 | 4.6953 | 41.0153 | 3.8 | 5.0817 | 1.0797 | 0.036312
2015-07-17 03:00 | 92.95 | 56.02 | 36.93 | 148.8142 | 21.4071 | -120.7745 | 75.6312 | 14.3688 | -124.3361 | 110.4334 | 0 | 42.015 | 0.2 | 0 | 4.6475 | 46.6625 | 3.5 | 4.9582 | 1.0802 | 0.041331
2015-07-17 04:00 | 96.0267 | 58.4233 | 37.6033 | 126.0175 | 21.4003 | -105.7757 | 72.6386 | 17.3614 | -110.1569 | 97.7951 | 0 | 43.8175 | 0.2 | 0 | 4.8013 | 48.6188 | 3.4 | 4.9193 | 1.0803 | 0.04307
2015-07-17 05:00 | 99.1033 | 60.8267 | 38.2767 | 108.5777 | 21.3935 | -90.7768 | 69.358 | 20.642 | -95.7995 | 84.5848 | 10.2468 | 45.62 | 0.2 | 0 | 4.9552 | 60.8219 | 3.2 | 5.1007 | 1.0796 | 0.053844
2015-07-17 06:00 | 102.18 | 63.23 | 38.95 | 95.7338 | 21.3867 | -75.7779 | 65.9924 | 24.0076 | -81.144 | 71.021 | 31.1347 | 47.4225 | 0.2 | 0 | 5.109 | 83.6662 | 4 | 6.6146 | 1.0735 | 0.073652
2015-07-17 07:00 | 76.75 | 50.7667 | 25.9833 | 56.7724 | 21.3799 | -60.779 | 62.7628 | 27.2372 | -66.0687 | 57.2359 | 30.7241 | 38.075 | 0.2 | 0 | 3.8375 | 72.6366 | 4.5 | 6.7699 | 1.0729 | 0.063905
2015-07-17 08:00 | 51.32 | 38.3033 | 13.0167 | 25.9548 | 21.373 | -45.78 | 59.8998 | 30.1002 | -50.4802 | 43.32 | 18.883 | 28.7275 | 0.2 | 0 | 2.566 | 50.1765 | 4.4 | 5.968 | 1.0761 | 0.044277
2015-07-17 09:00 | 25.89 | 25.84 | 0.05 | 0.093393 | 21.3662 | -30.7811 | 57.6307 | 32.3693 | -34.3513 | 29.3579 | 0.081399 | 19.38 | 0.2 | 0 | 1.2945 | 20.7559 | 4.5 | 5.1486 | 1.0794 | 0.018371
2015-07-17 10:00 | 27.3167 | 26.0033 | 1.3133 | 2.3581 | 21.3593 | -15.7822 | 56.1553 | 33.8447 | -17.7569 | 15.5317 | 2.272 | 19.5025 | 0.2 | 0 | 1.3658 | 23.1403 | 4 | 4.7231 | 1.0811 | 0.020514
2015-07-17 11:00 | 28.7433 | 26.1667 | 2.5767 | 4.5625 | 21.3525 | -0.7833 | 55.6156 | 34.3844 | -0.88401 | 4.4477 | 4.5488 | 19.625 | 0.2 | 0 | 1.4372 | 25.611 | 4.1 | 4.9003 | 1.0804 | 0.022689
2015-07-17 12:00 | 30.17 | 26.33 | 3.84 | 6.8789 | 21.3456 | 14.2156 | 56.0664 | 33.9336 | 16.0024 | 14.1166 | 6.6711 | 19.7475 | 0.2 | 0 | 1.5085 | 27.9271 | 3.6 | 4.4727 | 1.0821 | 0.024781
2015-07-17 13:00 | 58.7833 | 48.53 | 10.2533 | 19.0638 | 21.3387 | 29.2145 | 57.463 | 32.537 | 32.6334 | 27.9 | 16.8479 | 36.3975 | 0.2 | 0 | 2.9392 | 56.1846 | 3.5 | 5.2558 | 1.079 | 0.04971
2015-07-17 14:00 | 87.3967 | 70.73 | 16.6667 | 33.0058 | 21.3318 | 44.2135 | 59.6712 | 30.3288 | 48.8119 | 41.8636 | 24.5806 | 53.0475 | 0.2 | 0 | 4.3698 | 81.9979 | 4 | 6.5624 | 1.0738 | 0.072197
2015-07-17 15:00 | 116.01 | 92.93 | 23.08 | 49.9765 | 21.3249 | 59.2124 | 62.4956 | 27.5044 | 64.4524 | 55.7934 | 28.0957 | 69.6975 | 0.2 | 0 | 5.8005 | 103.5937 | 4.3 | 7.5373 | 1.0699 | 0.09088
2015-07-17 16:00 | 95.59 | 74.8633 | 20.7267 | 50.3881 | 21.3179 | 74.2113 | 65.7109 | 24.2891 | 79.5733 | 69.6027 | 17.5616 | 56.1475 | 0.2 | 0 | 4.7795 | 78.4886 | 4.1 | 6.5528 | 1.0738 | 0.06911
2015-07-17 17:00 | 75.17 | 56.7967 | 18.3733 | 51.4712 | 21.311 | 89.2103 | 69.0862 | 20.9138 | 94.2638 | 83.2039 | 6.0909 | 42.5975 | 0.2 | 0 | 3.7585 | 52.4469 | 3.2 | 4.839 | 1.0806 | 0.046475
2015-07-17 18:00 | 54.75 | 38.73 | 16.02 | 52.9789 | 21.3041 | 104.2092 | 72.3991 | 17.6009 | 108.6448 | 96.4718 | 0 | 29.0475 | 0.2 | 0 | 2.7375 | 31.785 | 3.1 | 4.0933 | 1.0836 | 0.028243
2015-07-17 19:00 | 43.42 | 31.8367 | 11.5833 | 46.0911 | 21.2971 | 119.2082 | 75.4447 | 14.5553 | 122.8376 | 109.2009 | 0 | 23.8775 | 0.2 | 0 | 2.171 | 26.0485 | 3.1 | 3.914 | 1.0843 | 0.023161
2015-07-17 20:00 | 32.09 | 24.9433 | 7.1467 | 34.4874 | 21.2901 | 134.2071 | 78.0402 | 11.9598 | 136.9432 | 121.0266 | 0 | 18.7075 | 0.2 | 0 | 1.6045 | 20.312 | 3.5 | 4.1348 | 1.0835 | 0.018046
2015-07-17 21:00 | 20.76 | 18.05 | 2.71 | 15.6542 | 21.2832 | 149.2061 | 80.0309 | 9.9691 | 151.0302 | 131.2744 | 0 | 13.5375 | 0.2 | 0 | 1.038 | 14.5755 | 3.8 | 4.2555 | 1.083 | 0.012944
2015-07-17 22:00 | 25.67 | 23.8433 | 1.8267 | 12.0728 | 21.2762 | 164.205 | 81.2975 | 8.7025 | 165.1317 | 138.7414 | 0 | 17.8825 | 0.2 | 0 | 1.2835 | 19.166 | 4.6 | 5.1989 | 1.0792 | 0.016961
2015-07-17 23:00 | 30.58 | 29.6367 | 0.94333 | 6.5844 | 21.2692 | 179.204 | 81.763 | 8.237 | 179.2505 | 141.7562 | 0 | 22.2275 | 0.2 | 0 | 1.529 | 23.7565 | 4.6 | 5.3424 | 1.0786 | 0.021012
2015-07-18 | 35.49 | 35.43 | 0.06 | 0.4012 | 21.2622 | -165.797 | 81.3991 | 8.6009 | -166.6289 | 139.3144 | 0 | 26.5725 | 0.2 | 0 | 1.7745 | 28.347 | 3.6 | 4.4858 | 1.0821 | 0.025152
2015-07-18 01:00 | 50.0133 | 47.1867 | 2.8267 | 16.655 | 21.2552 | -150.7981 | 80.2286 | 9.7714 | -152.5229 | 132.247 | 0 | 35.39 | 0.2 | 0 | 2.5007 | 37.8907 | 3 | 4.1841 | 1.0833 | 0.033657
2015-07-18 02:00 | 64.5367 | 58.9433 | 5.5933 | 27.6366 | 21.2481 | -135.7991 | 78.3233 | 11.6767 | -138.4316 | 122.2305 | 0 | 44.2075 | 0.2 | 0 | 3.2268 | 47.4343 | 3.2 | 4.6823 | 1.0813 | 0.042057
2015-07-18 03:00 | 79.06 | 70.7 | 8.36 | 34.0766 | 21.2411 | -120.8001 | 75.7987 | 14.2013 | -124.326 | 110.534 | 0 | 53.025 | 0.2 | 0 | 3.953 | 56.978 | 4 | 5.7806 | 1.0769 | 0.050314
2015-07-18 04:00 | 104.24 | 88.9667 | 15.2733 | 51.6673 | 21.2341 | -105.8011 | 72.8059 | 17.1941 | -110.1416 | 97.8787 | 0 | 66.725 | 0.2 | 0 | 5.212 | 71.937 | 4.2 | 6.448 | 1.0742 | 0.063366
2015-07-18 05:00 | 129.42 | 107.2333 | 22.1867 | 63.4279 | 21.227 | -90.8021 | 69.5253 | 20.4747 | -95.7811 | 84.6538 | 5.9098 | 80.425 | 0.2 | 0 | 6.471 | 92.8058 | 5.3 | 8.2002 | 1.0672 | 0.081215
2015-07-18 06:00 | 154.6 | 125.5 | 29.1 | 71.997 | 21.2199 | -75.8032 | 66.16 | 23.84 | -81.1254 | 71.077 | 23.3484 | 94.125 | 0.2 | 0 | 7.73 | 125.2034 | 6.1 | 10.0126 | 1.0599 | 0.10882
2015-07-18 07:00 | 212.1467 | 169.1833 | 42.9633 | 94.4113 | 21.2128 | -60.8042 | 62.9309 | 27.0691 | -66.053 | 57.2796 | 51.0331 | 126.8875 | 0.2 | 0 | 10.6073 | 188.5279 | 5.8 | 11.6915 | 1.0532 | 0.16282
2015-07-18 08:00 | 269.6933 | 212.8667 | 56.8267 | 113.8894 | 21.2058 | -45.8052 | 60.0685 | 29.9315 | -50.4707 | 43.3507 | 82.8165 | 159.65 | 0.2 | 0 | 13.4847 | 255.9512 | 5.8 | 13.7985 | 1.0448 | 0.21928
2015-07-18 09:00 | 327.24 | 256.55 | 70.69 | 132.6568 | 21.1987 | -30.8062 | 57.7998 | 32.2002 | -34.3516 | 29.3723 | 115.604 | 192.4125 | 0.2 | 0 | 16.362 | 324.3785 | 7 | 17.1368 | 1.0315 | 0.27436
2015-07-18 10:00 | 325.02 | 264.1567 | 60.8633 | 109.7643 | 21.1915 | -15.8072 | 56.3243 | 33.6757 | -17.7699 | 15.5154 | 105.7644 | 198.1175 | 0.2 | 0 | 16.251 | 320.1329 | 5.1 | 15.1042 | 1.0396 | 0.2729
2015-07-18 11:00 | 322.8 | 271.7633 | 51.0367 | 90.7611 | 21.1844 | -0.80816 | 55.7837 | 34.2163 | -0.91128 | 4.2863 | 90.5072 | 203.8225 | 0.2 | 0 | 16.14 | 310.4697 | 4.3 | 14.0022 | 1.044 | 0.26578
2015-07-18 12:00 | 320.58 | 279.37 | 41.21 | 74.1428 | 21.1773 | 14.1908 | 56.2328 | 33.7672 | 15.9612 | 14.0499 | 71.9248 | 209.5275 | 0.2 | 0 | 16.029 | 297.4813 | 4.1 | 13.3963 | 1.0464 | 0.25526
2015-07-18 13:00 | 344.3133 | 217.1467 | 127.1667 | 237.5049 | 21.1701 | 29.1899 | 57.6271 | 32.3729 | 32.5803 | 27.866 | 209.9646 | 162.86 | 0.2 | 0 | 17.2157 | 390.0403 | 3.6 | 15.7888 | 1.0368 | 0.33162
2015-07-18 14:00 | 368.0467 | 154.9233 | 213.1233 | 424.1068 | 21.163 | 44.1889 | 59.833 | 30.167 | 48.7503 | 41.8466 | 315.9313 | 116.1925 | 0.2 | 0 | 18.4023 | 450.5262 | 3.9 | 17.9789 | 1.0281 | 0.37981
2015-07-18 15:00 | 391.78 | 92.7 | 299.08 | 651.11 | 21.1558 | 59.1879 | 62.6556 | 27.3444 | 64.3857 | 55.79 | 366.0718 | 69.525 | 0.2 | 0 | 19.589 | 455.1858 | 3.3 | 17.5246 | 1.0299 | 0.38441
2015-07-18 16:00 | 305.8767 | 90.1233 | 215.7533 | 527.7605 | 21.1487 | 74.1869 | 65.8699 | 24.1301 | 79.5049 | 69.6125 | 183.855 | 67.5925 | 0.2 | 0 | 15.2938 | 266.7413 | 3.1 | 11.4357 | 1.0543 | 0.2306
2015-07-18 17:00 | 219.9733 | 87.5467 | 132.4267 | 373.697 | 21.1415 | 89.186 | 69.2452 | 20.7548 | 94.1965 | 83.2277 | 44.0678 | 65.66 | 0.2 | 0 | 10.9987 | 120.7265 | 3 | 6.7727 | 1.0729 | 0.10621
2015-07-18 18:00 | 134.07 | 84.97 | 49.1 | 163.8196 | 21.1343 | 104.185 | 72.5592 | 17.4408 | 108.5809 | 96.5117 | 0 | 63.7275 | 0.2 | 0 | 6.7035 | 70.431 | 2.8 | 5.001 | 1.08 | 0.062373
2015-07-18 19:00 | 115.3233 | 70.4467 | 44.8767 | 180.5337 | 21.1271 | 119.184 | 75.6066 | 14.3934 | 122.7791 | 109.2604 | 0 | 52.835 | 0.2 | 0 | 5.7662 | 58.6012 | 3.6 | 5.4313 | 1.0783 | 0.051814
2015-07-18 20:00 | 96.5767 | 55.9233 | 40.6533 | 198.8714 | 21.1199 | 134.1831 | 78.2044 | 11.7956 | 136.8918 | 121.1107 | 0 | 41.9425 | 0.2 | 0 | 4.8288 | 46.7713 | 3.5 | 4.9616 | 1.0802 | 0.041427
2015-07-18 21:00 | 77.83 | 41.4 | 36.43 | 213.9806 | 21.1126 | 149.1821 | 80.1977 | 9.8023 | 150.9874 | 131.3891 | 0 | 31.05 | 0.2 | 0 | 3.8915 | 34.9415 | 3.1 | 4.1919 | 1.0832 | 0.031037
2015-07-18 22:00 | 77.62 | 39.0433 | 38.5767 | 259.9747 | 21.1054 | 164.1812 | 81.4666 | 8.5334 | 165.0985 | 138.8895 | 0 | 29.2825 | 0.2 | 0 | 3.881 | 33.1635 | 3.2 | 4.2364 | 1.0831 | 0.029453
2015-07-18 23:00 | 77.41 | 36.6867 | 40.7233 | 290.2284 | 21.0981 | 179.1802 | 81.9339 | 8.0661 | 179.2275 | 141.9267 | 0 | 27.515 | 0.2 | 0 | 3.8705 | 31.3855 | 3 | 3.9808 | 1.0841 | 0.0279
2015-07-19 | 77.2 | 34.33 | 42.87 | 292.4719 | 21.0909 | -165.8207 | 81.5713 | 8.4287 | -166.6415 | 139.4822 | 0 | 25.7475 | 0.2 | 0 | 3.86 | 29.6075 | 2.9 | 3.8252 | 1.0847 | 0.026334
2015-07-19 01:00 | 85.0567 | 45.47 | 39.5867 | 237.4109 | 21.0836 | -150.8217 | 80.4015 | 9.5985 | -152.5257 | 132.394 | 0 | 34.1025 | 0.2 | 0 | 4.2528 | 38.3553 | 2.4 | 3.5986 | 1.0856 | 0.034144
2015-07-19 02:00 | 92.9133 | 56.61 | 36.3033 | 182.036 | 21.0763 | -135.8226 | 78.4964 | 11.5036 | -138.4256 | 122.3534 | 0 | 42.4575 | 0.2 | 0 | 4.6457 | 47.1032 | 3.1 | 4.572 | 1.0817 | 0.041781
2015-07-19 03:00 | 100.77 | 67.75 | 33.02 | 136.2196 | 21.0691 | -120.8235 | 75.9716 | 14.0284 | -124.3126 | 110.6357 | 0 | 50.8125 | 0.2 | 0 | 5.0385 | 55.851 | 3.7 | 5.4453 | 1.0782 | 0.04938
2015-07-19 04:00 | 132.1533 | 89.9533 | 42.2 | 144.1612 | 21.0618 | -105.8245 | 72.9787 | 17.0213 | -110.1228 | 97.9626 | 0 | 67.465 | 0.2 | 0 | 6.6077 | 74.0727 | 3.1 | 5.4148 | 1.0783 | 0.065498
2015-07-19 05:00 | 163.5367 | 112.1567 | 51.38 | 148.0826 | 21.0545 | -90.8254 | 69.698 | 20.302 | -95.7593 | 84.7226 | 13.6203 | 84.1175 | 0.2 | 0 | 8.1768 | 105.9146 | 3.3 | 6.6098 | 1.0736 | 0.093239
2015-07-19 06:00 | 194.92 | 134.36 | 60.56 | 150.8641 | 21.0471 | -75.8263 | 66.333 | 23.667 | -81.1032 | 71.1325 | 48.7865 | 100.77 | 0.2 | 0 | 9.746 | 159.3025 | 3.9 | 8.8782 | 1.0645 | 0.13905
2015-07-19 07:00 | 222.0033 | 165.4167 | 56.5867 | 125.0903 | 21.0398 | -60.8272 | 63.1044 | 26.8956 | -66.0336 | 57.3224 | 67.5378 | 124.0625 | 0.2 | 0 | 11.1002 | 202.7004 | 3.3 | 9.6344 | 1.0615 | 0.17643
2015-07-19 08:00 | 249.0867 | 196.4733 | 52.6133 | 106.0057 | 21.0325 | -45.8282 | 60.2428 | 29.7572 | -50.4577 | 43.3802 | 77.0462 | 147.355 | 0.2 | 0 | 12.4543 | 236.8555 | 4.2 | 11.6017 | 1.0536 | 0.20463
2015-07-19 09:00 | 276.17 | 227.53 | 48.64 | 91.7227 | 21.0251 | -30.8291 | 57.9747 | 32.0253 | -34.3486 | 29.3852 | 79.9217 | 170.6475 | 0.2 | 0 | 13.8085 | 264.3777 | 4.2 | 12.4618 | 1.0502 | 0.22766
2015-07-19 10:00 | 261.92 | 228.3867 | 33.5333 | 60.7545 | 21.0178 | -15.83 | 56.4992 | 33.5008 | -17.78 | 15.4978 | 58.5455 | 171.29 | 0.2 | 0 | 13.096 | 242.9315 | 3.7 | 11.2916 | 1.0548 | 0.21013
2015-07-19 11:00 | 247.67 | 229.2433 | 18.4267 | 32.9163 | 21.0104 | -0.83088 | 55.9578 | 34.0422 | -0.93606 | 4.1193 | 32.8313 | 171.9325 | 0.2 | 0 | 12.3835 | 217.1473 | 4.3 | 11.0859 | 1.0557 | 0.18797
2015-07-19 12:00 | 233.42 | 230.1 | 3.32 | 6.0002 | 21.003 | 14.1682 | 56.4053 | 33.5947 | 15.922 | 13.9853 | 5.8223 | 172.575 | 0.2 | 0 | 11.671 | 190.0683 | 4.4 | 10.3396 | 1.0586 | 0.165
2015-07-19 13:00 | 236.6767 | 204.46 | 32.2167 | 60.4537 | 20.9956 | 29.1673 | 57.7974 | 32.2026 | 32.5288 | 27.8345 | 53.4592 | 153.345 | 0.2 | 0 | 11.8338 | 218.6381 | 4.3 | 11.1324 | 1.0555 | 0.18923
2015-07-19 14:00 | 239.9333 | 178.82 | 61.1133 | 122.2305 | 20.9882 | 44.1664 | 60.001 | 29.999 | 48.6898 | 41.8324 | 91.0738 | 134.115 | 0.2 | 0 | 11.9967 | 237.1854 | 4.6 | 12.012 | 1.052 | 0.2046
2015-07-19 15:00 | 243.19 | 153.18 | 90.01 | 197.0624 | 20.9808 | 59.1656 | 62.8218 | 27.1782 | 64.3199 | 55.7897 | 110.7949 | 114.885 | 0.2 | 0 | 12.1595 | 237.8394 | 4.3 | 11.7325 | 1.0531 | 0.20538
2015-07-19 16:00 | 224.2333 | 129.0167 | 95.2167 | 234.4232 | 20.9734 | 74.1647 | 66.0353 | 23.9647 | 79.4372 | 69.6255 | 81.6157 | 96.7625 | 0.2 | 0 | 11.2117 | 189.5899 | 4 | 9.9247 | 1.0603 | 0.16484
2015-07-19 17:00 | 205.2767 | 104.8533 | 100.4233 | 285.5623 | 20.9659 | 89.1638 | 69.4106 | 20.5894 | 94.1298 | 83.255 | 33.5393 | 78.64 | 0.2 | 0 | 10.2638 | 122.4431 | 4.7 | 8.5263 | 1.0659 | 0.10702
2015-07-19 18:00 | 186.32 | 80.69 | 105.63 | 355.7185 | 20.9585 | 104.1629 | 72.7256 | 17.2744 | 108.5177 | 96.5556 | 0 | 60.5175 | 0.2 | 0 | 9.316 | 69.8335 | 3.5 | 5.6823 | 1.0773 | 0.061688
2015-07-19 19:00 | 154.1133 | 69.1033 | 85.01 | 345.9438 | 20.9511 | 119.162 | 75.7748 | 14.2252 | 122.7215 | 109.3243 | 0 | 51.8275 | 0.2 | 0 | 7.7057 | 59.5332 | 3.5 | 5.3604 | 1.0786 | 0.052652
2015-07-19 20:00 | 121.9067 | 57.5167 | 64.39 | 319.5425 | 20.9436 | 134.1612 | 78.3749 | 11.6251 | 136.8415 | 121.1997 | 0 | 43.1375 | 0.2 | 0 | 6.0953 | 49.2328 | 3.2 | 4.7385 | 1.081 | 0.043643
2015-07-19 21:00 | 89.7 | 45.93 | 43.77 | 261.6657 | 20.9361 | 149.1603 | 80.3706 | 9.6294 | 150.9459 | 131.5093 | 0 | 34.4475 | 0.2 | 0 | 4.485 | 38.9325 | 3.5 | 4.7166 | 1.0811 | 0.034515
2015-07-19 22:00 | 84.0833 | 44.21 | 39.8733 | 274.3032 | 20.9286 | 164.1594 | 81.6417 | 8.3583 | 165.067 | 139.0436 | 0 | 33.1575 | 0.2 | 0 | 4.2042 | 37.3617 | 3.9 | 5.0676 | 1.0797 | 0.033079
2015-07-19 23:00 | 78.4667 | 42.49 | 35.9767 | 262.1128 | 20.9211 | 179.1586 | 82.1109 | 7.8891 | 179.2066 | 142.1032 | 0 | 31.8675 | 0.2 | 0 | 3.9233 | 35.7908 | 3.7 | 4.8185 | 1.0807 | 0.031718
2015-07-20 | 72.85 | 40.77 | 32.08 | 223.55 | 20.9136 | -165.8423 | 81.7494 | 8.2506 | -166.6518 | 139.6547 | 0 | 30.5775 | 0.2 | 0 | 3.6425 | 34.22 | 3.4 | 4.4694 | 1.0821 | 0.030365
2015-07-20 01:00 | 94.19 | 51.15 | 43.04 | 262.9707 | 20.9061 | -150.8431 | 80.5801 | 9.4199 | -152.5258 | 132.5442 | 0 | 38.3625 | 0.2 | 0 | 4.7095 | 43.072 | 3.2 | 4.546 | 1.0818 | 0.038209
2015-07-20 02:00 | 115.53 | 61.53 | 54 | 274.9867 | 20.8986 | -135.844 | 78.6751 | 11.3249 | -138.4166 | 122.4782 | 0 | 46.1475 | 0.2 | 0 | 5.7765 | 51.924 | 3.7 | 5.3226 | 1.0787 | 0.045929
2015-07-20 03:00 | 136.87 | 71.91 | 64.96 | 271.3665 | 20.8911 | -120.8448 | 76.15 | 13.85 | -124.2961 | 110.7383 | 0 | 53.9325 | 0.2 | 0 | 6.8435 | 60.776 | 3.8 | 5.6992 | 1.0772 | 0.053684
2015-07-20 04:00 | 147.4267 | 87.0467 | 60.38 | 208.3833 | 20.8835 | -105.8456 | 73.1567 | 16.8433 | -110.1007 | 98.0468 | 0 | 65.285 | 0.2 | 0 | 7.3713 | 72.6563 | 3.8 | 6.0705 | 1.0757 | 0.064089
2015-07-20 05:00 | 157.9833 | 102.1833 | 55.8 | 162.1842 | 20.876 | -90.8465 | 69.876 | 20.124 | -95.734 | 84.7912 | 14.7238 | 76.6375 | 0.2 | 0 | 7.8992 | 99.2605 | 3.8 | 6.9019 | 1.0724 | 0.087286
2015-07-20 06:00 | 168.54 | 117.32 | 51.22 | 128.5096 | 20.8684 | -75.8473 | 66.5112 | 23.4888 | -81.0774 | 71.1873 | 41.4411 | 87.99 | 0.2 | 0 | 8.427 | 137.8581 | 4.1 | 8.4081 | 1.0664 | 0.12055
2015-07-20 07:00 | 202.1167 | 154.4 | 47.7167 | 106.1361 | 20.8608 | -60.8481 | 63.2833 | 26.7167 | -66.0107 | 57.3642 | 57.2389 | 115.8 | 0.2 | 0 | 10.1058 | 183.1447 | 4.1 | 9.8233 | 1.0607 | 0.1593
2015-07-20 08:00 | 235.6933 | 191.48 | 44.2133 | 89.5731 | 20.8532 | -45.8489 | 60.4225 | 29.5775 | -50.4413 | 43.4085 | 65.0724 | 143.61 | 0.2 | 0 | 11.7847 | 220.4671 | 4.3 | 11.1896 | 1.0552 | 0.19077
2015-07-20 09:00 | 269.27 | 228.56 | 40.71 | 77.1576 | 20.8456 | -30.8498 | 58.1551 | 31.8449 | -34.3424 | 29.3969 | 67.2228 | 171.42 | 0.2 | 0 | 13.4635 | 252.1063 | 5.6 | 13.4783 | 1.0461 | 0.21625
2015-07-20 10:00 | 274.9833 | 232.1733 | 42.81 | 77.9332 | 20.838 | -15.8506 | 56.6799 | 33.3201 | -17.7871 | 15.4788 | 75.1065 | 174.13 | 0.2 | 0 | 13.7492 | 262.9857 | 5.8 | 14.0183 | 1.0439 | 0.22512
2015-07-20 11:00 | 280.6967 | 235.7867 | 44.91 | 80.5999 | 20.8304 | -0.85138 | 56.1379 | 33.8621 | -0.95829 | 3.9468 | 80.4088 | 176.84 | 0.2 | 0 | 14.0348 | 271.2836 | 5.8 | 14.2776 | 1.0429 | 0.23199
2015-07-20 12:00 | 286.41 | 239.4 | 47.01 | 85.3616 | 20.8228 | 14.1478 | 56.5839 | 33.4161 | 15.8848 | 13.9231 | 82.8537 | 179.55 | 0.2 | 0 | 14.3205 | 276.7242 | 6.3 | 14.9476 | 1.0402 | 0.23604
2015-07-20 13:00 | 297.5 | 213.23 | 84.27 | 158.9083 | 20.8152 | 29.147 | 57.9739 | 32.0261 | 32.4789 | 27.8057 | 140.5599 | 159.9225 | 0.2 | 0 | 14.875 | 315.3574 | 5.4 | 15.2549 | 1.039 | 0.26867
2015-07-20 14:00 | 308.59 | 187.06 | 121.53 | 244.3562 | 20.8075 | 44.1462 | 60.1753 | 29.8247 | 48.6306 | 41.8211 | 182.1017 | 140.295 | 0.2 | 0 | 15.4295 | 337.8262 | 6.7 | 17.2571 | 1.031 | 0.2856
2015-07-20 15:00 | 319.68 | 160.89 | 158.79 | 349.6976 | 20.7998 | 59.1454 | 62.9944 | 27.0056 | 64.2551 | 55.7924 | 196.5977 | 120.6675 | 0.2 | 0 | 15.984 | 333.2492 | 5.6 | 16.014 | 1.0359 | 0.28309
2015-07-20 16:00 | 288.7033 | 131.03 | 157.6733 | 390.8262 | 20.7922 | 74.1446 | 66.2069 | 23.7931 | 79.3703 | 69.6418 | 135.9639 | 98.2725 | 0.2 | 0 | 14.4352 | 248.6716 | 7.2 | 14.971 | 1.0401 | 0.21209
2015-07-20 17:00 | 257.7267 | 101.17 | 156.5567 | 448.7624 | 20.7845 | 89.1438 | 69.5822 | 20.4178 | 94.0639 | 83.286 | 52.4664 | 75.8775 | 0.2 | 0 | 12.8863 | 141.2303 | 7.3 | 11.7134 | 1.0531 | 0.12196
2015-07-20 18:00 | 226.75 | 71.31 | 155.44 | 528.5815 | 20.7768 | 104.1431 | 72.8982 | 17.1018 | 108.4552 | 96.6033 | 0 | 53.4825 | 0.2 | 0 | 11.3375 | 64.82 | 6.6 | 8.6256 | 1.0655 | 0.056634
2015-07-20 19:00 | 193.0867 | 57.6433 | 135.4433 | 557.8803 | 20.7691 | 119.1423 | 75.9492 | 14.0508 | 122.6647 | 109.3925 | 0 | 43.2325 | 0.2 | 0 | 9.6543 | 52.8868 | 6.4 | 8.0527 | 1.0678 | 0.046307
2015-07-20 20:00 | 159.4233 | 43.9767 | 115.4467 | 581.6359 | 20.7614 | 134.1415 | 78.5516 | 11.4484 | 136.7923 | 121.2936 | 0 | 32.9825 | 0.2 | 0 | 7.9712 | 40.9537 | 6.1 | 7.3798 | 1.0705 | 0.035949
2015-07-20 21:00 | 125.76 | 30.31 | 95.45 | 581.3271 | 20.7537 | 149.1407 | 80.5496 | 9.4504 | 150.9058 | 131.6351 | 0 | 22.7325 | 0.2 | 0 | 6.288 | 29.0205 | 5.8 | 6.7069 | 1.0732 | 0.025538
2015-07-20 22:00 | 114.95 | 32.34 | 82.61 | 580.8076 | 20.746 | 164.14 | 81.8229 | 8.1771 | 165.0371 | 139.2038 | 0 | 24.255 | 0.2 | 0 | 5.7475 | 30.0025 | 4.9 | 5.8376 | 1.0766 | 0.026488
2015-07-20 23:00 | 104.14 | 34.37 | 69.77 | 520.3042 | 20.7382 | 179.1392 | 82.2937 | 7.7063 | 179.1876 | 142.2857 | 0 | 25.7775 | 0.2 | 0 | 5.207 | 30.9845 | 4.1 | 5.0683 | 1.0797 | 0.027433
2015-07-21 | 93.33 | 36.4 | 56.93 | 405.6986 | 20.7305 | -165.8616 | 81.9333 | 8.0667 | -166.6597 | 139.832 | 0 | 27.3 | 0.2 | 0 | 4.6665 | 31.9665 | 3.4 | 4.399 | 1.0824 | 0.028373
2015-07-21 01:00 | 119.3133 | 54.7067 | 64.6067 | 402.5461 | 20.7227 | -150.8623 | 80.7644 | 9.2356 | -152.5232 | 132.6975 | 0 | 41.03 | 0.2 | 0 | 5.9657 | 46.9957 | 4.1 | 5.5686 | 1.0777 | 0.041532
2015-07-21 02:00 | 145.2967 | 73.0133 | 72.2833 | 374.0968 | 20.715 | -135.8631 | 78.8592 | 11.1408 | -138.4046 | 122.6049 | 0 | 54.76 | 0.2 | 0 | 7.2648 | 62.0248 | 3.9 | 5.8383 | 1.0766 | 0.054759
2015-07-21 03:00 | 171.28 | 91.32 | 79.96 | 338.4318 | 20.7072 | -120.8638 | 76.3337 | 13.6663 | -124.2762 | 110.8418 | 0 | 68.49 | 0.2 | 0 | 8.564 | 77.054 | 3.9 | 6.3079 | 1.0748 | 0.067908
2015-07-21 04:00 | 213.52 | 118.2433 | 95.2767 | 332.3331 | 20.6994 | -105.8645 | 73.3401 | 16.6599 | -110.0751 | 98.1313 | 0 | 88.6825 | 0.2 | 0 | 10.676 | 99.3585 | 5 | 8.105 | 1.0676 | 0.08698
2015-07-21 05:00 | 255.76 | 145.1667 | 110.5933 | 324.2739 | 20.6916 | -90.8653 | 70.0592 | 19.9408 | -95.705 | 84.8596 | 29.0539 | 108.875 | 0.2 | 0 | 12.788 | 150.7169 | 4.8 | 9.5099 | 1.062 | 0.13125
2015-07-21 06:00 | 298 | 172.09 | 125.91 | 318.2514 | 20.6838 | -75.866 | 66.6947 | 23.3053 | -81.048 | 71.2415 | 102.3431 | 129.0675 | 0.2 | 0 | 14.9 | 246.3106 | 5.4 | 13.0972 | 1.0476 | 0.21159
2015-07-21 07:00 | 333.7233 | 214.1467 | 119.5767 | 267.6849 | 20.676 | -60.8668 | 63.4674 | 26.5326 | -65.9841 | 57.4051 | 144.2007 | 160.61 | 0.2 | 0 | 16.6862 | 321.4969 | 5 | 15.0468 | 1.0398 | 0.27412
2015-07-21 08:00 | 369.4467 | 256.2033 | 113.2433 | 230.7377 | 20.6681 | -45.8675 | 60.6076 | 29.3924 | -50.4213 | 43.4357 | 167.5493 | 192.1525 | 0.2 | 0 | 18.4723 | 378.1741 | 5.4 | 17.2179 | 1.0311 | 0.31976
2015-07-21 09:00 | 405.17 | 298.26 | 106.91 | 203.6918 | 20.6603 | -30.8682 | 58.3411 | 31.6589 | -34.3328 | 29.4073 | 177.4463 | 223.695 | 0.2 | 0 | 20.2585 | 421.3998 | 5.6 | 18.7687 | 1.0249 | 0.35416
2015-07-21 10:00 | 416.1667 | 272.04 | 144.1267 | 263.6806 | 20.6524 | -15.8689 | 56.8662 | 33.1338 | -17.7912 | 15.4587 | 254.1413 | 204.03 | 0.2 | 0 | 20.8083 | 478.9797 | 5.7 | 20.6681 | 1.0173 | 0.39957
2015-07-21 11:00 | 427.1633 | 245.82 | 181.3433 | 327.0397 | 20.6446 | -0.86963 | 56.3238 | 33.6762 | -0.97791 | 3.7689 | 326.3325 | 184.365 | 0.2 | 0 | 21.3582 | 532.0556 | 6.2 | 22.8267 | 1.0087 | 0.44008
2015-07-21 12:00 | 438.16 | 219.6 | 218.56 | 398.8144 | 20.6367 | 14.1297 | 56.7684 | 33.2316 | 15.8499 | 13.8637 | 387.1964 | 164.7 | 0.2 | 0 | 21.908 | 573.8044 | 6.5 | 24.4314 | 1.0023 | 0.47159
2015-07-21 13:00 | 391.7733 | 219.2967 | 172.4767 | 326.907 | 20.6288 | 29.1289 | 58.1564 | 31.8436 | 32.4308 | 27.7798 | 289.2295 | 164.4725 | 0.2 | 0 | 19.5887 | 473.2906 | 6.3 | 21.0903 | 1.0156 | 0.39417
2015-07-21 14:00 | 345.3867 | 218.9933 | 126.3933 | 255.5398 | 20.6209 | 44.1282 | 60.3558 | 29.6442 | 48.5727 | 41.8127 | 190.461 | 164.245 | 0.2 | 0 | 17.2693 | 371.9753 | 6.4 | 18.0242 | 1.0279 | 0.31353
2015-07-21 15:00 | 299 | 218.69 | 80.31 | 177.9539 | 20.613 | 59.1275 | 63.1731 | 26.8269 | 64.1913 | 55.7983 | 100.0294 | 164.0175 | 0.2 | 0 | 14.95 | 278.9969 | 7 | 15.7187 | 1.0371 | 0.23727
2015-07-21 16:00 | 246.5333 | 182.86 | 63.6733 | 158.947 | 20.6051 | 74.1269 | 66.3846 | 23.6154 | 79.3043 | 69.6615 | 55.2445 | 137.145 | 0.2 | 0 | 12.3267 | 204.7162 | 6.3 | 12.6974 | 1.0492 | 0.17613
2015-07-21 17:00 | 194.0667 | 147.03 | 47.0367 | 135.9626 | 20.5972 | 89.1262 | 69.76 | 20.24 | 93.9987 | 83.3206 | 15.8144 | 110.2725 | 0.2 | 0 | 9.7033 | 135.7902 | 6 | 10.2434 | 1.059 | 0.11792
2015-07-21 18:00 | 141.6 | 111.2 | 30.4 | 104.4365 | 20.5893 | 104.1255 | 73.077 | 16.923 | 108.3936 | 96.6551 | 0 | 83.4 | 0.2 | 0 | 7.08 | 90.48 | 5 | 7.8275 | 1.0687 | 0.07929
2015-07-21 19:00 | 118.0667 | 93.69 | 24.3767 | 101.6864 | 20.5813 | 119.1248 | 76.1297 | 13.8703 | 122.6089 | 109.4651 | 0 | 70.2675 | 0.2 | 0 | 5.9033 | 76.1708 | 5.5 | 7.8803 | 1.0685 | 0.066737
2015-07-21 20:00 | 94.5333 | 76.18 | 18.3533 | 93.9467 | 20.5734 | 134.1241 | 78.7343 | 11.2657 | 136.7443 | 121.3924 | 0 | 57.135 | 0.2 | 0 | 4.7267 | 61.8617 | 5.3 | 7.2332 | 1.0711 | 0.054332
2015-07-21 21:00 | 71 | 58.67 | 12.33 | 76.5809 | 20.5654 | 149.1234 | 80.7347 | 9.2653 | 150.8671 | 131.7663 | 0 | 44.0025 | 0.2 | 0 | 3.55 | 47.5525 | 4.5 | 5.986 | 1.0761 | 0.041959
2015-07-21 22:00 | 65.81 | 53.1633 | 12.6467 | 90.9836 | 20.5575 | 164.1228 | 82.0101 | 7.9899 | 165.009 | 139.3701 | 0 | 39.8725 | 0.2 | 0 | 3.2905 | 43.163 | 5.1 | 6.4488 | 1.0742 | 0.03802
2015-07-21 23:00 | 60.62 | 47.6567 | 12.9633 | 99.085 | 20.5495 | 179.1221 | 82.4824 | 7.5176 | 179.1708 | 142.474 | 0 | 35.7425 | 0.2 | 0 | 3.031 | 38.7735 | 4.4 | 5.6117 | 1.0776 | 0.03426
2015-07-22 | 55.43 | 42.15 | 13.28 | 96.8996 | 20.5415 | -165.8786 | 82.1229 | 7.8771 | -166.6651 | 140.0139 | 0 | 31.6125 | 0.2 | 0 | 2.7715 | 34.384 | 4.1 | 5.1745 | 1.0793 | 0.030431
2015-07-22 01:00 | 71.3733 | 55.2567 | 16.1167 | 102.5075 | 20.5335 | -150.8792 | 80.9542 | 9.0458 | -152.5178 | 132.8538 | 0 | 41.4425 | 0.2 | 0 | 3.5687 | 45.0112 | 3.4 | 4.8066 | 1.0808 | 0.03989
2015-07-22 02:00 | 87.3167 | 68.3633 | 18.9533 | 99.768 | 20.5255 | -135.8799 | 79.0487 | 10.9513 | -138.3895 | 122.7332 | 0 | 51.2725 | 0.2 | 0 | 4.3658 | 55.6383 | 3.7 | 5.4387 | 1.0782 | 0.049193
2015-07-22 03:00 | 103.26 | 81.47 | 21.79 | 93.4955 | 20.5175 | -120.8805 | 76.5228 | 13.4772 | -124.2532 | 110.9461 | 0 | 61.1025 | 0.2 | 0 | 5.163 | 66.2655 | 3.5 | 5.5708 | 1.0777 | 0.058561
2015-07-22 04:00 | 136.9833 | 98.2067 | 38.7767 | 136.7609 | 20.5094 | -105.8812 | 73.5286 | 16.4714 | -110.0461 | 98.2158 | 0 | 73.655 | 0.2 | 0 | 6.8492 | 80.5042 | 3.4 | 5.9158 | 1.0763 | 0.071053
2015-07-22 05:00 | 170.7067 | 114.9433 | 55.7633 | 165.0013 | 20.5014 | -90.8818 | 70.2475 | 19.7525 | -95.6725 | 84.9276 | 14.5885 | 86.2075 | 0.2 | 0 | 8.5353 | 109.3314 | 3.6 | 7.0166 | 1.0719 | 0.096101
2015-07-22 06:00 | 204.43 | 131.68 | 72.75 | 185.3007 | 20.4933 | -75.8824 | 66.8833 | 23.1167 | -81.015 | 71.295 | 59.4251 | 98.76 | 0.2 | 0 | 10.2215 | 168.4066 | 3.5 | 8.7627 | 1.0649 | 0.14706
2015-07-22 07:00 | 232.3833 | 163.9833 | 68.4 | 154.1418 | 20.4853 | -60.8831 | 63.6568 | 26.3432 | -65.9539 | 57.4451 | 82.9449 | 122.9875 | 0.2 | 0 | 11.6192 | 217.5516 | 4.1 | 10.8985 | 1.0564 | 0.18845
2015-07-22 08:00 | 260.3367 | 196.2867 | 64.05 | 131.2796 | 20.4772 | -45.8837 | 60.798 | 29.202 | -50.3978 | 43.4618 | 95.2871 | 147.215 | 0.2 | 0 | 13.0168 | 255.519 | 4.4 | 12.385 | 1.0505 | 0.2201
2015-07-22 09:00 | 288.29 | 228.59 | 59.7 | 114.3646 | 20.4691 | -30.8843 | 58.5325 | 31.4675 | -34.3199 | 29.4165 | 99.6198 | 171.4425 | 0.2 | 0 | 14.4145 | 285.4768 | 5.1 | 14.0212 | 1.0439 | 0.24437
2015-07-22 10:00 | 307.9633 | 224.3433 | 83.62 | 153.7735 | 20.461 | -15.885 | 57.0582 | 32.9418 | -17.7923 | 15.4377 | 148.2254 | 168.2575 | 0.2 | 0 | 15.3982 | 331.8811 | 5.7 | 16.0713 | 1.0357 | 0.28186
2015-07-22 11:00 | 327.6367 | 220.0967 | 107.54 | 194.9205 | 20.4529 | -0.88558 | 56.5155 | 33.4845 | -0.99488 | 3.5857 | 194.5389 | 165.0725 | 0.2 | 0 | 16.3818 | 375.9933 | 6.7 | 18.4498 | 1.0262 | 0.31639
2015-07-22 12:00 | 347.31 | 215.85 | 131.46 | 241.1047 | 20.4448 | 14.1138 | 56.9589 | 33.0411 | 15.8171 | 13.8073 | 234.1377 | 161.8875 | 0.2 | 0 | 17.3655 | 413.3907 | 5.4 | 18.3185 | 1.0267 | 0.34804
2015-07-22 13:00 | 283.92 | 195.2967 | 88.6233 | 168.8699 | 20.4367 | 29.1132 | 58.3451 | 31.6549 | 32.3844 | 27.7569 | 149.4383 | 146.4725 | 0.2 | 0 | 14.196 | 310.1068 | 5.3 | 14.9908 | 1.04 | 0.26447
2015-07-22 14:00 | 220.53 | 174.7433 | 45.7867 | 93.1038 | 20.4286 | 44.1126 | 60.5423 | 29.4577 | 48.5162 | 41.8075 | 69.3986 | 131.0575 | 0.2 | 0 | 11.0265 | 211.4826 | 5.4 | 12.0088 | 1.052 | 0.18243
2015-07-22 15:00 | 157.14 | 154.19 | 2.95 | 6.5787 | 20.4204 | 59.112 | 63.358 | 26.642 | 64.1286 | 55.8074 | 3.6971 | 115.6425 | 0.2 | 0 | 7.857 | 127.1966 | 5.1 | 9.0749 | 1.0637 | 0.11095
2015-07-22 16:00 | 135.05 | 130.53 | 4.52 | 11.3667 | 20.4123 | 74.1114 | 66.5686 | 23.4314 | 79.2392 | 69.6846 | 3.9464 | 97.8975 | 0.2 | 0 | 6.7525 | 108.5964 | 4.8 | 8.1936 | 1.0672 | 0.095035
2015-07-22 17:00 | 112.96 | 106.87 | 6.09 | 17.7583 | 20.4041 | 89.1108 | 69.944 | 20.056 | 93.9344 | 83.3589 | 2.0538 | 80.1525 | 0.2 | 0 | 5.648 | 87.8543 | 5.2 | 7.9454 | 1.0682 | 0.076955
2015-07-22 18:00 | 90.87 | 83.21 | 7.66 | 26.5975 | 20.396 | 104.1102 | 73.2619 | 16.7381 | 108.3329 | 96.7109 | 0 | 62.4075 | 0.2 | 0 | 4.5435 | 66.951 | 5.1 | 7.1922 | 1.0712 | 0.05881
2015-07-22 19:00 | 76.1933 | 66.43 | 9.7633 | 41.2721 | 20.3878 | 119.1096 | 76.3164 | 13.6836 | 122.5542 | 109.5421 | 0 | 49.8225 | 0.2 | 0 | 3.8097 | 53.6322 | 5.3 | 6.976 | 1.0721 | 0.047149
2015-07-22 20:00 | 61.5167 | 49.65 | 11.8667 | 61.765 | 20.3796 | 134.109 | 78.9231 | 11.0769 | 136.6975 | 121.496 | 0 | 37.2375 | 0.2 | 0 | 3.0758 | 40.3133 | 5.6 | 6.8598 | 1.0726 | 0.035456
2015-07-22 21:00 | 46.84 | 32.87 | 13.97 | 88.5778 | 20.3714 | 149.1085 | 80.9257 | 9.0743 | 150.8299 | 131.9031 | 0 | 24.6525 | 0.2 | 0 | 2.342 | 26.9945 | 4.8 | 5.6436 | 1.0774 | 0.023849
2015-07-22 22:00 | 43.25 | 33.8967 | 9.3533 | 68.9457 | 20.3632 | 164.1079 | 82.2031 | 7.7969 | 164.9828 | 139.5423 | 0 | 25.4225 | 0.2 | 0 | 2.1625 | 27.585 | 4.7 | 5.562 | 1.0778 | 0.024378
2015-07-22 23:00 | 39.66 | 34.9233 | 4.7367 | 37.1605 | 20.355 | 179.1073 | 82.6769 | 7.3231 | 179.1562 | 142.6681 | 0 | 26.1925 | 0.2 | 0 | 1.983 | 28.1755 | 3.8 | 4.6805 | 1.0813 | 0.024982
2015-07-23 | 36.07 | 35.95 | 0.12 | 0.89771 | 20.3467 | -165.8932 | 82.3181 | 7.6819 | -166.6681 | 140.2003 | 0 | 26.9625 | 0.2 | 0 | 1.8035 | 28.766 | 4.5 | 5.3989 | 1.0784 | 0.025438
2015-07-23 01:00 | 54.2667 | 51.51 | 2.7567 | 17.917 | 20.3385 | -150.8938 | 81.1495 | 8.8505 | -152.5096 | 133.0131 | 0 | 38.6325 | 0.2 | 0 | 2.7133 | 41.3458 | 4.2 | 5.4921 | 1.078 | 0.036549
2015-07-23 02:00 | 72.4633 | 67.07 | 5.3933 | 28.898 | 20.3303 | -135.8944 | 79.2436 | 10.7564 | -138.3714 | 122.8631 | 0 | 50.3025 | 0.2 | 0 | 3.6232 | 53.9257 | 4.3 | 5.9852 | 1.0761 | 0.047582
2015-07-23 03:00 | 90.66 | 82.63 | 8.03 | 34.9493 | 20.322 | -120.8949 | 76.717 | 13.283 | -124.2268 | 111.0511 | 0 | 61.9725 | 0.2 | 0 | 4.533 | 66.5055 | 4.3 | 6.3783 | 1.0745 | 0.058597
2015-07-23 04:00 | 103.97 | 97.5767 | 6.3933 | 22.8094 | 20.3137 | -105.8955 | 73.7223 | 16.2777 | -110.0135 | 98.3004 | 0 | 73.1825 | 0.2 | 0 | 5.1985 | 78.381 | 3.8 | 6.2494 | 1.075 | 0.069093
2015-07-23 05:00 | 117.28 | 112.5233 | 4.7567 | 14.2084 | 20.3055 | -90.896 | 70.441 | 19.559 | -95.6364 | 84.9952 | 1.2395 | 84.3925 | 0.2 | 0 | 5.864 | 91.496 | 4 | 6.8593 | 1.0726 | 0.080471
2015-07-23 06:00 | 130.59 | 127.47 | 3.12 | 8.0104 | 20.2972 | -75.8965 | 67.077 | 22.923 | -80.9783 | 71.3478 | 2.5619 | 95.6025 | 0.2 | 0 | 6.5295 | 104.6939 | 4.7 | 7.9717 | 1.0681 | 0.091696
2015-07-23 07:00 | 173.69 | 151.3133 | 22.3767 | 50.775 | 20.2889 | -60.8971 | 63.8513 | 26.1487 | -65.9201 | 57.484 | 27.2933 | 113.485 | 0.2 | 0 | 8.6845 | 149.4628 | 4.4 | 9.0707 | 1.0637 | 0.13037
2015-07-23 08:00 | 216.79 | 175.1567 | 41.6333 | 85.8585 | 20.2806 | -45.8976 | 60.9937 | 29.0063 | -50.3707 | 43.4867 | 62.2933 | 131.3675 | 0.2 | 0 | 10.8395 | 204.5003 | 4.4 | 10.7906 | 1.0568 | 0.17722
2015-07-23 09:00 | 259.89 | 199 | 60.89 | 117.3033 | 20.2722 | -30.8981 | 58.7293 | 31.2707 | -34.3037 | 29.4246 | 102.1716 | 149.25 | 0.2 | 0 | 12.9945 | 264.4161 | 4.6 | 12.863 | 1.0485 | 0.22735
2015-07-23 10:00 | 257.06 | 192.5233 | 64.5367 | 119.3157 | 20.2639 | -15.8987 | 57.2557 | 32.7443 | -17.7902 | 15.4159 | 115.0229 | 144.3925 | 0.2 | 0 | 12.853 | 272.2684 | 5.6 | 14.1084 | 1.0436 | 0.23299
2015-07-23 11:00 | 254.23 | 186.0467 | 68.1833 | 124.2328 | 20.2556 | -0.89917 | 56.7129 | 33.2871 | -1.0091 | 3.3975 | 124.0145 | 139.535 | 0.2 | 0 | 12.7115 | 276.261 | 5.2 | 13.8332 | 1.0447 | 0.23665
2015-07-23 12:00 | 251.4 | 179.57 | 71.83 | 132.4386 | 20.2472 | 14.1003 | 57.1553 | 32.8447 | 15.7867 | 13.7543 | 128.6408 | 134.6775 | 0.2 | 0 | 12.57 | 275.8883 | 5.2 | 13.8215 | 1.0447 | 0.23634
2015-07-23 13:00 | 221.6133 | 168.37 | 53.2433 | 102.0166 | 20.2389 | 29.0998 | 58.5396 | 31.4604 | 32.3399 | 27.7372 | 90.294 | 126.2775 | 0.2 | 0 | 11.0807 | 227.6522 | 5.1 | 12.2141 | 1.0511 | 0.19622
2015-07-23 14:00 | 191.8267 | 157.17 | 34.6567 | 70.8941 | 20.2305 | 44.0993 | 60.7349 | 29.2651 | 48.4612 | 41.8054 | 52.8454 | 117.8775 | 0.2 | 0 | 9.5913 | 180.3142 | 4.6 | 10.2348 | 1.0591 | 0.15659
2015-07-23 15:00 | 162.04 | 145.97 | 16.07 | 36.0772 | 20.2221 | 59.0988 | 63.5489 | 26.4511 | 64.0672 | 55.8198 | 20.2681 | 109.4775 | 0.2 | 0 | 8.102 | 137.8476 | 4.3 | 8.6077 | 1.0656 | 0.12045
2015-07-23 16:00 | 132.59 | 118.9867 | 13.6033 | 34.4732 | 20.2138 | 74.0983 | 66.7586 | 23.2414 | 79.1751 | 69.7113 | 11.9536 | 89.24 | 0.2 | 0 | 6.6295 | 107.8231 | 4.5 | 7.8695 | 1.0685 | 0.094473
2015-07-23 17:00 | 103.14 | 92.0033 | 11.1367 | 32.7722 | 20.2054 | 89.0978 | 70.134 | 19.866 | 93.8711 | 83.4008 | 3.7663 | 69.0025 | 0.2 | 0 | 5.157 | 77.9258 | 4.4 | 6.8352 | 1.0727 | 0.068542
2015-07-23 18:00 | 73.69 | 65.02 | 8.67 | 30.4421 | 20.197 | 104.0973 | 73.453 | 16.547 | 108.2732 | 96.7706 | 0 | 48.765 | 0.2 | 0 | 3.6845 | 52.4495 | 3.6 | 5.239 | 1.079 | 0.046408
2015-07-23 19:00 | 58.5767 | 52.7967 | 5.78 | 24.7759 | 20.1885 | 119.0968 | 76.5091 | 13.4909 | 122.5005 | 109.6234 | 0 | 39.5975 | 0.2 | 0 | 2.9288 | 42.5263 | 3.3 | 4.6289 | 1.0815 | 0.037713
2015-07-23 20:00 | 43.4633 | 40.5733 | 2.89 | 15.3081 | 20.1801 | 134.0963 | 79.1179 | 10.8821 | 136.652 | 121.6045 | 0 | 30.43 | 0.2 | 0 | 2.1732 | 32.6032 | 3.2 | 4.2188 | 1.0831 | 0.028957
2015-07-23 21:00 | 28.35 | 28.35 | 0 | 0 | 20.1717 | 149.0959 | 81.1227 | 8.8773 | 150.7944 | 132.0452 | 0 | 21.2625 | 0.2 | 0 | 1.4175 | 22.68 | 3 | 3.7088 | 1.0852 | 0.020181
2015-07-23 22:00 | 26.3767 | 26.3767 | 0 | 0 | 20.1632 | 164.0954 | 82.4019 | 7.5981 | 164.9584 | 139.7204 | 0 | 19.7825 | 0.2 | 0 | 1.3188 | 21.1013 | 2.9 | 3.5594 | 1.0858 | 0.018787
2015-07-23 23:00 | 24.4033 | 24.4033 | 0 | 0 | 20.1548 | 179.0949 | 82.877 | 7.123 | 179.1437 | 142.8679 | 0 | 18.3025 | 0.2 | 0 | 1.2202 | 19.5227 | 2.9 | 3.5101 | 1.086 | 0.017385
2015-07-24 | 22.43 | 22.43 | 0 | 0 | 20.1463 | -165.9055 | 82.5189 | 7.4811 | -166.6685 | 140.3912 | 0 | 16.8225 | 0.2 | 0 | 1.1215 | 17.944 | 2.8 | 3.3607 | 1.0866 | 0.015988
2015-07-24 01:00 | 32.0667 | 32.0667 | 0 | 0 | 20.1378 | -150.906 | 81.3502 | 8.6498 | -152.4986 | 133.175 | 0 | 24.05 | 0.2 | 0 | 1.6033 | 25.6533 | 2.7 | 3.5017 | 1.086 | 0.022845
2015-07-24 02:00 | 41.7033 | 41.7033 | 0 | 0 | 20.1294 | -135.9065 | 79.4438 | 10.5562 | -138.3501 | 122.9945 | 0 | 31.2775 | 0.2 | 0 | 2.0852 | 33.3627 | 2.7 | 3.7426 | 1.085 | 0.029684
2015-07-24 03:00 | 51.34 | 51.34 | 0 | 0 | 20.1209 | -120.9069 | 76.9164 | 13.0836 | -124.1971 | 111.1567 | 0 | 38.505 | 0.2 | 0 | 2.567 | 41.072 | 2.9 | 4.1835 | 1.0833 | 0.036483
2015-07-24 04:00 | 62.4133 | 62.4133 | 0 | 0 | 20.1124 | -105.9074 | 73.921 | 16.079 | -109.9775 | 98.3849 | 0 | 46.81 | 0.2 | 0 | 3.1207 | 49.9307 | 3.2 | 4.7603 | 1.081 | 0.044258
2015-07-24 05:00 | 73.4867 | 73.4867 | 0 | 0 | 20.1038 | -90.9078 | 70.6394 | 19.3606 | -95.5967 | 85.0623 | 0 | 55.115 | 0.2 | 0 | 3.6743 | 58.7893 | 3.2 | 5.0372 | 1.0799 | 0.052057
2015-07-24 06:00 | 84.56 | 84.56 | 0 | 0 | 20.0953 | -75.9082 | 67.2757 | 22.7243 | -80.9379 | 71.3997 | 0 | 63.42 | 0.2 | 0 | 4.228 | 67.648 | 3.3 | 5.414 | 1.0783 | 0.059817
2015-07-24 07:00 | 104.69 | 104.59 | 0.1 | 0.22853 | 20.0868 | -60.9087 | 64.0508 | 25.9492 | -65.8826 | 57.522 | 0.12272 | 78.4425 | 0.2 | 0 | 5.2345 | 83.7997 | 2.8 | 5.4187 | 1.0783 | 0.074098
2015-07-24 08:00 | 124.82 | 124.62 | 0.2 | 0.41508 | 20.0782 | -45.9091 | 61.1945 | 28.8055 | -50.3401 | 43.5105 | 0.30103 | 93.465 | 0.2 | 0 | 6.241 | 100.007 | 3 | 6.1252 | 1.0755 | 0.088197
2015-07-24 09:00 | 144.95 | 144.65 | 0.3 | 0.58132 | 20.0697 | -30.9095 | 58.9315 | 31.0685 | -34.284 | 29.4315 | 0.5063 | 108.4875 | 0.2 | 0 | 7.2475 | 116.2413 | 3 | 6.6325 | 1.0735 | 0.10232
2015-07-24 10:00 | 147.93 | 147.5467 | 0.38333 | 0.71264 | 20.0611 | -15.91 | 57.4588 | 32.5412 | -17.7851 | 15.3934 | 0.68707 | 110.66 | 0.2 | 0 | 7.3965 | 118.7436 | 3.2 | 6.9107 | 1.0724 | 0.10442
2015-07-24 11:00 | 150.91 | 150.4433 | 0.46667 | 0.85491 | 20.0526 | -0.91037 | 56.9159 | 33.0841 | -1.0207 | 3.2043 | 0.85357 | 112.8325 | 0.2 | 0 | 7.5455 | 121.2316 | 3.2 | 6.9885 | 1.072 | 0.10657
2015-07-24 12:00 | 153.89 | 153.34 | 0.55 | 1.0197 | 20.044 | 14.0892 | 57.3574 | 32.6426 | 15.7585 | 13.7051 | 0.99063 | 115.005 | 0.2 | 0 | 7.6945 | 123.6901 | 3.3 | 7.1653 | 1.0713 | 0.10866
2015-07-24 13:00 | 149.14 | 146.75 | 2.39 | 4.6057 | 20.0354 | 29.0888 | 58.7401 | 31.2599 | 32.2973 | 27.7208 | 4.0771 | 110.0625 | 0.2 | 0 | 7.457 | 121.5966 | 3.7 | 7.4999 | 1.07 | 0.10669
2015-07-24 14:00 | 144.39 | 140.16 | 4.23 | 8.7068 | 20.0268 | 44.0884 | 60.9335 | 29.0665 | 48.4078 | 41.8067 | 6.4901 | 105.12 | 0.2 | 0 | 7.2195 | 118.8296 | 3.3 | 7.0134 | 1.0719 | 0.10445
2015-07-24 15:00 | 139.64 | 133.57 | 6.07 | 13.722 | 20.0182 | 59.088 | 63.7458 | 26.2542 | 64.007 | 55.8356 | 7.7059 | 100.1775 | 0.2 | 0 | 6.982 | 114.8654 | 3.8 | 7.3895 | 1.0704 | 0.10082
2015-07-24 16:00 | 125.3 | 114.0567 | 11.2433 | 28.7216 | 20.0096 | 74.0876 | 66.9547 | 23.0453 | 79.1121 | 69.7415 | 9.945 | 85.5425 | 0.2 | 0 | 6.265 | 101.7525 | 4 | 7.1798 | 1.0713 | 0.089385
2015-07-24 17:00 | 110.96 | 94.5433 | 16.4167 | 48.772 | 20.0009 | 89.0872 | 70.3301 | 19.6699 | 93.8088 | 83.4466 | 5.5663 | 70.9075 | 0.2 | 0 | 5.548 | 82.0218 | 4 | 6.5632 | 1.0737 | 0.072218
2015-07-24 18:00 | 96.62 | 75.03 | 21.59 | 76.695 | 19.9923 | 104.0868 | 73.65 | 16.35 | 108.2146 | 96.8344 | 0 | 56.2725 | 0.2 | 0 | 4.831 | 61.1035 | 3.8 | 5.7095 | 1.0772 | 0.053971
2015-07-24 19:00 | 79.1467 | 61.5467 | 17.6 | 76.549 | 19.9836 | 119.0864 | 76.7077 | 13.2923 | 122.448 | 109.7091 | 0 | 46.16 | 0.2 | 0 | 3.9573 | 50.1173 | 3.5 | 5.0662 | 1.0797 | 0.044373
2015-07-24 20:00 | 61.6733 | 48.0633 | 13.61 | 73.4298 | 19.975 | 134.0861 | 79.3186 | 10.6814 | 136.6079 | 121.7178 | 0 | 36.0475 | 0.2 | 0 | 3.0837 | 39.1312 | 3.7 | 4.9228 | 1.0803 | 0.034664
2015-07-24 21:00 | 44.2 | 34.58 | 9.62 | 63.7844 | 19.9663 | 149.0857 | 81.3255 | 8.6745 | 150.7604 | 132.1927 | 0 | 25.935 | 0.2 | 0 | 2.21 | 28.145 | 3.5 | 4.3795 | 1.0825 | 0.024982
2015-07-24 22:00 | 45.3867 | 37.4 | 7.9867 | 62.0648 | 19.9576 | 164.0853 | 82.6065 | 7.3935 | 164.9359 | 139.9044 | 0 | 28.05 | 0.2 | 0 | 2.2693 | 30.3193 | 3.5 | 4.4475 | 1.0822 | 0.026906
2015-07-24 23:00 | 46.5733 | 40.22 | 6.3533 | 52.7534 | 19.949 | 179.0849 | 83.0828 | 6.9172 | 179.1335 | 143.0734 | 0 | 30.165 | 0.2 | 0 | 2.3287 | 32.4937 | 3.4 | 4.4154 | 1.0823 | 0.028839
2015-07-25 | 47.76 | 43.04 | 4.72 | 37.274 | 19.9403 | -165.9154 | 82.7251 | 7.2749 | -166.6664 | 140.5863 | 0 | 32.28 | 0.2 | 0 | 2.388 | 34.668 | 3 | 4.0834 | 1.0837 | 0.030806
2015-07-25 01:00 | 70.1333 | 61.1767 | 8.9567 | 60.9965 | 19.9316 | -150.9158 | 81.5562 | 8.4438 | -152.4847 | 133.3397 | 0 | 45.8825 | 0.2 | 0 | 3.5067 | 49.3892 | 3.2 | 4.7434 | 1.081 | 0.043781
2015-07-25 02:00 | 92.5067 | 79.3133 | 13.1933 | 73.4282 | 19.9228 | -135.9161 | 79.6491 | 10.3509 | -138.3258 | 123.1273 | 0 | 59.485 | 0.2 | 0 | 4.6253 | 64.1103 | 2.9 | 4.9034 | 1.0804 | 0.056796
2015-07-25 03:00 | 114.88 | 97.45 | 17.43 | 78.1977 | 19.9141 | -120.9165 | 77.1208 | 12.8792 | -124.164 | 111.2627 | 0 | 73.0875 | 0.2 | 0 | 5.744 | 78.8315 | 3.3 | 5.7635 | 1.0769 | 0.069616
2015-07-25 04:00 | 147.61 | 130.47 | 17.14 | 62.6587 | 19.9054 | -105.9168 | 74.1246 | 15.8754 | -109.938 | 98.4694 | 0 | 97.8525 | 0.2 | 0 | 7.3805 | 105.233 | 3.3 | 6.5885 | 1.0736 | 0.092646
2015-07-25 05:00 | 180.34 | 163.49 | 16.85 | 51.3465 | 19.8966 | -90.9172 | 70.8427 | 19.1573 | -95.5533 | 85.1288 | 4.3601 | 122.6175 | 0.2 | 0 | 9.017 | 135.9946 | 3.5 | 7.7498 | 1.069 | 0.11921
2015-07-25 06:00 | 213.07 | 196.51 | 16.56 | 43.2357 | 19.8879 | -75.9175 | 67.4793 | 22.5207 | -80.8938 | 71.4509 | 13.754 | 147.3825 | 0.2 | 0 | 10.6535 | 171.79 | 3.4 | 8.7684 | 1.0649 | 0.15001
2015-07-25 07:00 | 263.8067 | 231.66 | 32.1467 | 74.0091 | 19.8791 | -60.9178 | 64.2553 | 25.7447 | -65.8414 | 57.5589 | 39.7008 | 173.745 | 0.2 | 0 | 13.1903 | 226.6362 | 4.3 | 11.3824 | 1.0545 | 0.19596
2015-07-25 08:00 | 314.5433 | 266.81 | 47.7333 | 99.7175 | 19.8703 | -45.9182 | 61.4004 | 28.5996 | -50.3059 | 43.5332 | 72.2928 | 200.1075 | 0.2 | 0 | 15.7272 | 288.1274 | 4.6 | 13.604 | 1.0456 | 0.24703
2015-07-25 09:00 | 365.28 | 301.96 | 63.32 | 123.4406 | 19.8616 | -30.9185 | 59.1388 | 30.8612 | -34.2609 | 29.4375 | 107.5035 | 226.47 | 0.2 | 0 | 18.264 | 352.2375 | 4.9 | 15.9074 | 1.0364 | 0.29934
2015-07-25 10:00 | 402.47 | 271.0967 | 131.3733 | 245.6328 | 19.8528 | -15.9188 | 57.6672 | 32.3328 | -17.7769 | 15.3705 | 236.847 | 203.3225 | 0.2 | 0 | 20.1235 | 460.293 | 4.6 | 18.9842 | 1.0241 | 0.38652
2015-07-25 11:00 | 439.66 | 240.2333 | 199.4267 | 367.3939 | 19.844 | -0.91914 | 57.1246 | 32.8754 | -1.0294 | 3.0065 | 366.8882 | 180.175 | 0.2 | 0 | 21.983 | 569.0462 | 5.2 | 22.9827 | 1.0081 | 0.47038
2015-07-25 12:00 | 476.85 | 209.37 | 267.48 | 498.7147 | 19.8351 | 14.0805 | 57.5653 | 32.4347 | 15.7328 | 13.66 | 484.6083 | 157.0275 | 0.2 | 0 | 23.8425 | 665.4783 | 4.9 | 25.6962 | 0.99722 | 0.54417
2015-07-25 13:00 | 436.6167 | 203.2133 | 233.4033 | 452.4728 | 19.8263 | 29.0802 | 58.9464 | 31.0536 | 32.2567 | 27.708 | 400.587 | 152.41 | 0.2 | 0 | 21.8308 | 574.8279 | 5.4 | 23.3634 | 1.0065 | 0.47444
2015-07-25 14:00 | 396.3833 | 197.0567 | 199.3267 | 412.939 | 19.8175 | 44.0799 | 61.1379 | 28.8621 | 48.3559 | 41.8114 | 307.7813 | 147.7925 | 0.2 | 0 | 19.8192 | 475.393 | 5.3 | 20.156 | 1.0194 | 0.39738
2015-07-25 15:00 | 356.15 | 190.9 | 165.25 | 376.2738 | 19.8087 | 59.0796 | 63.9488 | 26.0512 | 63.9481 | 55.8549 | 211.1988 | 143.175 | 0.2 | 0 | 17.8075 | 372.1813 | 5.7 | 17.3307 | 1.0307 | 0.31455
2015-07-25 16:00 | 309.1333 | 147.4 | 161.7333 | 416.6105 | 19.7998 | 74.0793 | 67.1567 | 22.8433 | 79.0503 | 69.7752 | 144.0239 | 110.55 | 0.2 | 0 | 15.4567 | 270.0306 | 5.3 | 13.7385 | 1.045 | 0.2314
2015-07-25 17:00 | 262.1167 | 103.9 | 158.2167 | 474.7297 | 19.7909 | 89.0791 | 70.5322 | 19.4678 | 93.7476 | 83.4961 | 53.773 | 77.925 | 0.2 | 0 | 13.1058 | 144.8038 | 5.5 | 10.0251 | 1.0599 | 0.12585
2015-07-25 18:00 | 215.1 | 60.4 | 154.7 | 556.2672 | 19.7821 | 104.0788 | 73.8529 | 16.1471 | 108.157 | 96.9022 | 0 | 45.3 | 0.2 | 0 | 10.755 | 56.055 | 5.2 | 6.9517 | 1.0722 | 0.049283
2015-07-25 19:00 | 176.5233 | 50.8833 | 125.64 | 554.8446 | 19.7732 | 119.0785 | 76.9123 | 13.0877 | 122.3968 | 109.7992 | 0 | 38.1625 | 0.2 | 0 | 8.8262 | 46.9887 | 5.3 | 6.7684 | 1.0729 | 0.041341
2015-07-25 20:00 | 137.9467 | 41.3667 | 96.58 | 531.2346 | 19.7643 | 134.0782 | 79.5252 | 10.4748 | 136.5651 | 121.8359 | 0 | 31.025 | 0.2 | 0 | 6.8973 | 37.9223 | 5.2 | 6.3851 | 1.0745 | 0.033412
2015-07-25 21:00 | 99.37 | 31.85 | 67.52 | 458.6323 | 19.7554 | 149.0779 | 81.5341 | 8.4659 | 150.7281 | 132.3455 | 0 | 23.8875 | 0.2 | 0 | 4.9685 | 28.856 | 5.4 | 6.3018 | 1.0748 | 0.025432
2015-07-25 22:00 | 91.3133 | 32.48 | 58.8333 | 470.5074 | 19.7465 | 164.0777 | 82.8168 | 7.1832 | 164.9154 | 140.0942 | 0 | 24.36 | 0.2 | 0 | 4.5657 | 28.9257 | 5 | 5.9039 | 1.0764 | 0.025531
2015-07-25 23:00 | 83.2567 | 33.11 | 50.1467 | 429.4411 | 19.7376 | 179.0774 | 83.2942 | 6.7058 | 179.1256 | 143.2846 | 0 | 24.8325 | 0.2 | 0 | 4.1628 | 28.9953 | 4.8 | 5.7061 | 1.0772 | 0.025611
2015-07-26 | 75.2 | 33.74 | 41.46 | 337.1701 | 19.7287 | -165.9229 | 82.9368 | 7.0632 | -166.6616 | 140.7857 | 0 | 25.305 | 0.2 | 0 | 3.76 | 29.065 | 4.5 | 5.4083 | 1.0784 | 0.025701
2015-07-26 01:00 | 105.3267 | 48.56 | 56.7667 | 396.4421 | 19.7197 | -150.9231 | 81.7675 | 8.2325 | -152.4679 | 133.5068 | 0 | 36.42 | 0.2 | 0 | 5.2663 | 41.6863 | 4.7 | 6.0027 | 1.076 | 0.03678
2015-07-26 02:00 | 135.4533 | 63.38 | 72.0733 | 409.3624 | 19.7108 | -135.9234 | 79.8595 | 10.1405 | -138.2982 | 123.2613 | 0 | 47.535 | 0.2 | 0 | 6.7727 | 54.3077 | 4.8 | 6.4971 | 1.074 | 0.047828
2015-07-26 03:00 | 165.58 | 78.2 | 87.38 | 398.3908 | 19.7018 | -120.9236 | 77.3302 | 12.6698 | -124.1275 | 111.3691 | 0 | 58.65 | 0.2 | 0 | 8.279 | 66.929 | 4.3 | 6.3915 | 1.0744 | 0.058967
2015-07-26 04:00 | 214.3833 | 93.7067 | 120.6767 | 446.8798 | 19.6929 | -105.9239 | 74.3332 | 15.6668 | -109.8949 | 98.5536 | 0 | 70.28 | 0.2 | 0 | 10.7192 | 80.9992 | 4.5 | 7.0312 | 1.0719 | 0.071193
2015-07-26 05:00 | 263.1867 | 109.2133 | 153.9733 | 474.1598 | 19.6839 | -90.9241 | 71.0509 | 18.9491 | -95.5063 | 85.1948 | 39.7194 | 81.91 | 0.2 | 0 | 13.1593 | 134.7887 | 4.2 | 8.4121 | 1.0664 | 0.11786
2015-07-26 06:00 | 311.99 | 124.72 | 187.27 | 493.2648 | 19.6749 | -75.9243 | 67.6877 | 22.3123 | -80.846 | 71.5011 | 156.5061 | 93.54 | 0.2 | 0 | 15.5995 | 265.6456 | 5.1 | 13.4014 | 1.0464 | 0.22794
2015-07-26 07:00 | 347.9333 | 161.7633 | 186.17 | 431.8829 | 19.6659 | -60.9246 | 64.4648 | 25.5352 | -65.7965 | 57.5948 | 231.4475 | 121.3225 | 0.2 | 0 | 17.3967 | 370.1667 | 5.1 | 16.6677 | 1.0333 | 0.31365
2015-07-26 08:00 | 383.8767 | 198.8067 | 185.07 | 389.2521 | 19.6569 | -45.9248 | 61.6113 | 28.3887 | -50.268 | 43.5548 | 282.0972 | 149.105 | 0.2 | 0 | 19.1938 | 450.3961 | 5.8 | 19.8749 | 1.0205 | 0.3769
2015-07-26 09:00 | 419.82 | 235.85 | 183.97 | 360.887 | 19.6479 | -30.925 | 59.3514 | 30.6486 | -34.2345 | 29.4424 | 314.2785 | 176.8875 | 0.2 | 0 | 20.991 | 512.157 | 5.7 | 21.7049 | 1.0132 | 0.4255
2015-07-26 10:00 | 423.8767 | 252.88 | 170.9967 | 321.6156 | 19.6389 | -15.9252 | 57.8809 | 32.1191 | -17.7655 | 15.3473 | 310.1465 | 189.66 | 0.2 | 0 | 21.1938 | 521.0003 | 6 | 22.2813 | 1.0109 | 0.43187
2015-07-26 11:00 | 427.9333 | 269.91 | 158.0233 | 292.8138 | 19.6298 | -0.92543 | 57.3387 | 32.6613 | -1.0354 | 2.8043 | 292.4632 | 202.4325 | 0.2 | 0 | 21.3967 | 516.2923 | 6.6 | 22.7341 | 1.0091 | 0.4272
2015-07-26 12:00 | 431.99 | 286.94 | 145.05 | 272.042 | 19.6208 | 14.0744 | 57.7788 | 32.2212 | 15.7094 | 13.6192 | 264.3927 | 215.205 | 0.2 | 0 | 21.5995 | 501.1972 | 6.7 | 22.3624 | 1.0106 | 0.41532
2015-07-26 13:00 | 403.39 | 255.7333 | 147.6567 | 288.0179 | 19.6118 | 29.0742 | 59.1585 | 30.8415 | 32.2181 | 27.6989 | 255.0117 | 191.8 | 0.2 | 0 | 20.1695 | 466.9812 | 6.7 | 21.2932 | 1.0148 | 0.3886
2015-07-26 14:00 | 374.79 | 224.5267 | 150.2633 | 313.3853 | 19.6027 | 44.074 | 61.3483 | 28.6517 | 48.3058 | 41.8196 | 233.5496 | 168.395 | 0.2 | 0 | 18.7395 | 420.6841 | 6.6 | 19.7464 | 1.021 | 0.35221
2015-07-26 15:00 | 346.19 | 193.32 | 152.87 | 350.7014 | 19.5936 | 59.0738 | 64.1576 | 25.8424 | 63.8907 | 55.8778 | 196.7295 | 144.99 | 0.2 | 0 | 17.3095 | 359.029 | 6.8 | 18.0197 | 1.0279 | 0.30262
2015-07-26 16:00 | 282.6367 | 162.94 | 119.6967 | 311.0094 | 19.5845 | 74.0736 | 67.3646 | 22.6354 | 78.9897 | 69.8126 | 107.3266 | 122.205 | 0.2 | 0 | 14.1318 | 243.6634 | 6.3 | 13.9145 | 1.0443 | 0.20866
2015-07-26 17:00 | 219.0833 | 132.56 | 86.5233 | 262.3087 | 19.5755 | 89.0734 | 70.7401 | 19.2599 | 93.6875 | 83.5494 | 29.4693 | 99.42 | 0.2 | 0 | 10.9542 | 139.8435 | 5.8 | 10.1701 | 1.0593 | 0.12147
2015-07-26 18:00 | 155.53 | 102.18 | 53.35 | 194.2822 | 19.5664 | 104.0732 | 74.0618 | 15.9382 | 108.1006 | 96.974 | 0 | 76.635 | 0.2 | 0 | 7.7765 | 84.4115 | 5.6 | 8.2379 | 1.067 | 0.073858
2015-07-26 19:00 | 123.7233 | 84.2233 | 39.5 | 177.239 | 19.5573 | 119.073 | 77.1228 | 12.8772 | 122.3468 | 109.8936 | 0 | 63.1675 | 0.2 | 0 | 6.1862 | 69.3537 | 5.1 | 7.2673 | 1.0709 | 0.060904
2015-07-26 20:00 | 91.9167 | 66.2667 | 25.65 | 143.9744 | 19.5481 | 134.0729 | 79.7376 | 10.2624 | 136.5239 | 121.9588 | 0 | 49.7 | 0.2 | 0 | 4.5958 | 54.2958 | 5.8 | 7.4967 | 1.07 | 0.04764
2015-07-26 21:00 | 60.11 | 48.31 | 11.8 | 82.2188 | 19.539 | 149.0727 | 81.7484 | 8.2516 | 150.6975 | 132.5037 | 0 | 36.2325 | 0.2 | 0 | 3.0055 | 39.238 | 5 | 6.2262 | 1.0751 | 0.034591
2015-07-26 22:00 | 53.6267 | 42.6533 | 10.9733 | 90.4622 | 19.5299 | 164.0725 | 83.0327 | 6.9673 | 164.8969 | 140.2898 | 0 | 31.99 | 0.2 | 0 | 2.6813 | 34.6713 | 4.3 | 5.3835 | 1.0785 | 0.030661
2015-07-26 23:00 | 47.1433 | 36.9967 | 10.1467 | 89.7834 | 19.5207 | 179.0724 | 83.511 | 6.489 | 179.12 | 143.5012 | 0 | 27.7475 | 0.2 | 0 | 2.3572 | 30.1047 | 4.6 | 5.5408 | 1.0778 | 0.026607
2015-07-27 | 40.66 | 31.34 | 9.32 | 78.1845 | 19.5116 | -165.9278 | 83.1538 | 6.8462 | -166.6542 | 140.9892 | 0 | 23.505 | 0.2 | 0 | 2.033 | 25.538 | 4.9 | 5.6981 | 1.0772 | 0.022558
2015-07-27 01:00 | 53.2833 | 46.9233 | 6.36 | 45.6077 | 19.5024 | -150.9279 | 81.984 | 8.016 | -152.4482 | 133.6764 | 0 | 35.1925 | 0.2 | 0 | 2.6642 | 37.8567 | 4.5 | 5.683 | 1.0773 | 0.033441
2015-07-27 02:00 | 65.9067 | 62.5067 | 3.4 | 19.7262 | 19.4933 | -135.9281 | 80.075 | 9.925 | -138.2675 | 123.3964 | 0 | 46.88 | 0.2 | 0 | 3.2953 | 50.1753 | 5.1 | 6.668 | 1.0733 | 0.044161
2015-07-27 03:00 | 78.53 | 78.09 | 0.44 | 2.04 | 19.4841 | -120.9282 | 77.5445 | 12.4555 | -124.0877 | 111.4758 | 0 | 58.5675 | 0.2 | 0 | 3.9265 | 62.494 | 4.9 | 6.8529 | 1.0726 | 0.054965
2015-07-27 04:00 | 83.16 | 81.86 | 1.3 | 4.8789 | 19.4749 | -105.9284 | 74.5465 | 15.4535 | -109.8483 | 98.6376 | 0 | 61.395 | 0.2 | 0 | 4.158 | 65.553 | 5.1 | 7.1485 | 1.0714 | 0.057592
2015-07-27 05:00 | 87.79 | 85.63 | 2.16 | 6.7245 | 19.4657 | -90.9285 | 71.2638 | 18.7362 | -95.4557 | 85.2602 | 0.55566 | 64.2225 | 0.2 | 0 | 4.3895 | 69.1677 | 5.7 | 7.8615 | 1.0686 | 0.060606
2015-07-27 06:00 | 92.42 | 89.4 | 3.02 | 8.0275 | 19.4565 | -75.9286 | 67.9009 | 22.0991 | -80.7945 | 71.5505 | 2.5404 | 67.05 | 0.2 | 0 | 4.621 | 74.2114 | 5.1 | 7.4191 | 1.0703 | 0.065133
2015-07-27 07:00 | 94.8233 | 92.81 | 2.0133 | 4.7075 | 19.4473 | -60.9288 | 64.679 | 25.321 | -65.748 | 57.6296 | 2.5203 | 69.6075 | 0.2 | 0 | 4.7412 | 76.869 | 5.5 | 7.9022 | 1.0684 | 0.067343
2015-07-27 08:00 | 97.2267 | 96.22 | 1.0067 | 2.1322 | 19.438 | -45.9289 | 61.8272 | 28.1728 | -50.2266 | 43.5753 | 1.5447 | 72.165 | 0.2 | 0 | 4.8613 | 78.571 | 5.8 | 8.2553 | 1.067 | 0.068744
2015-07-27 09:00 | 99.63 | 99.63 | 0 | 0 | 19.4288 | -30.929 | 59.569 | 30.431 | -34.2046 | 29.4464 | 0 | 74.7225 | 0.2 | 0 | 4.9815 | 79.704 | 6.7 | 9.1907 | 1.0632 | 0.06949
2015-07-27 10:00 | 104.9967 | 104.0733 | 0.92333 | 1.7473 | 19.4195 | -15.9291 | 58.1 | 31.9 | -17.7509 | 15.3241 | 1.6852 | 78.055 | 0.2 | 0 | 5.2498 | 84.99 | 6.5 | 9.1559 | 1.0634 | 0.074109
2015-07-27 11:00 | 110.3633 | 108.5167 | 1.8467 | 3.4424 | 19.4103 | -0.92922 | 57.5583 | 32.4417 | -1.0385 | 2.5982 | 3.4389 | 81.3875 | 0.2 | 0 | 5.5182 | 90.3446 | 6 | 8.8233 | 1.0647 | 0.078876
2015-07-27 12:00 | 115.73 | 112.96 | 2.77 | 5.2269 | 19.401 | 14.0707 | 57.9979 | 32.0021 | 15.6885 | 13.5833 | 5.0807 | 84.72 | 0.2 | 0 | 5.7865 | 95.5872 | 6.9 | 9.8871 | 1.0605 | 0.08312
2015-07-27 13:00 | 105.02 | 103.1733 | 1.8467 | 3.6252 | 19.3918 | 29.0706 | 59.3763 | 30.6237 | 32.1816 | 27.6937 | 3.2099 | 77.38 | 0.2 | 0 | 5.251 | 85.8409 | 5.6 | 8.2825 | 1.0669 | 0.075096
2015-07-27 14:00 | 94.31 | 93.3867 | 0.92333 | 1.9391 | 19.3825 | 44.0705 | 61.5644 | 28.4356 | 48.2573 | 41.8315 | 1.4448 | 70.04 | 0.2 | 0 | 4.7155 | 76.2003 | 6.3 | 8.6813 | 1.0653 | 0.066563
2015-07-27 15:00 | 83.6 | 83.6 | 0 | 0 | 19.3732 | 59.0704 | 64.3722 | 25.6278 | 63.8347 | 55.9042 | 0 | 62.7 | 0.2 | 0 | 4.18 | 66.88 | 6.2 | 8.29 | 1.0668 | 0.058507
2015-07-27 16:00 | 57.0667 | 57.0667 | 0 | 0 | 19.3639 | 74.0703 | 67.5784 | 22.4216 | 78.9303 | 69.8537 | 0 | 42.8 | 0.2 | 0 | 2.8533 | 45.6533 | 6.2 | 7.6267 | 1.0695 | 0.040037
2015-07-27 17:00 | 30.5333 | 30.5333 | 0 | 0 | 19.3546 | 89.0702 | 70.9539 | 19.0461 | 93.6286 | 83.6066 | 0 | 22.9 | 0.2 | 0 | 1.5267 | 24.4267 | 5.6 | 6.3633 | 1.0745 | 0.021523
2015-07-27 18:00 | 4 | 4 | 0 | 0 | 19.3452 | 104.0702 | 74.2765 | 15.7235 | 108.0454 | 97.0499 | 0 | 3 | 0.2 | 0 | 0.2 | 3.2 | 6.5 | 6.6 | 1.0736 | 0.0028171
2015-07-27 19:00 | 3.5467 | 3.5467 | 0 | 0 | 19.3359 | 119.0701 | 77.339 | 12.661 | 122.2981 | 109.9924 | 0 | 2.66 | 0.2 | 0 | 0.17733 | 2.8373 | 5.5 | 5.5887 | 1.0776 | 0.0025073
2015-07-27 20:00 | 3.0933 | 3.0933 | 0 | 0 | 19.3266 | 134.07 | 79.9557 | 10.0443 | 136.4842 | 122.0864 | 0 | 2.32 | 0.2 | 0 | 0.15467 | 2.4747 | 5.8 | 5.8773 | 1.0765 | 0.0021844
2015-07-27 21:00 | 2.64 | 2.64 | 0 | 0 | 19.3172 | 149.0699 | 81.9684 | 8.0316 | 150.6687 | 132.6671 | 0 | 1.98 | 0.2 | 0 | 0.132 | 2.112 | 5.8 | 5.866 | 1.0765 | 0.0018644
2015-07-27 22:00 | 2.4467 | 2.4467 | 0 | 0 | 19.3079 | 164.0699 | 83.2541 | 6.7459 | 164.8805 | 140.4911 | 0 | 1.835 | 0.2 | 0 | 0.12233 | 1.9573 | 5.3 | 5.3612 | 1.0786 | 0.0017311
2015-07-27 23:00 | 2.2533 | 2.2533 | 0 | 0 | 19.2985 | 179.0698 | 83.7332 | 6.2668 | 179.1168 | 143.7233 | 0 | 1.69 | 0.2 | 0 | 0.11267 | 1.8027 | 5.8 | 5.8563 | 1.0766 | 0.0015914
2015-07-28 | 2.06 | 2.06 | 0 | 0 | 19.2891 | -165.9302 | 83.376 | 6.624 | -166.6441 | 141.1967 | 0 | 1.545 | 0.2 | 0 | 0.103 | 1.648 | 5.6 | 5.6515 | 1.0774 | 0.0014559
2015-07-28 01:00 | 3.1033 | 2.85 | 0.25333 | 1.868 | 19.2797 | -150.9303 | 82.2055 | 7.7945 | -152.4255 | 133.8483 | 0 | 2.1375 | 0.2 | 0 | 0.15517 | 2.2927 | 3.9 | 3.9716 | 1.0841 | 0.0020381
2015-07-28 02:00 | 4.1467 | 3.64 | 0.50667 | 3.0057 | 19.2703 | -135.9303 | 80.2954 | 9.7046 | -138.2336 | 123.5326 | 0 | 2.73 | 0.2 | 0 | 0.20733 | 2.9373 | 4.8 | 4.8918 | 1.0804 | 0.0026023
2015-07-28 03:00 | 5.19 | 4.43 | 0.76 | 3.5858 | 19.2609 | -120.9303 | 77.7636 | 12.2364 | -124.0444 | 111.5827 | 0 | 3.3225 | 0.2 | 0 | 0.2595 | 3.582 | 5 | 5.1119 | 1.0796 | 0.0031709
2015-07-28 04:00 | 6.29 | 5.7833 | 0.50667 | 1.9281 | 19.2515 | -105.9304 | 74.7646 | 15.2354 | -109.7981 | 98.7212 | 0 | 4.3375 | 0.2 | 0 | 0.3145 | 4.652 | 4.2 | 4.3454 | 1.0826 | 0.0041298
2015-07-28 05:00 | 7.39 | 7.1367 | 0.25333 | 0.79762 | 19.2421 | -90.9304 | 71.4813 | 18.5187 | -95.4013 | 85.3248 | 0.065012 | 5.3525 | 0.2 | 0 | 0.3695 | 5.787 | 3.7 | 3.8808 | 1.0845 | 0.0051462
2015-07-28 06:00 | 8.49 | 8.49 | 0 | 0 | 19.2327 | -75.9304 | 68.1188 | 21.8812 | -80.7394 | 71.5989 | 0 | 6.3675 | 0.2 | 0 | 0.4245 | 6.792 | 4 | 4.2123 | 1.0832 | 0.0060325
2015-07-28 07:00 | 24.2933 | 24.2933 | 0 | 0 | 19.2232 | -60.9304 | 64.898 | 25.102 | -65.6957 | 57.6634 | 0 | 18.22 | 0.2 | 0 | 1.2147 | 19.4347 | 3.9 | 4.5073 | 1.082 | 0.017243
2015-07-28 08:00 | 40.0967 | 40.0967 | 0 | 0 | 19.2138 | -45.9305 | 62.0479 | 27.9521 | -50.1816 | 43.5947 | 0 | 30.0725 | 0.2 | 0 | 2.0048 | 32.0773 | 4.6 | 5.6024 | 1.0776 | 0.028344
2015-07-28 09:00 | 55.9 | 55.9 | 0 | 0 | 19.2043 | -30.9305 | 59.7916 | 30.2084 | -34.1712 | 29.4497 | 0 | 41.925 | 0.2 | 0 | 2.795 | 44.72 | 4.4 | 5.7975 | 1.0768 | 0.039487
2015-07-28 10:00 | 46.69 | 46.69 | 0 | 0 | 19.1949 | -15.9305 | 58.3241 | 31.6759 | -17.7332 | 15.3009 | 0 | 35.0175 | 0.2 | 0 | 2.3345 | 37.352 | 4.3 | 5.4672 | 1.0781 | 0.033022
2015-07-28 11:00 | 37.48 | 37.48 | 0 | 0 | 19.1854 | -0.93047 | 57.7832 | 32.2168 | -1.0387 | 2.3885 | 0 | 28.11 | 0.2 | 0 | 1.874 | 29.984 | 4.1 | 5.037 | 1.0799 | 0.02655
2015-07-28 12:00 | 28.27 | 28.27 | 0 | 0 | 19.1759 | 14.0695 | 58.2225 | 31.7775 | 15.6701 | 13.5524 | 0 | 21.2025 | 0.2 | 0 | 1.4135 | 22.616 | 4.5 | 5.2068 | 1.0792 | 0.020013
2015-07-28 13:00 | 56.8667 | 32.1767 | 24.69 | 48.7907 | 19.1664 | 29.0695 | 59.5997 | 30.4003 | 32.1472 | 27.6924 | 43.202 | 24.1325 | 0.2 | 0 | 2.8433 | 70.1778 | 4.2 | 6.3931 | 1.0744 | 0.061829
2015-07-28 14:00 | 85.4633 | 36.0833 | 49.38 | 104.4497 | 19.1569 | 44.0696 | 61.7862 | 28.2138 | 48.2107 | 41.8471 | 77.8076 | 27.0625 | 0.2 | 0 | 4.2732 | 109.1432 | 4.3 | 7.7107 | 1.0692 | 0.095687
2015-07-28 15:00 | 114.06 | 39.99 | 74.07 | 172.6362 | 19.1474 | 59.0696 | 64.5926 | 25.4074 | 63.7802 | 55.9343 | 96.7009 | 29.9925 | 0.2 | 0 | 5.703 | 132.3964 | 5.1 | 9.2374 | 1.0631 | 0.11541
2015-07-28 16:00 | 86.9233 | 33.46 | 53.4633 | 141.4847 | 19.1379 | 74.0696 | 67.798 | 22.202 | 78.8723 | 69.8985 | 48.626 | 25.095 | 0.2 | 0 | 4.3462 | 78.0672 | 5.3 | 7.7396 | 1.069 | 0.068435
2015-07-28 17:00 | 59.7867 | 26.93 | 32.8567 | 101.817 | 19.1283 | 89.0696 | 71.1735 | 18.8265 | 93.571 | 83.6676 | 11.2301 | 20.1975 | 0.2 | 0 | 2.9893 | 34.4169 | 5.7 | 6.7755 | 1.0729 | 0.030279
2015-07-28 18:00 | 32.65 | 20.4 | 12.25 | 45.8303 | 19.1188 | 104.0696 | 74.4969 | 15.5031 | 107.9915 | 97.1298 | 0 | 15.3 | 0.2 | 0 | 1.6325 | 16.9325 | 5.5 | 6.0291 | 1.0759 | 0.014938
2015-07-28 19:00 | 34.3833 | 18.77 | 15.6133 | 72.4847 | 19.1092 | 119.0697 | 77.5609 | 12.4391 | 122.2508 | 110.0955 | 0 | 14.0775 | 0.2 | 0 | 1.7192 | 15.7967 | 5.8 | 6.2936 | 1.0748 | 0.013923
2015-07-28 20:00 | 36.1167 | 17.14 | 18.9767 | 111.2591 | 19.0997 | 134.0697 | 80.1795 | 9.8205 | 136.446 | 122.2187 | 0 | 12.855 | 0.2 | 0 | 1.8058 | 14.6608 | 6.1 | 6.5582 | 1.0738 | 0.012909
2015-07-28 21:00 | 37.85 | 15.51 | 22.34 | 164.4822 | 19.0901 | 149.0698 | 82.194 | 7.806 | 150.6417 | 132.8357 | 0 | 11.6325 | 0.2 | 0 | 1.8925 | 13.525 | 6.4 | 6.8227 | 1.0727 | 0.011897
2015-07-28 22:00 | 41.3433 | 17.0633 | 24.28 | 213.8597 | 19.0805 | 164.0698 | 83.481 | 6.519 | 164.8662 | 140.6981 | 0 | 12.7975 | 0.2 | 0 | 2.0672 | 14.8647 | 5.7 | 6.1645 | 1.0753 | 0.013107
2015-07-28 23:00 | 44.8367 | 18.6167 | 26.22 | 249.2176 | 19.0709 | 179.0699 | 83.9608 | 6.0392 | 179.116 | 143.9508 | 0 | 13.9625 | 0.2 | 0 | 2.2418 | 16.2043 | 4.5 | 5.0064 | 1.08 | 0.01435
2015-07-29 | 48.33 | 20.17 | 28.16 | 252.7618 | 19.0613 | -165.9301 | 83.6034 | 6.3966 | -166.6314 | 141.4081 | 0 | 15.1275 | 0.2 | 0 | 2.4165 | 17.544 | 5.7 | 6.2483 | 1.075 | 0.015465
2015-07-29 01:00 | 43.6667 | 24.8833 | 18.7833 | 142.6211 | 19.0517 | -150.93 | 82.4321 | 7.5679 | -152.3998 | 134.0223 | 0 | 18.6625 | 0.2 | 0 | 2.1833 | 20.8458 | 5.9 | 6.5514 | 1.0738 | 0.018355
2015-07-29 02:00 | 39.0033 | 29.5967 | 9.4067 | 57.1165 | 19.0421 | -135.93 | 80.5206 | 9.4794 | -138.1964 | 123.6697 | 0 | 22.1975 | 0.2 | 0 | 1.9502 | 24.1477 | 6.1 | 6.8546 | 1.0726 | 0.021238
2015-07-29 03:00 | 34.34 | 34.31 | 0.03 | 0.14414 | 19.0325 | -120.9299 | 77.9874 | 12.0126 | -123.9978 | 111.6897 | 0 | 25.7325 | 0.2 | 0 | 1.717 | 27.4495 | 5.4 | 6.2578 | 1.075 | 0.024196
2015-07-29 04:00 | 48.5933 | 43.2567 | 5.3367 | 20.6022 | 19.0229 | -105.9298 | 74.9873 | 15.0127 | -109.7443 | 98.8044 | 0 | 32.4425 | 0.2 | 0 | 2.4297 | 34.8722 | 6.3 | 7.3898 | 1.0704 | 0.030609
2015-07-29 05:00 | 62.8467 | 52.2033 | 10.6433 | 33.9031 | 19.0132 | -90.9297 | 71.7035 | 18.2965 | -95.3434 | 85.3887 | 2.7257 | 39.1525 | 0.2 | 0 | 3.1423 | 45.0205 | 7 | 8.4069 | 1.0664 | 0.039367
2015-07-29 06:00 | 77.1 | 61.15 | 15.95 | 43.2159 | 19.0036 | -75.9296 | 68.3413 | 21.6587 | -80.6805 | 71.6464 | 13.6079 | 45.8625 | 0.2 | 0 | 3.855 | 63.3254 | 6.9 | 8.8789 | 1.0645 | 0.055275
2015-07-29 07:00 | 89.7267 | 78.47 | 11.2567 | 26.7574 | 18.9939 | -60.9296 | 65.1217 | 24.8783 | -65.6398 | 57.6961 | 14.2994 | 58.8525 | 0.2 | 0 | 4.4863 | 77.6383 | 6 | 8.4262 | 1.0663 | 0.067884
2015-07-29 08:00 | 102.3533 | 95.79 | 6.5633 | 14.107 | 18.9842 | -45.9295 | 62.2734 | 27.7266 | -50.133 | 43.6131 | 10.2137 | 71.8425 | 0.2 | 0 | 5.1177 | 87.1738 | 6.5 | 9.2242 | 1.0631 | 0.075993
2015-07-29 09:00 | 114.98 | 113.11 | 1.87 | 3.7422 | 18.9746 | -30.9294 | 60.0192 | 29.9808 | -34.1345 | 29.4521 | 3.2586 | 84.8325 | 0.2 | 0 | 5.749 | 93.8401 | 6.6 | 9.5325 | 1.0619 | 0.08171
2015-07-29 10:00 | 117.8533 | 116.0033 | 1.85 | 3.5461 | 18.9649 | -15.9293 | 58.5534 | 31.4466 | -17.7123 | 15.2781 | 3.4208 | 87.0025 | 0.2 | 0 | 5.8927 | 96.3159 | 7.4 | 10.4099 | 1.0584 | 0.083588
2015-07-29 11:00 | 120.7267 | 118.8967 | 1.83 | 3.4546 | 18.9552 | -0.92916 | 58.0134 | 31.9866 | -1.0361 | 2.1761 | 3.4522 | 89.1725 | 0.2 | 0 | 6.0363 | 98.661 | 7.7 | 10.7832 | 1.0569 | 0.085503
2015-07-29 12:00 | 123.6 | 121.79 | 1.81 | 3.4594 | 18.9455 | 14.071 | 58.4525 | 31.5475 | 15.6543 | 13.527 | 3.3635 | 91.3425 | 0.2 | 0 | 6.18 | 100.886 | 7.7 | 10.8527 | 1.0566 | 0.087408
2015-07-29 13:00 | 112.2267 | 109.8433 | 2.3833 | 4.7421 | 18.9358 | 29.0711 | 59.8286 | 30.1714 | 32.1149 | 27.6953 | 4.1988 | 82.3825 | 0.2 | 0 | 5.6113 | 92.1927 | 7.5 | 10.381 | 1.0585 | 0.080019
2015-07-29 14:00 | 100.8533 | 97.8967 | 2.9567 | 6.3007 | 18.926 | 44.0712 | 62.0136 | 27.9864 | 48.1659 | 41.8665 | 4.6921 | 73.4225 | 0.2 | 0 | 5.0427 | 83.1573 | 6.6 | 9.1987 | 1.0632 | 0.072499
2015-07-29 15:00 | 89.48 | 85.95 | 3.53 | 8.2964 | 18.9163 | 59.0713 | 64.8186 | 25.1814 | 63.7273 | 55.9682 | 4.6431 | 64.4625 | 0.2 | 0 | 4.474 | 73.5796 | 6.4 | 8.6994 | 1.0652 | 0.064269
2015-07-29 16:00 | 73.63 | 64.4667 | 9.1633 | 24.4858 | 18.9066 | 74.0714 | 68.0232 | 21.9768 | 78.8158 | 69.9471 | 8.3959 | 48.35 | 0.2 | 0 | 3.6815 | 60.4274 | 7.8 | 9.6884 | 1.0612 | 0.052585
2015-07-29 17:00 | 57.78 | 42.9833 | 14.7967 | 46.3876 | 18.8968 | 89.0716 | 71.3988 | 18.6012 | 93.5147 | 83.7324 | 5.0642 | 32.2375 | 0.2 | 0 | 2.889 | 40.1907 | 6.7 | 7.956 | 1.0682 | 0.035203
2015-07-29 18:00 | 41.93 | 21.5 | 20.43 | 77.5375 | 18.8871 | 104.0717 | 74.723 | 15.277 | 107.939 | 97.2137 | 0 | 16.125 | 0.2 | 0 | 2.0965 | 18.2215 | 6.1 | 6.6694 | 1.0733 | 0.016037
2015-07-29 19:00 | 40.85 | 19.64 | 21.21 | 100.2736 | 18.8773 | 119.0719 | 77.7885 | 12.2115 | 122.205 | 110.2028 | 0 | 14.73 | 0.2 | 0 | 2.0425 | 16.7725 | 6.6 | 7.1241 | 1.0715 | 0.014737
2015-07-29 20:00 | 39.77 | 17.78 | 21.99 | 131.9792 | 18.8675 | 134.072 | 80.4088 | 9.5912 | 136.4094 | 122.3556 | 0 | 13.335 | 0.2 | 0 | 1.9885 | 15.3235 | 6.3 | 6.7789 | 1.0729 | 0.013481
2015-07-29 21:00 | 38.69 | 15.92 | 22.77 | 172.7302 | 18.8577 | 149.0722 | 82.425 | 7.575 | 150.6165 | 133.0094 | 0 | 11.94 | 0.2 | 0 | 1.9345 | 13.8745 | 6.7 | 7.1336 | 1.0715 | 0.01219
2015-07-29 22:00 | 42.3967 | 18.85 | 23.5467 | 215.031 | 18.8479 | 164.0723 | 83.7133 | 6.2867 | 164.8539 | 140.9106 | 0 | 14.1375 | 0.2 | 0 | 2.1198 | 16.2573 | 6.4 | 6.908 | 1.0724 | 0.014296
2015-07-29 23:00 | 46.1033 | 21.78 | 24.3233 | 240.426 | 18.8381 | 179.0725 | 84.1936 | 5.8064 | 179.1176 | 144.1836 | 0 | 16.335 | 0.2 | 0 | 2.3052 | 18.6402 | 7.3 | 7.8825 | 1.0685 | 0.016331
2015-07-30 | 49.81 | 24.71 | 25.1 | 233.7595 | 18.8283 | -165.9274 | 83.836 | 6.164 | -166.6158 | 141.6233 | 0 | 18.5325 | 0.2 | 0 | 2.4905 | 21.023 | 7.1 | 7.757 | 1.069 | 0.018428
2015-07-30 01:00 | 57.48 | 40.47 | 17.01 | 133.2086 | 18.8185 | -150.9272 | 82.6636 | 7.3364 | -152.3712 | 134.1983 | 0 | 30.3525 | 0.2 | 0 | 2.874 | 33.2265 | 5.9 | 6.9383 | 1.0722 | 0.029214
2015-07-30 02:00 | 65.15 | 56.23 | 8.92 | 55.4964 | 18.8087 | -135.927 | 80.7507 | 9.2493 | -138.156 | 123.8075 | 0 | 42.1725 | 0.2 | 0 | 3.2575 | 45.43 | 5.9 | 7.3197 | 1.0707 | 0.039887
2015-07-30 03:00 | 72.82 | 71.99 | 0.83 | 4.0642 | 18.7988 | -120.9268 | 78.2159 | 11.7841 | -123.9477 | 111.7967 | 0 | 53.9925 | 0.2 | 0 | 3.641 | 57.6335 | 6.1 | 7.901 | 1.0684 | 0.050492
2015-07-30 04:00 | 116.0533 | 97.3867 | 18.6667 | 73.1451 | 18.789 | -105.9267 | 75.2145 | 14.7855 | -109.687 | 98.8871 | 0 | 73.04 | 0.2 | 0 | 5.8027 | 78.8427 | 7.7 | 10.1638 | 1.0593 | 0.068488
2015-07-30 05:00 | 159.2867 | 122.7833 | 36.5033 | 117.6861 | 18.7791 | -90.9265 | 71.9302 | 18.0698 | -95.2817 | 85.4517 | 9.3324 | 92.0875 | 0.2 | 0 | 7.9643 | 109.3842 | 7.5 | 10.9183 | 1.0563 | 0.094747
2015-07-30 06:00 | 202.52 | 148.18 | 54.34 | 148.717 | 18.7693 | -75.9263 | 68.5683 | 21.4317 | -80.6179 | 71.6928 | 46.7137 | 111.135 | 0.2 | 0 | 10.126 | 167.9747 | 6.9 | 12.1492 | 1.0514 | 0.14482
2015-07-30 07:00 | 287.2567 | 148.7133 | 138.5433 | 332.1777 | 18.7594 | -60.9261 | 65.3499 | 24.6501 | -65.5802 | 57.7278 | 177.3638 | 111.535 | 0.2 | 0 | 14.3628 | 303.2616 | 6.8 | 16.2769 | 1.0349 | 0.25735
2015-07-30 08:00 | 371.9933 | 149.2467 | 222.7467 | 482.4553 | 18.7495 | -45.9259 | 62.5035 | 27.4965 | -50.0808 | 43.6305 | 349.2035 | 111.935 | 0.2 | 0 | 18.5997 | 479.7382 | 8.3 | 23.2918 | 1.0068 | 0.39607
2015-07-30 09:00 | 456.73 | 149.78 | 306.95 | 618.6099 | 18.7396 | -30.9257 | 60.2515 | 29.7485 | -34.0943 | 29.4538 | 538.6559 | 112.335 | 0.2 | 0 | 22.8365 | 673.8274 | 7.8 | 28.8571 | 0.98457 | 0.54401
2015-07-30 10:00 | 473.86 | 117.3467 | 356.5133 | 687.9704 | 18.7297 | -15.9255 | 58.7877 | 31.2123 | -17.6881 | 15.2558 | 663.7267 | 88.01 | 0.2 | 0 | 23.693 | 775.4297 | 9.2 | 33.4322 | 0.96627 | 0.61441
2015-07-30 11:00 | 490.99 | 84.9133 | 406.0767 | 771.6678 | 18.7198 | -0.92526 | 58.2487 | 31.7513 | -1.0306 | 1.9619 | 771.2154 | 63.685 | 0.2 | 0 | 24.5495 | 859.4499 | 12.3 | 39.1578 | 0.94337 | 0.66484
2015-07-30 12:00 | 508.12 | 52.48 | 455.64 | 876.7358 | 18.7099 | 14.075 | 58.6878 | 31.3122 | 15.641 | 13.5074 | 852.485 | 39.36 | 0.2 | 0 | 25.406 | 917.251 | 11.3 | 39.9641 | 0.94014 | 0.70713
2015-07-30 13:00 | 457.5233 | 78.19 | 379.3333 | 760.1157 | 18.6999 | 29.0752 | 60.063 | 29.937 | 32.0849 | 27.7025 | 672.9859 | 58.6425 | 0.2 | 0 | 22.8762 | 754.5046 | 12.2 | 35.7783 | 0.95689 | 0.59202
2015-07-30 14:00 | 406.9267 | 103.9 | 303.0267 | 650.7374 | 18.69 | 44.0754 | 62.2466 | 27.7534 | 48.1229 | 41.8898 | 484.4287 | 77.925 | 0.2 | 0 | 20.3463 | 582.7001 | 11.8 | 30.0094 | 0.97996 | 0.46824
2015-07-30 15:00 | 356.33 | 129.61 | 226.72 | 537.4774 | 18.6801 | 59.0756 | 65.0503 | 24.9497 | 63.676 | 56.0059 | 300.5081 | 97.2075 | 0.2 | 0 | 17.8165 | 415.5321 | 12.5 | 25.4854 | 0.99806 | 0.34007
2015-07-30 16:00 | 306.0833 | 109.2833 | 196.8 | 531.1881 | 18.6701 | 74.0759 | 68.2541 | 21.7459 | 78.7606 | 69.9995 | 181.6814 | 81.9625 | 0.2 | 0 | 15.3042 | 278.9481 | 11.4 | 20.1171 | 1.0195 | 0.23321
2015-07-30 17:00 | 255.8367 | 88.9567 | 166.88 | 529.5143 | 18.6601 | 89.0761 | 71.6297 | 18.3703 | 93.4598 | 83.8012 | 57.1764 | 66.7175 | 0.2 | 0 | 12.7918 | 136.6857 | 11.7 | 15.9714 | 1.0361 | 0.11613
2015-07-30 18:00 | 205.59 | 68.63 | 136.96 | 527.6178 | 18.6502 | 104.0764 | 74.9547 | 15.0453 | 107.8878 | 97.3017 | 0 | 51.4725 | 0.2 | 0 | 10.2795 | 61.752 | 9.8 | 11.7297 | 1.0531 | 0.053324
2015-07-30 19:00 | 165.2167 | 56.0233 | 109.1933 | 526.1259 | 18.6402 | 119.0766 | 78.0216 | 11.9784 | 122.1607 | 110.3145 | 0 | 42.0175 | 0.2 | 0 | 8.2608 | 50.2783 | 10.4 | 11.9712 | 1.0521 | 0.043377
2015-07-30 20:00 | 124.8433 | 43.4167 | 81.4267 | 500.859 | 18.6302 | 134.0769 | 80.6437 | 9.3563 | 136.3745 | 122.4972 | 0 | 32.5625 | 0.2 | 0 | 6.2422 | 38.8047 | 10.1 | 11.3126 | 1.0547 | 0.033562
2015-07-30 21:00 | 84.47 | 30.81 | 53.66 | 420.0985 | 18.6202 | 149.0771 | 82.6615 | 7.3385 | 150.5932 | 133.1882 | 0 | 23.1075 | 0.2 | 0 | 4.2235 | 27.331 | 10.5 | 11.3541 | 1.0546 | 0.023635
2015-07-30 22:00 | 77.56 | 28.5433 | 49.0167 | 465.1383 | 18.6102 | 164.0774 | 83.9509 | 6.0491 | 164.8439 | 141.1287 | 0 | 21.4075 | 0.2 | 0 | 3.878 | 25.2855 | 8.8 | 9.5902 | 1.0616 | 0.022012
2015-07-30 23:00 | 70.65 | 26.2767 | 44.3733 | 457.2942 | 18.6002 | 179.0777 | 84.4316 | 5.5684 | 179.1217 | 144.4216 | 0 | 19.7075 | 0.2 | 0 | 3.5325 | 23.24 | 10.5 | 11.2263 | 1.0551 | 0.020107
2015-07-31 | 63.74 | 24.01 | 39.73 | 384.7847 | 18.5901 | -165.9221 | 84.0735 | 5.9265 | -166.5976 | 141.8421 | 0 | 18.0075 | 0.2 | 0 | 3.187 | 21.1945 | 12.3 | 12.9623 | 1.0482 | 0.018216
2015-07-31 01:00 | 84.4167 | 44.15 | 40.2667 | 325.7774 | 18.5801 | -150.9218 | 82.9 | 7.1 | -152.3395 | 134.3763 | 0 | 33.1125 | 0.2 | 0 | 4.2208 | 37.3333 | 12.2 | 13.3667 | 1.0465 | 0.032038
2015-07-31 02:00 | 105.0933 | 64.29 | 40.8033 | 260.4147 | 18.5701 | -135.9215 | 80.9854 | 9.0146 | -138.1124 | 123.946 | 0 | 48.2175 | 0.2 | 0 | 5.2547 | 53.4722 | 12.4 | 14.071 | 1.0437 | 0.045764
2015-07-31 03:00 | 125.77 | 84.43 | 41.34 | 206.4514 | 18.56 | -120.9212 | 78.449 | 11.551 | -123.8942 | 111.9036 | 0 | 63.3225 | 0.2 | 0 | 6.2885 | 69.611 | 9.4 | 11.5753 | 1.0537 | 0.060146
2015-07-31 04:00 | 170.77 | 107.3767 | 63.3933 | 252.2736 | 18.55 | -105.9209 | 75.4463 | 14.5537 | -109.6262 | 98.9692 | 0 | 80.5325 | 0.2 | 0 | 8.5385 | 89.071 | 10.7 | 13.4835 | 1.0461 | 0.076403
2015-07-31 05:00 | 215.77 | 130.3233 | 85.4467 | 278.9292 | 18.5399 | -90.9206 | 72.1613 | 17.8387 | -95.2165 | 85.5139 | 21.8169 | 97.7425 | 0.2 | 0 | 10.7885 | 130.3479 | 10 | 14.0734 | 1.0437 | 0.11156
2015-07-31 06:00 | 260.77 | 153.27 | 107.5 | 297.266 | 18.5298 | -75.9203 | 68.7997 | 21.2003 | -80.5517 | 71.7383 | 93.1508 | 114.9525 | 0.2 | 0 | 13.0385 | 221.1418 | 14 | 20.9107 | 1.0164 | 0.1843
2015-07-31 07:00 | 330.2433 | 130.0433 | 200.2 | 484.2992 | 18.5197 | -60.92 | 65.5826 | 24.4174 | -65.517 | 57.7583 | 258.3694 | 97.5325 | 0.2 | 0 | 16.5122 | 372.414 | 13.2 | 24.8379 | 1.0006 | 0.30558
2015-07-31 08:00 | 399.7167 | 106.8167 | 292.9 | 639.4426 | 18.5096 | -45.9197 | 62.7383 | 27.2617 | -50.025 | 43.6469 | 462.7054 | 80.1125 | 0.2 | 0 | 19.9858 | 562.8037 | 13.5 | 31.0876 | 0.97565 | 0.45026
2015-07-31 09:00 | 469.19 | 83.59 | 385.6 | 782.7928 | 18.4995 | -30.9194 | 60.4887 | 29.5113 | -34.0507 | 29.455 | 681.6107 | 62.6925 | 0.2 | 0 | 23.4595 | 767.7627 | 13.8 | 37.7926 | 0.94883 | 0.59735
2015-07-31 10:00 | 426.5 | 110.82 | 315.68 | 613.406 | 18.4894 | -15.9191 | 59.027 | 30.973 | -17.6608 | 15.2343 | 591.8506 | 83.115 | 0.2 | 0 | 21.325 | 696.2906 | 14.5 | 36.2591 | 0.95496 | 0.54524
2015-07-31 11:00 | 383.81 | 138.05 | 245.76 | 470.2112 | 18.4793 | -0.91875 | 58.4892 | 31.5108 | -1.0221 | 1.7475 | 469.9925 | 103.5375 | 0.2 | 0 | 19.1905 | 592.7205 | 15.1 | 33.6225 | 0.96551 | 0.46927
2015-07-31 12:00 | 341.12 | 165.28 | 175.84 | 340.704 | 18.4691 | 14.0816 | 58.9285 | 31.0715 | 15.6303 | 13.4939 | 331.2988 | 123.96 | 0.2 | 0 | 17.056 | 472.3148 | 15.3 | 30.0598 | 0.97976 | 0.37946
2015-07-31 13:00 | 282.3967 | 148.0533 | 134.3433 | 271.1731 | 18.459 | 29.0819 | 60.3029 | 29.6971 | 32.0571 | 27.7142 | 240.0636 | 111.04 | 0.2 | 0 | 14.1198 | 365.2235 | 12.6 | 24.0132 | 1.0039 | 0.30067
2015-07-31 14:00 | 223.6733 | 130.8267 | 92.8467 | 200.9759 | 18.4489 | 44.0823 | 62.4851 | 27.5149 | 48.0819 | 41.9171 | 149.5486 | 98.12 | 0.2 | 0 | 11.1837 | 258.8522 | 11.1 | 19.1891 | 1.0232 | 0.21719
2015-07-31 15:00 | 164.95 | 113.6 | 51.35 | 122.8278 | 18.4387 | 59.0826 | 65.2875 | 24.7125 | 63.6264 | 56.0474 | 68.6003 | 85.2 | 0.2 | 0 | 8.2475 | 162.0478 | 8.1 | 13.164 | 1.0473 | 0.13917
2015-07-31 16:00 | 126.5767 | 88.1433 | 38.4333 | 104.8219 | 18.4285 | 74.0829 | 68.4906 | 21.5094 | 78.707 | 70.0557 | 35.7554 | 66.1075 | 0.2 | 0 | 6.3288 | 108.1918 | 9 | 12.381 | 1.0505 | 0.093195
2015-07-31 17:00 | 88.2033 | 62.6867 | 25.5167 | 81.9847 | 18.4184 | 89.0833 | 71.8662 | 18.1338 | 93.4063 | 83.8738 | 8.7493 | 47.015 | 0.2 | 0 | 4.4102 | 60.1745 | 7.6 | 9.4805 | 1.0621 | 0.052406
2015-07-31 18:00 | 49.83 | 37.23 | 12.6 | 49.2996 | 18.4082 | 104.0836 | 75.192 | 14.808 | 107.8381 | 97.3937 | 0 | 27.9225 | 0.2 | 0 | 2.4915 | 30.414 | 8.1 | 9.0504 | 1.0638 | 0.026531
2015-07-31 19:00 | 37.8933 | 29.48 | 8.4133 | 41.3501 | 18.398 | 119.084 | 78.2603 | 11.7397 | 122.1178 | 110.4304 | 0 | 22.11 | 0.2 | 0 | 1.8947 | 24.0047 | 7.5 | 8.2501 | 1.067 | 0.021003
2015-07-31 20:00 | 25.9567 | 21.73 | 4.2267 | 26.6777 | 18.3878 | 134.0844 | 80.884 | 9.116 | 136.3413 | 122.6434 | 0 | 16.2975 | 0.2 | 0 | 1.2978 | 17.5953 | 8.8 | 9.3499 | 1.0626 | 0.015331
2015-07-31 21:00 | 14.02 | 13.98 | 0.04 | 0.32377 | 18.3776 | 149.0847 | 82.9033 | 7.0967 | 150.5719 | 133.3721 | 0 | 10.485 | 0.2 | 0 | 0.701 | 11.186 | 7.3 | 7.6496 | 1.0694 | 0.0098091
2015-07-31 22:00 | 23.7533 | 19.7533 | 4 | 39.5392 | 18.3674 | 164.0851 | 84.1937 | 5.8063 | 164.8361 | 141.3523 | 0 | 14.815 | 0.2 | 0 | 1.1877 | 16.0027 | 8 | 8.5001 | 1.066 | 0.013988
2015-07-31 23:00 | 33.4867 | 25.5267 | 7.96 | 85.7654 | 18.3571 | 179.0855 | 84.6746 | 5.3254 | 179.1283 | 144.6648 | 0 | 19.145 | 0.2 | 0 | 1.6743 | 20.8193 | 7.8 | 8.4506 | 1.0662 | 0.018202
2015-08-01 | 43.22 | 31.3 | 11.92 | 120.3526 | 18.3469 | -165.9141 | 84.316 | 5.684 | -166.5765 | 142.0645 | 0 | 23.475 | 0.2 | 0 | 2.161 | 25.636 | 7.1 | 7.9011 | 1.0684 | 0.022459
2015-08-01 01:00 | 76.1867 | 38.3133 | 37.8733 | 317.1324 | 18.3366 | -150.9137 | 83.1411 | 6.8589 | -152.3047 | 134.5561 | 0 | 28.735 | 0.2 | 0 | 3.8093 | 32.5443 | 6.9 | 7.917 | 1.0683 | 0.02851
2015-08-01 02:00 | 109.1533 | 45.3267 | 63.8267 | 418.3746 | 18.3264 | -135.9133 | 81.2248 | 8.7752 | -138.0655 | 124.0851 | 0 | 33.995 | 0.2 | 0 | 5.4577 | 39.4527 | 7.9 | 9.1329 | 1.0635 | 0.034404
2015-08-01 03:00 | 142.12 | 52.34 | 89.78 | 457.6475 | 18.3161 | -120.9129 | 78.6865 | 11.3135 | -123.8372 | 112.0104 | 0 | 39.255 | 0.2 | 0 | 7.106 | 46.361 | 8 | 9.4488 | 1.0622 | 0.040381
2015-08-01 04:00 | 195.7433 | 60.21 | 135.5333 | 548.0588 | 18.3059 | -105.9125 | 75.6824 | 14.3176 | -109.5617 | 99.0508 | 0 | 45.1575 | 0.2 | 0 | 9.7872 | 54.9447 | 8.1 | 9.817 | 1.0607 | 0.047791
2015-08-01 05:00 | 249.3667 | 68.08 | 181.2867 | 599.4459 | 18.2956 | -90.9121 | 72.3968 | 17.6032 | -95.1475 | 85.5752 | 46.2472 | 51.06 | 0.2 | 0 | 12.4683 | 109.7755 | 8.2 | 11.6305 | 1.0535 | 0.09483
2015-08-01 06:00 | 302.99 | 75.95 | 227.04 | 634.5637 | 18.2853 | -75.9117 | 69.0355 | 20.9645 | -80.4817 | 71.7827 | 198.3788 | 56.9625 | 0.2 | 0 | 15.1495 | 270.4908 | 8.2 | 16.6528 | 1.0334 | 0.22921
2015-08-01 07:00 | 363.4033 | 66.51 | 296.8933 | 724.8222 | 18.275 | -60.9113 | 65.8198 | 24.1802 | -65.45 | 57.7878 | 386.3707 | 49.8825 | 0.2 | 0 | 18.1702 | 454.4233 | 8.5 | 22.7007 | 1.0092 | 0.37605
2015-08-01 08:00 | 423.8167 | 57.07 | 366.7467 | 807.2106 | 18.2647 | -45.9109 | 62.9776 | 27.0224 | -49.9657 | 43.6623 | 583.9532 | 42.8025 | 0.2 | 0 | 21.1908 | 647.9466 | 8.3 | 28.5483 | 0.98581 | 0.52378
2015-08-01 09:00 | 484.23 | 47.63 | 436.6 | 892.993 | 18.2544 | -30.9105 | 60.7305 | 29.2695 | -34.0036 | 29.4556 | 777.5619 | 35.7225 | 0.2 | 0 | 24.2115 | 837.4959 | 9.3 | 35.4717 | 0.95811 | 0.65798
2015-08-01 10:00 | 489.9233 | 51.2467 | 438.6767 | 858.5053 | 18.244 | -15.91 | 59.2711 | 30.7289 | -17.6302 | 15.2137 | 828.4181 | 38.435 | 0.2 | 0 | 24.4962 | 891.3492 | 8.8 | 36.6547 | 0.95338 | 0.69683
2015-08-01 11:00 | 495.6167 | 54.8633 | 440.7533 | 849.2346 | 18.2337 | -0.9096 | 58.7348 | 31.2652 | -1.0107 | 1.5353 | 848.9297 | 41.1475 | 0.2 | 0 | 24.7808 | 914.8581 | 10.2 | 38.7893 | 0.94484 | 0.70881
2015-08-01 12:00 | 501.31 | 58.48 | 442.83 | 864.1797 | 18.2234 | 14.0908 | 59.1743 | 30.8257 | 15.6221 | 13.4868 | 840.3487 | 43.86 | 0.2 | 0 | 25.0655 | 909.2742 | 10.9 | 39.3148 | 0.94274 | 0.70291
2015-08-01 13:00 | 428.8567 | 96.1333 | 332.7233 | 676.6873 | 18.213 | 29.0913 | 60.548 | 29.452 | 32.0316 | 27.7306 | 598.9668 | 72.1 | 0.2 | 0 | 21.4428 | 692.5096 | 10.9 | 32.5409 | 0.96984 | 0.55073
2015-08-01 14:00 | 356.4033 | 133.7867 | 222.6167 | 485.8509 | 18.2027 | 44.0917 | 62.729 | 27.271 | 48.0429 | 41.9486 | 361.3494 | 100.34 | 0.2 | 0 | 17.8202 | 479.5095 | 13.5 | 28.4847 | 0.98606 | 0.38772
2015-08-01 15:00 | 283.95 | 171.44 | 112.51 | 271.6232 | 18.1923 | 59.0922 | 65.5302 | 24.4698 | 63.5785 | 56.0928 | 151.525 | 128.58 | 0.2 | 0 | 14.1975 | 294.3025 | 14.2 | 23.397 | 1.0064 | 0.24288
2015-08-01 16:00 | 218.4367 | 143.3567 | 75.08 | 206.9908 | 18.1819 | 74.0926 | 68.7326 | 21.2674 | 78.6549 | 70.1158 | 70.4019 | 107.5175 | 0.2 | 0 | 10.9218 | 188.8412 | 13.5 | 19.4013 | 1.0224 | 0.15832
2015-08-01 17:00 | 152.9233 | 115.2733 | 37.65 | 122.5503 | 18.1716 | 89.0931 | 72.1082 | 17.8918 | 93.3542 | 83.9503 | 12.9156 | 86.455 | 0.2 | 0 | 7.6462 | 107.0168 | 9.8 | 13.1443 | 1.0474 | 0.091915
2015-08-01 18:00 | 87.41 | 87.19 | 0.22 | 0.87481 | 18.1612 | 104.0936 | 75.4348 | 14.5652 | 107.7898 | 97.4897 | 0 | 65.3925 | 0.2 | 0 | 4.3705 | 69.763 | 9.5 | 11.6801 | 1.0533 | 0.060254
2015-08-01 19:00 | 73.6233 | 69.4033 | 4.22 | 21.1748 | 18.1508 | 119.094 | 78.5044 | 11.4956 | 122.0766 | 110.5505 | 0 | 52.0525 | 0.2 | 0 | 3.6812 | 55.7337 | 9.8 | 11.5417 | 1.0538 | 0.048162
2015-08-01 20:00 | 59.8367 | 51.6167 | 8.22 | 53.3075 | 18.1404 | 134.0945 | 81.1296 | 8.8704 | 136.3098 | 122.7941 | 0 | 38.7125 | 0.2 | 0 | 2.9918 | 41.7043 | 9.2 | 10.5033 | 1.058 | 0.036181
2015-08-01 21:00 | 46.05 | 33.83 | 12.22 | 102.4613 | 18.1299 | 149.095 | 83.1503 | 6.8497 | 150.5525 | 133.5609 | 0 | 25.3725 | 0.2 | 0 | 2.3025 | 27.675 | 8.2 | 9.0648 | 1.0637 | 0.02414
2015-08-01 22:00 | 40.3533 | 31.31 | 9.0433 | 93.3662 | 18.1195 | 164.0955 | 84.4417 | 5.5583 | 164.8305 | 141.5812 | 0 | 23.4825 | 0.2 | 0 | 2.0177 | 25.5002 | 8.3 | 9.0969 | 1.0636 | 0.02224
2015-08-01 23:00 | 34.6567 | 28.79 | 5.8667 | 66.2906 | 18.1091 | 179.096 | 84.9227 | 5.0773 | 179.1374 | 144.913 | 0 | 21.5925 | 0.2 | 0 | 1.7328 | 23.3253 | 8.2 | 8.9289 | 1.0643 | 0.020356
2015-08-02 | 28.96 | 26.27 | 2.69 | 28.3917 | 18.0986 | -165.9036 | 84.5633 | 5.4367 | -166.5527 | 142.2904 | 0 | 19.7025 | 0.2 | 0 | 1.448 | 21.1505 | 10.4 | 11.061 | 1.0558 | 0.01831
2015-08-02 01:00 | 42.97 | 40.52 | 2.45 | 21.2741 | 18.0882 | -150.9031 | 83.3869 | 6.6131 | -152.267 | 134.7375 | 0 | 30.39 | 0.2 | 0 | 2.1485 | 32.5385 | 11.8 | 12.8168 | 1.0487 | 0.027982
2015-08-02 02:00 | 56.98 | 54.77 | 2.21 | 14.8972 | 18.0777 | -135.9026 | 81.4687 | 8.5313 | -138.0153 | 124.2247 | 0 | 41.0775 | 0.2 | 0 | 2.849 | 43.9265 | 9.8 | 11.1727 | 1.0553 | 0.038012
2015-08-02 03:00 | 70.99 | 69.02 | 1.97 | 10.2586 | 18.0673 | -120.902 | 78.9284 | 11.0716 | -123.7768 | 112.1168 | 0 | 51.765 | 0.2 | 0 | 3.5495 | 55.3145 | 10.6 | 12.3286 | 1.0507 | 0.047657
2015-08-02 04:00 | 96.7133 | 94.58 | 2.1333 | 8.7709 | 18.0568 | -105.9015 | 75.9228 | 14.0772 | -109.4937 | 99.1316 | 0 | 70.935 | 0.2 | 0 | 4.8357 | 75.7707 | 11.3 | 13.6678 | 1.0453 | 0.064948
2015-08-02 05:00 | 122.4367 | 120.14 | 2.2967 | 7.6958 | 18.0463 | -90.901 | 72.6365 | 17.3635 | -95.075 | 85.6356 | 0.58564 | 90.105 | 0.2 | 0 | 6.1218 | 96.8125 | 12.3 | 15.3254 | 1.0387 | 0.082458
2015-08-02 06:00 | 148.16 | 145.7 | 2.46 | 6.9516 | 18.0358 | -75.9005 | 69.2756 | 20.7244 | -80.4081 | 71.826 | 2.1682 | 109.275 | 0.2 | 0 | 7.408 | 118.8512 | 12.5 | 16.2141 | 1.0351 | 0.10088
2015-08-02 07:00 | 208.7133 | 161.7967 | 46.9167 | 115.6267 | 18.0253 | -60.9 | 66.0612 | 23.9388 | -65.3795 | 57.8163 | 61.5869 | 121.3475 | 0.2 | 0 | 10.4357 | 193.3701 | 12.5 | 18.5428 | 1.0258 | 0.16266
2015-08-02 08:00 | 269.2667 | 177.8933 | 91.3733 | 202.8067 | 18.0148 | -45.8994 | 63.2214 | 26.7786 | -49.9028 | 43.6769 | 146.6791 | 133.42 | 0.2 | 0 | 13.4633 | 293.5624 | 8.8 | 17.9738 | 1.0281 | 0.24749
2015-08-02 09:00 | 329.82 | 193.99 | 135.83 | 279.9689 | 18.0043 | -30.8989 | 60.977 | 29.023 | -33.9532 | 29.4558 | 243.7788 | 145.4925 | 0.2 | 0 | 16.491 | 405.7623 | 8.9 | 21.5801 | 1.0137 | 0.33728
2015-08-02 10:00 | 317.9767 | 174.8533 | 143.1233 | 282.1617 | 17.9937 | -15.8984 | 59.5199 | 30.4801 | -17.5965 | 15.1943 | 272.2981 | 131.14 | 0.2 | 0 | 15.8988 | 419.337 | 8.7 | 21.8043 | 1.0128 | 0.34825
2015-08-02 11:00 | 306.1333 | 155.7167 | 150.4167 | 291.9243 | 17.9832 | -0.89782 | 58.9852 | 31.0148 | -0.99642 | 1.3292 | 291.8458 | 116.7875 | 0.2 | 0 | 15.3067 | 423.94 | 10.1 | 23.3481 | 1.0066 | 0.34993
2015-08-02 12:00 | 294.29 | 136.58 | 157.71 | 310.0485 | 17.9727 | 14.1027 | 59.4252 | 30.5748 | 15.6166 | 13.4865 | 301.4989 | 102.435 | 0.2 | 0 | 14.7145 | 418.6484 | 14 | 27.0828 | 0.99167 | 0.34043
2015-08-02 13:00 | 246.8967 | 129.5867 | 117.31 | 240.4462 | 17.9621 | 29.1033 | 60.7984 | 29.2016 | 32.0084 | 27.7516 | 212.7888 | 97.19 | 0.2 | 0 | 12.3448 | 322.3236 | 10.2 | 20.2726 | 1.0189 | 0.2693
2015-08-02 14:00 | 199.5033 | 122.5933 | 76.91 | 169.2827 | 17.9515 | 44.1038 | 62.9782 | 27.0218 | 48.0059 | 41.9842 | 125.8329 | 91.945 | 0.2 | 0 | 9.9752 | 227.753 | 10.3 | 17.4173 | 1.0303 | 0.19242
2015-08-02 15:00 | 152.11 | 115.6 | 36.51 | 88.9904 | 17.941 | 59.1044 | 65.7783 | 24.2217 | 63.5324 | 56.1421 | 49.5797 | 86.7 | 0.2 | 0 | 7.6055 | 143.8852 | 9 | 13.4964 | 1.046 | 0.12341
2015-08-02 16:00 | 124.0967 | 91.2533 | 32.8433 | 91.5635 | 17.9304 | 74.105 | 68.9799 | 21.0201 | 78.6044 | 70.1797 | 31.0465 | 68.44 | 0.2 | 0 | 6.2048 | 105.6914 | 8.6 | 11.9029 | 1.0524 | 0.091207
2015-08-02 17:00 | 96.0833 | 66.9067 | 29.1767 | 96.258 | 17.9198 | 89.1055 | 72.3556 | 17.6444 | 93.3037 | 84.0308 | 10.0103 | 50.18 | 0.2 | 0 | 4.8042 | 64.9944 | 8.2 | 10.2311 | 1.0591 | 0.056444
2015-08-02 18:00 | 68.07 | 42.56 | 25.51 | 103.159 | 17.9092 | 104.1061 | 75.6829 | 14.3171 | 107.743 | 97.5898 | 0 | 31.92 | 0.2 | 0 | 3.4035 | 35.3235 | 8.9 | 10.0039 | 1.06 | 0.030703
2015-08-02 19:00 | 51.8133 | 33.9167 | 17.8967 | 91.7659 | 17.8986 | 119.1067 | 78.7538 | 11.2462 | 122.0369 | 110.6748 | 0 | 25.4375 | 0.2 | 0 | 2.5907 | 28.0282 | 8.7 | 9.5759 | 1.0617 | 0.024401
2015-08-02 20:00 | 35.5567 | 25.2733 | 10.2833 | 68.6146 | 17.888 | 134.1073 | 81.3806 | 8.6194 | 136.2801 | 122.9492 | 0 | 18.955 | 0.2 | 0 | 1.7778 | 20.7328 | 8.8 | 9.4479 | 1.0622 | 0.018059
2015-08-02 21:00 | 19.3 | 16.63 | 2.67 | 23.2392 | 17.8774 | 149.1079 | 83.4026 | 6.5974 | 150.5351 | 133.7547 | 0 | 12.4725 | 0.2 | 0 | 0.965 | 13.4375 | 7.8 | 8.2199 | 1.0671 | 0.011758
2015-08-02 22:00 | 22.7033 | 15.7267 | 6.9767 | 75.4543 | 17.8667 | 164.1085 | 84.6947 | 5.3053 | 164.8271 | 141.8155 | 0 | 11.795 | 0.2 | 0 | 1.1352 | 12.9302 | 8.3 | 8.7041 | 1.0652 | 0.011294
2015-08-02 23:00 | 26.1067 | 14.8233 | 11.2833 | 134.1659 | 17.8561 | 179.1091 | 85.1757 | 4.8243 | 179.149 | 145.1662 | 0 | 11.1175 | 0.2 | 0 | 1.3053 | 12.4228 | 8.5 | 8.8882 | 1.0644 | 0.010843
2015-08-03 | 29.51 | 13.92 | 15.59 | 172.5224 | 17.8455 | -165.8903 | 84.8154 | 5.1846 | -166.5261 | 142.5195 | 0 | 10.44 | 0.2 | 0 | 1.4755 | 11.9155 | 7.8 | 8.1724 | 1.0673 | 0.010428
2015-08-03 01:00 | 37.6433 | 23.5467 | 14.0967 | 127.2024 | 17.8348 | -150.8897 | 83.6374 | 6.3626 | -152.2261 | 134.9204 | 0 | 17.66 | 0.2 | 0 | 1.8822 | 19.5422 | 7.9 | 8.5107 | 1.066 | 0.017082
2015-08-03 02:00 | 45.7767 | 33.1733 | 12.6033 | 87.485 | 17.8241 | -135.8891 | 81.717 | 8.283 | -137.9619 | 124.3645 | 0 | 24.88 | 0.2 | 0 | 2.2888 | 27.1688 | 7.7 | 8.549 | 1.0658 | 0.023744
2015-08-03 03:00 | 53.91 | 42.8 | 11.11 | 59.154 | 17.8135 | -120.8885 | 79.1747 | 10.8253 | -123.713 | 112.2229 | 0 | 32.1 | 0.2 | 0 | 2.6955 | 34.7955 | 6.3 | 7.3874 | 1.0705 | 0.030542
2015-08-03 04:00 | 61.68 | 51.5167 | 10.1633 | 42.5093 | 17.8028 | -105.8879 | 76.1675 | 13.8325 | -109.4222 | 99.2116 | 0 | 38.6375 | 0.2 | 0 | 3.084 | 41.7215 | 5.7 | 7.0038 | 1.072 | 0.036674
2015-08-03 05:00 | 69.45 | 60.2333 | 9.2167 | 31.3101 | 17.7921 | -90.8872 | 72.8804 | 17.1196 | -94.9988 | 85.695 | 2.3503 | 45.175 | 0.2 | 0 | 3.4725 | 50.9978 | 6 | 7.5937 | 1.0696 | 0.04473
2015-08-03 06:00 | 77.22 | 68.95 | 8.27 | 23.6365 | 17.7814 | -75.8866 | 69.5198 | 20.4802 | -80.3309 | 71.8683 | 7.3557 | 51.7125 | 0.2 | 0 | 3.861 | 62.9292 | 6.4 | 8.3665 | 1.0665 | 0.055035
2015-08-03 07:00 | 92.69 | 85.9067 | 6.7833 | 16.8808 | 17.7707 | -60.886 | 66.307 | 23.693 | -65.3054 | 57.8436 | 8.9845 | 64.43 | 0.2 | 0 | 4.6345 | 78.049 | 7.4 | 9.839 | 1.0606 | 0.067881
2015-08-03 08:00 | 108.16 | 102.8633 | 5.2967 | 11.858 | 17.76 | -45.8853 | 63.4695 | 26.5305 | -49.8364 | 43.6906 | 8.5743 | 77.1475 | 0.2 | 0 | 5.408 | 91.1298 | 6.3 | 9.1478 | 1.0634 | 0.079465
2015-08-03 09:00 | 123.63 | 119.82 | 3.81 | 7.9156 | 17.7493 | -30.8847 | 61.2279 | 28.7721 | -33.8993 | 29.4557 | 6.8924 | 89.865 | 0.2 | 0 | 6.1815 | 102.9389 | 6.3 | 9.5168 | 1.0619 | 0.089638
2015-08-03 10:00 | 121.63 | 118.33 | 3.3 | 6.5552 | 17.7385 | -15.884 | 59.7735 | 30.2265 | -17.5596 | 15.1763 | 6.3266 | 88.7475 | 0.2 | 0 | 6.0815 | 101.1556 | 6.3 | 9.4611 | 1.0622 | 0.088103
2015-08-03 11:00 | 119.63 | 116.84 | 2.79 | 5.4552 | 17.7278 | -0.88339 | 59.2406 | 30.7594 | -0.9792 | 1.1359 | 5.4542 | 87.63 | 0.2 | 0 | 5.9815 | 99.0657 | 6.6 | 9.6958 | 1.0612 | 0.086207
2015-08-03 12:00 | 117.63 | 115.35 | 2.28 | 4.5165 | 17.7171 | 14.1173 | 59.6812 | 30.3188 | 15.6137 | 13.4933 | 4.3919 | 86.5125 | 0.2 | 0 | 5.8815 | 96.7859 | 6.4 | 9.4246 | 1.0623 | 0.084309
2015-08-03 13:00 | 181.6467 | 100.47 | 81.1767 | 167.725 | 17.7063 | 29.1179 | 61.0539 | 28.9461 | 31.9875 | 27.7776 | 148.3969 | 75.3525 | 0.2 | 0 | 9.0823 | 232.8318 | 6.8 | 14.076 | 1.0437 | 0.19926
2015-08-03 14:00 | 245.6633 | 85.59 | 160.0733 | 355.4281 | 17.6955 | 44.1186 | 63.2327 | 26.7673 | 47.9709 | 42.024 | 264.0349 | 64.1925 | 0.2 | 0 | 12.2832 | 340.5105 | 6.1 | 16.741 | 1.033 | 0.28844
2015-08-03 15:00 | 309.68 | 70.71 | 238.97 | 588.2602 | 17.6848 | 59.1193 | 66.0317 | 23.9683 | 63.4881 | 56.1955 | 327.2852 | 53.0325 | 0.2 | 0 | 15.484 | 395.8017 | 6 | 18.3688 | 1.0265 | 0.33317
2015-08-03 16:00 | 261.9667 | 59.7733 | 202.1933 | 570.2429 | 17.674 | 74.12 | 69.2327 | 20.7673 | 78.5556 | 70.2476 | 192.7175 | 44.83 | 0.2 | 0 | 13.0983 | 250.6458 | 5.2 | 13.0327 | 1.0479 | 0.21537
2015-08-03 17:00 | 214.2533 | 48.8367 | 165.4167 | 553.4133 | 17.6632 | 89.1206 | 72.6083 | 17.3917 | 93.2548 | 84.1151 | 56.7415 | 36.6275 | 0.2 | 0 | 10.7127 | 104.0817 | 5.1 | 8.3526 | 1.0666 | 0.09103
2015-08-03 18:00 | 166.54 | 37.9 | 128.64 | 529.3837 | 17.6524 | 104.1213 | 75.9364 | 14.0636 | 107.6978 | 97.6938 | 0 | 28.425 | 0.2 | 0 | 8.327 | 36.752 | 4.3 | 5.4485 | 1.0782 | 0.032494
2015-08-03 19:00 | 124.43 | 31.5233 | 92.9067 | 487.2814 | 17.6416 | 119.122 | 79.0085 | 10.9915 | 121.9989 | 110.8032 | 0 | 23.6425 | 0.2 | 0 | 6.2215 | 29.864 | 4.3 | 5.2332 | 1.0791 | 0.026425
2015-08-03 20:00 | 82.32 | 25.1467 | 57.1733 | 393.0807 | 17.6308 | 134.1227 | 81.6367 | 8.3633 | 136.2522 | 123.1088 | 0 | 18.86 | 0.2 | 0 | 4.116 | 22.976 | 4.7 | 5.418 | 1.0783 | 0.020316
2015-08-03 21:00 | 40.21 | 18.77 | 21.44 | 194.1528 | 17.62 | 149.1234 | 83.66 | 6.34 | 150.5197 | 133.9533 | 0 | 14.0775 | 0.2 | 0 | 2.0105 | 16.088 | 4.1 | 4.6027 | 1.0816 | 0.014268
2015-08-03 22:00 | 35.3767 | 17.3867 | 17.99 | 204.4854 | 17.6091 | 164.1241 | 84.9528 | 5.0472 | 164.826 | 142.0551 | 0 | 13.04 | 0.2 | 0 | 1.7688 | 14.8088 | 3.7 | 4.1628 | 1.0833 | 0.013155
2015-08-03 23:00 | 30.5433 | 16.0033 | 14.54 | 182.63 | 17.5983 | 179.1248 | 85.4336 | 4.5664 | 179.1631 | 145.4243 | 0 | 12.0025 | 0.2 | 0 | 1.5272 | 13.5297 | 3.6 | 4.0228 | 1.0839 | 0.012025
2015-08-04 | 25.71 | 14.62 | 11.09 | 129.1022 | 17.5875 | -165.8745 | 85.0722 | 4.9278 | -166.4966 | 142.7519 | 0 | 10.965 | 0.2 | 0 | 1.2855 | 12.2505 | 3.5 | 3.8828 | 1.0845 | 0.010894
2015-08-04 01:00 | 36.6367 | 24.1167 | 12.52 | 117.672 | 17.5766 | -150.8737 | 83.8923 | 6.1077 | -152.1822 | 135.1047 | 0 | 18.0875 | 0.2 | 0 | 1.8318 | 19.9193 | 3.6 | 4.2225 | 1.0831 | 0.017691
2015-08-04 02:00 | 47.5633 | 33.6133 | 13.95 | 99.859 | 17.5657 | -135.873 | 81.9697 | 8.0303 | -137.9052 | 124.5046 | 0 | 25.21 | 0.2 | 0 | 2.3782 | 27.5882 | 4.1 | 4.9621 | 1.0802 | 0.024436
2015-08-04 03:00 | 58.49 | 43.11 | 15.38 | 83.806 | 17.5549 | -120.8723 | 79.4252 | 10.5748 | -123.6458 | 112.3286 | 0 | 32.3325 | 0.2 | 0 | 2.9245 | 35.257 | 3.5 | 4.6018 | 1.0816 | 0.03127
2015-08-04 04:00 | 75.57 | 62.47 | 13.1 | 55.7764 | 17.544 | -105.8715 | 76.4163 | 13.5837 | -109.3471 | 99.2909 | 0 | 46.8525 | 0.2 | 0 | 3.7785 | 50.631 | 3.5 | 5.0822 | 1.0797 | 0.044825
2015-08-04 05:00 | 92.65 | 81.83 | 10.82 | 37.281 | 17.5331 | -90.8708 | 73.1284 | 16.8716 | -94.919 | 85.7533 | 2.7607 | 61.3725 | 0.2 | 0 | 4.6325 | 68.7657 | 3.5 | 5.6489 | 1.0774 | 0.060753
2015-08-04 06:00 | 109.73 | 101.19 | 8.54 | 24.695 | 17.5222 | -75.8701 | 69.7682 | 20.2318 | -80.2501 | 71.9094 | 7.6683 | 75.8925 | 0.2 | 0 | 5.4865 | 89.0473 | 3.6 | 6.3827 | 1.0745 | 0.078456
2015-08-04 07:00 | 128.38 | 122.1 | 6.28 | 15.7853 | 17.5113 | -60.8693 | 66.5569 | 23.4431 | -65.2276 | 57.87 | 8.3953 | 91.575 | 0.2 | 0 | 6.419 | 106.3893 | 4.6 | 7.9247 | 1.0683 | 0.093198
2015-08-04 08:00 | 147.03 | 143.01 | 4.02 | 9.0801 | 17.5004 | -45.8686 | 63.722 | 26.278 | -49.7664 | 43.7034 | 6.5642 | 107.2575 | 0.2 | 0 | 7.3515 | 121.1732 | 5.2 | 8.9867 | 1.0641 | 0.10573
2015-08-04 09:00 | 165.68 | 163.92 | 1.76 | 3.6865 | 17.4895 | -30.8678 | 61.4833 | 28.5167 | -33.8421 | 29.4553 | 3.21 | 122.94 | 0.2 | 0 | 8.284 | 134.434 | 6.5 | 10.7011 | 1.0572 | 0.11654
2015-08-04 10:00 | 170.5233 | 166 | 4.5233 | 9.0553 | 17.4785 | -15.8671 | 60.0317 | 29.9683 | -17.5195 | 15.1599 | 8.7402 | 124.5 | 0.2 | 0 | 8.5262 | 141.7664 | 4.5 | 8.9302 | 1.0643 | 0.12372
2015-08-04 11:00 | 175.3667 | 168.08 | 7.2867 | 14.3572 | 17.4676 | -0.86629 | 59.5007 | 30.4993 | -0.95904 | 0.96729 | 14.3551 | 126.06 | 0.2 | 0 | 8.7683 | 149.1835 | 4.4 | 9.062 | 1.0638 | 0.13013
2015-08-04 12:00 | 180.21 | 170.16 | 10.05 | 20.0649 | 17.4567 | 14.1345 | 59.9421 | 30.0579 | 15.6135 | 13.5073 | 19.5099 | 127.62 | 0.2 | 0 | 9.0105 | 156.1404 | 4.3 | 9.1794 | 1.0633 | 0.13614
2015-08-04 13:00 | 143.09 | 136.39 | 6.7 | 13.9583 | 17.4457 | 29.1353 | 61.3145 | 28.6855 | 31.9689 | 27.8085 | 12.3463 | 102.2925 | 0.2 | 0 | 7.1545 | 121.7933 | 4.4 | 8.206 | 1.0672 | 0.10658
2015-08-04 14:00 | 105.97 | 102.62 | 3.35 | 7.5059 | 17.4348 | 44.136 | 63.4924 | 26.5076 | 47.9379 | 42.0682 | 5.572 | 76.965 | 0.2 | 0 | 5.2985 | 87.8355 | 4 | 6.7449 | 1.073 | 0.077284
2015-08-04 15:00 | 68.85 | 68.85 | 0 | 0 | 17.4238 | 59.1368 | 66.2903 | 23.7097 | 63.4456 | 56.2529 | 0 | 51.6375 | 0.2 | 0 | 3.4425 | 55.08 | 4 | 5.7213 | 1.0771 | 0.048649
2015-08-04 16:00 | 60.4233 | 60.3867 | 0.036667 | 0.10465 | 17.4128 | 74.1376 | 69.4906 | 20.5094 | 78.5084 | 70.3193 | 0.035245 | 45.29 | 0.2 | 0 | 3.0212 | 48.3464 | 5.4 | 6.9108 | 1.0724 | 0.042513
2015-08-04 17:00 | 51.9967 | 51.9233 | 0.073333 | 0.24892 | 17.4018 | 89.1384 | 72.8663 | 17.1337 | 93.2074 | 84.2034 | 0.025141 | 38.9425 | 0.2 | 0 | 2.5998 | 41.5675 | 4.3 | 5.599 | 1.0776 | 0.03673
2015-08-04 18:00 | 43.57 | 43.46 | 0.11 | 0.46099 | 17.3908 | 104.1392 | 76.195 | 13.805 | 107.6542 | 97.8017 | 0 | 32.595 | 0.2 | 0 | 2.1785 | 34.7735 | 4.6 | 5.6867 | 1.0773 | 0.030717
2015-08-04 19:00 | 34.1667 | 34.0733 | 0.093333 | 0.50123 | 17.3798 | 119.14 | 79.2684 | 10.7316 | 121.9625 | 110.9357 | 0 | 25.555 | 0.2 | 0 | 1.7083 | 27.2633 | 4.5 | 5.352 | 1.0786 | 0.024113
2015-08-04 20:00 | 24.7633 | 24.6867 | 0.076667 | 0.54398 | 17.3688 | 134.1408 | 81.898 | 8.102 | 136.2261 | 123.2728 | 0 | 18.515 | 0.2 | 0 | 1.2382 | 19.7532 | 4.9 | 5.5173 | 1.0779 | 0.01746
2015-08-04 21:00 | 15.36 | 15.3 | 0.06 | 0.5667 | 17.3578 | 149.1416 | 83.9224 | 6.0776 | 150.5064 | 134.1567 | 0 | 11.475 | 0.2 | 0 | 0.768 | 12.243 | 5.9 | 6.2826 | 1.0749 | 0.010791
2015-08-04 22:00 | 14.23 | 13.5667 | 0.66333 | 7.9532 | 17.3468 | 164.1424 | 85.2157 | 4.7843 | 164.8272 | 142.2999 | 0 | 10.175 | 0.2 | 0 | 0.7115 | 10.8865 | 5.8 | 6.1402 | 1.0754 | 0.0096004
2015-08-04 23:00 | 13.1 | 11.8333 | 1.2667 | 16.8788 | 17.3357 | 179.1433 | 85.6962 | 4.3038 | 179.1799 | 145.6872 | 0 | 8.875 | 0.2 | 0 | 0.655 | 9.53 | 8.1 | 8.3978 | 1.0664 | 0.0083336
2015-08-05 | 11.97 | 10.1 | 1.87 | 22.9857 | 17.3247 | -165.8559 | 85.3335 | 4.6665 | -166.4643 | 142.9873 | 0 | 7.575 | 0.2 | 0 | 0.5985 | 8.1735 | 8.6 | 8.8554 | 1.0646 | 0.0071351
2015-08-05 01:00 | 22.83 | 21.56 | 1.27 | 12.4638 | 17.3137 | -150.8551 | 84.1517 | 5.8483 | -152.1352 | 135.2903 | 0 | 16.17 | 0.2 | 0 | 1.1415 | 17.3115 | 8.4 | 8.941 | 1.0642 | 0.015107
2015-08-05 02:00 | 33.69 | 33.02 | 0.67 | 4.9536 | 17.3026 | -135.8542 | 82.2267 | 7.7733 | -137.8452 | 124.6449 | 0 | 24.765 | 0.2 | 0 | 1.6845 | 26.4495 | 9.2 | 10.0265 | 1.0599 | 0.022988
2015-08-05 03:00 | 44.55 | 44.48 | 0.07 | 0.39074 | 17.2915 | -120.8534 | 79.6798 | 10.3202 | -123.5751 | 112.4338 | 0 | 33.36 | 0.2 | 0 | 2.2275 | 35.5875 | 8 | 9.1121 | 1.0636 | 0.031036
2015-08-05 04:00 | 56.0733 | 55.9367 | 0.13667 | 0.59272 | 17.2805 | -105.8526 | 76.6691 | 13.3309 | -109.2685 | 99.3693 | 0 | 41.9525 | 0.2 | 0 | 2.8037 | 44.7562 | 8.1 | 9.4986 | 1.062 | 0.038976
2015-08-05 05:00 | 67.5967 | 67.3933 | 0.20333 | 0.71092 | 17.2694 | -90.8517 | 73.3804 | 16.6196 | -94.8357 | 85.8106 | 0.051934 | 50.545 | 0.2 | 0 | 3.3798 | 53.9768 | 8.7 | 10.3868 | 1.0585 | 0.046848
2015-08-05 06:00 | 79.12 | 78.85 | 0.27 | 0.79021 | 17.2583 | -75.8509 | 70.0206 | 19.9794 | -80.1656 | 71.9494 | 0.24485 | 59.1375 | 0.2 | 0 | 3.956 | 63.3384 | 8.7 | 10.6793 | 1.0573 | 0.054913
2015-08-05 07:00 | 66.02 | 65.84 | 0.18 | 0.45712 | 17.2472 | -60.85 | 66.8109 | 23.1891 | -65.1463 | 57.8952 | 0.24295 | 49.38 | 0.2 | 0 | 3.301 | 52.9239 | 6.3 | 7.9539 | 1.0682 | 0.046357
2015-08-05 08:00 | 52.92 | 52.83 | 0.09 | 0.20515 | 17.2361 | -45.8491 | 63.9786 | 26.0214 | -49.693 | 43.7154 | 0.14828 | 39.6225 | 0.2 | 0 | 2.646 | 42.4168 | 7.2 | 8.5255 | 1.0659 | 0.037074
2015-08-05 09:00 | 39.82 | 39.82 | 0 | 0 | 17.225 | -30.8483 | 61.7431 | 28.2569 | -33.7816 | 29.4547 | 0 | 29.865 | 0.2 | 0 | 1.991 | 31.856 | 8.5 | 9.4955 | 1.062 | 0.027742
2015-08-05 10:00 | 41.82 | 41.82 | 0 | 0 | 17.2138 | -15.8474 | 60.2944 | 29.7056 | -17.4762 | 15.1454 | 0 | 31.365 | 0.2 | 0 | 2.091 | 33.456 | 7.1 | 8.1455 | 1.0674 | 0.029283
2015-08-05 11:00 | 43.82 | 43.82 | 0 | 0 | 17.2027 | -0.84652 | 59.7655 | 30.2345 | -0.93598 | 0.84289 | 0 | 32.865 | 0.2 | 0 | 2.191 | 35.056 | 8 | 9.0955 | 1.0636 | 0.030575
2015-08-05 12:00 | 45.82 | 45.82 | 0 | 0 | 17.1916 | 14.1544 | 60.2079 | 29.7921 | 15.6159 | 13.529 | 0 | 34.365 | 0.2 | 0 | 2.291 | 36.656 | 5.9 | 7.0455 | 1.0718 | 0.032217
2015-08-05 13:00 | 72.17 | 40.29 | 31.88 | 66.9847 | 17.1804 | 29.1552 | 61.5801 | 28.4199 | 31.9527 | 27.8446 | 59.229 | 30.2175 | 0.2 | 0 | 3.6085 | 93.055 | 5.3 | 8.208 | 1.0672 | 0.08143
2015-08-05 14:00 | 98.52 | 34.76 | 63.76 | 144.1955 | 17.1693 | 44.1561 | 63.7571 | 26.2429 | 47.9071 | 42.1168 | 106.9613 | 26.07 | 0.2 | 0 | 4.926 | 137.9573 | 4.8 | 9.1112 | 1.0636 | 0.12031
2015-08-05 15:00 | 124.87 | 29.23 | 95.64 | 240.3715 | 17.1581 | 59.157 | 66.554 | 23.446 | 63.4049 | 56.3144 | 133.3187 | 21.9225 | 0.2 | 0 | 6.2435 | 161.4847 | 5.5 | 10.5464 | 1.0578 | 0.14007
2015-08-05 16:00 | 114.8067 | 30.7867 | 84.02 | 242.7936 | 17.1469 | 74.1579 | 69.7538 | 20.2462 | 78.4629 | 70.395 | 81.4653 | 23.09 | 0.2 | 0 | 5.7403 | 110.2956 | 4.9 | 8.3467 | 1.0666 | 0.096467
2015-08-05 17:00 | 104.7433 | 32.3433 | 72.4 | 249.4742 | 17.1358 | 89.1588 | 73.1294 | 16.8706 | 93.1616 | 84.2955 | 24.7972 | 24.2575 | 0.2 | 0 | 5.2372 | 54.2918 | 4.5 | 6.1966 | 1.0752 | 0.047868
2015-08-05 18:00 | 94.68 | 33.9 | 60.78 | 259.585 | 17.1246 | 104.1597 | 76.4589 | 13.5411 | 107.6122 | 97.9137 | 0 | 25.425 | 0.2 | 0 | 4.734 | 30.159 | 3.8 | 4.7425 | 1.081 | 0.026734
2015-08-05 19:00 | 82.2333 | 29.7633 | 52.47 | 288.8326 | 17.1134 | 119.1607 | 79.5334 | 10.4666 | 121.9279 | 111.0724 | 0 | 22.3225 | 0.2 | 0 | 4.1117 | 26.4342 | 3.6 | 4.4261 | 1.0823 | 0.02346
2015-08-05 20:00 | 69.7867 | 25.6267 | 44.16 | 323.9118 | 17.1022 | 134.1616 | 82.1643 | 7.8357 | 136.2019 | 123.4411 | 0 | 19.22 | 0.2 | 0 | 3.4893 | 22.7093 | 2.8 | 3.5097 | 1.086 | 0.020222
2015-08-05 21:00 | 57.34 | 21.49 | 35.85 | 354.1283 | 17.091 | 149.1625 | 84.1897 | 5.8103 | 150.4951 | 134.3648 | 0 | 16.1175 | 0.2 | 0 | 2.867 | 18.9845 | 3 | 3.5933 | 1.0856 | 0.0169
2015-08-05 22:00 | 48.4667 | 19.68 | 28.7867 | 365.5602 | 17.0797 | 164.1634 | 85.4835 | 4.5165 | 164.8307 | 142.5497 | 0 | 14.76 | 0.2 | 0 | 2.4233 | 17.1833 | 3.1 | 3.637 | 1.0855 | 0.015294
2015-08-05 23:00 | 39.5933 | 17.87 | 21.7233 | 308.6054 | 17.0685 | 179.1644 | 85.9635 | 4.0365 | 179.1992 | 145.9549 | 0 | 13.4025 | 0.2 | 0 | 1.9797 | 15.3822 | 3.2 | 3.6807 | 1.0853 | 0.013689
2015-08-06 | 30.72 | 16.06 | 14.66 | 191.0622 | 17.0573 | -165.8347 | 85.5994 | 4.4006 | -166.4292 | 143.2257 | 0 | 12.045 | 0.2 | 0 | 1.536 | 13.581 | 2.5 | 2.9244 | 1.0883 | 0.01212
2015-08-06 01:00 | 42.4933 | 27.3133 | 15.18 | 155.9881 | 17.046 | -150.8338 | 84.4154 | 5.5846 | -152.0852 | 135.477 | 0 | 20.485 | 0.2 | 0 | 2.1247 | 22.6097 | 2.7 | 3.4066 | 1.0864 | 0.020141
2015-08-06 02:00 | 54.2667 | 38.5667 | 15.7 | 120.0888 | 17.0348 | -135.8328 | 82.4878 | 7.5122 | -137.782 | 124.7851 | 0 | 28.925 | 0.2 | 0 | 2.7133 | 31.6383 | 2.9 | 3.8887 | 1.0844 | 0.028134
2015-08-06 03:00 | 66.04 | 49.82 | 16.22 | 92.8426 | 17.0235 | -120.8319 | 79.9385 | 10.0615 | -123.501 | 112.5383 | 0 | 37.365 | 0.2 | 0 | 3.302 | 40.667 | 3 | 4.2708 | 1.0829 | 0.036112
2015-08-06 04:00 | 82.14 | 70.2 | 11.94 | 52.7827 | 17.0123 | -105.8309 | 76.9259 | 13.0741 | -109.1864 | 99.4467 | 0 | 52.65 | 0.2 | 0 | 4.107 | 56.757 | 3.4 | 5.1737 | 1.0793 | 0.050232
2015-08-06 05:00 | 98.24 | 90.58 | 7.66 | 27.1889 | 17.001 | -90.8299 | 73.6364 | 16.3636 | -94.7488 | 85.8669 | 1.9596 | 67.935 | 0.2 | 0 | 4.912 | 74.8066 | 3.6 | 5.9377 | 1.0762 | 0.066019
2015-08-06 06:00 | 114.34 | 110.96 | 3.38 | 10.0156 | 16.9897 | -75.829 | 70.277 | 19.723 | -80.0776 | 71.9884 | 3.0969 | 83.22 | 0.2 | 0 | 5.717 | 92.0339 | 4 | 6.8761 | 1.0725 | 0.080939
2015-08-06 07:00 | 154.7133 | 152.4433 | 2.27 | 5.8261 | 16.9784 | -60.828 | 67.069 | 22.931 | -65.0615 | 57.9195 | 3.0943 | 114.3325 | 0.2 | 0 | 7.7357 | 125.1625 | 4.1 | 8.0113 | 1.068 | 0.10961
2015-08-06 08:00 | 195.0867 | 193.9267 | 1.16 | 2.669 | 16.9671 | -45.827 | 64.2394 | 25.7606 | -49.6162 | 43.7268 | 1.9288 | 145.445 | 0.2 | 0 | 9.7543 | 157.1281 | 4.5 | 9.4103 | 1.0624 | 0.13688
2015-08-06 09:00 | 235.46 | 235.41 | 0.05 | 0.10653 | 16.9558 | -30.8261 | 62.0072 | 27.9928 | -33.7177 | 29.4541 | 0.092759 | 176.5575 | 0.2 | 0 | 11.773 | 188.4233 | 5.2 | 11.0882 | 1.0556 | 0.1631
2015-08-06 10:00 | 254.4967 | 237.1667 | 17.33 | 35.2602 | 16.9445 | -15.8251 | 60.5615 | 29.4385 | -17.4298 | 15.1331 | 34.0375 | 177.875 | 0.2 | 0 | 12.7248 | 224.6373 | 5.3 | 12.3199 | 1.0507 | 0.19355
2015-08-06 11:00 | 273.5333 | 238.9233 | 34.61 | 69.2933 | 16.9332 | -0.82409 | 60.035 | 29.965 | -0.91001 | 0.789 | 69.2867 | 179.1925 | 0.2 | 0 | 13.6767 | 262.1558 | 5 | 13.1924 | 1.0472 | 0.22512
2015-08-06 12:00 | 292.57 | 240.68 | 51.89 | 105.3066 | 16.9218 | 14.1769 | 60.4784 | 29.5216 | 15.6209 | 13.5586 | 102.3718 | 180.51 | 0.2 | 0 | 14.6285 | 297.5103 | 4.5 | 13.7972 | 1.0448 | 0.25489
2015-08-06 13:00 | 281.44 | 214.86 | 66.58 | 141.1274 | 16.9105 | 29.1779 | 61.8506 | 28.1494 | 31.9389 | 27.8859 | 124.7397 | 161.145 | 0.2 | 0 | 14.072 | 299.9567 | 4.3 | 13.6736 | 1.0453 | 0.25711
2015-08-06 14:00 | 270.31 | 189.04 | 81.27 | 185.5692 | 16.8992 | 44.1789 | 64.0269 | 25.9731 | 47.8783 | 42.1698 | 137.5362 | 141.78 | 0.2 | 0 | 13.5155 | 292.8317 | 3.7 | 12.851 | 1.0486 | 0.25179
2015-08-06 15:00 | 259.18 | 163.22 | 95.96 | 243.8162 | 16.8878 | 59.1799 | 66.8229 | 23.1771 | 63.3661 | 56.3799 | 134.9969 | 122.415 | 0.2 | 0 | 12.959 | 270.3709 | 4.5 | 12.9491 | 1.0482 | 0.23239
2015-08-06 16:00 | 220.5833 | 136.2333 | 84.35 | 246.8836 | 16.8765 | 74.1809 | 70.022 | 19.978 | 78.4191 | 70.4747 | 82.5142 | 102.175 | 0.2 | 0 | 11.0292 | 195.7184 | 4.2 | 10.3162 | 1.0587 | 0.16992
2015-08-06 17:00 | 181.9867 | 109.2467 | 72.74 | 254.579 | 16.8651 | 89.1819 | 73.3977 | 16.6023 | 93.1174 | 84.3915 | 24.88 | 81.935 | 0.2 | 0 | 9.0993 | 115.9143 | 3.9 | 7.5223 | 1.0699 | 0.10169
2015-08-06 18:00 | 143.39 | 82.26 | 61.13 | 266.2719 | 16.8537 | 104.183 | 76.7278 | 13.2722 | 107.5719 | 98.0295 | 0 | 61.695 | 0.2 | 0 | 7.1695 | 68.8645 | 3.1 | 5.252 | 1.079 | 0.060929
2015-08-06 19:00 | 113.99 | 62.5667 | 51.4233 | 290.485 | 16.8423 | 119.184 | 79.8034 | 10.1966 | 121.8949 | 111.213 | 0 | 46.925 | 0.2 | 0 | 5.6995 | 52.6245 | 3.9 | 5.5445 | 1.0778 | 0.04651
2015-08-06 20:00 | 84.59 | 42.8733 | 41.7167 | 316.8956 | 16.8309 | 134.185 | 82.4355 | 7.5645 | 136.1795 | 123.6137 | 0 | 32.155 | 0.2 | 0 | 4.2295 | 36.3845 | 3.5 | 4.637 | 1.0815 | 0.032265
2015-08-06 21:00 | 55.19 | 23.18 | 32.01 | 331.6864 | 16.8195 | 149.186 | 84.4619 | 5.5381 | 150.4859 | 134.5775 | 0 | 17.385 | 0.2 | 0 | 2.7595 | 20.1445 | 3.9 | 4.5295 | 1.0819 | 0.017871
2015-08-06 22:00 | 48.7933 | 21 | 27.7933 | 375.5623 | 16.8081 | 164.1871 | 85.756 | 4.244 | 164.8366 | 142.8047 | 0 | 15.75 | 0.2 | 0 | 2.4397 | 18.1897 | 3.7 | 4.2684 | 1.0829 | 0.016152
2015-08-06 23:00 | 42.3967 | 18.82 | 23.5767 | 359.0847 | 16.7967 | 179.1881 | 86.2354 | 3.7646 | 179.2211 | 146.2272 | 0 | 14.115 | 0.2 | 0 | 2.1198 | 16.2348 | 4.1 | 4.6073 | 1.0816 | 0.014398
2015-08-07 | 36 | 16.64 | 19.36 | 268.7989 | 16.7853 | -165.8108 | 85.8697 | 4.1303 | -166.3912 | 143.4669 | 0 | 12.48 | 0.2 | 0 | 1.8 | 14.28 | 4.8 | 5.2462 | 1.079 | 0.012635
2015-08-07 01:00 | 64.9867 | 23.2233 | 41.7633 | 450.7209 | 16.7739 | -150.8098 | 84.6834 | 5.3166 | -152.0321 | 135.6647 | 0 | 17.4175 | 0.2 | 0 | 3.2493 | 20.6668 | 4.6 | 5.2458 | 1.079 | 0.018286
2015-08-07 02:00 | 93.9733 | 29.8067 | 64.1667 | 508.6744 | 16.7624 | -135.8087 | 82.7531 | 7.2469 | -137.7155 | 124.9252 | 0 | 22.355 | 0.2 | 0 | 4.6987 | 27.0537 | 3.7 | 4.5454 | 1.0818 | 0.023999
2015-08-07 03:00 | 122.96 | 36.39 | 86.57 | 508.6723 | 16.751 | -120.8077 | 80.2012 | 9.7988 | -123.4235 | 112.6421 | 0 | 27.2925 | 0.2 | 0 | 6.148 | 33.4405 | 4.2 | 5.245 | 1.079 | 0.029588
2015-08-07 04:00 | 140.63 | 73.4867 | 67.1433 | 302.7538 | 16.7395 | -105.8066 | 77.1867 | 12.8133 | -109.1008 | 99.5231 | 0 | 55.115 | 0.2 | 0 | 7.0315 | 62.1465 | 3.8 | 5.7421 | 1.077 | 0.054886
2015-08-07 05:00 | 158.3 | 110.5833 | 47.7167 | 172.0274 | 16.728 | -90.8055 | 73.8962 | 16.1038 | -94.6584 | 85.9219 | 12.2338 | 82.9375 | 0.2 | 0 | 7.915 | 103.0863 | 3.9 | 7.1214 | 1.0715 | 0.090576
2015-08-07 06:00 | 175.97 | 147.68 | 28.29 | 84.9053 | 16.7166 | -75.8044 | 70.5372 | 19.4628 | -79.9861 | 72.0261 | 26.2003 | 110.76 | 0.2 | 0 | 8.7985 | 145.7588 | 3.9 | 8.455 | 1.0662 | 0.12743
2015-08-07 07:00 | 240.1333 | 152.5533 | 87.58 | 227.2399 | 16.7051 | -60.8034 | 67.3309 | 22.6691 | -64.9732 | 57.9427 | 120.6113 | 114.415 | 0.2 | 0 | 12.0067 | 247.033 | 3.7 | 11.4198 | 1.0543 | 0.21357
2015-08-07 08:00 | 304.2967 | 157.4267 | 146.87 | 341.2053 | 16.6936 | -45.8023 | 64.5042 | 25.4958 | -49.5359 | 43.7374 | 246.5264 | 118.07 | 0.2 | 0 | 15.2148 | 379.8112 | 3.9 | 15.7691 | 1.0369 | 0.32294
2015-08-07 09:00 | 368.46 | 162.3 | 206.16 | 443.143 | 16.6821 | -30.8012 | 62.2754 | 27.7246 | -33.6505 | 29.4536 | 385.8687 | 121.725 | 0.2 | 0 | 18.423 | 526.0167 | 3.9 | 20.338 | 1.0186 | 0.43938
2015-08-07 10:00 | 373.09 | 158.43 | 214.66 | 440.4582 | 16.6706 | -15.8001 | 60.833 | 29.167 | -17.3804 | 15.1231 | 425.2041 | 118.8225 | 0.2 | 0 | 18.6545 | 562.6811 | 5 | 22.5838 | 1.0097 | 0.46586
2015-08-07 11:00 | 377.72 | 154.56 | 223.16 | 450.5342 | 16.6591 | -0.79899 | 60.3089 | 29.6911 | -0.88114 | 0.82436 | 450.4876 | 115.92 | 0.2 | 0 | 18.886 | 585.2936 | 5.3 | 23.5904 | 1.0056 | 0.48265
2015-08-07 12:00 | 382.35 | 150.69 | 231.66 | 474.1635 | 16.6476 | 14.2021 | 60.7536 | 29.2464 | 15.6286 | 13.5962 | 460.8757 | 113.0175 | 0.2 | 0 | 19.1175 | 593.0107 | 4.9 | 23.4316 | 1.0063 | 0.48932
2015-08-07 13:00 | 339.9867 | 155.8467 | 184.14 | 393.8571 | 16.6361 | 29.2032 | 62.1259 | 27.8741 | 31.9274 | 27.9326 | 347.9724 | 116.885 | 0.2 | 0 | 16.9993 | 481.8567 | 5 | 20.058 | 1.0198 | 0.40293
2015-08-07 14:00 | 297.6233 | 161.0033 | 136.62 | 315.0574 | 16.6245 | 44.2043 | 64.3015 | 25.6985 | 47.8516 | 42.2273 | 233.295 | 120.7525 | 0.2 | 0 | 14.8812 | 368.9287 | 4.8 | 16.329 | 1.0347 | 0.31301
2015-08-07 15:00 | 255.26 | 166.16 | 89.1 | 228.9444 | 16.613 | 59.2055 | 67.0967 | 22.9033 | 63.3293 | 56.4497 | 126.5305 | 124.62 | 0.2 | 0 | 12.763 | 263.9135 | 5 | 13.2473 | 1.047 | 0.22658
2015-08-07 16:00 | 217.1967 | 139.1467 | 78.05 | 231.4836 | 16.6014 | 74.2066 | 70.2953 | 19.7047 | 78.3771 | 70.5583 | 77.0487 | 104.36 | 0.2 | 0 | 10.8598 | 192.2685 | 4.8 | 10.8084 | 1.0568 | 0.16661
2015-08-07 17:00 | 179.1333 | 112.1333 | 67 | 238.3047 | 16.5899 | 89.2077 | 73.671 | 16.329 | 93.075 | 84.4915 | 22.8759 | 84.1 | 0.2 | 0 | 8.9567 | 115.9325 | 4 | 7.6229 | 1.0695 | 0.10167
2015-08-07 18:00 | 141.07 | 85.12 | 55.95 | 248.7532 | 16.5783 | 104.2088 | 77.0017 | 12.9983 | 107.5332 | 98.1492 | 0 | 63.84 | 0.2 | 0 | 7.0535 | 70.8935 | 4.3 | 6.5154 | 1.0739 | 0.062431
2015-08-07 19:00 | 107.5267 | 66.81 | 40.7167 | 236.3123 | 16.5668 | 119.21 | 80.0784 | 9.9216 | 121.8637 | 111.3576 | 0 | 50.1075 | 0.2 | 0 | 5.3763 | 55.4838 | 3.8 | 5.5339 | 1.0779 | 0.049039
2015-08-07 20:00 | 73.9833 | 48.5 | 25.4833 | 200.8735 | 16.5552 | 134.2111 | 82.7117 | 7.2883 | 136.1591 | 123.7904 | 0 | 36.375 | 0.2 | 0 | 3.6992 | 40.0742 | 4.4 | 5.6523 | 1.0774 | 0.035404
2015-08-07 21:00 | 40.44 | 30.19 | 10.25 | 111.7849 | 16.5436 | 149.2123 | 84.7389 | 5.2611 | 150.4788 | 134.7949 | 0 | 22.6425 | 0.2 | 0 | 2.022 | 24.6645 | 4.6 | 5.3708 | 1.0785 | 0.021813
2015-08-07 22:00 | 36.2233 | 25.4133 | 10.81 | 156.2595 | 16.532 | 164.2134 | 86.0331 | 3.9669 | 164.8448 | 143.0646 | 0 | 19.06 | 0.2 | 0 | 1.8112 | 20.8712 | 4.5 | 5.1522 | 1.0794 | 0.018473
2015-08-07 23:00 | 32.0067 | 20.6367 | 11.37 | 186.873 | 16.5204 | 179.2146 | 86.5118 | 3.4882 | 179.2456 | 146.504 | 0 | 15.4775 | 0.2 | 0 | 1.6003 | 17.0778 | 4.7 | 5.2337 | 1.0791 | 0.015111
2015-08-08 | 27.79 | 15.86 | 11.93 | 177.4188 | 16.5088 | -165.7843 | 86.1444 | 3.8556 | -166.3504 | 143.7109 | 0 | 11.895 | 0.2 | 0 | 1.3895 | 13.2845 | 4.8 | 5.2151 | 1.0791 | 0.011755
2015-08-08 01:00 | 54.3967 | 23.4533 | 30.9433 | 351.9159 | 16.4972 | -150.7831 | 84.9556 | 5.0444 | -151.9759 | 135.8533 | 0 | 17.59 | 0.2 | 0 | 2.7198 | 20.3098 | 3.2 | 3.8347 | 1.0847 | 0.018064
2015-08-08 02:00 | 81.0033 | 31.0467 | 49.9567 | 411.231 | 16.4855 | -135.782 | 83.0224 | 6.9776 | -137.6458 | 125.0651 | 0 | 23.285 | 0.2 | 0 | 4.0502 | 27.3352 | 3.4 | 4.2542 | 1.083 | 0.024275
2015-08-08 03:00 | 107.61 | 38.64 | 68.97 | 416.4821 | 16.4739 | -120.7808 | 80.4678 | 9.5322 | -123.3427 | 112.7452 | 0 | 28.98 | 0.2 | 0 | 5.3805 | 34.3605 | 2.5 | 3.5738 | 1.0857 | 0.03059
2015-08-08 04:00 | 119.47 | 65.6867 | 53.7833 | 247.5404 | 16.4623 | -105.7796 | 77.4512 | 12.5488 | -109.0117 | 99.5985 | 0 | 49.265 | 0.2 | 0 | 5.9735 | 55.2385 | 2.5 | 4.2262 | 1.0831 | 0.049059
2015-08-08 05:00 | 131.33 | 92.7333 | 38.5967 | 141.4028 | 16.4506 | -90.7784 | 74.1598 | 15.8402 | -94.5644 | 85.9759 | 9.9232 | 69.55 | 0.2 | 0 | 6.5665 | 86.0397 | 3.3 | 5.9887 | 1.076 | 0.075918
2015-08-08 06:00 | 143.19 | 119.78 | 23.41 | 71.1882 | 16.439 | -75.7772 | 70.8012 | 19.1988 | -79.8911 | 72.0628 | 21.9241 | 89.835 | 0.2 | 0 | 7.1595 | 118.9186 | 3.6 | 7.3162 | 1.0707 | 0.10441
2015-08-08 07:00 | 177.2367 | 156.95 | 20.2867 | 53.2287 | 16.4273 | -60.776 | 67.5968 | 22.4032 | -64.8814 | 57.965 | 28.2345 | 117.7125 | 0.2 | 0 | 8.8618 | 154.8088 | 3.2 | 8.0378 | 1.0678 | 0.13556
2015-08-08 08:00 | 211.2833 | 194.12 | 17.1633 | 40.2701 | 16.4156 | -45.7748 | 64.773 | 25.227 | -49.4523 | 43.7474 | 29.0909 | 145.59 | 0.2 | 0 | 10.5642 | 185.2451 | 4.4 | 10.1889 | 1.0592 | 0.1609
2015-08-08 09:00 | 245.33 | 231.29 | 14.04 | 30.4549 | 16.404 | -30.7736 | 62.5477 | 27.4523 | -33.5801 | 29.4532 | 26.5189 | 173.4675 | 0.2 | 0 | 12.2665 | 212.2529 | 3.5 | 10.1329 | 1.0595 | 0.1844
2015-08-08 10:00 | 249.6933 | 236.8267 | 12.8667 | 26.6309 | 16.3923 | -15.7724 | 61.1088 | 28.8912 | -17.3278 | 15.1157 | 25.7095 | 177.62 | 0.2 | 0 | 12.4847 | 215.8142 | 3.6 | 10.3442 | 1.0586 | 0.18734
2015-08-08 11:00 | 254.0567 | 242.3633 | 11.6933 | 23.8107 | 16.3806 | -0.77123 | 60.5874 | 29.4126 | -0.84942 | 0.94304 | 23.8075 | 181.7725 | 0.2 | 0 | 12.7028 | 218.2828 | 3.2 | 10.0213 | 1.0599 | 0.18972
2015-08-08 12:00 | 258.42 | 247.9 | 10.52 | 21.7221 | 16.3689 | 14.23 | 61.0335 | 28.9665 | 15.6389 | 13.6422 | 21.1093 | 185.925 | 0.2 | 0 | 12.921 | 219.9553 | 3.9 | 10.7736 | 1.0569 | 0.19063
2015-08-08 13:00 | 241.1733 | 205.5 | 35.6733 | 77.0144 | 16.3572 | 29.2312 | 62.406 | 27.594 | 31.9183 | 27.9848 | 68.0093 | 154.125 | 0.2 | 0 | 12.0587 | 234.1929 | 4.8 | 12.1185 | 1.0515 | 0.20193
2015-08-08 14:00 | 223.9267 | 163.1 | 60.8267 | 141.7097 | 16.3455 | 44.2324 | 64.581 | 25.419 | 47.8271 | 42.2895 | 104.8304 | 122.325 | 0.2 | 0 | 11.1963 | 238.3518 | 4.2 | 11.6485 | 1.0534 | 0.20589
2015-08-08 15:00 | 206.68 | 120.7 | 85.98 | 223.5035 | 16.3337 | 59.2337 | 67.3754 | 22.6246 | 63.2943 | 56.5236 | 123.2832 | 90.525 | 0.2 | 0 | 10.334 | 224.1422 | 4.3 | 11.3044 | 1.0548 | 0.19387
2015-08-08 16:00 | 173.82 | 95.4467 | 78.3733 | 235.6398 | 16.322 | 74.2349 | 70.5735 | 19.4265 | 78.3368 | 70.6459 | 78.0924 | 71.585 | 0.2 | 0 | 8.691 | 158.3684 | 3.7 | 8.649 | 1.0654 | 0.13836
2015-08-08 17:00 | 140.96 | 70.1933 | 70.7667 | 255.947 | 16.3103 | 89.2361 | 73.9492 | 16.0508 | 93.0342 | 84.5952 | 24.108 | 52.645 | 0.2 | 0 | 7.048 | 83.801 | 4.3 | 6.9188 | 1.0723 | 0.073687
2015-08-08 18:00 | 108.1 | 44.94 | 63.16 | 286.8595 | 16.2985 | 104.2374 | 77.2805 | 12.7195 | 107.4962 | 98.2728 | 0 | 33.705 | 0.2 | 0 | 5.405 | 39.11 | 5 | 6.2222 | 1.0751 | 0.034479
2015-08-08 19:00 | 83.5667 | 35.93 | 47.6367 | 284.4198 | 16.2868 | 119.2386 | 80.3583 | 9.6417 | 121.8343 | 111.5062 | 0 | 26.9475 | 0.2 | 0 | 4.1783 | 31.1258 | 5.5 | 6.4727 | 1.0741 | 0.027415
2015-08-08 20:00 | 59.0333 | 26.92 | 32.1133 | 263.2292 | 16.275 | 134.2399 | 82.9926 | 7.0074 | 136.1405 | 123.9713 | 0 | 20.19 | 0.2 | 0 | 2.9517 | 23.1417 | 5.4 | 6.1232 | 1.0755 | 0.020409
2015-08-08 21:00 | 34.5 | 17.91 | 16.59 | 191.1349 | 16.2632 | 149.2411 | 85.0206 | 4.9794 | 150.4738 | 135.0167 | 0 | 13.4325 | 0.2 | 0 | 1.725 | 15.1575 | 5.5 | 5.9737 | 1.0761 | 0.013375
2015-08-08 22:00 | 28.4467 | 14.77 | 13.6767 | 212.7874 | 16.2515 | 164.2424 | 86.3148 | 3.6852 | 164.8553 | 143.3294 | 0 | 11.0775 | 0.2 | 0 | 1.4223 | 12.4998 | 5.8 | 6.1906 | 1.0752 | 0.011021
2015-08-08 23:00 | 22.3933 | 11.63 | 10.7633 | 192.3712 | 16.2397 | 179.2436 | 86.7926 | 3.2074 | 179.2727 | 146.7853 | 0 | 8.7225 | 0.2 | 0 | 1.1197 | 9.8422 | 6 | 6.3076 | 1.0748 | 0.008674
2015-08-09 | 16.34 | 8.49 | 7.85 | 125.8329 | 16.2279 | -165.7551 | 86.4233 | 3.5767 | -166.3067 | 143.9573 | 0 | 6.3675 | 0.2 | 0 | 0.817 | 7.1845 | 5.7 | 5.9245 | 1.0763 | 0.0063408
2015-08-09 01:00 | 32.2867 | 13.7033 | 18.5833 | 223.5608 | 16.2161 | -150.7538 | 85.2318 | 4.7682 | -151.9167 | 136.0426 | 0 | 10.2775 | 0.2 | 0 | 1.6143 | 11.8918 | 5.6 | 5.9716 | 1.0761 | 0.010494
2015-08-09 02:00 | 48.2333 | 18.9167 | 29.3167 | 251.1155 | 16.2043 | -135.7525 | 83.2957 | 6.7043 | -137.5729 | 125.2048 | 0 | 14.1875 | 0.2 | 0 | 2.4117 | 16.5992 | 5.4 | 5.9187 | 1.0763 | 0.01465
2015-08-09 03:00 | 64.18 | 24.13 | 40.05 | 248.8423 | 16.1925 | -120.7513 | 80.7382 | 9.2618 | -123.2585 | 112.8475 | 0 | 18.0975 | 0.2 | 0 | 3.209 | 21.3065 | 5.6 | 6.2658 | 1.0749 | 0.018781
2015-08-09 04:00 | 61.5833 | 34.42 | 27.1633 | 127.7083 | 16.1806 | -105.75 | 77.7195 | 12.2805 | -108.9193 | 99.6728 | 0 | 25.815 | 0.2 | 0 | 3.0792 | 28.8942 | 5.9 | 6.8029 | 1.0728 | 0.025418
2015-08-09 05:00 | 58.9867 | 44.71 | 14.2767 | 53.179 | 16.1688 | -90.7487 | 74.4271 | 15.5729 | -94.467 | 86.0286 | 3.6831 | 33.5325 | 0.2 | 0 | 2.9493 | 40.1649 | 5.5 | 6.7552 | 1.073 | 0.035339
2015-08-09 06:00 | 56.39 | 55 | 1.39 | 4.2844 | 16.157 | -75.7474 | 71.0689 | 18.9311 | -79.7926 | 72.0983 | 1.317 | 41.25 | 0.2 | 0 | 2.8195 | 45.3865 | 4.9 | 6.3183 | 1.0747 | 0.039998
2015-08-09 07:00 | 74.29 | 72.82 | 1.47 | 3.9016 | 16.1451 | -60.7461 | 67.8664 | 22.1336 | -64.7862 | 57.9863 | 2.0683 | 54.615 | 0.2 | 0 | 3.7145 | 60.3978 | 4.8 | 6.6874 | 1.0733 | 0.053154
2015-08-09 08:00 | 92.19 | 90.64 | 1.55 | 3.6739 | 16.1333 | -45.7448 | 65.0457 | 24.9543 | -49.3653 | 43.7568 | 2.6536 | 67.98 | 0.2 | 0 | 4.6095 | 75.2431 | 4.1 | 6.4513 | 1.0742 | 0.066277
2015-08-09 09:00 | 110.09 | 108.46 | 1.63 | 3.5689 | 16.1214 | -30.7435 | 62.8241 | 27.1759 | -33.5065 | 29.4531 | 3.1077 | 81.345 | 0.2 | 0 | 5.5045 | 89.9572 | 3.5 | 6.3112 | 1.0748 | 0.079279
2015-08-09 10:00 | 119.0833 | 115.1533 | 3.93 | 8.2069 | 16.1096 | -15.7421 | 61.3888 | 28.6112 | -17.2722 | 15.1112 | 7.9232 | 86.365 | 0.2 | 0 | 5.9542 | 100.2423 | 3.9 | 7.0326 | 1.0719 | 0.088106
2015-08-09 11:00 | 128.0767 | 121.8467 | 6.23 | 12.7981 | 16.0977 | -0.74082 | 60.8702 | 29.1298 | -0.81484 | 1.1223 | 12.7957 | 91.385 | 0.2 | 0 | 6.4038 | 110.5845 | 3.5 | 6.9558 | 1.0722 | 0.097224
2015-08-09 12:00 | 137.07 | 128.54 | 8.53 | 17.7727 | 16.0858 | 14.2605 | 61.3179 | 28.6821 | 15.6518 | 13.6967 | 17.2673 | 96.405 | 0.2 | 0 | 6.8535 | 120.5258 | 3.4 | 7.1664 | 1.0713 | 0.10588
2015-08-09 13:00 | 132.9433 | 125.12 | 7.8233 | 17.052 | 16.0739 | 29.2618 | 62.6907 | 27.3093 | 31.9115 | 28.0425 | 15.05 | 93.84 | 0.2 | 0 | 6.6472 | 115.5372 | 3.6 | 7.2105 | 1.0712 | 0.10148
2015-08-09 14:00 | 128.8167 | 121.7 | 7.1167 | 16.755 | 16.062 | 44.2632 | 64.8653 | 25.1347 | 47.8047 | 42.3562 | 12.3815 | 91.275 | 0.2 | 0 | 6.4408 | 110.0973 | 3.5 | 6.9405 | 1.0722 | 0.096801
2015-08-09 15:00 | 124.69 | 118.28 | 6.41 | 16.8631 | 16.0501 | 59.2645 | 67.6589 | 22.3411 | 63.2613 | 56.6016 | 9.2824 | 88.71 | 0.2 | 0 | 6.2345 | 104.2269 | 3.4 | 6.6571 | 1.0734 | 0.091737
2015-08-09 16:00 | 116.0033 | 88.71 | 27.2933 | 83.2278 | 16.0382 | 74.2658 | 70.8565 | 19.1435 | 78.2983 | 70.7374 | 27.4567 | 66.5325 | 0.2 | 0 | 5.8002 | 99.7894 | 3.9 | 7.0184 | 1.0719 | 0.087713
2015-08-09 17:00 | 107.3167 | 59.14 | 48.1767 | 177.2906 | 16.0263 | 89.2672 | 74.2323 | 15.7677 | 92.9951 | 84.7028 | 16.3677 | 44.355 | 0.2 | 0 | 5.3658 | 66.0885 | 3.5 | 5.5653 | 1.0777 | 0.058405
2015-08-09 18:00 | 98.63 | 29.57 | 69.06 | 320.6936 | 16.0144 | 104.2685 | 77.5642 | 12.4358 | 107.4609 | 98.4001 | 0 | 22.1775 | 0.2 | 0 | 4.9315 | 27.109 | 3 | 3.8472 | 1.0846 | 0.02411
2015-08-09 19:00 | 73.4 | 23.3733 | 50.0267 | 307.6901 | 16.0024 | 119.2699 | 80.6429 | 9.3571 | 121.8067 | 111.6586 | 0 | 17.53 | 0.2 | 0 | 3.67 | 21.2 | 2.4 | 3.0625 | 1.0877 | 0.018909
2015-08-09 20:00 | 48.17 | 17.1767 | 30.9933 | 264.7912 | 15.9905 | 134.2713 | 83.2782 | 6.7218 | 136.1239 | 124.1562 | 0 | 12.8825 | 0.2 | 0 | 2.4085 | 15.291 | 2.3 | 2.7778 | 1.0889 | 0.013653
2015-08-09 21:00 | 22.94 | 10.98 | 11.96 | 146.1771 | 15.9785 | 149.2726 | 85.3069 | 4.6931 | 150.4709 | 135.2429 | 0 | 8.235 | 0.2 | 0 | 1.147 | 9.382 | 2.4 | 2.6932 | 1.0892 | 0.0083797
2015-08-09 22:00 | 21.2 | 10.92 | 10.28 | 173.39 | 15.9666 | 164.274 | 86.601 | 3.399 | 164.8682 | 143.599 | 0 | 8.19 | 0.2 | 0 | 1.06 | 9.25 | 2.6 | 2.8891 | 1.0884 | 0.0082558
2015-08-09 23:00 | 19.46 | 10.86 | 8.6 | 0 | 15.9546 | 179.2754 | 87.0777 | 2.9223 | 179.3024 | 147.071 | 0 | 8.145 | 0.2 | 0 | 0.973 | 9.118 | 2.5 | 2.7849 | 1.0889 | 0.0081411
2015-08-10 | 17.72 | 10.8 | 6.92 | 120.4474 | 15.9427 | -165.7232 | 86.7064 | 3.2936 | -166.2602 | 144.2063 | 0 | 8.1 | 0.2 | 0 | 0.886 | 8.986 | 2.3 | 2.5808 | 1.0897 | 0.0080293
2015-08-10 01:00 | 32.7433 | 22.3 | 10.4433 | 133.4632 | 15.9307 | -150.7219 | 85.5121 | 4.4879 | -151.8544 | 136.2326 | 0 | 16.725 | 0.2 | 0 | 1.6372 | 18.3622 | 2.2 | 2.7738 | 1.0889 | 0.016396
2015-08-10 02:00 | 47.7667 | 33.8 | 13.9667 | 124.7678 | 15.9187 | -135.7205 | 83.5728 | 6.4272 | -137.4967 | 125.344 | 0 | 25.35 | 0.2 | 0 | 2.3883 | 27.7383 | 2.8 | 3.6668 | 1.0853 | 0.024686
2015-08-10 03:00 | 62.79 | 45.3 | 17.49 | 111.9565 | 15.9067 | -120.7191 | 81.0124 | 8.9876 | -123.171 | 112.9488 | 0 | 33.975 | 0.2 | 0 | 3.1395 | 37.1145 | 2.6 | 3.7598 | 1.085 | 0.03302
2015-08-10 04:00 | 77.19 | 65.1667 | 12.0233 | 57.7882 | 15.8947 | -105.7177 | 77.9914 | 12.0086 | -108.8234 | 99.746 | 0 | 48.875 | 0.2 | 0 | 3.8595 | 52.7345 | 2.5 | 4.148 | 1.0834 | 0.046849
2015-08-10 05:00 | 91.59 | 85.0333 | 6.5567 | 24.8446 | 15.8827 | -90.7163 | 74.698 | 15.302 | -94.3662 | 86.0802 | 1.6984 | 63.775 | 0.2 | 0 | 4.5795 | 70.0529 | 2.5 | 4.6892 | 1.0812 | 0.06211
2015-08-10 06:00 | 105.99 | 104.9 | 1.09 | 3.4068 | 15.8707 | -75.7149 | 71.3403 | 18.6597 | -79.6906 | 72.1327 | 1.0453 | 78.675 | 0.2 | 0 | 5.2995 | 85.0198 | 3.7 | 6.3569 | 1.0746 | 0.074915
2015-08-10 07:00 | 127.3367 | 119.56 | 7.7767 | 20.8856 | 15.8587 | -60.7135 | 68.1397 | 21.8603 | -64.6876 | 58.0067 | 11.0656 | 89.67 | 0.2 | 0 | 6.3668 | 107.1025 | 3.5 | 6.847 | 1.0726 | 0.094201
2015-08-10 08:00 | 148.6833 | 134.22 | 14.4633 | 34.6414 | 15.8466 | -45.712 | 65.3222 | 24.6778 | -49.275 | 43.7657 | 25.0172 | 100.665 | 0.2 | 0 | 7.4342 | 133.1163 | 2.8 | 6.9599 | 1.0722 | 0.11703
2015-08-10 09:00 | 170.03 | 148.88 | 21.15 | 46.7543 | 15.8346 | -30.7106 | 63.1045 | 26.8955 | -33.4297 | 29.4533 | 40.7116 | 111.66 | 0.2 | 0 | 8.5015 | 160.8731 | 3.3 | 8.3273 | 1.0667 | 0.14071
2015-08-10 10:00 | 178.42 | 153.07 | 25.35 | 53.4242 | 15.8226 | -15.7092 | 61.6729 | 28.3271 | -17.2135 | 15.1098 | 51.5772 | 114.8025 | 0.2 | 0 | 8.921 | 175.3007 | 3.5 | 8.9781 | 1.0641 | 0.15296
2015-08-10 11:00 | 186.81 | 157.26 | 29.55 | 61.2553 | 15.8105 | -0.70777 | 61.1572 | 28.8428 | -0.77744 | 1.3408 | 61.2385 | 117.945 | 0.2 | 0 | 9.3405 | 188.524 | 3.8 | 9.6914 | 1.0612 | 0.16406
2015-08-10 12:00 | 195.2 | 161.45 | 33.75 | 70.9746 | 15.7984 | 14.2937 | 61.6067 | 28.3933 | 15.6673 | 13.7599 | 68.9377 | 121.0875 | 0.2 | 0 | 9.76 | 199.7852 | 3.4 | 9.6433 | 1.0614 | 0.17389
2015-08-10 13:00 | 187.1967 | 163.61 | 23.5867 | 51.9185 | 15.7864 | 29.2951 | 62.98 | 27.02 | 31.9071 | 28.1058 | 45.7962 | 122.7075 | 0.2 | 0 | 9.3598 | 177.8636 | 3.9 | 9.4582 | 1.0622 | 0.15492
2015-08-10 14:00 | 179.1933 | 165.77 | 13.4233 | 31.9468 | 15.7743 | 44.2965 | 65.1542 | 24.8458 | 47.7844 | 42.4276 | 23.5809 | 124.3275 | 0.2 | 0 | 8.9597 | 156.8681 | 3.7 | 8.6021 | 1.0656 | 0.13707
2015-08-10 15:00 | 171.19 | 167.93 | 3.26 | 8.6826 | 15.7622 | 59.298 | 67.9471 | 22.0529 | 63.2302 | 56.6839 | 4.769 | 125.9475 | 0.2 | 0 | 8.5595 | 139.276 | 4.5 | 8.8524 | 1.0646 | 0.12158
2015-08-10 16:00 | 159.63 | 127.2467 | 32.3833 | 100.2002 | 15.7501 | 74.2994 | 71.1443 | 18.8557 | 78.2617 | 70.8329 | 32.8982 | 95.435 | 0.2 | 0 | 7.9815 | 136.3147 | 4.3 | 8.5598 | 1.0658 | 0.11913
2015-08-10 17:00 | 148.07 | 86.5633 | 61.5067 | 230.4477 | 15.7381 | 89.3009 | 74.5201 | 15.4799 | 92.9578 | 84.8143 | 20.8289 | 64.9225 | 0.2 | 0 | 7.4035 | 93.1549 | 3.7 | 6.6111 | 1.0736 | 0.082006
2015-08-10 18:00 | 136.51 | 45.88 | 90.63 | 430.6938 | 15.7259 | 104.3024 | 77.8526 | 12.1474 | 107.4273 | 98.5313 | 0 | 34.41 | 0.2 | 0 | 6.8255 | 41.2355 | 4.3 | 5.5886 | 1.0776 | 0.036439
2015-08-10 19:00 | 97.15 | 35.8 | 61.35 | 389.2676 | 15.7138 | 119.3038 | 80.9322 | 9.0678 | 121.7808 | 111.8148 | 0 | 26.85 | 0.2 | 0 | 4.8575 | 31.7075 | 3.6 | 4.5909 | 1.0816 | 0.028123
2015-08-10 20:00 | 57.79 | 25.72 | 32.07 | 286.2989 | 15.7017 | 134.3053 | 83.5685 | 6.4315 | 136.1092 | 124.3451 | 0 | 19.29 | 0.2 | 0 | 2.8895 | 22.1795 | 3.7 | 4.3931 | 1.0824 | 0.019686
2015-08-10 21:00 | 18.43 | 15.64 | 2.79 | 36.3475 | 15.6896 | 149.3068 | 85.5977 | 4.4023 | 150.4702 | 135.4734 | 0 | 11.73 | 0.2 | 0 | 0.9215 | 12.6515 | 3.3 | 3.6954 | 1.0852 | 0.011258
2015-08-10 22:00 | 13.63 | 11.75 | 1.88 | 34.6705 | 15.6775 | 164.3083 | 86.8916 | 3.1084 | 164.8834 | 143.8734 | 0 | 8.8125 | 0.2 | 0 | 0.6815 | 9.494 | 4 | 4.2967 | 1.0828 | 0.0084298
2015-08-10 23:00 | 8.83 | 7.86 | 0.97 | 0 | 15.6653 | 179.3097 | 87.3671 | 2.6329 | 179.3347 | 147.3609 | 0 | 5.895 | 0.2 | 0 | 0.4415 | 6.3365 | 5.7 | 5.898 | 1.0764 | 0.0055929
2015-08-11 | 4.03 | 3.97 | 0.06 | 1.144 | 15.6532 | -165.6888 | 86.9936 | 3.0064 | -166.2109 | 144.4575 | 0 | 2.9775 | 0.2 | 0 | 0.2015 | 3.179 | 6.2 | 6.2993 | 1.0748 | 0.0028018
2015-08-11 01:00 | 7.4633 | 7.41 | 0.053333 | 0.72757 | 15.641 | -150.6873 | 85.7963 | 4.2037 | -151.7891 | 136.423 | 0 | 5.5575 | 0.2 | 0 | 0.37317 | 5.9307 | 6.9 | 7.0853 | 1.0717 | 0.0052116
2015-08-11 02:00 | 10.8967 | 10.85 | 0.046667 | 0.43586 | 15.6289 | -135.6858 | 83.8536 | 6.1464 | -137.4173 | 125.4826 | 0 | 8.1375 | 0.2 | 0 | 0.54483 | 8.6823 | 7 | 7.2713 | 1.0709 | 0.0076244
2015-08-11 03:00 | 14.33 | 14.29 | 0.04 | 0.26415 | 15.6167 | -120.6843 | 81.2901 | 8.7099 | -123.0802 | 113.0491 | 0 | 10.7175 | 0.2 | 0 | 0.7165 | 11.434 | 7.8 | 8.1573 | 1.0674 | 0.010008
2015-08-11 04:00 | 26.7933 | 25.1067 | 1.6867 | 8.2943 | 15.6045 | -105.6828 | 78.2669 | 11.7331 | -108.7241 | 99.818 | 0 | 18.83 | 0.2 | 0 | 1.3397 | 20.1697 | 7.9 | 8.5303 | 1.0659 | 0.017629
2015-08-11 05:00 | 39.2567 | 35.9233 | 3.3333 | 12.8559 | 15.5924 | -90.6813 | 74.9724 | 15.0276 | -94.2619 | 86.1305 | 0.86756 | 26.9425 | 0.2 | 0 | 1.9628 | 29.7729 | 7.5 | 8.4304 | 1.0663 | 0.026032
2015-08-11 06:00 | 51.72 | 46.74 | 4.98 | 15.7896 | 15.5802 | -75.6797 | 71.6152 | 18.3848 | -79.5853 | 72.166 | 4.8357 | 35.055 | 0.2 | 0 | 2.586 | 42.4767 | 6.4 | 7.7274 | 1.0691 | 0.037237
2015-08-11 07:00 | 66.0767 | 62.7033 | 3.3733 | 9.1703 | 15.568 | -60.6782 | 68.4166 | 21.5834 | -64.5856 | 58.0261 | 4.856 | 47.0275 | 0.2 | 0 | 3.3038 | 55.1873 | 5.7 | 7.4246 | 1.0703 | 0.048435
2015-08-11 08:00 | 80.4333 | 78.6667 | 1.7667 | 4.277 | 15.5558 | -45.6767 | 65.6024 | 24.3976 | -49.1814 | 43.7741 | 3.0883 | 59 | 0.2 | 0 | 4.0217 | 66.1099 | 5.1 | 7.1659 | 1.0713 | 0.058077
2015-08-11 09:00 | 94.79 | 94.63 | 0.16 | 0.35719 | 15.5436 | -30.6752 | 63.3887 | 26.6113 | -33.3498 | 29.4541 | 0.31103 | 70.9725 | 0.2 | 0 | 4.7395 | 76.023 | 4.4 | 6.7757 | 1.0729 | 0.066883
2015-08-11 10:00 | 109.4533 | 104.5933 | 4.86 | 10.3389 | 15.5314 | -15.6736 | 61.9611 | 28.0389 | -17.1519 | 15.1117 | 9.9813 | 78.445 | 0.2 | 0 | 5.4727 | 93.899 | 4.3 | 7.2343 | 1.0711 | 0.082469
2015-08-11 11:00 | 124.1167 | 114.5567 | 9.56 | 20.0022 | 15.5191 | -0.6721 | 61.4485 | 28.5515 | -0.73726 | 1.5848 | 19.9945 | 85.9175 | 0.2 | 0 | 6.2058 | 112.1178 | 3.7 | 7.2037 | 1.0712 | 0.098481
2015-08-11 12:00 | 138.78 | 124.52 | 14.26 | 30.275 | 15.5069 | 14.3294 | 61.8998 | 28.1002 | 15.6854 | 13.8319 | 29.3971 | 93.39 | 0.2 | 0 | 6.939 | 129.7261 | 3.5 | 7.5539 | 1.0698 | 0.1138
2015-08-11 13:00 | 137.06 | 127.4 | 9.66 | 21.4796 | 15.4947 | 29.331 | 63.2737 | 26.7263 | 31.9051 | 28.1749 | 18.9345 | 95.55 | 0.2 | 0 | 6.853 | 121.3375 | 3.7 | 7.4918 | 1.07 | 0.10646
2015-08-11 14:00 | 135.34 | 130.28 | 5.06 | 12.1774 | 15.4824 | 44.3325 | 65.4477 | 24.5523 | 47.7663 | 42.5037 | 8.9776 | 97.71 | 0.2 | 0 | 6.767 | 113.4546 | 3 | 6.5455 | 1.0738 | 0.0999
2015-08-11 15:00 | 133.62 | 133.16 | 0.46 | 1.2408 | 15.4702 | 59.3341 | 68.24 | 21.76 | 63.201 | 56.7704 | 0.67997 | 99.87 | 0.2 | 0 | 6.681 | 107.231 | 3.3 | 6.651 | 1.0734 | 0.094383
2015-08-11 16:00 | 112.1333 | 107.5133 | 4.62 | 14.5122 | 15.4579 | 74.3357 | 71.4367 | 18.5633 | 78.2268 | 70.9323 | 4.7409 | 80.635 | 0.2 | 0 | 5.6067 | 90.9826 | 2.9 | 5.7432 | 1.077 | 0.080352
2015-08-11 17:00 | 90.6467 | 81.8667 | 8.78 | 33.5143 | 15.4456 | 89.3372 | 74.8126 | 15.1874 | 92.9221 | 84.9295 | 2.9621 | 61.4 | 0.2 | 0 | 4.5323 | 68.8944 | 2.7 | 4.8529 | 1.0806 | 0.061046
2015-08-11 18:00 | 69.16 | 56.22 | 12.94 | 62.9912 | 15.4334 | 104.3388 | 78.1456 | 11.8544 | 107.3955 | 98.6662 | 0 | 42.165 | 0.2 | 0 | 3.458 | 45.623 | 2.4 | 3.8257 | 1.0847 | 0.040579
2015-08-11 19:00 | 51.38 | 42.3433 | 9.0367 | 59.2428 | 15.4211 | 119.3404 | 81.2261 | 8.7739 | 121.7567 | 111.9748 | 0 | 31.7575 | 0.2 | 0 | 2.569 | 34.3265 | 2.7 | 3.7727 | 1.0849 | 0.030538
2015-08-11 20:00 | 33.6 | 28.4667 | 5.1333 | 48.0191 | 15.4088 | 134.3419 | 83.8632 | 6.1368 | 136.0964 | 124.5379 | 0 | 21.35 | 0.2 | 0 | 1.68 | 23.03 | 2.6 | 3.3197 | 1.0867 | 0.020522
2015-08-11 21:00 | 15.82 | 14.59 | 1.23 | 17.1738 | 15.3965 | 149.3435 | 85.8929 | 4.1071 | 150.4715 | 135.7082 | 0 | 10.9425 | 0.2 | 0 | 0.791 | 11.7335 | 2.6 | 2.9667 | 1.0881 | 0.010469
2015-08-11 22:00 | 13.8633 | 12.86 | 1.0033 | 0 | 15.3842 | 164.3451 | 87.1865 | 2.8135 | 164.901 | 144.1524 | 0 | 9.645 | 0.2 | 0 | 0.69317 | 10.3382 | 1.9 | 2.2231 | 1.0911 | 0.0092496
2015-08-11 23:00 | 11.9067 | 11.13 | 0.77667 | 0 | 15.3719 | 179.3467 | 87.6606 | 2.3394 | 179.3696 | 147.655 | 0 | 8.3475 | 0.2 | 0 | 0.59533 | 8.9428 | 2.4 | 2.6795 | 1.0893 | 0.0079878
2015-08-12 | 9.95 | 9.4 | 0.55 | 0 | 15.3596 | -165.6517 | 87.2847 | 2.7153 | -166.1587 | 144.7109 | 0 | 7.05 | 0.2 | 0 | 0.4975 | 7.5475 | 2.5 | 2.7359 | 1.0891 | 0.0067401
2015-08-12 01:00 | 27.3933 | 19.6333 | 7.76 | 113.6344 | 15.3473 | -150.6501 | 86.0843 | 3.9157 | -151.7208 | 136.6137 | 0 | 14.725 | 0.2 | 0 | 1.3697 | 16.0947 | 2.4 | 2.903 | 1.0884 | 0.014364
2015-08-12 02:00 | 44.8367 | 29.8667 | 14.97 | 146.5782 | 15.3349 | -135.6485 | 84.1382 | 5.8618 | -137.3348 | 125.6207 | 0 | 22.4 | 0.2 | 0 | 2.2418 | 24.6418 | 2.5 | 3.2701 | 1.0869 | 0.021963
2015-08-12 03:00 | 62.28 | 40.1 | 22.18 | 151.3213 | 15.3226 | -120.6469 | 81.5715 | 8.4285 | -122.9861 | 113.1484 | 0 | 30.075 | 0.2 | 0 | 3.114 | 33.189 | 3 | 4.0372 | 1.0839 | 0.029497
2015-08-12 04:00 | 77.2333 | 61.8333 | 15.4 | 77.549 | 15.3102 | -105.6453 | 78.5458 | 11.4542 | -108.6215 | 99.8888 | 0 | 46.375 | 0.2 | 0 | 3.8617 | 50.2367 | 3.1 | 4.6699 | 1.0813 | 0.044544
2015-08-12 05:00 | 92.1867 | 83.5667 | 8.62 | 33.8574 | 15.2979 | -90.6436 | 75.2503 | 14.7497 | -94.1543 | 86.1797 | 2.2559 | 62.675 | 0.2 | 0 | 4.6093 | 69.5402 | 3.3 | 5.4731 | 1.0781 | 0.061477
2015-08-12 06:00 | 107.14 | 105.3 | 1.84 | 5.9205 | 15.2855 | -75.642 | 71.8935 | 18.1065 | -79.4767 | 72.1981 | 1.8101 | 78.975 | 0.2 | 0 | 5.357 | 86.1421 | 3.9 | 6.5919 | 1.0736 | 0.075838
2015-08-12 07:00 | 123.1933 | 109.0133 | 14.18 | 39.0312 | 15.2732 | -60.6404 | 68.697 | 21.303 | -64.4804 | 58.0447 | 20.6575 | 81.76 | 0.2 | 0 | 6.1597 | 108.5772 | 3.2 | 6.593 | 1.0736 | 0.095589
2015-08-12 08:00 | 139.2467 | 112.7267 | 26.52 | 64.9125 | 15.2608 | -45.6388 | 65.8862 | 24.1138 | -49.0847 | 43.7821 | 46.8653 | 84.545 | 0.2 | 0 | 6.9623 | 138.3726 | 5.5 | 9.8241 | 1.0607 | 0.12035
2015-08-12 09:00 | 155.3 | 116.44 | 38.86 | 87.6337 | 15.2484 | -30.6371 | 63.6767 | 26.3233 | -33.2668 | 29.4554 | 76.3061 | 87.33 | 0.2 | 0 | 7.765 | 171.4011 | 6.5 | 11.8563 | 1.0526 | 0.14794
2015-08-12 10:00 | 149.4233 | 122.98 | 26.4433 | 56.7983 | 15.236 | -15.6355 | 62.2532 | 27.7468 | -17.0874 | 15.1172 | 54.8327 | 92.235 | 0.2 | 0 | 7.4712 | 154.5389 | 6 | 10.8293 | 1.0567 | 0.1339
2015-08-12 11:00 | 143.5467 | 129.52 | 14.0267 | 29.6288 | 15.2236 | -0.63383 | 61.7439 | 28.2561 | -0.69433 | 1.8463 | 29.6134 | 97.14 | 0.2 | 0 | 7.1773 | 133.9307 | 5.6 | 9.7853 | 1.0609 | 0.11651
2015-08-12 12:00 | 137.67 | 136.06 | 1.61 | 3.4518 | 15.2112 | 14.3678 | 62.1972 | 27.8028 | 15.7061 | 13.9128 | 3.3505 | 102.045 | 0.2 | 0 | 6.8835 | 112.279 | 7.2 | 10.7087 | 1.0572 | 0.097332
2015-08-12 13:00 | 127.84 | 125.58 | 2.26 | 5.0778 | 15.1988 | 29.3695 | 63.5719 | 26.4281 | 31.9054 | 28.2497 | 4.473 | 94.185 | 0.2 | 0 | 6.392 | 105.05 | 6 | 9.2828 | 1.0629 | 0.091557
2015-08-12 14:00 | 118.01 | 115.1 | 2.91 | 7.0839 | 15.1864 | 44.3711 | 65.7456 | 24.2544 | 47.7503 | 42.5845 | 5.2158 | 86.325 | 0.2 | 0 | 5.9005 | 97.4413 | 6.3 | 9.345 | 1.0626 | 0.084905
2015-08-12 15:00 | 108.18 | 104.62 | 3.56 | 9.7296 | 15.174 | 59.3728 | 68.5375 | 21.4625 | 63.1738 | 56.8611 | 5.3189 | 78.465 | 0.2 | 0 | 5.409 | 89.1929 | 6.8 | 9.5873 | 1.0617 | 0.077647
2015-08-12 16:00 | 100.01 | 84.47 | 15.54 | 49.58 | 15.1616 | 74.3745 | 71.7338 | 18.2662 | 78.1937 | 71.0356 | 16.1125 | 63.3525 | 0.2 | 0 | 5.0005 | 84.4655 | 6.6 | 9.2395 | 1.063 | 0.073628
2015-08-12 17:00 | 91.84 | 64.32 | 27.52 | 107.094 | 15.1491 | 89.3761 | 75.1096 | 14.8904 | 92.8883 | 85.0485 | 9.2436 | 48.24 | 0.2 | 0 | 4.592 | 62.0756 | 5.2 | 7.1399 | 1.0714 | 0.054538
2015-08-12 18:00 | 83.67 | 44.17 | 39.5 | 197.1653 | 15.1367 | 104.3778 | 78.4432 | 11.5568 | 107.3654 | 98.8047 | 0 | 33.1275 | 0.2 | 0 | 4.1835 | 37.311 | 5.9 | 7.066 | 1.0717 | 0.03279
2015-08-12 19:00 | 62.43 | 33.6067 | 28.8233 | 195.5627 | 15.1242 | 119.3795 | 81.5245 | 8.4755 | 121.7345 | 112.1385 | 0 | 25.205 | 0.2 | 0 | 3.1215 | 28.3265 | 6.2 | 7.0852 | 1.0717 | 0.024892
2015-08-12 20:00 | 41.19 | 23.0433 | 18.1467 | 178.419 | 15.1118 | 134.3812 | 84.1625 | 5.8375 | 136.0855 | 124.7345 | 0 | 17.2825 | 0.2 | 0 | 2.0595 | 19.342 | 6.5 | 7.1044 | 1.0716 | 0.016996
2015-08-12 21:00 | 19.95 | 12.48 | 7.47 | 112.4921 | 15.0993 | 149.3829 | 86.1925 | 3.8075 | 150.475 | 135.9471 | 0 | 9.36 | 0.2 | 0 | 0.9975 | 10.3575 | 6.8 | 7.1237 | 1.0715 | 0.0091005
2015-08-12 22:00 | 17.19 | 10.5233 | 6.6667 | 0 | 15.0869 | 164.3846 | 87.4856 | 2.5144 | 164.9209 | 144.436 | 0 | 7.8925 | 0.2 | 0 | 0.8595 | 8.752 | 6.8 | 7.0735 | 1.0717 | 0.0076912
2015-08-12 23:00 | 14.43 | 8.5667 | 5.8633 | 0 | 15.0744 | 179.3863 | 87.9582 | 2.0418 | 179.407 | 147.9532 | 0 | 6.425 | 0.2 | 0 | 0.7215 | 7.1465 | 6.8 | 7.0233 | 1.0719 | 0.0062815
2015-08-13 | 11.67 | 6.61 | 5.06 | 0 | 15.0619 | -165.612 | 87.5798 | 2.4202 | -166.1038 | 144.9663 | 0 | 4.9575 | 0.2 | 0 | 0.5835 | 5.541 | 6.9 | 7.0732 | 1.0717 | 0.0048694
2015-08-13 01:00 | 34.1833 | 14.6033 | 19.58 | 309.77 | 15.0494 | -150.6103 | 86.376 | 3.624 | -151.6494 | 136.8047 | 0 | 10.9525 | 0.2 | 0 | 1.7092 | 12.6617 | 6.2 | 6.5957 | 1.0736 | 0.011147
2015-08-13 02:00 | 56.6967 | 22.5967 | 34.1 | 351.0911 | 15.0369 | -135.6086 | 84.4263 | 5.5737 | -137.2491 | 125.758 | 0 | 16.9475 | 0.2 | 0 | 2.8348 | 19.7823 | 7.4 | 8.0182 | 1.0679 | 0.017323
2015-08-13 03:00 | 79.21 | 30.59 | 48.62 | 343.2249 | 15.0244 | -120.6069 | 81.8563 | 8.1437 | -122.8887 | 113.2466 | 0 | 22.9425 | 0.2 | 0 | 3.9605 | 26.903 | 6.7 | 7.5407 | 1.0698 | 0.023601
2015-08-13 04:00 | 86.2233 | 39.3867 | 46.8367 | 241.7355 | 15.0119 | -105.6052 | 78.8282 | 11.1718 | -108.5157 | 99.9583 | 0 | 29.54 | 0.2 | 0 | 4.3112 | 33.8512 | 7.8 | 8.8578 | 1.0646 | 0.02955
2015-08-13 05:00 | 93.2367 | 48.1833 | 45.0533 | 180.3234 | 14.9994 | -90.6034 | 75.5315 | 14.4685 | -94.0435 | 86.2275 | 11.8643 | 36.1375 | 0.2 | 0 | 4.6618 | 52.6636 | 7 | 8.6457 | 1.0654 | 0.046009
2015-08-13 06:00 | 100.25 | 56.98 | 43.27 | 141.3563 | 14.9869 | -75.6017 | 72.1753 | 17.8247 | -79.3648 | 72.2292 | 43.1435 | 42.735 | 0.2 | 0 | 5.0125 | 90.891 | 7.8 | 10.6403 | 1.0574 | 0.078812
2015-08-13 07:00 | 120.3433 | 71.76 | 48.5833 | 135.451 | 14.9743 | -60.6 | 68.981 | 21.019 | -64.372 | 58.0625 | 71.6528 | 53.82 | 0.2 | 0 | 6.0172 | 131.4899 | 7.7 | 11.8091 | 1.0528 | 0.11351
2015-08-13 08:00 | 140.4367 | 86.54 | 53.8967 | 133.4188 | 14.9618 | -45.5982 | 66.1736 | 23.8264 | -48.9848 | 43.7899 | 96.3127 | 64.905 | 0.2 | 0 | 7.0218 | 168.2395 | 7.5 | 12.7575 | 1.049 | 0.14471
2015-08-13 09:00 | 160.53 | 101.32 | 59.21 | 134.9154 | 14.9492 | -30.5965 | 63.9683 | 26.0317 | -33.1808 | 29.4575 | 117.4736 | 75.99 | 0.2 | 0 | 8.0265 | 201.4901 | 7.1 | 13.3966 | 1.0464 | 0.17289
2015-08-13 10:00 | 177.73 | 99.43 | 78.3 | 169.8525 | 14.9367 | -15.5947 | 62.5491 | 27.4509 | -17.0199 | 15.1266 | 163.9674 | 74.5725 | 0.2 | 0 | 8.8865 | 247.4264 | 7.8 | 15.5321 | 1.0379 | 0.21057
2015-08-13 11:00 | 194.93 | 97.54 | 97.39 | 207.7413 | 14.9241 | -0.59297 | 62.0433 | 27.9567 | -0.64867 | 2.1206 | 207.599 | 73.155 | 0.2 | 0 | 9.7465 | 290.5005 | 8.4 | 17.4781 | 1.0301 | 0.24538
2015-08-13 12:00 | 212.13 | 95.65 | 116.48 | 252.2482 | 14.9116 | 14.4088 | 62.4988 | 27.5012 | 15.7292 | 14.0028 | 244.7524 | 71.7375 | 0.2 | 0 | 10.6065 | 327.0964 | 8.4 | 18.6218 | 1.0255 | 0.27506
2015-08-13 13:00 | 202.2333 | 102.8467 | 99.3867 | 225.7036 | 14.899 | 29.4105 | 63.8743 | 26.1257 | 31.908 | 28.3304 | 198.6701 | 77.135 | 0.2 | 0 | 10.1117 | 285.9168 | 8.7 | 17.6349 | 1.0295 | 0.24136
2015-08-13 14:00 | 192.3367 | 110.0433 | 82.2933 | 202.7073 | 14.8864 | 44.4123 | 66.048 | 23.952 | 47.7364 | 42.6701 | 149.0442 | 82.5325 | 0.2 | 0 | 9.6168 | 241.1936 | 10.7 | 18.2373 | 1.0271 | 0.20313
2015-08-13 15:00 | 182.44 | 117.24 | 65.2 | 180.6174 | 14.8738 | 59.4141 | 68.8394 | 21.1606 | 63.1485 | 56.956 | 98.4874 | 87.93 | 0.2 | 0 | 9.122 | 195.5394 | 7.6 | 13.7106 | 1.0452 | 0.16758
2015-08-13 16:00 | 168.7667 | 90.9067 | 77.86 | 252.4387 | 14.8612 | 74.4159 | 72.0353 | 17.9647 | 78.1624 | 71.1429 | 81.5905 | 68.18 | 0.2 | 0 | 8.4383 | 158.2088 | 5.3 | 10.244 | 1.059 | 0.13739
2015-08-13 17:00 | 155.0933 | 64.5733 | 90.52 | 359.377 | 14.8486 | 89.4176 | 75.4112 | 14.5888 | 92.8561 | 85.1712 | 30.2521 | 48.43 | 0.2 | 0 | 7.7547 | 86.4368 | 6.1 | 8.8011 | 1.0648 | 0.075471
2015-08-13 18:00 | 141.42 | 38.24 | 103.18 | 528.6629 | 14.836 | 104.4194 | 78.7452 | 11.2548 | 107.337 | 98.9469 | 0 | 28.68 | 0.2 | 0 | 7.071 | 35.751 | 6.6 | 7.7172 | 1.0691 | 0.031342
2015-08-13 19:00 | 102.5267 | 29.86 | 72.6667 | 511.1727 | 14.8234 | 119.4212 | 81.8273 | 8.1727 | 121.714 | 112.3058 | 0 | 22.395 | 0.2 | 0 | 5.1263 | 27.5213 | 5.5 | 6.36 | 1.0746 | 0.02425
2015-08-13 20:00 | 63.6333 | 21.48 | 42.1533 | 437.1118 | 14.8108 | 134.423 | 84.466 | 5.534 | 136.0766 | 124.9349 | 0 | 16.11 | 0.2 | 0 | 3.1817 | 19.2917 | 3.8 | 4.4029 | 1.0824 | 0.017122
2015-08-13 21:00 | 24.74 | 13.1 | 11.64 | 190.4673 | 14.7982 | 149.4248 | 86.4963 | 3.5037 | 150.4806 | 136.1901 | 0 | 9.825 | 0.2 | 0 | 1.237 | 11.062 | 3.9 | 4.2457 | 1.083 | 0.0098239
2015-08-13 22:00 | 19.48 | 11.2633 | 8.2167 | 0 | 14.7855 | 164.4266 | 87.7889 | 2.2111 | 164.9432 | 144.724 | 0 | 8.4475 | 0.2 | 0 | 0.974 | 9.4215 | 3.8 | 4.0944 | 1.0836 | 0.0083717
2015-08-13 23:00 | 14.22 | 9.4267 | 4.7933 | 0 | 14.7729 | 179.4284 | 88.2598 | 1.7402 | 179.4471 | 148.2554 | 0 | 7.07 | 0.2 | 0 | 0.711 | 7.781 | 4.5 | 4.7432 | 1.081 | 0.0068974
2015-08-14 | 8.96 | 7.59 | 1.37 | 0 | 14.7603 | -165.5698 | 87.8787 | 2.1213 | -166.046 | 145.2237 | 0 | 5.6925 | 0.2 | 0 | 0.448 | 6.1405 | 3.5 | 3.6919 | 1.0852 | 0.0054644
2015-08-14 01:00 | 29.8467 | 17.56 | 12.2867 | 211.6136 | 14.7476 | -150.568 | 86.6714 | 3.3286 | -151.5751 | 136.9958 | 0 | 13.17 | 0.2 | 0 | 1.4923 | 14.6623 | 2.5 | 2.9582 | 1.0882 | 0.013083
2015-08-14 02:00 | 50.7333 | 27.53 | 23.2033 | 252.0504 | 14.7349 | -135.5661 | 84.718 | 5.282 | -137.1603 | 125.8946 | 0 | 20.6475 | 0.2 | 0 | 2.5367 | 23.1842 | 2.8 | 3.5245 | 1.0859 | 0.020644
2015-08-14 03:00 | 71.62 | 37.5 | 34.12 | 249.6431 | 14.7223 | -120.5643 | 82.1445 | 7.8555 | -122.7882 | 113.3436 | 0 | 28.125 | 0.2 | 0 | 3.581 | 31.706 | 4 | 4.9908 | 1.08 | 0.02808
2015-08-14 04:00 | 102.9 | 62.12 | 40.78 | 215.9297 | 14.7096 | -105.5625 | 79.1139 | 10.8861 | -108.4065 | 100.0265 | 0 | 46.59 | 0.2 | 0 | 5.145 | 51.735 | 3.9 | 5.5167 | 1.0779 | 0.045729
2015-08-14 05:00 | 134.18 | 86.74 | 47.44 | 193.6045 | 14.6969 | -90.5607 | 75.8161 | 14.1839 | -93.9293 | 86.2742 | 12.5809 | 65.055 | 0.2 | 0 | 6.709 | 84.3449 | 2.5 | 5.1358 | 1.0795 | 0.074658
2015-08-14 06:00 | 165.46 | 111.36 | 54.1 | 179.5162 | 14.6842 | -75.5588 | 72.4604 | 17.5396 | -79.2496 | 72.2591 | 54.7009 | 83.52 | 0.2 | 0 | 8.273 | 146.4939 | 3.3 | 7.8779 | 1.0685 | 0.12835
2015-08-14 07:00 | 215.7467 | 128.05 | 87.6967 | 247.7355 | 14.6715 | -60.557 | 69.2682 | 20.7318 | -64.2604 | 58.0795 | 130.9883 | 96.0375 | 0.2 | 0 | 10.7873 | 237.8131 | 3.3 | 10.7317 | 1.0571 | 0.20614
2015-08-14 08:00 | 266.0333 | 144.74 | 121.2933 | 303.7524 | 14.6588 | -45.5551 | 66.4645 | 23.5355 | -48.8819 | 43.7973 | 219.2462 | 108.555 | 0.2 | 0 | 13.3017 | 341.1029 | 3.8 | 14.4595 | 1.0422 | 0.2915
2015-08-14 09:00 | 316.32 | 161.43 | 154.89 | 356.7 | 14.6461 | -30.5533 | 64.2637 | 25.7363 | -33.0918 | 29.4605 | 310.577 | 121.0725 | 0.2 | 0 | 15.816 | 447.4655 | 5.2 | 19.1833 | 1.0233 | 0.37546
2015-08-14 10:00 | 312.9533 | 158.2333 | 154.72 | 339.0456 | 14.6334 | -15.5514 | 62.8488 | 27.1512 | -16.9497 | 15.14 | 327.2775 | 118.675 | 0.2 | 0 | 15.6477 | 461.6002 | 4.6 | 19.025 | 1.0239 | 0.38756
2015-08-14 11:00 | 309.5867 | 155.0367 | 154.55 | 332.9948 | 14.6207 | -0.54957 | 62.3466 | 27.6534 | -0.60035 | 2.4048 | 332.7015 | 116.2775 | 0.2 | 0 | 15.4793 | 464.4583 | 5.1 | 19.6143 | 1.0215 | 0.38906
2015-08-14 12:00 | 306.22 | 151.84 | 154.38 | 337.7904 | 14.608 | 14.4523 | 62.8044 | 27.1956 | 15.7549 | 14.1018 | 327.6108 | 113.88 | 0.2 | 0 | 15.311 | 456.8018 | 4.7 | 18.9751 | 1.0241 | 0.3836
2015-08-14 13:00 | 268.9867 | 163.6367 | 105.35 | 241.8892 | 14.5952 | 29.4542 | 64.181 | 25.819 | 31.9129 | 28.4169 | 212.7434 | 122.7275 | 0.2 | 0 | 13.4493 | 348.9203 | 4.6 | 15.5038 | 1.038 | 0.29698
2015-08-14 14:00 | 231.7533 | 175.4333 | 56.32 | 140.4229 | 14.5825 | 44.456 | 66.3547 | 23.6453 | 47.7246 | 42.7605 | 103.0983 | 131.575 | 0.2 | 0 | 11.5877 | 246.261 | 3.8 | 11.4957 | 1.054 | 0.21284
2015-08-14 15:00 | 194.52 | 187.23 | 7.29 | 20.4779 | 14.5697 | 59.4579 | 69.1456 | 20.8544 | 63.1252 | 57.0552 | 11.1365 | 140.4225 | 0.2 | 0 | 9.726 | 161.285 | 4 | 9.0402 | 1.0638 | 0.1407
2015-08-14 16:00 | 174.9767 | 137.2133 | 37.7633 | 124.4885 | 14.557 | 74.4598 | 72.3412 | 17.6588 | 78.133 | 71.254 | 40.0072 | 102.91 | 0.2 | 0 | 8.7488 | 151.6661 | 3.9 | 8.6396 | 1.0654 | 0.1325
2015-08-14 17:00 | 155.4333 | 87.1967 | 68.2367 | 276.5878 | 14.5442 | 89.4617 | 75.7172 | 14.2828 | 92.8257 | 85.2975 | 22.675 | 65.3975 | 0.2 | 0 | 7.7717 | 95.8442 | 3.8 | 6.7951 | 1.0728 | 0.084315
2015-08-14 18:00 | 135.89 | 37.18 | 98.71 | 519.736 | 14.5315 | 104.4636 | 79.0517 | 10.9483 | 107.3103 | 99.0926 | 0 | 27.885 | 0.2 | 0 | 6.7945 | 34.6795 | 3.6 | 4.6837 | 1.0813 | 0.030748
2015-08-14 19:00 | 99.4233 | 28.9167 | 70.5067 | 515.2186 | 14.5187 | 119.4655 | 82.1345 | 7.8655 | 121.6954 | 112.4767 | 0 | 21.6875 | 0.2 | 0 | 4.9712 | 26.6587 | 3.4 | 4.2331 | 1.0831 | 0.023676
2015-08-14 20:00 | 62.9567 | 20.6533 | 42.3033 | 464.4267 | 14.5059 | 134.4674 | 84.7738 | 5.2262 | 136.0696 | 125.1389 | 0 | 15.49 | 0.2 | 0 | 3.1478 | 18.6378 | 2.9 | 3.4824 | 1.0861 | 0.016598
2015-08-14 21:00 | 26.49 | 12.39 | 14.1 | 252.9293 | 14.4931 | 149.4693 | 86.8043 | 3.1957 | 150.4883 | 136.4371 | 0 | 9.2925 | 0.2 | 0 | 1.3245 | 10.617 | 2.8 | 3.1318 | 1.0875 | 0.0094675
2015-08-14 22:00 | 21.16 | 10.41 | 10.75 | 0 | 14.4803 | 164.4712 | 88.0961 | 1.9039 | 164.9678 | 145.0165 | 0 | 7.8075 | 0.2 | 0 | 1.058 | 8.8655 | 2.7 | 2.977 | 1.0881 | 0.0079101
2015-08-14 23:00 | 15.83 | 8.43 | 7.4 | 0 | 14.4675 | 179.4731 | 88.5653 | 1.4347 | 179.4896 | 148.5615 | 0 | 6.3225 | 0.2 | 0 | 0.7915 | 7.114 | 2.9 | 3.1223 | 1.0875 | 0.006344
2015-08-15 | 10.5 | 6.45 | 4.05 | 0 | 14.4547 | -165.525 | 88.1813 | 1.8187 | -165.9855 | 145.4828 | 0 | 4.8375 | 0.2 | 0 | 0.525 | 5.3625 | 2.8 | 2.9676 | 1.0881 | 0.0047848
2015-08-15 01:00 | 24.8333 | 21.65 | 3.1833 | 60.2315 | 14.4419 | -150.5231 | 86.9704 | 3.0296 | -151.4979 | 137.1868 | 0 | 16.2375 | 0.2 | 0 | 1.2417 | 17.4792 | 2.5 | 3.0462 | 1.0878 | 0.015592
2015-08-15 02:00 | 39.1667 | 36.85 | 2.3167 | 26.6502 | 14.4291 | -135.5212 | 85.0131 | 4.9869 | -137.0685 | 126.0302 | 0 | 27.6375 | 0.2 | 0 | 1.9583 | 29.5958 | 2.3 | 3.2249 | 1.0871 | 0.026382
2015-08-15 03:00 | 53.5 | 52.05 | 1.45 | 11.0155 | 14.4163 | -120.5192 | 82.436 | 7.564 | -122.6844 | 113.4394 | 0 | 39.0375 | 0.2 | 0 | 2.675 | 41.7125 | 2.1 | 3.4035 | 1.0864 | 0.037159
2015-08-15 04:00 | 82.7333 | 77.0933 | 5.64 | 30.6683 | 14.4034 | -105.5173 | 79.4028 | 10.5972 | -108.2942 | 100.0934 | 0 | 57.82 | 0.2 | 0 | 4.1367 | 61.9567 | 1.8 | 3.7361 | 1.0851 | 0.055126
2015-08-15 05:00 | 111.9667 | 102.1367 | 9.83 | 40.9305 | 14.3906 | -90.5154 | 76.1038 | 13.8962 | -93.8119 | 86.3195 | 2.6274 | 76.6025 | 0.2 | 0 | 5.5983 | 84.8282 | 1.7 | 4.3509 | 1.0826 | 0.075304
2015-08-15 06:00 | 141.2 | 127.18 | 14.02 | 47.2748 | 14.3777 | -75.5134 | 72.7487 | 17.2513 | -79.1313 | 72.288 | 14.3826 | 95.385 | 0.2 | 0 | 7.06 | 116.8276 | 2.1 | 5.7509 | 1.077 | 0.10317
2015-08-15 07:00 | 179.0533 | 156.2433 | 22.81 | 65.3123 | 14.3649 | -60.5115 | 69.5588 | 20.4412 | -64.1457 | 58.0957 | 34.5177 | 117.1825 | 0.2 | 0 | 8.9527 | 160.6528 | 2.5 | 7.5204 | 1.0699 | 0.14095
2015-08-15 08:00 | 216.9067 | 185.3067 | 31.6 | 80.0807 | 14.352 | -45.5095 | 66.7589 | 23.2411 | -48.7759 | 43.8046 | 57.7946 | 138.98 | 0.2 | 0 | 10.8453 | 207.62 | 3 | 9.4881 | 1.062 | 0.18081
2015-08-15 09:00 | 254.76 | 214.37 | 40.39 | 94.0339 | 14.3392 | -30.5076 | 64.5625 | 25.4375 | -32.9999 | 29.4644 | 81.8717 | 160.7775 | 0.2 | 0 | 12.738 | 255.3872 | 3 | 10.9809 | 1.0561 | 0.22116
2015-08-15 10:00 | 271.0333 | 217.15 | 53.8833 | 119.3109 | 14.3263 | -15.5056 | 63.1522 | 26.8478 | -16.8766 | 15.1578 | 115.16 | 162.8625 | 0.2 | 0 | 13.5517 | 291.5741 | 3.2 | 12.3117 | 1.0508 | 0.25123
2015-08-15 11:00 | 287.3067 | 219.93 | 67.3767 | 146.6732 | 14.3134 | -0.50363 | 62.6538 | 27.3462 | -0.5494 | 2.6972 | 146.5107 | 164.9475 | 0.2 | 0 | 14.3653 | 325.8236 | 3.7 | 13.882 | 1.0445 | 0.27906
2015-08-15 12:00 | 303.58 | 222.71 | 80.87 | 178.8307 | 14.3005 | 14.4983 | 63.1141 | 26.8859 | 15.783 | 14.21 | 173.3589 | 167.0325 | 0.2 | 0 | 15.179 | 355.5704 | 3.9 | 15.0116 | 1.04 | 0.30322
2015-08-15 13:00 | 278.1 | 202.5467 | 75.5533 | 175.4438 | 14.2876 | 29.5003 | 64.4917 | 25.5083 | 31.9201 | 28.5094 | 154.1692 | 151.91 | 0.2 | 0 | 13.905 | 319.9842 | 4 | 13.9995 | 1.044 | 0.27393
2015-08-15 14:00 | 252.62 | 182.3833 | 70.2367 | 177.3215 | 14.2747 | 44.5023 | 66.6655 | 23.3345 | 47.7149 | 42.8556 | 129.9891 | 136.7875 | 0.2 | 0 | 12.631 | 279.4076 | 3.8 | 12.5315 | 1.0499 | 0.24054
2015-08-15 15:00 | 227.14 | 162.22 | 64.92 | 184.9972 | 14.2618 | 59.5043 | 69.4561 | 20.5439 | 63.1038 | 57.1585 | 100.327 | 121.665 | 0.2 | 0 | 11.357 | 233.349 | 4.3 | 11.5922 | 1.0536 | 0.20161
2015-08-15 16:00 | 169.7867 | 125.2733 | 44.5133 | 149.2814 | 14.2489 | 74.5063 | 72.6514 | 17.3486 | 78.1053 | 71.369 | 47.6912 | 93.955 | 0.2 | 0 | 8.4893 | 150.1355 | 4.1 | 8.7917 | 1.0648 | 0.13109
2015-08-15 17:00 | 112.4333 | 88.3267 | 24.1067 | 99.8382 | 14.236 | 89.5082 | 76.0274 | 13.9726 | 92.797 | 85.4276 | 7.959 | 66.245 | 0.2 | 0 | 5.6217 | 79.8257 | 3.9 | 6.3946 | 1.0744 | 0.070328
2015-08-15 18:00 | 55.08 | 51.38 | 3.7 | 20.0438 | 14.2231 | 104.5102 | 79.3624 | 10.6376 | 107.2854 | 99.2419 | 0 | 38.535 | 0.2 | 0 | 2.754 | 41.289 | 4.3 | 5.5903 | 1.0776 | 0.036486
2015-08-15 19:00 | 40.37 | 37.88 | 2.49 | 18.9408 | 14.2101 | 119.5122 | 82.4459 | 7.5541 | 121.6785 | 112.651 | 0 | 28.41 | 0.2 | 0 | 2.0185 | 30.4285 | 3.1 | 4.0509 | 1.0838 | 0.027042
2015-08-15 20:00 | 25.66 | 24.38 | 1.28 | 14.9422 | 14.1972 | 134.5142 | 85.0858 | 4.9142 | 136.0646 | 125.3465 | 0 | 18.285 | 0.2 | 0 | 1.283 | 19.568 | 3.1 | 3.7115 | 1.0852 | 0.017412
2015-08-15 21:00 | 10.95 | 10.88 | 0.07 | 0 | 14.1843 | 149.5162 | 87.1163 | 2.8837 | 150.4982 | 136.6879 | 0 | 8.16 | 0.2 | 0 | 0.5475 | 8.7075 | 2.6 | 2.8721 | 1.0885 | 0.0077721
2015-08-15 22:00 | 8.2433 | 8.1967 | 0.046667 | 0 | 14.1713 | 164.5183 | 88.4073 | 1.5927 | 164.9947 | 145.3132 | 0 | 6.1475 | 0.2 | 0 | 0.41217 | 6.5597 | 2.7 | 2.905 | 1.0884 | 0.0058543
2015-08-15 23:00 | 5.5367 | 5.5133 | 0.023333 | 0 | 14.1583 | 179.5203 | 88.8746 | 1.1254 | 179.5348 | 148.8714 | 0 | 4.135 | 0.2 | 0 | 0.27683 | 4.4118 | 2.7 | 2.8379 | 1.0886 | 0.0039384
2015-08-16 | 2.83 | 2.83 | 0 | 0 | 14.1454 | -165.4777 | 88.4875 | 1.5125 | -165.9223 | 145.7435 | 0 | 2.1225 | 0.2 | 0 | 0.1415 | 2.264 | 2.4 | 2.4707 | 1.0901 | 0.0020238
2015-08-16 01:00 | 10.1133 | 10.1133 | 0 | 0 | 14.1324 | -150.4757 | 87.2729 | 2.7271 | -151.4177 | 137.3777 | 0 | 7.585 | 0.2 | 0 | 0.50567 | 8.0907 | 2.9 | 3.1528 | 1.0874 | 0.0072141
2015-08-16 02:00 | 17.3967 | 17.3967 | 0 | 0 | 14.1194 | -135.4737 | 85.3115 | 4.6885 | -136.9736 | 126.1649 | 0 | 13.0475 | 0.2 | 0 | 0.86983 | 13.9173 | 2.9 | 3.3349 | 1.0867 | 0.012401
2015-08-16 03:00 | 24.68 | 24.68 | 0 | 0 | 14.1064 | -120.4716 | 82.7308 | 7.2692 | -122.5776 | 113.5338 | 0 | 18.51 | 0.2 | 0 | 1.234 | 19.744 | 3 | 3.617 | 1.0855 | 0.017575
2015-08-16 04:00 | 35.4267 | 35.4267 | 0 | 0 | 14.0935 | -105.4696 | 79.6949 | 10.3051 | -108.1787 | 100.159 | 0 | 26.57 | 0.2 | 0 | 1.7713 | 28.3413 | 3.3 | 4.1857 | 1.0833 | 0.025175
2015-08-16 05:00 | 46.1733 | 46.1733 | 0 | 0 | 14.0805 | -90.4675 | 76.3947 | 13.6053 | -93.6914 | 86.3637 | 0 | 34.63 | 0.2 | 0 | 2.3087 | 36.9387 | 3 | 4.1543 | 1.0834 | 0.032815
2015-08-16 06:00 | 56.92 | 56.92 | 0 | 0 | 14.0675 | -75.4655 | 73.0401 | 16.9599 | -79.0098 | 72.3158 | 0 | 42.69 | 0.2 | 0 | 2.846 | 45.536 | 3.5 | 4.923 | 1.0803 | 0.040338
2015-08-16 07:00 | 87.2967 | 84.3533 | 2.9433 | 8.5454 | 14.0545 | -60.4634 | 69.8527 | 20.1473 | -64.0279 | 58.1112 | 4.5143 | 63.265 | 0.2 | 0 | 4.3648 | 72.1441 | 3.6 | 5.8545 | 1.0766 | 0.063689
2015-08-16 08:00 | 117.6733 | 111.7867 | 5.8867 | 15.1009 | 14.0414 | -45.4614 | 67.0565 | 22.9435 | -48.6669 | 43.8118 | 10.8971 | 83.84 | 0.2 | 0 | 5.8837 | 100.6207 | 5.1 | 8.2444 | 1.067 | 0.088039
2015-08-16 09:00 | 148.05 | 139.22 | 8.83 | 20.7885 | 14.0284 | -30.4593 | 64.8649 | 25.1351 | -32.9051 | 29.4694 | 18.0988 | 104.415 | 0.2 | 0 | 7.4025 | 129.9163 | 4 | 8.0599 | 1.0678 | 0.11375
2015-08-16 10:00 | 179.0733 | 172.7333 | 6.34 | 14.1887 | 14.0154 | -15.4573 | 63.4593 | 26.5407 | -16.8009 | 15.1801 | 13.6936 | 129.55 | 0.2 | 0 | 8.9537 | 152.1973 | 4.3 | 9.0562 | 1.0638 | 0.13276
2015-08-16 11:00 | 210.0967 | 206.2467 | 3.85 | 8.4701 | 14.0024 | -0.4552 | 62.9648 | 27.0352 | -0.49586 | 2.9966 | 8.4585 | 154.685 | 0.2 | 0 | 10.5048 | 173.6484 | 4.9 | 10.3265 | 1.0587 | 0.15075
2015-08-16 12:00 | 241.12 | 239.76 | 1.36 | 3.0403 | 13.9893 | 14.5469 | 63.4276 | 26.5724 | 15.8135 | 14.3274 | 2.9457 | 179.82 | 0.2 | 0 | 12.056 | 194.8217 | 5.4 | 11.4882 | 1.054 | 0.16839
2015-08-16 13:00 | 204.9733 | 201.2233 | 3.75 | 8.8095 | 13.9763 | 29.5489 | 64.8065 | 25.1935 | 31.9295 | 28.6079 | 7.734 | 150.9175 | 0.2 | 0 | 10.2487 | 168.9002 | 5.5 | 10.7781 | 1.0569 | 0.14638
2015-08-16 14:00 | 168.8267 | 162.6867 | 6.14 | 15.7016 | 13.9632 | 44.551 | 66.9805 | 23.0195 | 47.7072 | 42.9556 | 11.4917 | 122.015 | 0.2 | 0 | 8.4413 | 141.948 | 6.6 | 11.0359 | 1.0559 | 0.1229
2015-08-16 15:00 | 132.68 | 124.15 | 8.53 | 24.6692 | 13.9502 | 59.5531 | 69.7709 | 20.2291 | 63.0843 | 57.2661 | 13.3396 | 93.1125 | 0.2 | 0 | 6.634 | 113.0861 | 6.3 | 9.8339 | 1.0607 | 0.098356
2015-08-16 16:00 | 119.7667 | 96.6333 | 23.1333 | 78.9692 | 13.9371 | 74.5552 | 72.9659 | 17.0341 | 78.0794 | 71.4879 | 25.0732 | 72.475 | 0.2 | 0 | 5.9883 | 103.5365 | 6.9 | 10.1355 | 1.0595 | 0.089948
2015-08-16 17:00 | 106.8533 | 69.1167 | 37.7367 | 159.815 | 13.924 | 89.5573 | 76.3419 | 13.6581 | 92.77 | 85.5612 | 12.3687 | 51.8375 | 0.2 | 0 | 5.3427 | 69.5489 | 6 | 8.1734 | 1.0673 | 0.060869
2015-08-16 18:00 | 93.94 | 41.6 | 52.34 | 292.09 | 13.9109 | 104.5594 | 79.6773 | 10.3227 | 107.2622 | 99.3946 | 0 | 31.2 | 0.2 | 0 | 4.697 | 35.897 | 6.8 | 7.9218 | 1.0683 | 0.031446
2015-08-16 19:00 | 67.8 | 30.7333 | 37.0667 | 294.1792 | 13.8979 | 119.5615 | 82.7615 | 7.2385 | 121.6634 | 112.8287 | 0 | 23.05 | 0.2 | 0 | 3.39 | 26.44 | 5.9 | 6.7263 | 1.0731 | 0.023266
2015-08-16 20:00 | 41.66 | 19.8667 | 21.7933 | 271.853 | 13.8848 | 134.5636 | 85.4019 | 4.5981 | 136.0614 | 125.5576 | 0 | 14.9 | 0.2 | 0 | 2.083 | 16.983 | 4.8 | 5.3307 | 1.0787 | 0.015022
2015-08-16 21:00 | 15.52 | 9 | 6.52 | 0 | 13.8717 | 149.5657 | 87.4324 | 2.5676 | 150.5101 | 136.9425 | 0 | 6.75 | 0.2 | 0 | 0.776 | 7.526 | 5.4 | 5.6352 | 1.0775 | 0.0066493
2015-08-16 22:00 | 11.8833 | 7.1667 | 4.7167 | 0 | 13.8586 | 164.5678 | 88.7224 | 1.2776 | 165.0239 | 145.6142 | 0 | 5.375 | 0.2 | 0 | 0.59417 | 5.9692 | 3.9 | 4.0865 | 1.0837 | 0.0053042
2015-08-16 23:00 | 8.2467 | 5.3333 | 2.9133 | 0 | 13.8454 | 179.5699 | 89.1875 | 0.81247 | 179.5824 | 149.185 | 0 | 4 | 0.2 | 0 | 0.41233 | 4.4123 | 4.3 | 4.4379 | 1.0822 | 0.0039157
2015-08-17 | 4.61 | 3.5 | 1.11 | 0 | 13.8323 | -165.4279 | 88.7973 | 1.2027 | -165.8563 | 146.0057 | 0 | 2.625 | 0.2 | 0 | 0.2305 | 2.8555 | 3.9 | 3.9892 | 1.084 | 0.0025383
2015-08-17 01:00 | 24.9867 | 12.86 | 12.1267 | 0 | 13.8192 | -150.4258 | 87.5787 | 2.4213 | -151.3347 | 137.5682 | 0 | 9.645 | 0.2 | 0 | 1.2493 | 10.8943 | 4.5 | 4.8404 | 1.0806 | 0.0096537
2015-08-17 02:00 | 45.3633 | 22.22 | 23.1433 | 302.5668 | 13.8061 | -135.4237 | 85.6132 | 4.3868 | -136.8757 | 126.2984 | 0 | 16.665 | 0.2 | 0 | 2.2682 | 18.9332 | 4.8 | 5.3917 | 1.0784 | 0.016743
2015-08-17 03:00 | 65.74 | 31.58 | 34.16 | 281.4484 | 13.7929 | -120.4216 | 83.0287 | 6.9713 | -122.4677 | 113.6269 | 0 | 23.685 | 0.2 | 0 | 3.287 | 26.972 | 5.4 | 6.2429 | 1.075 | 0.023776
2015-08-17 04:00 | 88.47 | 54.8367 | 33.6333 | 193.4957 | 13.7798 | -105.4194 | 79.99 | 10.01 | -108.06 | 100.2232 | 0 | 41.1275 | 0.2 | 0 | 4.4235 | 45.551 | 5.1 | 6.5235 | 1.0739 | 0.040112
2015-08-17 05:00 | 111.2 | 78.0933 | 33.1067 | 143.7903 | 13.7667 | -90.4173 | 76.6886 | 13.3114 | -93.5678 | 86.4065 | 9.0124 | 58.57 | 0.2 | 0 | 5.56 | 73.1424 | 4.4 | 6.6857 | 1.0733 | 0.06437
2015-08-17 06:00 | 133.93 | 101.35 | 32.58 | 113.6059 | 13.7535 | -75.4151 | 73.3347 | 16.6653 | -78.8853 | 72.3425 | 34.4596 | 76.0125 | 0.2 | 0 | 6.6965 | 117.1686 | 4.5 | 8.1615 | 1.0674 | 0.10255
2015-08-17 07:00 | 121.9433 | 98.6433 | 23.3 | 68.6172 | 13.7403 | -60.413 | 70.1496 | 19.8504 | -63.9071 | 58.126 | 36.2335 | 73.9825 | 0.2 | 0 | 6.0972 | 116.3131 | 4.3 | 7.9348 | 1.0683 | 0.10189
2015-08-17 08:00 | 109.9567 | 95.9367 | 14.02 | 36.4173 | 13.7272 | -45.4108 | 67.3574 | 22.6426 | -48.5551 | 43.8189 | 26.2762 | 71.9525 | 0.2 | 0 | 5.4978 | 103.7266 | 4.1 | 7.3415 | 1.0706 | 0.091064
2015-08-17 09:00 | 97.97 | 93.23 | 4.74 | 11.2879 | 13.714 | -30.4087 | 65.1706 | 24.8294 | -32.8075 | 29.4757 | 9.8269 | 69.9225 | 0.2 | 0 | 4.8985 | 84.6479 | 3.9 | 6.5452 | 1.0738 | 0.074535
2015-08-17 10:00 | 98.0433 | 94.8667 | 3.1767 | 7.1874 | 13.7008 | -15.4065 | 63.7698 | 26.2302 | -16.7224 | 15.2072 | 6.9357 | 71.15 | 0.2 | 0 | 4.9022 | 82.9879 | 4.4 | 6.9934 | 1.072 | 0.072951
2015-08-17 11:00 | 98.1167 | 96.5033 | 1.6133 | 3.5881 | 13.6876 | -0.40432 | 63.2794 | 26.7206 | -0.4398 | 3.3021 | 3.5821 | 72.3775 | 0.2 | 0 | 4.9058 | 80.8654 | 4.4 | 6.927 | 1.0723 | 0.071103
2015-08-17 12:00 | 98.19 | 98.14 | 0.05 | 0.11303 | 13.6744 | 14.5979 | 63.745 | 26.255 | 15.8464 | 14.454 | 0.10945 | 73.605 | 0.2 | 0 | 4.9095 | 78.624 | 7.2 | 9.657 | 1.0614 | 0.068428
2015-08-17 13:00 | 91.7967 | 91.7633 | 0.033333 | 0.079245 | 13.6612 | 29.6 | 65.1253 | 24.8747 | 31.9412 | 28.7123 | 0.069501 | 68.8225 | 0.2 | 0 | 4.5898 | 73.4818 | 7.8 | 10.0963 | 1.0596 | 0.063847
2015-08-17 14:00 | 85.4033 | 85.3867 | 0.016667 | 0.043188 | 13.648 | 44.6022 | 67.2996 | 22.7004 | 47.7016 | 43.0603 | 0.031554 | 64.04 | 0.2 | 0 | 4.2702 | 68.3417 | 7.5 | 9.6357 | 1.0615 | 0.059484
2015-08-17 15:00 | 79.01 | 79.01 | 0 | 0 | 13.6348 | 59.6044 | 70.0897 | 19.9103 | 63.0666 | 57.3778 | 0 | 59.2575 | 0.2 | 0 | 3.9505 | 63.208 | 6.7 | 8.6753 | 1.0653 | 0.055215
2015-08-17 16:00 | 80.0167 | 63.8167 | 16.2 | 56.3242 | 13.6216 | 74.6066 | 73.2844 | 16.7156 | 78.0553 | 71.6105 | 17.7689 | 47.8625 | 0.2 | 0 | 4.0008 | 69.6322 | 5.7 | 7.876 | 1.0685 | 0.061009
2015-08-17 17:00 | 81.0233 | 48.6233 | 32.4 | 140.43 | 13.6084 | 89.6088 | 76.6605 | 13.3395 | 92.7448 | 85.6984 | 10.5332 | 36.4675 | 0.2 | 0 | 4.0512 | 51.0519 | 5.6 | 7.1954 | 1.0712 | 0.044844
2015-08-17 18:00 | 82.03 | 33.43 | 48.6 | 279.7756 | 13.5952 | 104.611 | 79.9964 | 10.0036 | 107.2407 | 99.5507 | 0 | 25.0725 | 0.2 | 0 | 4.1015 | 29.174 | 4.4 | 5.3117 | 1.0788 | 0.025807
2015-08-17 19:00 | 58.0933 | 24.54 | 33.5533 | 278.5331 | 13.5819 | 119.6132 | 83.0811 | 6.9189 | 121.6501 | 113.0098 | 0 | 18.405 | 0.2 | 0 | 2.9047 | 21.3097 | 4.3 | 4.9659 | 1.0801 | 0.018874
2015-08-17 20:00 | 34.1567 | 15.65 | 18.5067 | 248.0897 | 13.5687 | 134.6154 | 85.722 | 4.278 | 136.0601 | 125.772 | 0 | 11.7375 | 0.2 | 0 | 1.7078 | 13.4453 | 5.5 | 5.9202 | 1.0763 | 0.011867
2015-08-17 21:00 | 10.22 | 6.76 | 3.46 | 0 | 13.5554 | 149.6176 | 87.7523 | 2.2477 | 150.524 | 137.2007 | 0 | 5.07 | 0.2 | 0 | 0.511 | 5.581 | 5.6 | 5.7744 | 1.0769 | 0.0049284
2015-08-17 22:00 | 7.9067 | 5.2233 | 2.6833 | 0 | 13.5422 | 164.6198 | 89.0412 | 0.95877 | 165.0554 | 145.9193 | 0 | 3.9175 | 0.2 | 0 | 0.39533 | 4.3128 | 5.4 | 5.5348 | 1.0779 | 0.0038119
2015-08-17 23:00 | 5.5933 | 3.6867 | 1.9067 | 0 | 13.5289 | 179.622 | 89.5041 | 0.49587 | 179.6325 | 149.5021 | 0 | 2.765 | 0.2 | 0 | 0.27967 | 3.0447 | 5.9 | 5.9951 | 1.076 | 0.0026864
2015-08-18 | 3.28 | 2.15 | 1.13 | 0 | 13.5157 | -165.3757 | 89.1106 | 0.88938 | -165.7876 | 146.2693 | 0 | 1.6125 | 0.2 | 0 | 0.164 | 1.7765 | 3.9 | 3.9555 | 1.0842 | 0.0015794
2015-08-18 01:00 | 20.5067 | 10.08 | 10.4267 | 0 | 13.5024 | -150.3735 | 87.8879 | 2.1121 | -151.2488 | 137.7583 | 0 | 7.56 | 0.2 | 0 | 1.0253 | 8.5853 | 3.2 | 3.4683 | 1.0861 | 0.0076463
2015-08-18 02:00 | 37.7333 | 18.01 | 19.7233 | 277.0766 | 13.4891 | -135.3713 | 85.918 | 4.082 | -136.7748 | 126.4308 | 0 | 13.5075 | 0.2 | 0 | 1.8867 | 15.3942 | 3.3 | 3.7811 | 1.0849 | 0.013695
2015-08-18 03:00 | 54.96 | 25.94 | 29.02 | 249.8357 | 13.4758 | -120.3691 | 83.3297 | 6.6703 | -122.3547 | 113.7187 | 0 | 19.455 | 0.2 | 0 | 2.748 | 22.203 | 4.3 | 4.9938 | 1.08 | 0.019663
2015-08-18 04:00 | 75.9567 | 51.0667 | 24.89 | 147.5465 | 13.4625 | -105.3668 | 80.2882 | 9.7118 | -107.9384 | 100.286 | 0 | 38.3 | 0.2 | 0 | 3.7978 | 42.0978 | 4.1 | 5.4156 | 1.0783 | 0.037224
2015-08-18 05:00 | 96.9533 | 76.1933 | 20.76 | 92.1861 | 13.4492 | -90.3646 | 76.9856 | 13.0144 | -93.4411 | 86.4481 | 5.7112 | 57.145 | 0.2 | 0 | 4.8477 | 67.7038 | 5 | 7.1157 | 1.0715 | 0.059489
2015-08-18 06:00 | 117.95 | 101.32 | 16.63 | 59.013 | 13.4359 | -75.3623 | 73.6322 | 16.3678 | -78.7577 | 72.3683 | 17.8749 | 75.99 | 0.2 | 0 | 5.8975 | 99.7624 | 5.4 | 8.5176 | 1.0659 | 0.087199
2015-08-18 07:00 | 142.4033 | 117.8833 | 24.52 | 73.2739 | 13.4226 | -60.3601 | 70.4497 | 19.5503 | -63.7834 | 58.1403 | 38.677 | 88.4125 | 0.2 | 0 | 7.1202 | 134.2096 | 4.8 | 8.9941 | 1.064 | 0.1171
2015-08-18 08:00 | 166.8567 | 134.4467 | 32.41 | 85.2719 | 13.4093 | -45.3578 | 67.6615 | 22.3385 | -48.4404 | 43.8262 | 61.5189 | 100.835 | 0.2 | 0 | 8.3428 | 170.6968 | 4.8 | 10.1343 | 1.0595 | 0.14829
2015-08-18 09:00 | 191.31 | 151.01 | 40.3 | 97.1043 | 13.396 | -30.3556 | 65.4796 | 24.5204 | -32.7072 | 29.4833 | 84.5292 | 113.2575 | 0.2 | 0 | 9.5655 | 207.3522 | 5.4 | 11.8798 | 1.0525 | 0.17895
2015-08-18 10:00 | 180.6567 | 153.3967 | 27.26 | 62.3719 | 13.3827 | -15.3533 | 64.0838 | 25.9162 | -16.6414 | 15.2394 | 60.1787 | 115.0475 | 0.2 | 0 | 9.0328 | 184.259 | 4.6 | 10.3581 | 1.0586 | 0.15994
2015-08-18 11:00 | 170.0033 | 155.7833 | 14.22 | 31.9786 | 13.3693 | -0.35102 | 63.5976 | 26.4024 | -0.38127 | 3.6132 | 31.915 | 116.8375 | 0.2 | 0 | 8.5002 | 157.2527 | 4.5 | 9.4141 | 1.0623 | 0.13699
2015-08-18 12:00 | 159.35 | 158.17 | 1.18 | 2.6982 | 13.356 | 14.6513 | 64.0661 | 25.9339 | 15.8816 | 14.5896 | 2.6112 | 118.6275 | 0.2 | 0 | 7.9675 | 129.2062 | 4.8 | 8.8377 | 1.0646 | 0.1128
2015-08-18 13:00 | 148.66 | 139.8133 | 8.8467 | 21.2905 | 13.3426 | 29.6535 | 65.4478 | 24.5522 | 31.955 | 28.8228 | 18.6529 | 104.86 | 0.2 | 0 | 7.433 | 130.9459 | 5.1 | 9.1921 | 1.0632 | 0.11417
2015-08-18 14:00 | 137.97 | 121.4567 | 16.5133 | 43.3754 | 13.3293 | 44.6558 | 67.6225 | 22.3775 | 47.698 | 43.1698 | 31.635 | 91.0925 | 0.2 | 0 | 6.8985 | 129.626 | 5 | 9.0508 | 1.0638 | 0.11307
2015-08-18 15:00 | 127.28 | 103.1 | 24.18 | 72.126 | 13.3159 | 59.6581 | 70.4125 | 19.5875 | 63.0509 | 57.4937 | 38.76 | 77.325 | 0.2 | 0 | 6.364 | 122.449 | 4.6 | 8.4265 | 1.0663 | 0.10706
2015-08-18 16:00 | 104.13 | 81.94 | 22.19 | 78.6255 | 13.3026 | 74.6604 | 73.607 | 16.393 | 78.033 | 71.7369 | 24.6398 | 61.455 | 0.2 | 0 | 5.2065 | 91.3013 | 4.3 | 7.1532 | 1.0714 | 0.080212
2015-08-18 17:00 | 80.98 | 60.78 | 20.2 | 89.6833 | 13.2892 | 89.6627 | 76.9832 | 13.0168 | 92.7213 | 85.839 | 6.5073 | 45.585 | 0.2 | 0 | 4.049 | 56.1413 | 4.4 | 6.1544 | 1.0754 | 0.049506
2015-08-18 18:00 | 57.83 | 39.62 | 18.21 | 108.2925 | 13.2758 | 104.665 | 80.3194 | 9.6806 | 107.2209 | 99.7102 | 0 | 29.715 | 0.2 | 0 | 2.8915 | 32.6065 | 4.7 | 5.719 | 1.0771 | 0.028799
2015-08-18 19:00 | 42.2933 | 28.58 | 13.7133 | 119.3957 | 13.2625 | 119.6673 | 83.4047 | 6.5953 | 121.6386 | 113.1941 | 0 | 21.435 | 0.2 | 0 | 2.1147 | 23.5497 | 4.1 | 4.8359 | 1.0807 | 0.020868
2015-08-18 20:00 | 26.7567 | 17.54 | 9.2167 | 133.6573 | 13.2491 | 134.6696 | 86.0459 | 3.9541 | 136.0608 | 125.9898 | 0 | 13.155 | 0.2 | 0 | 1.3378 | 14.4928 | 4.9 | 5.3529 | 1.0786 | 0.012818
2015-08-18 21:00 | 11.22 | 6.5 | 4.72 | 0 | 13.2357 | 149.6719 | 88.076 | 1.924 | 150.54 | 137.4626 | 0 | 4.875 | 0.2 | 0 | 0.561 | 5.436 | 4.4 | 4.5699 | 1.0817 | 0.0048218
2015-08-18 22:00 | 8.3667 | 4.89 | 3.4767 | 0 | 13.2223 | 164.6742 | 89.3637 | 0.63627 | 165.0891 | 146.2284 | 0 | 3.6675 | 0.2 | 0 | 0.41833 | 4.0858 | 4.4 | 4.5277 | 1.0819 | 0.0036247
2015-08-18 23:00 | 5.5133 | 3.28 | 2.2333 | 0 | 13.2089 | 179.6765 | 89.8243 | 0.17573 | 179.6851 | 149.8228 | 0 | 2.46 | 0.2 | 0 | 0.27567 | 2.7357 | 4 | 4.0855 | 1.0837 | 0.0024309
2015-08-19 | 2.66 | 1.67 | 0.99 | 0 | 13.1955 | -165.3211 | 89.4273 | 0.57273 | -165.7163 | 146.534 | 0 | 1.2525 | 0.2 | 0 | 0.133 | 1.3855 | 4.4 | 4.4433 | 1.0822 | 0.0012295
2015-08-19 01:00 | 22.3133 | 9.1367 | 13.1767 | 0 | 13.182 | -150.3188 | 88.2003 | 1.7997 | -151.1601 | 137.9479 | 0 | 6.8525 | 0.2 | 0 | 1.1157 | 7.9682 | 4.8 | 5.049 | 1.0798 | 0.0070553
2015-08-19 02:00 | 41.9667 | 16.6033 | 25.3633 | 385.3351 | 13.1686 | -135.3165 | 86.226 | 3.774 | -136.671 | 126.562 | 0 | 12.4525 | 0.2 | 0 | 2.0983 | 14.5508 | 4.8 | 5.2547 | 1.079 | 0.012874
2015-08-19 03:00 | 61.62 | 24.07 | 37.55 | 338.6378 | 13.1552 | -120.3142 | 83.6336 | 6.3664 | -122.2388 | 113.809 | 0 | 18.0525 | 0.2 | 0 | 3.081 | 21.1335 | 4.9 | 5.5604 | 1.0778 | 0.018677
2015-08-19 04:00 | 65.6967 | 40.4133 | 25.2833 | 154.6281 | 13.1418 | -105.3118 | 80.5893 | 9.4107 | -107.8137 | 100.3474 | 0 | 30.31 | 0.2 | 0 | 3.2848 | 33.5948 | 4.4 | 5.4498 | 1.0782 | 0.029702
2015-08-19 05:00 | 69.7733 | 56.7567 | 13.0167 | 59.1411 | 13.1283 | -90.3095 | 77.2854 | 12.7146 | -93.3115 | 86.4885 | 3.6224 | 42.5675 | 0.2 | 0 | 3.4887 | 49.6785 | 4.9 | 6.4525 | 1.0742 | 0.043759
2015-08-19 06:00 | 73.85 | 73.1 | 0.75 | 2.7099 | 13.1149 | -75.3071 | 73.9327 | 16.0673 | -78.6273 | 72.3931 | 0.81969 | 54.825 | 0.2 | 0 | 3.6925 | 59.3372 | 4.8 | 6.6543 | 1.0734 | 0.052227
2015-08-19 07:00 | 90.7467 | 85.2633 | 5.4833 | 16.634 | 13.1014 | -60.3048 | 70.7527 | 19.2473 | -63.6569 | 58.154 | 8.7767 | 63.9475 | 0.2 | 0 | 4.5373 | 77.2616 | 4.2 | 6.6144 | 1.0735 | 0.068014
2015-08-19 08:00 | 107.6433 | 97.4267 | 10.2167 | 27.2362 | 13.088 | -45.3024 | 67.9686 | 22.0314 | -48.3229 | 43.8335 | 19.647 | 73.07 | 0.2 | 0 | 5.3822 | 98.0991 | 5 | 8.0656 | 1.0677 | 0.08589
2015-08-19 09:00 | 124.54 | 109.59 | 14.95 | 36.4587 | 13.0745 | -30.3001 | 65.7918 | 24.2082 | -32.6043 | 29.4924 | 31.7344 | 82.1925 | 0.2 | 0 | 6.227 | 120.1539 | 4.7 | 8.4548 | 1.0662 | 0.10505
2015-08-19 10:00 | 138.09 | 121.29 | 16.8 | 38.8829 | 13.061 | -15.2977 | 64.4012 | 25.5988 | -16.5578 | 15.2767 | 37.5089 | 90.9675 | 0.2 | 0 | 6.9045 | 135.3809 | 5 | 9.2307 | 1.0631 | 0.11801
2015-08-19 11:00 | 151.64 | 132.99 | 18.65 | 42.4214 | 13.0475 | -0.29534 | 63.9193 | 26.0807 | -0.32033 | 3.9295 | 42.3217 | 99.7425 | 0.2 | 0 | 7.582 | 149.6462 | 6 | 10.6764 | 1.0573 | 0.12974
2015-08-19 12:00 | 165.19 | 144.69 | 20.5 | 47.4285 | 13.0341 | 14.707 | 64.3909 | 25.6091 | 15.9191 | 14.7344 | 45.8688 | 108.5175 | 0.2 | 0 | 8.2595 | 162.6458 | 5 | 10.0827 | 1.0597 | 0.14133
2015-08-19 13:00 | 151.49 | 135.3133 | 16.1767 | 39.4231 | 13.0206 | 29.7094 | 65.7742 | 24.2258 | 31.9709 | 28.9392 | 34.5005 | 101.485 | 0.2 | 0 | 7.5745 | 143.56 | 4.6 | 9.0862 | 1.0637 | 0.12521
2015-08-19 14:00 | 137.79 | 125.9367 | 11.8533 | 31.573 | 13.0071 | 44.7118 | 67.9493 | 22.0507 | 47.6964 | 43.2842 | 22.9839 | 94.4525 | 0.2 | 0 | 6.8895 | 124.3259 | 5.4 | 9.2852 | 1.0629 | 0.10836
2015-08-19 15:00 | 124.09 | 116.56 | 7.53 | 22.8272 | 12.9936 | 59.7142 | 70.7392 | 19.2608 | 63.037 | 57.6137 | 12.2268 | 87.42 | 0.2 | 0 | 6.2045 | 105.8513 | 5.4 | 8.7079 | 1.0652 | 0.092455
2015-08-19 16:00 | 99.4233 | 90.68 | 8.7433 | 31.5927 | 12.9801 | 74.7166 | 73.9335 | 16.0665 | 78.0124 | 71.867 | 9.8324 | 68.01 | 0.2 | 0 | 4.9712 | 82.8136 | 3.8 | 6.3879 | 1.0744 | 0.072963
2015-08-19 17:00 | 74.7567 | 64.8 | 9.9567 | 45.3235 | 12.9666 | 89.7189 | 77.3098 | 12.6902 | 92.6994 | 85.9831 | 3.1749 | 48.6 | 0.2 | 0 | 3.7378 | 55.5128 | 4.5 | 6.2348 | 1.0751 | 0.048937
2015-08-19 18:00 | 50.09 | 38.92 | 11.17 | 68.7266 | 12.953 | 104.7213 | 80.6463 | 9.3537 | 107.2028 | 99.8728 | 0 | 29.19 | 0.2 | 0 | 2.5045 | 31.6945 | 3.8 | 4.7905 | 1.0808 | 0.02809
2015-08-19 19:00 | 35.7967 | 27.6033 | 8.1933 | 75.0462 | 12.9395 | 119.7237 | 83.7321 | 6.2679 | 121.6287 | 113.3815 | 0 | 20.7025 | 0.2 | 0 | 1.7898 | 22.4923 | 4.4 | 5.1029 | 1.0796 | 0.019912
2015-08-19 20:00 | 21.5033 | 16.2867 | 5.2167 | 82.4771 | 12.926 | 134.7261 | 86.3736 | 3.6264 | 136.0632 | 126.2107 | 0 | 12.215 | 0.2 | 0 | 1.0752 | 13.2902 | 4.8 | 5.2153 | 1.0791 | 0.01176
2015-08-19 21:00 | 7.21 | 4.97 | 2.24 | 0 | 12.9124 | 149.7286 | 88.4034 | 1.5966 | 150.5581 | 137.7278 | 0 | 3.7275 | 0.2 | 0 | 0.3605 | 4.088 | 3.7 | 3.8277 | 1.0847 | 0.0036361
2015-08-19 22:00 | 5.4 | 3.7133 | 1.6867 | 0 | 12.8989 | 164.731 | 89.6898 | 0.31018 | 165.1251 | 146.5414 | 0 | 2.785 | 0.2 | 0 | 0.27 | 3.055 | 4.3 | 4.3955 | 1.0824 | 0.0027116
2015-08-19 23:00 | 3.59 | 2.4567 | 1.1333 | 0 | 12.8854 | 179.7334 | 90.1478 | -0.14784 | 179.7401 | 150.1468 | 0 | 1.8425 | 0.2 | 0 | 0.1795 | 2.022 | 5.6 | 5.6632 | 1.0773 | 0.0017863
2015-08-20 | 1.78 | 1.2 | 0.58 | 0 | 12.8718 | -165.2642 | 89.7472 | 0.25278 | -165.6424 | 146.7998 | 0 | 0.9 | 0.2 | 0 | 0.089 | 0.989 | 4.1 | 4.1309 | 1.0835 | 0.00087868
2015-08-20 01:00 | 15.2233 | 9.7267 | 5.4967 | 0 | 12.8582 | -150.2618 | 88.5159 | 1.4841 | -151.0686 | 138.1369 | 0 | 7.295 | 0.2 | 0 | 0.76117 | 8.0562 | 3.4 | 3.6518 | 1.0854 | 0.0071702
2015-08-20 02:00 | 28.6667 | 18.2533 | 10.4133 | 172.392 | 12.8447 | -135.2594 | 86.5369 | 3.4631 | -136.5643 | 126.6918 | 0 | 13.69 | 0.2 | 0 | 1.4333 | 15.1233 | 3.4 | 3.8726 | 1.0845 | 0.013449
2015-08-20 03:00 | 42.11 | 26.78 | 15.33 | 145.2242 | 12.8311 | -120.2569 | 83.9405 | 6.0595 | -122.1199 | 113.8978 | 0 | 20.085 | 0.2 | 0 | 2.1055 | 22.1905 | 3.6 | 4.2935 | 1.0828 | 0.019703
2015-08-20 04:00 | 69.6633 | 52.4733 | 17.19 | 108.6083 | 12.8175 | -105.2545 | 80.8932 | 9.1068 | -107.6861 | 100.4074 | 0 | 39.355 | 0.2 | 0 | 3.4832 | 42.8382 | 3.4 | 4.7387 | 1.081 | 0.037974
2015-08-20 05:00 | 97.2167 | 78.1667 | 19.05 | 88.6297 | 12.804 | -90.252 | 77.588 | 12.412 | -93.1789 | 86.5276 | 5.3681 | 58.625 | 0.2 | 0 | 4.8608 | 68.8539 | 3.2 | 5.3517 | 1.0786 | 0.060898
2015-08-20 06:00 | 124.77 | 103.86 | 20.91 | 76.9668 | 12.7904 | -75.2496 | 74.236 | 15.764 | -78.494 | 72.417 | 23.2507 | 77.895 | 0.2 | 0 | 6.2385 | 107.3842 | 3.3 | 6.6558 | 1.0734 | 0.094516
2015-08-20 07:00 | 182.1 | 115.25 | 66.85 | 205.9456 | 12.7768 | -60.2472 | 71.0586 | 18.9414 | -63.5275 | 58.1672 | 108.6245 | 86.4375 | 0.2 | 0 | 9.105 | 204.167 | 3.1 | 9.4802 | 1.0621 | 0.17781
2015-08-20 08:00 | 239.43 | 126.64 | 112.79 | 304.7638 | 12.7632 | -45.2447 | 68.2788 | 21.7212 | -48.2028 | 43.8411 | 219.8151 | 94.98 | 0.2 | 0 | 11.9715 | 326.7666 | 4.4 | 14.6115 | 1.0416 | 0.27908
2015-08-20 09:00 | 296.76 | 138.03 | 158.73 | 391.8999 | 12.7496 | -30.2423 | 66.1072 | 23.8928 | -32.4988 | 29.5031 | 341.082 | 103.5225 | 0.2 | 0 | 14.838 | 459.4425 | 5.4 | 19.7576 | 1.021 | 0.38464
2015-08-20 10:00 | 312.7033 | 138.9667 | 173.7367 | 406.865 | 12.736 | -15.2398 | 64.7219 | 25.2781 | -16.4717 | 15.3195 | 392.4081 | 104.225 | 0.2 | 0 | 15.6352 | 512.2682 | 3.7 | 19.7084 | 1.0212 | 0.42895
2015-08-20 11:00 | 328.6467 | 139.9033 | 188.7433 | 434.3595 | 12.7223 | -0.23733 | 64.2445 | 25.7555 | -0.25704 | 4.2505 | 433.1648 | 104.9275 | 0.2 | 0 | 16.4323 | 554.5247 | 4.8 | 22.1289 | 1.0115 | 0.45993
2015-08-20 12:00 | 344.59 | 140.84 | 203.75 | 477.104 | 12.7087 | 14.7651 | 64.7191 | 25.2809 | 15.9588 | 14.8881 | 461.0874 | 105.63 | 0.2 | 0 | 17.2295 | 583.9469 | 5.6 | 23.8483 | 1.0046 | 0.48104
2015-08-20 13:00 | 314.44 | 123.6633 | 190.7767 | 470.9657 | 12.6951 | 29.7676 | 66.1041 | 23.8959 | 31.9889 | 29.0617 | 411.6698 | 92.7475 | 0.2 | 0 | 15.722 | 520.1393 | 5.9 | 22.1544 | 1.0114 | 0.43137
2015-08-20 14:00 | 284.29 | 106.4867 | 177.8033 | 480.4544 | 12.6814 | 44.7701 | 68.2799 | 21.7201 | 47.6967 | 43.4032 | 349.0674 | 79.865 | 0.2 | 0 | 14.2145 | 443.1469 | 4.5 | 18.3483 | 1.0266 | 0.37305
2015-08-20 15:00 | 254.14 | 89.31 | 164.83 | 508.0784 | 12.6678 | 59.7726 | 71.0697 | 18.9303 | 63.0248 | 57.7378 | 271.2097 | 66.9825 | 0.2 | 0 | 12.707 | 350.8992 | 5.9 | 16.8656 | 1.0325 | 0.2971
2015-08-20 16:00 | 203.8333 | 71.09 | 132.7433 | 489.454 | 12.6542 | 74.775 | 74.2639 | 15.7361 | 77.9935 | 72.0007 | 151.2437 | 53.3175 | 0.2 | 0 | 10.1917 | 214.7529 | 5.2 | 11.911 | 1.0524 | 0.18532
2015-08-20 17:00 | 153.5267 | 52.87 | 100.6567 | 470.2477 | 12.6405 | 89.7775 | 77.6402 | 12.3598 | 92.6792 | 86.1306 | 31.7336 | 39.6525 | 0.2 | 0 | 7.6763 | 79.0624 | 5.8 | 8.2707 | 1.0669 | 0.069169
2015-08-20 18:00 | 103.22 | 34.65 | 68.57 | 437.2274 | 12.6269 | 104.78 | 80.9771 | 9.0229 | 107.1864 | 100.0387 | 0 | 25.9875 | 0.2 | 0 | 5.161 | 31.1485 | 4.9 | 5.8734 | 1.0765 | 0.027496
2015-08-20 19:00 | 71.57 | 24.7967 | 46.7733 | 452.2259 | 12.6132 | 119.7825 | 84.0633 | 5.9367 | 121.6206 | 113.572 | 0 | 18.5975 | 0.2 | 0 | 3.5785 | 22.176 | 4.3 | 4.993 | 1.08 | 0.01964
2015-08-20 20:00 | 39.92 | 14.9433 | 24.9767 | 434.5604 | 12.5995 | 134.785 | 86.7051 | 3.2949 | 136.0675 | 126.4347 | 0 | 11.2075 | 0.2 | 0 | 1.996 | 13.2035 | 2.7 | 3.1126 | 1.0875 | 0.011775
2015-08-20 21:00 | 8.27 | 5.09 | 3.18 | 0 | 12.5858 | 149.7875 | 88.7344 | 1.2656 | 150.5781 | 137.9965 | 0 | 3.8175 | 0.2 | 0 | 0.4135 | 4.231 | 3.5 | 3.6322 | 1.0855 | 0.003766
2015-08-20 22:00 | 6.0067 | 3.74 | 2.2667 | 0 | 12.5722 | 164.79 | 90.0194 | -0.019392 | 165.1632 | 146.8582 | 0 | 2.805 | 0.2 | 0 | 0.30033 | 3.1053 | 2.8 | 2.897 | 1.0884 | 0.0027715
2015-08-20 23:00 | 3.7433 | 2.39 | 1.3533 | 0 | 12.5585 | 179.7925 | 90.4748 | -0.47477 | 179.7975 | 150.4741 | 0 | 1.7925 | 0.2 | 0 | 0.18717 | 1.9797 | 2 | 2.0619 | 1.0918 | 0.0017723
2015-08-21 | 1.48 | 1.04 | 0.44 | 0 | 12.5448 | -165.205 | 90.0704 | -0.070365 | -165.5659 | 147.0666 | 0 | 0.78 | 0.2 | 0 | 0.074 | 0.854 | 1.9 | 1.9267 | 1.0923 | 0.00076491
2015-08-21 01:00 | 19.79 | 10.91 | 8.88 | 0 | 12.5311 | -150.2024 | 88.8345 | 1.1655 | -150.9744 | 138.325 | 0 | 8.1825 | 0.2 | 0 | 0.9895 | 9.172 | 1.8 | 2.0866 | 1.0917 | 0.0082104
2015-08-21 02:00 | 38.1 | 20.78 | 17.32 | 315.278 | 12.5174 | -135.1999 | 86.8508 | 3.1492 | -136.4548 | 126.8202 | 0 | 15.585 | 0.2 | 0 | 1.905 | 17.49 | 1.5 | 2.0466 | 1.0918 | 0.015659
2015-08-21 03:00 | 56.41 | 30.65 | 25.76 | 257.126 | 12.5037 | -120.1974 | 84.2502 | 5.7498 | -121.9982 | 113.9851 | 0 | 22.9875 | 0.2 | 0 | 2.8205 | 25.808 | 2.6 | 3.4065 | 1.0864 | 0.02299
2015-08-21 04:00 | 108.3467 | 38.3367 | 70.01 | 457.6191 | 12.49 | -105.1949 | 81.1999 | 8.8001 | -107.5556 | 100.4659 | 0 | 28.7525 | 0.2 | 0 | 5.4173 | 34.1698 | 3.4 | 4.4678 | 1.0821 | 0.03032
2015-08-21 05:00 | 160.2833 | 46.0233 | 114.26 | 544.7943 | 12.4763 | -90.1923 | 77.8934 | 12.1066 | -93.0435 | 86.5655 | 32.6373 | 34.5175 | 0.2 | 0 | 8.0142 | 75.169 | 2.7 | 5.049 | 1.0798 | 0.066558
2015-08-21 06:00 | 212.22 | 53.71 | 158.51 | 594.7174 | 12.4625 | -75.1898 | 74.5421 | 15.4579 | -78.3579 | 72.4399 | 179.4295 | 40.2825 | 0.2 | 0 | 10.611 | 230.323 | 3.9 | 11.0976 | 1.0556 | 0.19937
2015-08-21 07:00 | 265.4767 | 56.3567 | 209.12 | 654.5271 | 12.4488 | -60.1872 | 71.3674 | 18.6326 | -63.3955 | 58.1799 | 345.1017 | 42.2675 | 0.2 | 0 | 13.2738 | 400.643 | 4.2 | 16.7201 | 1.0331 | 0.33941
2015-08-21 08:00 | 318.7333 | 59.0033 | 259.73 | 711.575 | 12.4351 | -45.1847 | 68.592 | 21.408 | -48.08 | 43.849 | 513.1655 | 44.2525 | 0.2 | 0 | 15.9367 | 573.3546 | 4.5 | 22.4173 | 1.0103 | 0.47501
2015-08-21 09:00 | 371.99 | 61.65 | 310.34 | 775.9682 | 12.4213 | -30.1821 | 66.4256 | 23.5744 | -32.3907 | 29.5155 | 675.2648 | 46.2375 | 0.2 | 0 | 18.5995 | 740.1018 | 5 | 28.1282 | 0.98749 | 0.59929
2015-08-21 10:00 | 381.78 | 59.81 | 321.97 | 763.1514 | 12.4076 | -15.1796 | 65.0457 | 24.9543 | -16.3833 | 15.368 | 735.864 | 44.8575 | 0.2 | 0 | 19.089 | 799.8105 | 4.6 | 29.5941 | 0.98162 | 0.64379
2015-08-21 11:00 | 391.57 | 57.97 | 333.6 | 776.9666 | 12.3938 | -0.17704 | 64.5729 | 25.4271 | -0.19146 | 4.5761 | 774.4899 | 43.4775 | 0.2 | 0 | 19.5785 | 837.5459 | 5.4 | 31.5733 | 0.97371 | 0.66873
2015-08-21 12:00 | 401.36 | 56.13 | 345.23 | 818.4429 | 12.3801 | 14.8255 | 65.0509 | 24.9491 | 16.0007 | 15.0507 | 790.3674 | 42.0975 | 0.2 | 0 | 20.068 | 852.5329 | 6.1 | 32.7417 | 0.96903 | 0.67743
2015-08-21 13:00 | 362.33 | 54.2033 | 308.1267 | 770.8058 | 12.3663 | 29.8281 | 66.4377 | 23.5623 | 32.0089 | 29.1901 | 672.9182 | 40.6525 | 0.2 | 0 | 18.1165 | 731.6872 | 5.9 | 28.7652 | 0.98494 | 0.59095
2015-08-21 14:00 | 323.3 | 52.2767 | 271.0233 | 743.2459 | 12.3525 | 44.8307 | 68.6141 | 21.3859 | 47.699 | 43.5271 | 538.8899 | 39.2075 | 0.2 | 0 | 16.165 | 594.2624 | 5 | 23.5707 | 1.0057 | 0.49008
2015-08-21 15:00 | 284.27 | 50.35 | 233.92 | 733.5321 | 12.3387 | 59.8332 | 71.4039 | 18.5961 | 63.0145 | 57.8659 | 390.1675 | 37.7625 | 0.2 | 0 | 14.2135 | 442.1435 | 5.2 | 19.017 | 1.0239 | 0.37123
2015-08-21 16:00 | 222.4633 | 48.1633 | 174.3 | 656.2748 | 12.325 | 74.8358 | 74.598 | 15.402 | 77.9762 | 72.1381 | 201.2951 | 36.1225 | 0.2 | 0 | 11.1232 | 248.5408 | 5.5 | 13.2669 | 1.0469 | 0.21337
2015-08-21 17:00 | 160.6567 | 45.9767 | 114.68 | 550.4208 | 12.3112 | 89.8384 | 77.9743 | 12.0257 | 92.6606 | 86.2814 | 35.6987 | 34.4825 | 0.2 | 0 | 8.0328 | 78.214 | 4.4 | 6.8442 | 1.0726 | 0.068793
2015-08-21 18:00 | 98.85 | 43.79 | 55.06 | 364.4887 | 12.2974 | 104.841 | 81.3116 | 8.6884 | 107.1715 | 100.2076 | 0 | 32.8425 | 0.2 | 0 | 4.9425 | 37.785 | 3.7 | 4.8808 | 1.0805 | 0.033477
2015-08-21 19:00 | 68.3467 | 30.7333 | 37.6133 | 385.3281 | 12.2836 | 119.8436 | 84.3982 | 5.6018 | 121.6142 | 113.7654 | 0 | 23.05 | 0.2 | 0 | 3.4173 | 26.4673 | 3.3 | 4.1271 | 1.0835 | 0.023515
2015-08-21 20:00 | 37.8433 | 17.6767 | 20.1667 | 0 | 12.2698 | 134.8461 | 87.0401 | 2.9599 | 136.0736 | 126.6617 | 0 | 13.2575 | 0.2 | 0 | 1.8922 | 15.1497 | 2.4 | 2.8734 | 1.0885 | 0.013522
2015-08-21 21:00 | 7.34 | 4.62 | 2.72 | 0 | 12.256 | 149.8487 | 89.0689 | 0.93107 | 150.6001 | 138.2683 | 0 | 3.465 | 0.2 | 0 | 0.367 | 3.832 | 2.3 | 2.4198 | 1.0903 | 0.0034261
2015-08-21 22:00 | 5.19 | 3.26 | 1.93 | 0 | 12.2422 | 164.8513 | 90.3524 | -0.35236 | 165.2035 | 147.1788 | 0 | 2.445 | 0.2 | 0 | 0.2595 | 2.7045 | 3.1 | 3.1845 | 1.0873 | 0.0024112
2015-08-21 23:00 | 3.04 | 1.9 | 1.14 | 0 | 12.2283 | 179.8539 | 90.805 | -0.80496 | 179.8572 | 150.8046 | 0 | 1.425 | 0.2 | 0 | 0.152 | 1.577 | 1.2 | 1.2493 | 1.095 | 0.001416
2015-08-22 | 0.89 | 0.54 | 0.35 | 0 | 12.2145 | -165.1434 | 90.3966 | -0.39663 | -165.4869 | 147.3341 | 0 | 0.405 | 0.2 | 0 | 0.0445 | 0.4495 | 1.5 | 1.514 | 1.0939 | 0.00040322
2015-08-22 01:00 | 15.9133 | 7.6833 | 8.23 | 0 | 12.2007 | -150.1408 | 89.1561 | 0.84393 | -150.8776 | 138.5123 | 0 | 5.7625 | 0.2 | 0 | 0.79567 | 6.5582 | 1.4 | 1.6049 | 1.0936 | 0.0058809
2015-08-22 02:00 | 30.9367 | 14.8267 | 16.11 | 0 | 12.1868 | -135.1382 | 87.1676 | 2.8324 | -136.3425 | 126.9472 | 0 | 11.12 | 0.2 | 0 | 1.5468 | 12.6668 | 1.9 | 2.2958 | 1.0908 | 0.01133
2015-08-22 03:00 | 45.96 | 21.97 | 23.99 | 253.1739 | 12.173 | -120.1356 | 84.5627 | 5.4373 | -121.8736 | 114.0708 | 0 | 16.4775 | 0.2 | 0 | 2.298 | 18.7755 | 2 | 2.5867 | 1.0897 | 0.016776
2015-08-22 04:00 | 62.81 | 45.23 | 17.58 | 119.0662 | 12.1592 | -105.133 | 81.5093 | 8.4907 | -107.4222 | 100.5231 | 0 | 33.9225 | 0.2 | 0 | 3.1405 | 37.063 | 2.6 | 3.7582 | 1.085 | 0.032974
2015-08-22 05:00 | 79.66 | 68.49 | 11.17 | 54.629 | 12.1453 | -90.1304 | 78.2015 | 11.7985 | -92.9053 | 86.6022 | 3.2378 | 51.3675 | 0.2 | 0 | 3.983 | 58.5883 | 4.1 | 5.9309 | 1.0763 | 0.051707
2015-08-22 06:00 | 96.51 | 91.75 | 4.76 | 18.2144 | 12.1314 | -75.1277 | 74.8509 | 15.1491 | -78.2191 | 72.462 | 5.4887 | 68.8125 | 0.2 | 0 | 4.8255 | 79.1267 | 4.3 | 6.7727 | 1.0729 | 0.069615
2015-08-22 07:00 | 108.35 | 105.1767 | 3.1733 | 10.0952 | 12.1176 | -60.1251 | 71.679 | 18.321 | -63.2608 | 58.1923 | 5.3209 | 78.8825 | 0.2 | 0 | 5.4175 | 89.6209 | 4.9 | 7.7007 | 1.0692 | 0.078574
2015-08-22 08:00 | 120.19 | 118.6033 | 1.5867 | 4.409 | 12.1037 | -45.1225 | 68.908 | 21.092 | -47.9548 | 43.8573 | 3.1792 | 88.9525 | 0.2 | 0 | 6.0095 | 98.1412 | 5.9 | 8.9669 | 1.0641 | 0.085637
2015-08-22 09:00 | 132.03 | 132.03 | 0 | 0 | 12.0898 | -30.1198 | 66.7471 | 23.2529 | -32.2803 | 29.5299 | 0 | 99.0225 | 0.2 | 0 | 6.6015 | 105.624 | 5 | 8.3008 | 1.0668 | 0.092397
2015-08-22 10:00 | 118.06 | 118.0367 | 0.023333 | 0.055994 | 12.076 | -15.1172 | 65.3727 | 24.6273 | -16.2925 | 15.4222 | 0.053977 | 88.5275 | 0.2 | 0 | 5.903 | 94.4845 | 4.6 | 7.5526 | 1.0698 | 0.082884
2015-08-22 11:00 | 104.09 | 104.0433 | 0.046667 | 0.11003 | 12.0621 | -0.11452 | 64.9046 | 25.0954 | -0.12366 | 4.9059 | 0.10963 | 78.0325 | 0.2 | 0 | 5.2045 | 83.3466 | 4.4 | 7.0046 | 1.072 | 0.073264
2015-08-22 12:00 | 90.12 | 90.05 | 0.07 | 0.16807 | 12.0482 | 14.8881 | 65.386 | 24.614 | 16.0447 | 15.2221 | 0.16217 | 67.5375 | 0.2 | 0 | 4.506 | 72.2057 | 4.3 | 6.5564 | 1.0738 | 0.063577
2015-08-22 13:00 | 75.6633 | 75.6167 | 0.046667 | 0.11834 | 12.0343 | 29.8908 | 66.7747 | 23.2253 | 32.0309 | 29.3245 | 0.10317 | 56.7125 | 0.2 | 0 | 3.7832 | 60.5988 | 4.1 | 5.9937 | 1.076 | 0.053469
2015-08-22 14:00 | 61.2067 | 61.1833 | 0.023333 | 0.064968 | 12.0204 | 44.8935 | 68.9518 | 21.0482 | 47.703 | 43.6556 | 0.047004 | 45.8875 | 0.2 | 0 | 3.0603 | 48.9948 | 3.1 | 4.6311 | 1.0815 | 0.043449
2015-08-22 15:00 | 46.75 | 46.75 | 0 | 0 | 12.0065 | 59.8961 | 71.7417 | 18.2583 | 63.0059 | 57.9981 | 0 | 35.0625 | 0.2 | 0 | 2.3375 | 37.4 | 4 | 5.1688 | 1.0793 | 0.033101
2015-08-22 16:00 | 38.37 | 38.37 | 0 | 0 | 11.9926 | 74.8988 | 74.9357 | 15.0643 | 77.9607 | 72.279 | 0 | 28.7775 | 0.2 | 0 | 1.9185 | 30.696 | 4.6 | 5.5592 | 1.0778 | 0.027128
2015-08-22 17:00 | 29.99 | 29.99 | 0 | 0 | 11.9786 | 89.9015 | 78.3121 | 11.6879 | 92.6436 | 86.4354 | 0 | 22.4925 | 0.2 | 0 | 1.4995 | 23.992 | 4.3 | 5.0498 | 1.0798 | 0.021243
2015-08-22 18:00 | 21.61 | 21.61 | 0 | 0 | 11.9647 | 104.9041 | 81.6497 | 8.3503 | 107.1583 | 100.3795 | 0 | 16.2075 | 0.2 | 0 | 1.0805 | 17.288 | 5.6 | 6.1402 | 1.0754 | 0.015246
2015-08-22 19:00 | 14.9067 | 14.9067 | 0 | 0 | 11.9508 | 119.9068 | 84.7367 | 5.2633 | 121.6095 | 113.9618 | 0 | 11.18 | 0.2 | 0 | 0.74533 | 11.9253 | 5.8 | 6.1727 | 1.0753 | 0.010515
2015-08-22 20:00 | 8.2033 | 8.2033 | 0 | 0 | 11.9368 | 134.9095 | 87.3787 | 2.6213 | 136.0815 | 126.8915 | 0 | 6.1525 | 0.2 | 0 | 0.41017 | 6.5627 | 6.2 | 6.4051 | 1.0744 | 0.0057817
2015-08-22 21:00 | 1.5 | 1.5 | 0 | 0 | 11.9229 | 149.9122 | 89.4069 | 0.59312 | 150.6241 | 138.5432 | 0 | 1.125 | 0.2 | 0 | 0.075 | 1.2 | 7 | 7.0375 | 1.0718 | 0.0010547
2015-08-22 22:00 | 1.0233 | 1.0233 | 0 | 0 | 11.909 | 164.9149 | 90.6886 | -0.68864 | 165.2459 | 147.503 | 0 | 0.7675 | 0.2 | 0 | 0.051167 | 0.81867 | 5.7 | 5.7256 | 1.0771 | 0.00072306
2015-08-22 23:00 | 0.54667 | 0.54667 | 0 | 0 | 11.895 | 179.9176 | 91.1383 | -1.1383 | 179.9193 | 151.1382 | 0 | 0.41 | 0.2 | 0 | 0.027333 | 0.43733 | 5.5 | 5.5137 | 1.0779 | 0.00038657
2015-08-23 | 0.07 | 0.07 | 0 | 0 | 11.881 | -165.0797 | 90.7259 | -0.72592 | -165.4054 | 147.6022 | 0 | 0.0525 | 0.2 | 0 | 0.0035 | 0.056 | 5.9 | 5.9018 | 1.0764 | 4.9428e-05
2015-08-23 01:00 | 4.7233 | 3.44 | 1.2833 | 0 | 11.8671 | -150.077 | 89.4805 | 0.51947 | -150.7781 | 138.6985 | 0 | 2.58 | 0.2 | 0 | 0.23617 | 2.8162 | 5.5 | 5.588 | 1.0776 | 0.0024886
2015-08-23 02:00 | 9.3767 | 6.81 | 2.5667 | 0 | 11.8531 | -135.0743 | 87.4871 | 2.5129 | -136.2275 | 127.0726 | 0 | 5.1075 | 0.2 | 0 | 0.46883 | 5.5763 | 5.3 | 5.4743 | 1.0781 | 0.0049297
2015-08-23 03:00 | 14.03 | 10.18 | 3.85 | 43.1226 | 11.8391 | -120.0716 | 84.8778 | 5.1222 | -121.7463 | 114.155 | 0 | 7.635 | 0.2 | 0 | 0.7015 | 8.3365 | 6 | 6.2605 | 1.075 | 0.0073483
2015-08-23 04:00 | 23.4767 | 20.8767 | 2.6 | 18.2763 | 11.8252 | -105.0689 | 81.8213 | 8.1787 | -107.2862 | 100.5788 | 0 | 15.6575 | 0.2 | 0 | 1.1738 | 16.8313 | 5.1 | 5.626 | 1.0775 | 0.014871
2015-08-23 05:00 | 32.9233 | 31.5733 | 1.35 | 6.7785 | 11.8112 | -90.0662 | 78.5122 | 11.4878 | -92.7644 | 86.6377 | 0.39755 | 23.68 | 0.2 | 0 | 1.6462 | 25.7237 | 5.3 | 6.1039 | 1.0756 | 0.022688
2015-08-23 06:00 | 42.37 | 42.27 | 0.1 | 0.3905 | 11.7972 | -75.0635 | 75.1624 | 14.8376 | -78.0776 | 72.4833 | 0.11753 | 31.7025 | 0.2 | 0 | 2.1185 | 33.9385 | 5.6 | 6.6606 | 1.0734 | 0.029871
2015-08-23 07:00 | 76.2067 | 67.07 | 9.1367 | 29.5562 | 11.7832 | -60.0608 | 71.9933 | 18.0067 | -63.1236 | 58.2044 | 15.5729 | 50.3025 | 0.2 | 0 | 3.8103 | 69.6857 | 3.9 | 6.0777 | 1.0757 | 0.061467
2015-08-23 08:00 | 110.0433 | 91.87 | 18.1733 | 51.2401 | 11.7692 | -45.058 | 69.2268 | 20.7732 | -47.827 | 43.866 | 36.9422 | 68.9025 | 0.2 | 0 | 5.5022 | 111.3468 | 3.8 | 7.2796 | 1.0709 | 0.097776
2015-08-23 09:00 | 143.88 | 116.67 | 27.21 | 69.8438 | 11.7552 | -30.0553 | 67.0714 | 22.9286 | -32.1675 | 29.5462 | 60.7612 | 87.5025 | 0.2 | 0 | 7.194 | 155.4577 | 3.7 | 8.5581 | 1.0658 | 0.13586
2015-08-23 10:00 | 142.5867 | 122.3667 | 20.22 | 49.1406 | 11.7412 | -15.0526 | 65.7026 | 24.2974 | -16.1995 | 15.4825 | 47.3574 | 91.775 | 0.2 | 0 | 7.1293 | 146.2617 | 3.4 | 7.9707 | 1.0681 | 0.1281
2015-08-23 11:00 | 141.2933 | 128.0633 | 13.23 | 31.5883 | 11.7272 | -0.049821 | 65.2395 | 24.7605 | -0.053719 | 5.2397 | 31.4563 | 96.0475 | 0.2 | 0 | 7.0647 | 134.5685 | 3.8 | 8.0053 | 1.068 | 0.11785
2015-08-23 12:00 | 140 | 133.76 | 6.24 | 15.1778 | 11.7132 | 14.9529 | 65.7244 | 24.2756 | 16.0907 | 15.4021 | 14.6327 | 100.32 | 0.2 | 0 | 7 | 121.9527 | 3 | 6.811 | 1.0728 | 0.10728
2015-08-23 13:00 | 120.3 | 115.98 | 4.32 | 11.1088 | 11.6991 | 29.9557 | 67.1151 | 22.8849 | 32.0549 | 29.4648 | 9.672 | 86.985 | 0.2 | 0 | 6.015 | 102.672 | 3.4 | 6.6085 | 1.0736 | 0.090385
2015-08-23 14:00 | 100.6 | 98.2 | 2.4 | 6.7875 | 11.6851 | 44.9584 | 69.293 | 20.707 | 47.7089 | 43.7888 | 4.8999 | 73.65 | 0.2 | 0 | 5.03 | 83.5799 | 4.4 | 7.0119 | 1.072 | 0.073467
2015-08-23 15:00 | 80.9 | 80.42 | 0.48 | 1.5603 | 11.6711 | 59.9612 | 72.083 | 17.917 | 62.999 | 58.1342 | 0.82372 | 60.315 | 0.2 | 0 | 4.045 | 65.1837 | 4.1 | 6.137 | 1.0755 | 0.057484
2015-08-23 16:00 | 68.5733 | 63.0633 | 5.51 | 21.6804 | 11.657 | 74.9639 | 75.277 | 14.723 | 77.9467 | 72.4235 | 6.547 | 47.2975 | 0.2 | 0 | 3.4287 | 57.2732 | 3.9 | 5.6898 | 1.0772 | 0.050592
2015-08-23 17:00 | 56.2467 | 45.7067 | 10.54 | 53.5727 | 11.643 | 89.9667 | 78.6535 | 11.3465 | 92.6281 | 86.5925 | 3.1842 | 34.28 | 0.2 | 0 | 2.8123 | 40.2765 | 3.3 | 4.5586 | 1.0818 | 0.035727
2015-08-23 18:00 | 43.92 | 28.35 | 15.57 | 111.7546 | 11.6289 | 104.9695 | 81.9913 | 8.0087 | 107.1466 | 100.5543 | 0 | 21.2625 | 0.2 | 0 | 2.196 | 23.4585 | 4.1 | 4.8331 | 1.0807 | 0.020788
2015-08-23 19:00 | 30.11 | 19.5233 | 10.5867 | 123.4047 | 11.6149 | 119.9722 | 85.0786 | 4.9214 | 121.6063 | 114.1608 | 0 | 14.6425 | 0.2 | 0 | 1.5055 | 16.148 | 5.4 | 5.9046 | 1.0764 | 0.014253
2015-08-23 20:00 | 16.3 | 10.6967 | 5.6033 | 0 | 11.6008 | 134.975 | 87.7207 | 2.2793 | 136.0911 | 127.1241 | 0 | 8.0225 | 0.2 | 0 | 0.815 | 8.8375 | 5.4 | 5.6762 | 1.0773 | 0.0078069
2015-08-23 21:00 | 2.49 | 1.87 | 0.62 | 0 | 11.5867 | 149.9778 | 89.7482 | 0.25184 | 150.6499 | 138.8212 | 0 | 1.4025 | 0.2 | 0 | 0.1245 | 1.527 | 5.4 | 5.4477 | 1.0782 | 0.0013501
2015-08-23 22:00 | 1.6833 | 1.27 | 0.41333 | 0 | 11.5727 | 164.9805 | 91.0281 | -1.0281 | 165.2904 | 147.8307 | 0 | 0.9525 | 0.2 | 0 | 0.084167 | 1.0367 | 4.7 | 4.7324 | 1.0811 | 0.00091898
2015-08-23 23:00 | 0.87667 | 0.67 | 0.20667 | 0 | 11.5586 | 179.9833 | 91.4748 | -1.4748 | 179.9837 | 151.4748 | 0 | 0.5025 | 0.2 | 0 | 0.043833 | 0.54633 | 4 | 4.0171 | 1.0839 | 0.00048559
2015-08-24 | 0.07 | 0.07 | 0 | 0 | 11.5445 | -165.0139 | 91.0582 | -1.0582 | -165.3214 | 147.8708 | 0 | 0.0525 | 0.2 | 0 | 0.0035 | 0.056 | 4.4 | 4.4018 | 1.0824 | 4.9703e-05
2015-08-24 01:00 | 4.3967 | 4.3233 | 0.073333 | 0 | 11.5304 | -150.0111 | 89.8078 | 0.19219 | -150.676 | 138.8836 | 0 | 3.2425 | 0.2 | 0 | 0.21983 | 3.4623 | 5.2 | 5.3082 | 1.0788 | 0.0030627
2015-08-24 02:00 | 8.7233 | 8.5767 | 0.14667 | 0 | 11.5163 | -135.0083 | 87.8093 | 2.1907 | -136.1099 | 127.1965 | 0 | 6.4325 | 0.2 | 0 | 0.43617 | 6.8687 | 5 | 5.2146 | 1.0791 | 0.0060781
2015-08-24 03:00 | 13.05 | 12.83 | 0.22 | 2.6267 | 11.5022 | -120.0055 | 85.1955 | 4.8045 | -121.6163 | 114.2376 | 0 | 9.6225 | 0.2 | 0 | 0.6525 | 10.275 | 5 | 5.3211 | 1.0787 | 0.0090887
2015-08-24 04:00 | 25.9267 | 25.5767 | 0.35 | 2.558 | 11.4881 | -105.0027 | 82.1359 | 7.8641 | -107.1474 | 100.633 | 0 | 19.1825 | 0.2 | 0 | 1.2963 | 20.4788 | 4.6 | 5.24 | 1.079 | 0.01812
2015-08-24 05:00 | 38.8033 | 38.3233 | 0.48 | 2.4768 | 11.474 | -89.9999 | 78.8254 | 11.1746 | -92.6208 | 86.6721 | 0.14378 | 28.7425 | 0.2 | 0 | 1.9402 | 30.8264 | 4.3 | 5.2633 | 1.0789 | 0.027273
2015-08-24 06:00 | 51.68 | 51.07 | 0.61 | 2.4324 | 11.4599 | -74.9971 | 75.4764 | 14.5236 | -77.9336 | 72.5038 | 0.73129 | 38.3025 | 0.2 | 0 | 2.584 | 41.6178 | 2.9 | 4.2006 | 1.0832 | 0.036966
2015-08-24 07:00 | 70.8133 | 67.5567 | 3.2567 | 10.7175 | 11.4458 | -59.9943 | 72.3102 | 17.6898 | -62.9839 | 58.2162 | 5.6451 | 50.6675 | 0.2 | 0 | 3.5407 | 59.8533 | 3.1 | 4.9704 | 1.0801 | 0.053012
2015-08-24 08:00 | 89.9467 | 84.0433 | 5.9033 | 16.8948 | 11.4316 | -44.9915 | 69.5483 | 20.4517 | -47.6969 | 43.8754 | 12.1786 | 63.0325 | 0.2 | 0 | 4.4973 | 79.7084 | 2.8 | 5.2909 | 1.0788 | 0.070514
2015-08-24 09:00 | 109.08 | 100.53 | 8.55 | 22.2472 | 11.4175 | -29.9887 | 67.3986 | 22.6014 | -32.0524 | 29.5647 | 19.3506 | 75.3975 | 0.2 | 0 | 5.454 | 100.2021 | 3.2 | 6.3313 | 1.0747 | 0.088301
2015-08-24 10:00 | 127.0333 | 121.31 | 5.7233 | 14.091 | 11.4034 | -14.9858 | 66.0356 | 23.9644 | -16.1043 | 15.5489 | 13.5753 | 90.9825 | 0.2 | 0 | 6.3517 | 110.9095 | 3.7 | 7.1659 | 1.0713 | 0.097434
2015-08-24 11:00 | 144.9867 | 142.09 | 2.8967 | 7.0059 | 11.3892 | 0.016995 | 65.5774 | 24.4226 | 0.018298 | 5.5775 | 6.9727 | 106.5675 | 0.2 | 0 | 7.2493 | 120.7895 | 4.3 | 8.0747 | 1.0677 | 0.10575
2015-08-24 12:00 | 162.94 | 162.87 | 0.07 | 0.17255 | 11.3751 | 15.0198 | 66.0659 | 23.9341 | 16.1387 | 15.5906 | 0.1662 | 122.1525 | 0.2 | 0 | 8.147 | 130.4657 | 5.6 | 9.6771 | 1.0613 | 0.11354
2015-08-24 13:00 | 153.12 | 138.2533 | 14.8667 | 38.7811 | 11.3609 | 30.0227 | 67.4588 | 22.5412 | 32.0807 | 29.611 | 33.7163 | 103.69 | 0.2 | 0 | 7.656 | 145.0623 | 4.6 | 9.1332 | 1.0635 | 0.1265
2015-08-24 14:00 | 143.3 | 113.6367 | 29.6633 | 85.25 | 11.3468 | 45.0255 | 69.6376 | 20.3624 | 47.7166 | 43.9266 | 61.3995 | 85.2275 | 0.2 | 0 | 7.165 | 153.792 | 4.7 | 9.506 | 1.062 | 0.13393
2015-08-24 15:00 | 133.48 | 89.02 | 44.46 | 147.2635 | 11.3326 | 60.0283 | 72.4278 | 17.5722 | 62.9938 | 58.2742 | 77.4391 | 66.765 | 0.2 | 0 | 6.674 | 150.8781 | 6.1 | 10.8149 | 1.0567 | 0.13074
2015-08-24 16:00 | 112.9567 | 69.0867 | 43.87 | 176.6652 | 11.3184 | 75.0312 | 75.6217 | 14.3783 | 77.9343 | 72.5713 | 52.9145 | 51.815 | 0.2 | 0 | 5.6478 | 110.3773 | 5.3 | 8.7493 | 1.065 | 0.096393
2015-08-24 17:00 | 92.4333 | 49.1533 | 43.28 | 226.7889 | 11.3043 | 90.034 | 78.9983 | 11.0017 | 92.6142 | 86.7528 | 12.8463 | 36.865 | 0.2 | 0 | 4.6217 | 54.333 | 5 | 6.6979 | 1.0732 | 0.047815
2015-08-24 18:00 | 71.91 | 29.22 | 42.69 | 320.1183 | 11.2901 | 105.0369 | 82.3364 | 7.6636 | 107.1365 | 100.732 | 0 | 21.915 | 0.2 | 0 | 3.5955 | 25.5105 | 4.9 | 5.6972 | 1.0772 | 0.022534
2015-08-24 19:00 | 48.9667 | 20.12 | 28.8467 | 361.5704 | 11.2759 | 120.0397 | 85.424 | 4.576 | 121.6048 | 114.3626 | 0 | 15.09 | 0.2 | 0 | 2.4483 | 17.5383 | 3.8 | 4.3481 | 1.0826 | 0.015569
2015-08-24 20:00 | 26.0233 | 11.02 | 15.0033 | 0 | 11.2617 | 135.0426 | 88.0659 | 1.9341 | 136.1024 | 127.3593 | 0 | 8.265 | 0.2 | 0 | 1.3012 | 9.5662 | 3.9 | 4.1989 | 1.0832 | 0.0084969
2015-08-24 21:00 | 3.08 | 1.92 | 1.16 | 0 | 11.2475 | 150.0454 | 90.0927 | -0.092666 | 150.6776 | 139.102 | 0 | 1.44 | 0.2 | 0 | 0.154 | 1.594 | 3.5 | 3.5498 | 1.0858 | 0.0014192
2015-08-24 22:00 | 2.0767 | 1.28 | 0.79667 | 0 | 11.2333 | 165.0483 | 91.3707 | -1.3707 | 165.337 | 148.1618 | 0 | 0.96 | 0.2 | 0 | 0.10383 | 1.0638 | 4 | 4.0332 | 1.0839 | 0.0009455
2015-08-24 23:00 | 1.0733 | 0.64 | 0.43333 | 0 | 11.2191 | 180.0512 | 91.8142 | -1.8142 | -179.9498 | 151.8142 | 0 | 0.48 | 0.2 | 0 | 0.053667 | 0.53367 | 3.6 | 3.6167 | 1.0855 | 0.00047504
2015-08-25 | 0.07 | 0 | 0.07 | 0 | 11.2049 | -164.9459 | 91.3932 | -1.3932 | -165.235 | 148.1398 | 0 | 0 | 0.2 | 0 | 0.0035 | 0.0035 | 3.5 | 3.5001 | 1.086 | 3.1168e-06
2015-08-25 01:00 | 13.9333 | 6.9267 | 7.0067 | 0 | 11.1907 | -149.9431 | 90.1378 | -0.1378 | -150.5714 | 139.0674 | 0 | 5.195 | 0.2 | 0 | 0.69667 | 5.8917 | 3.4 | 3.5841 | 1.0857 | 0.005245
2015-08-25 02:00 | 27.7967 | 13.8533 | 13.9433 | 0 | 11.1765 | -134.9402 | 88.1341 | 1.8659 | -135.9896 | 127.3186 | 0 | 10.39 | 0.2 | 0 | 1.3898 | 11.7798 | 3.5 | 3.8681 | 1.0845 | 0.010476
2015-08-25 03:00 | 41.66 | 20.78 | 20.88 | 267.0581 | 11.1623 | -119.9373 | 85.5157 | 4.4843 | -121.4836 | 114.3185 | 0 | 15.585 | 0.2 | 0 | 2.083 | 17.668 | 3.5 | 4.0521 | 1.0838 | 0.015702
2015-08-25 04:00 | 87.25 | 37.29 | 49.96 | 380.3818 | 11.148 | -104.9344 | 82.4529 | 7.5471 | -107.0061 | 100.6859 | 0 | 27.9675 | 0.2 | 0 | 4.3625 | 32.33 | 3.4 | 4.4103 | 1.0824 | 0.028694
2015-08-25 05:00 | 132.84 | 53.8 | 79.04 | 419.553 | 11.1338 | -89.9315 | 79.1411 | 10.8589 | -92.4747 | 86.7053 | 24.1122 | 40.35 | 0.2 | 0 | 6.642 | 71.1042 | 3 | 5.222 | 1.0791 | 0.062918
2015-08-25 06:00 | 178.43 | 70.31 | 108.12 | 440.5369 | 11.1196 | -74.9286 | 75.7929 | 14.2071 | -77.7871 | 72.5235 | 132.2994 | 52.7325 | 0.2 | 0 | 8.9215 | 193.9534 | 2.9 | 8.961 | 1.0642 | 0.16925
2015-08-25 07:00 | 197.0467 | 118.5967 | 78.45 | 262.7725 | 11.1053 | -59.9258 | 72.6296 | 17.3704 | -62.8418 | 58.2278 | 138.3609 | 88.9475 | 0.2 | 0 | 9.8523 | 237.1608 | 2.6 | 10.0113 | 1.06 | 0.20613
2015-08-25 08:00 | 215.6633 | 166.8833 | 48.78 | 141.7565 | 11.0911 | -44.9229 | 69.8725 | 20.1275 | -47.5645 | 43.8855 | 102.1678 | 125.1625 | 0.2 | 0 | 10.7832 | 238.1134 | 2.8 | 10.241 | 1.059 | 0.20678
2015-08-25 09:00 | 234.28 | 215.17 | 19.11 | 50.4227 | 11.0768 | -29.9199 | 67.7285 | 22.2715 | -31.9351 | 29.5855 | 43.8486 | 161.3775 | 0.2 | 0 | 11.714 | 216.9401 | 2.5 | 9.2794 | 1.0629 | 0.18908
2015-08-25 10:00 | 235.18 | 214.6867 | 20.4933 | 51.1302 | 11.0626 | -14.917 | 66.3714 | 23.6286 | -16.007 | 15.6217 | 49.2415 | 161.015 | 0.2 | 0 | 11.759 | 222.0155 | 3.1 | 10.038 | 1.0598 | 0.19295
2015-08-25 11:00 | 236.08 | 214.2033 | 21.8767 | 53.6143 | 11.0483 | 0.085869 | 65.9184 | 24.0816 | 0.092312 | 5.9189 | 53.3285 | 160.6525 | 0.2 | 0 | 11.804 | 225.785 | 3.7 | 10.7558 | 1.057 | 0.19569
2015-08-25 12:00 | 236.98 | 213.72 | 23.26 | 58.1239 | 11.034 | 15.0888 | 66.4106 | 23.5894 | 16.1886 | 15.7874 | 55.9314 | 160.29 | 0.2 | 0 | 11.849 | 228.0704 | 3.5 | 10.6272 | 1.0575 | 0.19777
2015-08-25 13:00 | 200.0467 | 184.4633 | 15.5833 | 41.2531 | 11.0198 | 30.0917 | 67.8057 | 22.1943 | 32.1084 | 29.7631 | 35.8112 | 138.3475 | 0.2 | 0 | 10.0023 | 184.1611 | 3.8 | 9.555 | 1.0618 | 0.16034
2015-08-25 14:00 | 163.1133 | 155.2067 | 7.9067 | 23.1014 | 11.0055 | 45.0946 | 69.9854 | 20.0146 | 47.7259 | 44.069 | 16.5984 | 116.405 | 0.2 | 0 | 8.1557 | 141.1591 | 4.1 | 8.5112 | 1.066 | 0.12338
2015-08-25 15:00 | 126.18 | 125.95 | 0.23 | 0.77674 | 10.9912 | 60.0975 | 72.7758 | 17.2242 | 62.9902 | 58.4181 | 0.40679 | 94.4625 | 0.2 | 0 | 6.309 | 101.1783 | 3.5 | 6.6618 | 1.0734 | 0.089052
2015-08-25 16:00 | 108.4267 | 94.5 | 13.9267 | 57.4452 | 10.9769 | 75.1005 | 75.9698 | 14.0302 | 77.9235 | 72.7225 | 17.0612 | 70.875 | 0.2 | 0 | 5.4213 | 93.3575 | 3.3 | 6.2174 | 1.0751 | 0.082305
2015-08-25 17:00 | 90.6733 | 63.05 | 27.6233 | 149.4201 | 10.9626 | 90.1034 | 79.3464 | 10.6536 | 92.6018 | 86.916 | 8.0387 | 47.2875 | 0.2 | 0 | 4.5337 | 59.8599 | 3.8 | 5.6706 | 1.0773 | 0.05288
2015-08-25 18:00 | 72.92 | 31.6 | 41.32 | 324.5153 | 10.9483 | 105.1063 | 82.6848 | 7.3152 | 107.1278 | 100.9124 | 0 | 23.7 | 0.2 | 0 | 3.646 | 27.346 | 3.3 | 4.1546 | 1.0834 | 0.024293
2015-08-25 19:00 | 49.33 | 21.56 | 27.77 | 376.7216 | 10.934 | 120.1093 | 85.7726 | 4.2274 | 121.6048 | 114.5668 | 0 | 16.17 | 0.2 | 0 | 2.4665 | 18.6365 | 3.1 | 3.6824 | 1.0853 | 0.016585
2015-08-25 20:00 | 25.74 | 11.52 | 14.22 | 0 | 10.9197 | 135.1122 | 88.4145 | 1.5855 | 136.1154 | 127.597 | 0 | 8.64 | 0.2 | 0 | 1.287 | 9.927 | 2.6 | 2.9102 | 1.0884 | 0.0088594
2015-08-25 21:00 | 2.15 | 1.48 | 0.67 | 0 | 10.9054 | 150.1152 | 90.4403 | -0.44031 | 150.7071 | 139.3855 | 0 | 1.11 | 0.2 | 0 | 0.1075 | 1.2175 | 2.3 | 2.338 | 1.0906 | 0.0010888
2015-08-25 22:00 | 1.4333 | 0.98667 | 0.44667 | 0 | 10.8911 | 165.1181 | 91.7164 | -1.7164 | 165.3855 | 148.4962 | 0 | 0.74 | 0.2 | 0 | 0.071667 | 0.81167 | 2 | 2.0254 | 1.0919 | 0.00072673
2015-08-25 23:00 | 0.71667 | 0.49333 | 0.22333 | 0 | 10.8768 | 180.1211 | 92.1565 | -2.1565 | -179.881 | 152.1563 | 0 | 0.37 | 0.2 | 0 | 0.035833 | 0.40583 | 1.5 | 1.5127 | 1.0939 | 0.00036405
2015-08-26 | 0 | 0 | 0 | 0 | 10.8624 | -164.876 | 91.7311 | -1.7311 | -165.1463 | 148.4089 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0932 | 0
2015-08-26 01:00 | 14.8533 | 5.57 | 9.2833 | 0 | 10.8481 | -149.873 | 90.4704 | -0.47043 | -150.4643 | 139.25 | 0 | 4.1775 | 0.2 | 0 | 0.74267 | 4.9202 | 1.6 | 1.7538 | 1.093 | 0.0044097
2015-08-26 02:00 | 29.7067 | 11.14 | 18.5667 | 0 | 10.8338 | -134.8701 | 88.4614 | 1.5386 | -135.8669 | 127.4391 | 0 | 8.355 | 0.2 | 0 | 1.4853 | 9.8403 | 1.4 | 1.7075 | 1.0932 | 0.0088209
2015-08-26 03:00 | 44.56 | 16.71 | 27.85 | 383.7698 | 10.8194 | -119.8671 | 85.8384 | 4.1616 | -121.3485 | 114.3978 | 0 | 12.5325 | 0.2 | 0 | 2.228 | 14.7605 | 1.1 | 1.5613 | 1.0938 | 0.013238
2015-08-26 04:00 | 94.42 | 29.5033 | 64.9167 | 515.9765 | 10.8051 | -104.8641 | 82.7723 | 7.2277 | -106.8622 | 100.7373 | 0 | 22.1275 | 0.2 | 0 | 4.721 | 26.8485 | 1.2 | 2.039 | 1.0918 | 0.024038
2015-08-26 05:00 | 144.28 | 42.2967 | 101.9833 | 557.4801 | 10.7907 | -89.8612 | 79.4592 | 10.5408 | -92.3262 | 86.7375 | 31.7268 | 31.7225 | 0.2 | 0 | 7.214 | 70.6633 | 1 | 3.2082 | 1.0872 | 0.062995
2015-08-26 06:00 | 194.14 | 55.09 | 139.05 | 579.3072 | 10.7764 | -74.8582 | 76.1118 | 13.8882 | -77.6382 | 72.5426 | 173.79 | 41.3175 | 0.2 | 0 | 9.707 | 224.8145 | 1.2 | 8.2255 | 1.0671 | 0.19672
2015-08-26 07:00 | 238.93 | 66.7333 | 172.1967 | 587.3412 | 10.762 | -59.8552 | 72.9516 | 17.0484 | -62.6974 | 58.2394 | 309.1596 | 50.05 | 0.2 | 0 | 11.9465 | 371.1561 | 1.9 | 13.4986 | 1.046 | 0.31835
2015-08-26 08:00 | 283.72 | 78.3767 | 205.3433 | 606.1774 | 10.7477 | -44.8522 | 70.1992 | 19.8008 | -47.4299 | 43.8963 | 436.809 | 58.7825 | 0.2 | 0 | 14.186 | 509.7775 | 2.1 | 18.0305 | 1.0279 | 0.42967
2015-08-26 09:00 | 328.51 | 90.02 | 238.49 | 638.326 | 10.7333 | -29.8492 | 68.0611 | 21.9389 | -31.8158 | 29.6087 | 554.9734 | 67.515 | 0.2 | 0 | 16.4255 | 638.9139 | 3.5 | 23.4661 | 1.0061 | 0.52712
2015-08-26 10:00 | 332.8233 | 85.34 | 247.4833 | 625.9295 | 10.7189 | -14.8463 | 66.71 | 23.29 | -15.9078 | 15.7009 | 602.5746 | 64.005 | 0.2 | 0 | 16.6412 | 683.2207 | 3.7 | 25.0506 | 0.9998 | 0.56013
2015-08-26 11:00 | 337.1367 | 80.66 | 256.4767 | 637.127 | 10.7045 | 0.15674 | 66.2622 | 23.7378 | 0.16824 | 6.264 | 633.3232 | 60.495 | 0.2 | 0 | 16.8568 | 710.675 | 5.2 | 27.4086 | 0.99037 | 0.57714
2015-08-26 12:00 | 341.45 | 75.98 | 265.47 | 672.7382 | 10.6901 | 15.1597 | 66.7583 | 23.2417 | 16.2404 | 15.9923 | 646.7023 | 56.985 | 0.2 | 0 | 17.0725 | 720.7598 | 3.5 | 26.0237 | 0.99591 | 0.5886
2015-08-26 13:00 | 292.2067 | 88.32 | 203.8867 | 547.9547 | 10.6757 | 30.1627 | 68.1556 | 21.8444 | 32.1377 | 29.9209 | 474.9205 | 66.24 | 0.2 | 0 | 14.6103 | 555.7709 | 5.7 | 23.0678 | 1.0077 | 0.45925
2015-08-26 14:00 | 242.9633 | 100.66 | 142.3033 | 422.897 | 10.6614 | 45.1657 | 70.3364 | 19.6636 | 47.7369 | 44.216 | 303.0972 | 75.495 | 0.2 | 0 | 12.1482 | 390.7404 | 7.1 | 19.3106 | 1.0228 | 0.3277
2015-08-26 15:00 | 193.72 | 113 | 80.72 | 278.1058 | 10.647 | 60.1687 | 73.1271 | 16.8729 | 62.9881 | 58.5658 | 145.0376 | 84.75 | 0.2 | 0 | 9.686 | 239.4736 | 6.7 | 14.1836 | 1.0433 | 0.20486
2015-08-26 16:00 | 152.1133 | 86.3 | 65.8133 | 278.3032 | 10.6325 | 75.1717 | 76.3211 | 13.6789 | 77.9141 | 72.877 | 81.939 | 64.725 | 0.2 | 0 | 7.6057 | 154.2696 | 6.4 | 11.2209 | 1.0551 | 0.13347
2015-08-26 17:00 | 110.5067 | 59.6 | 50.9067 | 284.6498 | 10.6181 | 90.1748 | 79.6978 | 10.3022 | 92.5909 | 87.0822 | 14.4896 | 44.7 | 0.2 | 0 | 5.5253 | 64.7149 | 6.3 | 8.3223 | 1.0667 | 0.056606
2015-08-26 18:00 | 68.9 | 32.9 | 36 | 296.9338 | 10.6037 | 105.1778 | 83.0364 | 6.9636 | 107.1206 | 101.0955 | 0 | 24.675 | 0.2 | 0 | 3.445 | 28.12 | 5.6 | 6.4787 | 1.0741 | 0.024767
2015-08-26 19:00 | 46.46 | 22.3 | 24.16 | 357.4496 | 10.5893 | 120.1808 | 86.1244 | 3.8756 | 121.6063 | 114.7736 | 0 | 16.725 | 0.2 | 0 | 2.323 | 19.048 | 5 | 5.5953 | 1.0776 | 0.016832
2015-08-26 20:00 | 24.02 | 11.7 | 12.32 | 0 | 10.5749 | 135.1838 | 88.7661 | 1.2339 | 136.13 | 127.8371 | 0 | 8.775 | 0.2 | 0 | 1.201 | 9.976 | 4.4 | 4.7118 | 1.0812 | 0.0088442
2015-08-26 21:00 | 1.58 | 1.1 | 0.48 | 0 | 10.5604 | 150.1868 | 90.791 | -0.791 | 150.7383 | 139.6716 | 0 | 0.825 | 0.2 | 0 | 0.079 | 0.904 | 3.8 | 3.8283 | 1.0847 | 0.00080406
2015-08-26 22:00 | 1.0533 | 0.73333 | 0.32 | 0 | 10.546 | 165.1899 | 92.065 | -2.065 | 165.4359 | 148.8338 | 0 | 0.55 | 0.2 | 0 | 0.052667 | 0.60267 | 3.1 | 3.1188 | 1.0875 | 0.00053744
2015-08-26 23:00 | 0.52667 | 0.36667 | 0.16 | 0 | 10.5316 | 180.1929 | 92.5017 | -2.5017 | -179.8102 | 152.5011 | 0 | 0.275 | 0.2 | 0 | 0.026333 | 0.30133 | 2.1 | 2.1094 | 1.0916 | 0.00026972
2015-08-27 | 0 | 0 | 0 | 0 | 10.5171 | -164.8041 | 92.0716 | -2.0716 | -165.0554 | 148.6781 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2 | 2 | 1.092 | 0
2015-08-27 01:00 | 12.78 | 5.1767 | 7.6033 | 0 | 10.5027 | -149.801 | 90.8056 | -0.80561 | -150.3549 | 139.431 | 0 | 3.8825 | 0.2 | 0 | 0.639 | 4.5215 | 1 | 1.1413 | 1.0954 | 0.0040615
2015-08-27 02:00 | 25.56 | 10.3533 | 15.2067 | 0 | 10.4882 | -134.798 | 88.7911 | 1.2089 | -135.7416 | 127.5577 | 0 | 7.765 | 0.2 | 0 | 1.278 | 9.043 | 1 | 1.2826 | 1.0949 | 0.0081187
2015-08-27 03:00 | 38.34 | 15.53 | 22.81 | 340.9039 | 10.4738 | -119.7949 | 86.1635 | 3.8365 | -121.2108 | 114.4754 | 0 | 11.6475 | 0.2 | 0 | 1.917 | 13.5645 | 1.4 | 1.8239 | 1.0927 | 0.012154
2015-08-27 04:00 | 86.83 | 27.1967 | 59.6333 | 495.95 | 10.4593 | -104.7919 | 83.094 | 6.906 | -106.7159 | 100.7873 | 0 | 20.3975 | 0.2 | 0 | 4.3415 | 24.739 | 2.1 | 2.8731 | 1.0885 | 0.022081
2015-08-27 05:00 | 135.32 | 38.8633 | 96.4567 | 543.6135 | 10.4448 | -89.7888 | 79.7795 | 10.2205 | -92.1752 | 86.7686 | 30.6432 | 29.1475 | 0.2 | 0 | 6.766 | 66.5567 | 2.5 | 4.5799 | 1.0817 | 0.059034
2015-08-27 06:00 | 183.81 | 50.53 | 133.28 | 568.1616 | 10.4304 | -74.7858 | 76.4331 | 13.5669 | -77.487 | 72.5611 | 170.2718 | 37.8975 | 0.2 | 0 | 9.1905 | 217.3598 | 2.7 | 9.4925 | 1.062 | 0.18929
2015-08-27 07:00 | 227.48 | 58.5667 | 168.9133 | 586.9875 | 10.4159 | -59.7827 | 73.2759 | 16.7241 | -62.5508 | 58.2509 | 308.8731 | 43.925 | 0.2 | 0 | 11.374 | 364.1721 | 3.1 | 14.4804 | 1.0421 | 0.31119
2015-08-27 08:00 | 271.15 | 66.6033 | 204.5467 | 613.6292 | 10.4014 | -44.7797 | 70.5284 | 19.4716 | -47.2932 | 43.908 | 442.0917 | 49.9525 | 0.2 | 0 | 13.5575 | 505.6017 | 3.3 | 19.1001 | 1.0236 | 0.42438
2015-08-27 09:00 | 314.82 | 74.64 | 240.18 | 652.3353 | 10.3869 | -29.7766 | 68.3963 | 21.6037 | -31.6944 | 29.6344 | 567.0085 | 55.98 | 0.2 | 0 | 15.741 | 638.7295 | 3.4 | 23.3603 | 1.0066 | 0.52719
2015-08-27 10:00 | 307.01 | 112.3267 | 194.6833 | 499.3073 | 10.3724 | -14.7735 | 67.0513 | 22.9487 | -15.8066 | 15.7867 | 480.474 | 84.245 | 0.2 | 0 | 15.3505 | 580.0695 | 3.2 | 21.3272 | 1.0147 | 0.48265
2015-08-27 11:00 | 299.2 | 150.0133 | 149.1867 | 375.779 | 10.3579 | 0.22954 | 66.6088 | 23.3912 | 0.24601 | 6.6125 | 373.2792 | 112.51 | 0.2 | 0 | 14.96 | 500.7492 | 4.4 | 20.0484 | 1.0198 | 0.41875
2015-08-27 12:00 | 291.39 | 187.7 | 103.69 | 266.5679 | 10.3434 | 15.2326 | 67.1089 | 22.8911 | 16.2939 | 16.2052 | 255.9768 | 140.775 | 0.2 | 0 | 14.5695 | 411.3213 | 4 | 16.8538 | 1.0326 | 0.34827
2015-08-27 13:00 | 240.8433 | 169.24 | 71.6033 | 195.4445 | 10.3289 | 30.2357 | 68.5086 | 21.4914 | 32.1688 | 30.0844 | 169.1157 | 126.93 | 0.2 | 0 | 12.0422 | 308.0879 | 4.3 | 13.9277 | 1.0443 | 0.26382
2015-08-27 14:00 | 190.2967 | 150.78 | 39.5167 | 119.5046 | 10.3144 | 45.2388 | 70.6905 | 19.3095 | 47.7495 | 44.3674 | 85.4304 | 113.085 | 0.2 | 0 | 9.5148 | 208.0302 | 4.5 | 11.0009 | 1.056 | 0.18014
2015-08-27 15:00 | 139.75 | 132.32 | 7.43 | 26.1321 | 10.2999 | 60.2419 | 73.4815 | 16.5185 | 62.9876 | 58.7172 | 13.5694 | 99.24 | 0.2 | 0 | 6.9875 | 119.7969 | 4.8 | 8.5437 | 1.0658 | 0.1047
2015-08-27 16:00 | 114.71 | 97.9633 | 16.7467 | 72.6646 | 10.2854 | 75.2449 | 76.6755 | 13.3245 | 77.9062 | 73.0348 | 21.2029 | 73.4725 | 0.2 | 0 | 5.7355 | 100.4109 | 4.3 | 7.4378 | 1.0702 | 0.088121
2015-08-27 17:00 | 89.67 | 63.6067 | 26.0633 | 150.8747 | 10.2709 | 90.248 | 80.0524 | 9.9476 | 92.5813 | 87.2512 | 7.2355 | 47.705 | 0.2 | 0 | 4.4835 | 59.424 | 4.7 | 6.557 | 1.0738 | 0.052322
2015-08-27 18:00 | 64.63 | 29.25 | 35.38 | 307.4086 | 10.2563 | 105.2511 | 83.3911 | 6.6089 | 107.1149 | 101.2811 | 0 | 21.9375 | 0.2 | 0 | 3.2315 | 25.169 | 3.1 | 3.8865 | 1.0845 | 0.022382
2015-08-27 19:00 | 43.4067 | 19.7267 | 23.68 | 385.6135 | 10.2418 | 120.2542 | 86.4793 | 3.5207 | 121.6093 | 114.9826 | 0 | 14.795 | 0.2 | 0 | 2.1703 | 16.9653 | 2.3 | 2.8302 | 1.0887 | 0.015145
2015-08-27 20:00 | 22.1833 | 10.2033 | 11.98 | 0 | 10.2273 | 135.2573 | 89.1208 | 0.87921 | 136.1462 | 128.0794 | 0 | 7.6525 | 0.2 | 0 | 1.1092 | 8.7617 | 1.3 | 1.5738 | 1.0937 | 0.0078578
2015-08-27 21:00 | 0.96 | 0.68 | 0.28 | 0 | 10.2127 | 150.2604 | 91.1446 | -1.1446 | 150.7713 | 139.9603 | 0 | 0.51 | 0.2 | 0 | 0.048 | 0.558 | 1.2 | 1.2174 | 1.0951 | 0.00050109
2015-08-27 22:00 | 0.64 | 0.45333 | 0.18667 | 0 | 10.1982 | 165.2635 | 92.4164 | -2.4164 | 165.4883 | 149.1744 | 0 | 0.34 | 0.2 | 0 | 0.032 | 0.372 | 0.8 | 0.81163 | 1.0968 | 0.00033455
2015-08-27 23:00 | 0.32 | 0.22667 | 0.093333 | 0 | 10.1836 | 180.2666 | 92.8496 | -2.8496 | -179.7372 | 152.8484 | 0 | 0.17 | 0.2 | 0 | 0.016 | 0.186 | 0.7 | 0.70581 | 1.0972 | 0.00016734
2015-08-28 | 0 | 0 | 0 | 0 | 10.1691 | -164.7303 | 92.4148 | -2.4148 | -164.9622 | 148.9472 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-08-28 01:00 | 4.67 | 4.5633 | 0.10667 | 0 | 10.1545 | -149.7271 | 91.1433 | -1.1433 | -150.2431 | 139.6105 | 0 | 3.4225 | 0.2 | 0 | 0.2335 | 3.656 | 0.4 | 0.51425 | 1.0979 | 0.0032915
2015-08-28 02:00 | 9.34 | 9.1267 | 0.21333 | 0 | 10.14 | -134.724 | 89.1233 | 0.87674 | -135.614 | 127.6746 | 0 | 6.845 | 0.2 | 0 | 0.467 | 7.312 | 0.4 | 0.6285 | 1.0975 | 0.0065804
2015-08-28 03:00 | 14.01 | 13.69 | 0.32 | 5.228 | 10.1254 | -119.7209 | 86.4908 | 3.5092 | -121.0707 | 114.5514 | 0 | 10.2675 | 0.2 | 0 | 0.7005 | 10.968 | 0.4 | 0.74275 | 1.097 | 0.0098664
2015-08-28 04:00 | 35.8 | 33.1367 | 2.6633 | 23.2351 | 10.1108 | -104.7178 | 83.418 | 6.582 | -106.5672 | 100.8359 | 0 | 24.8525 | 0.2 | 0 | 1.79 | 26.6425 | 0.1 | 0.93258 | 1.0963 | 0.02395
2015-08-28 05:00 | 57.59 | 52.5833 | 5.0067 | 29.1269 | 10.0962 | -89.7146 | 80.1022 | 9.8978 | -92.0219 | 86.7986 | 1.6266 | 39.4375 | 0.2 | 0 | 2.8795 | 43.9436 | 1.8 | 3.1732 | 1.0873 | 0.03918
2015-08-28 06:00 | 79.38 | 72.03 | 7.35 | 32.0837 | 10.0816 | -74.7115 | 76.7566 | 13.2434 | -77.3336 | 72.579 | 9.6056 | 54.0225 | 0.2 | 0 | 3.969 | 67.5971 | 3.5 | 5.6124 | 1.0776 | 0.059728
2015-08-28 07:00 | 87.1533 | 82.08 | 5.0733 | 17.9716 | 10.0671 | -59.7084 | 73.6026 | 16.3974 | -62.4021 | 58.2625 | 9.4536 | 61.56 | 0.2 | 0 | 4.3577 | 75.3712 | 3.4 | 5.7554 | 1.077 | 0.066562
2015-08-28 08:00 | 94.9267 | 92.13 | 2.7967 | 8.5296 | 10.0525 | -44.7052 | 70.8601 | 19.1399 | -47.1545 | 43.9207 | 6.1439 | 69.0975 | 0.2 | 0 | 4.7463 | 79.9877 | 2.9 | 5.3996 | 1.0784 | 0.070732
2015-08-28 09:00 | 102.7 | 102.18 | 0.52 | 1.4337 | 10.0379 | -29.7021 | 68.734 | 21.266 | -31.5711 | 29.6629 | 1.2458 | 76.635 | 0.2 | 0 | 5.135 | 83.0158 | 2.7 | 5.2942 | 1.0788 | 0.073439
2015-08-28 10:00 | 107.79 | 104.9 | 2.89 | 7.5188 | 10.0233 | -14.699 | 67.3952 | 22.6048 | -15.7035 | 15.8792 | 7.2318 | 78.675 | 0.2 | 0 | 5.3895 | 91.2963 | 3 | 5.853 | 1.0766 | 0.080597
2015-08-28 11:00 | 112.88 | 107.62 | 5.26 | 13.4388 | 10.0087 | 0.30419 | 66.9582 | 23.0418 | 0.32554 | 6.9643 | 13.3397 | 80.715 | 0.2 | 0 | 5.644 | 99.6987 | 3 | 6.1156 | 1.0755 | 0.087928
2015-08-28 12:00 | 117.97 | 110.34 | 7.63 | 19.9065 | 9.9941 | 15.3073 | 67.4623 | 22.5377 | 16.3491 | 16.4258 | 19.0941 | 82.755 | 0.2 | 0 | 5.8985 | 107.7476 | 3.1 | 6.4671 | 1.0741 | 0.094903
2015-08-28 13:00 | 105.1867 | 91.7133 | 13.4733 | 37.3662 | 9.9794 | 30.3105 | 68.8645 | 21.1355 | 32.2015 | 30.2535 | 32.2771 | 68.785 | 0.2 | 0 | 5.2593 | 106.3214 | 2.7 | 6.0225 | 1.0759 | 0.093802
2015-08-28 14:00 | 92.4033 | 73.0867 | 19.3167 | 59.4756 | 9.9648 | 45.3137 | 71.0476 | 18.9524 | 47.7637 | 44.5232 | 42.4041 | 54.815 | 0.2 | 0 | 4.6202 | 101.8393 | 2.3 | 5.4825 | 1.0781 | 0.090028
2015-08-28 15:00 | 79.62 | 54.46 | 25.16 | 90.3936 | 9.9502 | 60.3168 | 73.839 | 16.161 | 62.9885 | 58.8722 | 46.7289 | 40.845 | 0.2 | 0 | 3.981 | 91.5549 | 2 | 4.8611 | 1.0806 | 0.081123
2015-08-28 16:00 | 59.82 | 42.8867 | 16.9333 | 75.464 | 9.9356 | 75.32 | 77.033 | 12.967 | 77.8997 | 73.1956 | 21.817 | 32.165 | 0.2 | 0 | 2.991 | 56.973 | 3.1 | 4.8804 | 1.0805 | 0.050478
2015-08-28 17:00 | 40.02 | 31.3133 | 8.7067 | 52.2616 | 9.9209 | 90.3231 | 80.4099 | 9.5901 | 92.5731 | 87.423 | 2.3498 | 23.485 | 0.2 | 0 | 2.001 | 27.8358 | 2.3 | 3.1699 | 1.0873 | 0.024819
2015-08-28 18:00 | 20.22 | 19.74 | 0.48 | 4.4083 | 9.9063 | 105.3263 | 83.7489 | 6.2511 | 107.1104 | 101.4691 | 0 | 14.805 | 0.2 | 0 | 1.011 | 15.816 | 2.3 | 2.7942 | 1.0888 | 0.014121
2015-08-28 19:00 | 13.58 | 13.26 | 0.32 | 5.8 | 9.8916 | 120.3295 | 86.8372 | 3.1628 | 121.6137 | 115.1939 | 0 | 9.945 | 0.2 | 0 | 0.679 | 10.624 | 2.1 | 2.432 | 1.0903 | 0.0094981
2015-08-28 20:00 | 6.94 | 6.78 | 0.16 | 0 | 9.877 | 135.3327 | 89.4784 | 0.52161 | 136.1638 | 128.3239 | 0 | 5.085 | 0.2 | 0 | 0.347 | 5.432 | 2.5 | 2.6698 | 1.0893 | 0.0048521
2015-08-28 21:00 | 0.3 | 0.3 | 0 | 0 | 9.8624 | 150.3358 | 91.5011 | -1.5011 | 150.806 | 140.2512 | 0 | 0.225 | 0.2 | 0 | 0.015 | 0.24 | 3 | 3.0075 | 1.088 | 0.00021411
2015-08-28 22:00 | 0.2 | 0.2 | 0 | 0 | 9.8477 | 165.339 | 92.7706 | -2.7706 | 165.5425 | 149.5181 | 0 | 0.15 | 0.2 | 0 | 0.01 | 0.16 | 3.2 | 3.205 | 1.0872 | 0.00014264
2015-08-28 23:00 | 0.1 | 0.1 | 0 | 0 | 9.833 | 180.3422 | 93.2001 | -3.2001 | -179.6623 | 153.1982 | 0 | 0.075 | 0.2 | 0 | 0.005 | 0.08 | 3.3 | 3.3025 | 1.0868 | 7.1293e-05
2015-08-29 | 0 | 0 | 0 | 0 | 9.8184 | -164.6546 | 92.7604 | -2.7604 | -164.8668 | 149.216 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.084 | 0
2015-08-29 01:00 | 3.5233 | 1.64 | 1.8833 | 0 | 9.8037 | -149.6514 | 91.4833 | -1.4833 | -150.1291 | 139.7884 | 0 | 1.23 | 0.2 | 0 | 0.17617 | 1.4062 | 4.6 | 4.6439 | 1.0814 | 0.0012469
2015-08-29 02:00 | 7.0467 | 3.28 | 3.7667 | 0 | 9.789 | -134.6482 | 89.4577 | 0.54232 | -135.484 | 127.7896 | 0 | 2.46 | 0.2 | 0 | 0.35233 | 2.8123 | 4.6 | 4.6879 | 1.0812 | 0.0024935
2015-08-29 03:00 | 10.57 | 4.92 | 5.65 | 101.8618 | 9.7743 | -119.645 | 86.8203 | 3.1797 | -120.9283 | 114.6257 | 0 | 3.69 | 0.2 | 0 | 0.5285 | 4.2185 | 5 | 5.1318 | 1.0795 | 0.0037341
2015-08-29 04:00 | 14.0833 | 6.5533 | 7.53 | 69.1026 | 9.7597 | -104.6418 | 83.7441 | 6.2559 | -106.4161 | 100.8832 | 0 | 4.915 | 0.2 | 0 | 0.70417 | 5.6192 | 5.1 | 5.2756 | 1.0789 | 0.0049713
2015-08-29 05:00 | 17.5967 | 8.1867 | 9.41 | 56.5829 | 9.745 | -89.6386 | 80.427 | 9.573 | -91.8664 | 86.8277 | 3.1312 | 6.14 | 0.2 | 0 | 0.87983 | 10.1511 | 5.8 | 6.1172 | 1.0755 | 0.0089526
2015-08-29 06:00 | 21.11 | 9.82 | 11.29 | 50.5032 | 9.7303 | -74.6354 | 77.0824 | 12.9176 | -77.178 | 72.5964 | 15.1056 | 7.365 | 0.2 | 0 | 1.0555 | 23.5261 | 5.3 | 6.0352 | 1.0759 | 0.020755
2015-08-29 07:00 | 29.8433 | 21.7567 | 8.0867 | 29.2164 | 9.7156 | -59.6322 | 73.9316 | 16.0684 | -62.2514 | 58.2742 | 15.3636 | 16.3175 | 0.2 | 0 | 1.4922 | 33.1733 | 5.3 | 6.3367 | 1.0747 | 0.029233
2015-08-29 08:00 | 38.5767 | 33.6933 | 4.8833 | 15.1485 | 9.7009 | -44.629 | 71.1941 | 18.8059 | -47.0139 | 43.9345 | 10.909 | 25.27 | 0.2 | 0 | 1.9288 | 38.1078 | 5.4 | 6.5909 | 1.0736 | 0.033549
2015-08-29 09:00 | 47.31 | 45.63 | 1.68 | 4.7038 | 9.6862 | -29.6258 | 69.0742 | 20.9258 | -31.446 | 29.6941 | 4.0861 | 34.2225 | 0.2 | 0 | 2.3655 | 40.6741 | 5.1 | 6.3711 | 1.0745 | 0.035838
2015-08-29 10:00 | 52.0433 | 50.2433 | 1.8 | 4.7521 | 9.6715 | -14.6226 | 67.7417 | 22.2583 | -15.5988 | 15.9785 | 4.5685 | 37.6825 | 0.2 | 0 | 2.6022 | 44.8531 | 5.6 | 7.0017 | 1.072 | 0.039427
2015-08-29 11:00 | 56.7767 | 54.8567 | 1.92 | 4.9774 | 9.6568 | 0.38064 | 67.3102 | 22.6898 | 0.40673 | 7.3193 | 4.9369 | 41.1425 | 0.2 | 0 | 2.8388 | 48.9182 | 4.8 | 6.3287 | 1.0747 | 0.043109
2015-08-29 12:00 | 61.51 | 59.47 | 2.04 | 5.4034 | 9.642 | 15.3839 | 67.8184 | 22.1816 | 16.4059 | 16.6539 | 5.1767 | 44.6025 | 0.2 | 0 | 3.0755 | 52.8547 | 5 | 6.6517 | 1.0734 | 0.046522
2015-08-29 13:00 | 76.2833 | 68.2767 | 8.0067 | 22.5712 | 9.6273 | 30.3871 | 69.2232 | 20.7768 | 32.2357 | 30.4282 | 19.4624 | 51.2075 | 0.2 | 0 | 3.8142 | 74.484 | 3.8 | 6.1276 | 1.0755 | 0.065688
2015-08-29 14:00 | 91.0567 | 77.0833 | 13.9733 | 43.8262 | 9.6126 | 45.3903 | 71.4075 | 18.5925 | 47.7793 | 44.6833 | 31.1606 | 57.8125 | 0.2 | 0 | 4.5528 | 93.5259 | 4.7 | 7.6227 | 1.0695 | 0.082022
2015-08-29 15:00 | 105.83 | 85.89 | 19.94 | 73.2302 | 9.5979 | 60.3936 | 74.1993 | 15.8007 | 62.9908 | 59.0308 | 37.6826 | 64.4175 | 0.2 | 0 | 5.2915 | 107.3916 | 4.1 | 7.456 | 1.0702 | 0.094241
2015-08-29 16:00 | 81.0933 | 65.1233 | 15.97 | 73.1714 | 9.5831 | 75.3968 | 77.3935 | 12.6065 | 77.8945 | 73.3595 | 20.9538 | 48.8425 | 0.2 | 0 | 4.0547 | 73.8509 | 4.6 | 6.9078 | 1.0724 | 0.06494
2015-08-29 17:00 | 56.3567 | 44.3567 | 12 | 74.8176 | 9.5684 | 90.4 | 80.7705 | 9.2295 | 92.5662 | 87.5973 | 3.1365 | 33.2675 | 0.2 | 0 | 2.8178 | 39.2218 | 4.9 | 6.1257 | 1.0755 | 0.03459
2015-08-29 18:00 | 31.62 | 23.59 | 8.03 | 78.2451 | 9.5536 | 105.4033 | 84.1096 | 5.8904 | 107.1073 | 101.6594 | 0 | 17.6925 | 0.2 | 0 | 1.581 | 19.2735 | 4.6 | 5.2023 | 1.0792 | 0.017056
2015-08-29 19:00 | 21.1233 | 15.77 | 5.3533 | 0 | 9.5389 | 120.4065 | 87.198 | 2.802 | 121.6194 | 115.4073 | 0 | 11.8275 | 0.2 | 0 | 1.0562 | 12.8837 | 4.1 | 4.5026 | 1.082 | 0.011431
2015-08-29 20:00 | 10.6267 | 7.95 | 2.6767 | 0 | 9.5241 | 135.4098 | 89.8388 | 0.16117 | 136.183 | 128.5704 | 0 | 5.9625 | 0.2 | 0 | 0.53133 | 6.4938 | 4.8 | 5.0029 | 1.08 | 0.0057509
2015-08-29 21:00 | 0.13 | 0.13 | 0 | 0 | 9.5094 | 150.413 | 91.8604 | -1.8604 | 150.8422 | 140.5444 | 0 | 0.0975 | 0.2 | 0 | 0.0065 | 0.104 | 4.9 | 4.9033 | 1.0804 | 9.2135e-05
2015-08-29 22:00 | 0.086667 | 0.086667 | 0 | 0 | 9.4946 | 165.4163 | 93.1274 | -3.1274 | 165.5985 | 149.8645 | 0 | 0.065 | 0.2 | 0 | 0.0043333 | 0.069333 | 4.2 | 4.2022 | 1.0832 | 6.1583e-05
2015-08-29 23:00 | 0.043333 | 0.043333 | 0 | 0 | 9.4799 | 180.4195 | 93.5531 | -3.5531 | -179.5854 | 153.5502 | 0 | 0.0325 | 0.2 | 0 | 0.0021667 | 0.034667 | 4.4 | 4.4011 | 1.0824 | 3.0769e-05
2015-08-30 | 0 | 0 | 0 | 0 | 9.4651 | -164.5772 | 93.1085 | -3.1085 | -164.7694 | 149.4844 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.4 | 4.4 | 1.0824 | 0
2015-08-30 01:00 | 0.40667 | 0.40667 | 0 | 0 | 9.4503 | -149.574 | 91.8257 | -1.8257 | -150.0128 | 139.9644 | 0 | 0.305 | 0.2 | 0 | 0.020333 | 0.32533 | 4.7 | 4.7102 | 1.0812 | 0.00028842
2015-08-30 02:00 | 0.81333 | 0.81333 | 0 | 0 | 9.4355 | -134.5707 | 89.7943 | 0.20569 | -135.3518 | 127.9027 | 0 | 0.61 | 0.2 | 0 | 0.040667 | 0.65067 | 4.1 | 4.1203 | 1.0835 | 0.00057811
2015-08-30 03:00 | 1.22 | 1.22 | 0 | 0 | 9.4208 | -119.5674 | 87.152 | 2.848 | -120.7837 | 114.6982 | 0 | 0.915 | 0.2 | 0 | 0.061 | 0.976 | 4.3 | 4.3305 | 1.0827 | 0.00086649
2015-08-30 04:00 | 2.8767 | 2.8767 | 0 | 0 | 9.406 | -104.5642 | 84.0724 | 5.9276 | -106.2629 | 100.9291 | 0 | 2.1575 | 0.2 | 0 | 0.14383 | 2.3013 | 4.4 | 4.4719 | 1.0821 | 0.002042
2015-08-30 05:00 | 4.5333 | 4.5333 | 0 | 0 | 9.3912 | -89.5609 | 80.7539 | 9.2461 | -91.7088 | 86.8558 | 0 | 3.4 | 0.2 | 0 | 0.22667 | 3.6267 | 5 | 5.1133 | 1.0795 | 0.0032104
2015-08-30 06:00 | 6.19 | 6.19 | 0 | 0 | 9.3764 | -74.5576 | 77.4103 | 12.5897 | -77.0205 | 72.6133 | 0 | 4.6425 | 0.2 | 0 | 0.3095 | 4.952 | 4.6 | 4.7547 | 1.081 | 0.0043895
2015-08-30 07:00 | 7.5367 | 7.5367 | 0 | 0 | 9.3616 | -59.5543 | 74.2627 | 15.7373 | -62.0987 | 58.2861 | 0 | 5.6525 | 0.2 | 0 | 0.37683 | 6.0293 | 4.9 | 5.0884 | 1.0796 | 0.0053378
2015-08-30 08:00 | 8.8833 | 8.8833 | 0 | 0 | 9.3468 | -44.5511 | 71.5304 | 18.4696 | -46.8715 | 43.9494 | 0 | 6.6625 | 0.2 | 0 | 0.44417 | 7.1067 | 4.7 | 4.9221 | 1.0803 | 0.0062955
2015-08-30 09:00 | 10.23 | 10.23 | 0 | 0 | 9.332 | -29.5478 | 69.4167 | 20.5833 | -31.3192 | 29.7283 | 0 | 7.6725 | 0.2 | 0 | 0.5115 | 8.184 | 3.6 | 3.8558 | 1.0846 | 0.0072785
2015-08-30 10:00 | 9.7567 | 9.7333 | 0.023333 | 0.062532 | 9.3172 | -14.5445 | 68.0906 | 21.9094 | -15.4924 | 16.0847 | 0.060085 | 7.3 | 0.2 | 0 | 0.48783 | 7.8479 | 3.5 | 3.7452 | 1.085 | 0.0069824
2015-08-30 11:00 | 9.2833 | 9.2367 | 0.046667 | 0.1228 | 9.3023 | 0.45881 | 67.6648 | 22.3352 | 0.4895 | 7.6773 | 0.1217 | 6.9275 | 0.2 | 0 | 0.46417 | 7.5134 | 2.5 | 2.7348 | 1.0891 | 0.0067097
2015-08-30 12:00 | 8.81 | 8.74 | 0.07 | 0.1883 | 9.2875 | 15.4621 | 68.1772 | 21.8228 | 16.4642 | 16.8893 | 0.18018 | 6.555 | 0.2 | 0 | 0.4405 | 7.1757 | 3.3 | 3.5242 | 1.0859 | 0.0063895
2015-08-30 13:00 | 32.8033 | 23.3733 | 9.43 | 27.0337 | 9.2727 | 30.4654 | 69.5846 | 20.4154 | 32.2713 | 30.6084 | 23.267 | 17.53 | 0.2 | 0 | 1.6402 | 42.4372 | 2.8 | 4.1262 | 1.0835 | 0.037704
2015-08-30 14:00 | 56.7967 | 38.0067 | 18.79 | 60.0648 | 9.2579 | 45.4687 | 71.7702 | 18.2298 | 47.7963 | 44.8477 | 42.585 | 28.505 | 0.2 | 0 | 2.8398 | 73.9298 | 3.3 | 5.6103 | 1.0776 | 0.065324
2015-08-30 15:00 | 80.79 | 52.64 | 28.15 | 105.7524 | 9.243 | 60.472 | 74.5625 | 15.4375 | 62.9944 | 59.1929 | 54.161 | 39.48 | 0.2 | 0 | 4.0395 | 97.6805 | 3.6 | 6.6525 | 1.0734 | 0.085976
2015-08-30 16:00 | 59.6033 | 40.1433 | 19.46 | 91.7652 | 9.2282 | 75.4753 | 77.7567 | 12.2433 | 77.8905 | 73.5264 | 26.0222 | 30.1075 | 0.2 | 0 | 2.9802 | 59.1099 | 4 | 5.8472 | 1.0766 | 0.052183
2015-08-30 17:00 | 38.4167 | 27.6467 | 10.77 | 69.8774 | 9.2133 | 90.4786 | 81.1338 | 8.8662 | 92.5605 | 87.7743 | 2.7138 | 20.735 | 0.2 | 0 | 1.9208 | 25.3696 | 3.6 | 4.3928 | 1.0824 | 0.022518
2015-08-30 18:00 | 17.23 | 15.15 | 2.08 | 21.5962 | 9.1985 | 105.4819 | 84.4731 | 5.5269 | 107.1054 | 101.852 | 0 | 11.3625 | 0.2 | 0 | 0.8615 | 12.224 | 3.7 | 4.082 | 1.0837 | 0.010862
2015-08-30 19:00 | 11.4967 | 10.11 | 1.3867 | 0 | 9.1837 | 120.4852 | 87.5616 | 2.4384 | 121.6265 | 115.6226 | 0 | 7.5825 | 0.2 | 0 | 0.57483 | 8.1573 | 3.6 | 3.8549 | 1.0846 | 0.0072548
2015-08-30 20:00 | 5.7633 | 5.07 | 0.69333 | 0 | 9.1688 | 135.4885 | 90.202 | -0.20201 | 136.2035 | 128.8187 | 0 | 3.8025 | 0.2 | 0 | 0.28817 | 4.0907 | 3.3 | 3.4278 | 1.0863 | 0.0036438
2015-08-30 21:00 | 0.03 | 0.03 | 0 | 0 | 9.1539 | 150.4919 | 92.2223 | -2.2223 | 150.88 | 140.8396 | 0 | 0.0225 | 0.2 | 0 | 0.0015 | 0.024 | 2.8 | 2.8007 | 1.0888 | 2.1428e-05
2015-08-30 22:00 | 0.02 | 0.02 | 0 | 0 | 9.1391 | 165.4952 | 93.4868 | -3.4868 | 165.6562 | 150.2137 | 0 | 0.015 | 0.2 | 0 | 0.001 | 0.016 | 3.1 | 3.1005 | 1.0876 | 1.4269e-05
2015-08-30 23:00 | 0.01 | 0.01 | 0 | 0 | 9.1242 | 180.4985 | 93.9086 | -3.9086 | -179.5067 | 153.9045 | 0 | 0.0075 | 0.2 | 0 | 0.0005 | 0.008 | 3.5 | 3.5002 | 1.086 | 7.1242e-06
2015-08-31 | 0 | 0 | 0 | 0 | 9.1093 | -164.4982 | 93.4589 | -3.4589 | -164.6699 | 149.7523 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.4 | 3.4 | 1.0864 | 0
2015-08-31 01:00 | 3.45 | 3.4 | 0.05 | 0 | 9.0945 | -149.4948 | 92.1703 | -2.1703 | -149.8944 | 140.1387 | 0 | 2.55 | 0.2 | 0 | 0.1725 | 2.7225 | 3.5 | 3.5851 | 1.0857 | 0.0024237
2015-08-31 02:00 | 6.9 | 6.8 | 0.1 | 0 | 9.0796 | -134.4915 | 90.1331 | -0.13307 | -135.2175 | 128.0138 | 0 | 5.1 | 0.2 | 0 | 0.345 | 5.445 | 3.4 | 3.5702 | 1.0857 | 0.0048476
2015-08-31 03:00 | 10.35 | 10.2 | 0.15 | 0 | 9.0647 | -119.4882 | 87.4858 | 2.5142 | -120.6368 | 114.7692 | 0 | 7.65 | 0.2 | 0 | 0.5175 | 8.1675 | 3.6 | 3.8552 | 1.0846 | 0.0072638
2015-08-31 04:00 | 34.14 | 28.43 | 5.71 | 58.5426 | 9.0498 | -104.4848 | 84.4027 | 5.5973 | -106.1076 | 100.9737 | 0 | 21.3225 | 0.2 | 0 | 1.707 | 23.0295 | 6.3 | 7.0197 | 1.0719 | 0.020242
2015-08-31 05:00 | 57.93 | 46.66 | 11.27 | 72.7067 | 9.0349 | -89.4815 | 81.0828 | 8.9172 | -91.5491 | 86.8831 | 3.9533 | 34.995 | 0.2 | 0 | 2.8965 | 41.8448 | 6 | 7.3077 | 1.0708 | 0.036741
2015-08-31 06:00 | 81.72 | 64.89 | 16.83 | 79.258 | 9.02 | -74.4781 | 77.7402 | 12.2598 | -76.8609 | 72.6298 | 23.662 | 48.6675 | 0.2 | 0 | 4.086 | 76.4155 | 5.5 | 7.888 | 1.0684 | 0.06695
2015-08-31 07:00 | 99.31 | 86.78 | 12.53 | 47.1721 | 9.0051 | -59.4748 | 74.596 | 15.404 | -61.9442 | 58.2982 | 24.7888 | 65.085 | 0.2 | 0 | 4.9655 | 94.8393 | 5.3 | 8.2637 | 1.0669 | 0.082974
2015-08-31 08:00 | 116.9 | 108.67 | 8.23 | 26.4466 | 8.9902 | -44.4715 | 71.8689 | 18.1311 | -46.7273 | 43.9657 | 19.0351 | 81.5025 | 0.2 | 0 | 5.845 | 106.3826 | 5.9 | 9.2245 | 1.0631 | 0.092738
2015-08-31 09:00 | 134.49 | 130.56 | 3.93 | 11.3607 | 8.9753 | -29.4681 | 69.7615 | 20.2385 | -31.1908 | 29.7655 | 9.8619 | 97.92 | 0.2 | 0 | 6.7245 | 114.5064 | 4.8 | 8.3783 | 1.0665 | 0.10014
2015-08-31 10:00 | 148.4267 | 141.9533 | 6.4733 | 17.6172 | 8.9604 | -14.4647 | 68.4419 | 21.5581 | -15.3844 | 16.1979 | 16.9179 | 106.465 | 0.2 | 0 | 7.4213 | 130.8042 | 4.4 | 8.4876 | 1.066 | 0.11434
2015-08-31 11:00 | 162.3633 | 153.3467 | 9.0167 | 24.0924 | 8.9455 | 0.53861 | 68.0218 | 21.9782 | 0.57376 | 8.0383 | 23.8557 | 115.01 | 0.2 | 0 | 8.1182 | 146.9838 | 6.1 | 10.6932 | 1.0572 | 0.12742
2015-08-31 12:00 | 176.3 | 164.74 | 11.56 | 31.5954 | 8.9306 | 15.542 | 68.5385 | 21.4615 | 16.524 | 17.1317 | 30.1935 | 123.555 | 0.2 | 0 | 8.815 | 162.5635 | 5.8 | 10.8801 | 1.0565 | 0.14083
2015-08-31 13:00 | 165.4833 | 137.9767 | 27.5067 | 80.2264 | 8.9156 | 30.5453 | 69.9486 | 20.0514 | 32.3084 | 30.7938 | 68.9157 | 103.4825 | 0.2 | 0 | 8.2742 | 180.6724 | 6.1 | 11.746 | 1.053 | 0.15601
2015-08-31 14:00 | 154.6667 | 111.2133 | 43.4533 | 141.6499 | 8.9007 | 45.5487 | 72.1356 | 17.8644 | 47.8146 | 45.0162 | 100.1332 | 83.41 | 0.2 | 0 | 7.7333 | 191.2766 | 6.1 | 12.0774 | 1.0517 | 0.16495
2015-08-31 15:00 | 143.85 | 84.45 | 59.4 | 228.4378 | 8.8858 | 60.5521 | 74.9283 | 15.0717 | 62.9993 | 59.3584 | 116.4269 | 63.3375 | 0.2 | 0 | 7.1925 | 186.9569 | 5.4 | 11.2424 | 1.055 | 0.16174
2015-08-31 16:00 | 107.0767 | 63.3733 | 43.7033 | 212.3419 | 8.8708 | 75.5554 | 78.1227 | 11.8773 | 77.8878 | 73.6961 | 59.6112 | 47.53 | 0.2 | 0 | 5.3538 | 112.4951 | 5.2 | 8.7155 | 1.0651 | 0.098255
2015-08-31 17:00 | 70.3033 | 42.2967 | 28.0067 | 189.4767 | 8.8559 | 90.5588 | 81.4999 | 8.5001 | 92.556 | 87.9537 | 6.7658 | 31.7225 | 0.2 | 0 | 3.5152 | 42.0034 | 3.4 | 4.7126 | 1.0811 | 0.037238
2015-08-31 18:00 | 33.53 | 21.22 | 12.31 | 136.8558 | 8.8409 | 105.5622 | 84.8393 | 5.1607 | 107.1048 | 102.0467 | 0 | 15.915 | 0.2 | 0 | 1.6765 | 17.5915 | 3.1 | 3.6497 | 1.0854 | 0.015657
2015-08-31 19:00 | 22.3633 | 14.1567 | 8.2067 | 0 | 8.826 | 120.5656 | 87.9278 | 2.0722 | 121.6348 | 115.8398 | 0 | 10.6175 | 0.2 | 0 | 1.1182 | 11.7357 | 3 | 3.3667 | 1.0865 | 0.010456
2015-08-31 20:00 | 11.1967 | 7.0933 | 4.1033 | 0 | 8.811 | 135.5689 | 90.5678 | -0.56782 | 136.2254 | 129.0688 | 0 | 5.32 | 0.2 | 0 | 0.55983 | 5.8798 | 3.3 | 3.4837 | 1.0861 | 0.0052364
2015-08-31 21:00 | 0.03 | 0.03 | 0 | 0 | 8.7961 | 150.5723 | 92.5867 | -2.5867 | 150.9193 | 141.1367 | 0 | 0.0225 | 0.2 | 0 | 0.0015 | 0.024 | 2.8 | 2.8007 | 1.0888 | 2.1428e-05
2015-08-31 22:00 | 0.02 | 0.02 | 0 | 0 | 8.7811 | 165.5757 | 93.8487 | -3.8487 | 165.7155 | 150.5655 | 0 | 0.015 | 0.2 | 0 | 0.001 | 0.016 | 2.4 | 2.4005 | 1.0904 | 1.4306e-05
2015-08-31 23:00 | 0.01 | 0.01 | 0 | 0 | 8.7662 | 180.5791 | 94.2665 | -4.2665 | -179.4261 | 154.2608 | 0 | 0.0075 | 0.2 | 0 | 0.0005 | 0.008 | 1.8 | 1.8002 | 1.0928 | 7.1688e-06
2015-09-01 | 0 | 0 | 0 | 0 | 8.7512 | -164.4175 | 93.8116 | -3.8116 | -164.5685 | 150.0195 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0944 | 0
2015-09-01 01:00 | 6.2667 | 4.5633 | 1.7033 | 0 | 8.7362 | -149.4141 | 92.517 | -2.517 | -149.774 | 140.311 | 0 | 3.4225 | 0.2 | 0 | 0.31333 | 3.7358 | 0.9 | 1.0167 | 1.0959 | 0.0033573
2015-09-01 02:00 | 12.5333 | 9.1267 | 3.4067 | 0 | 8.7212 | -134.4107 | 90.4739 | -0.47389 | -135.081 | 128.123 | 0 | 6.845 | 0.2 | 0 | 0.62667 | 7.4717 | 1.1 | 1.3335 | 1.0947 | 0.0067068
2015-09-01 03:00 | 18.8 | 13.69 | 5.11 | 0 | 8.7063 | -119.4073 | 87.8215 | 2.1785 | -120.4879 | 114.8384 | 0 | 10.2675 | 0.2 | 0 | 0.94 | 11.2075 | 1.2 | 1.5502 | 1.0938 | 0.010052
2015-09-01 04:00 | 59.27 | 37.8767 | 21.3933 | 233.1376 | 8.6913 | -104.4039 | 84.735 | 5.265 | -105.9502 | 101.017 | 0 | 28.4075 | 0.2 | 0 | 2.9635 | 31.371 | 1.5 | 2.4803 | 1.0901 | 0.028041
2015-09-01 05:00 | 99.74 | 62.0633 | 37.6767 | 252.3587 | 8.6763 | -89.4005 | 81.4138 | 8.5862 | -91.3875 | 86.9095 | 13.6056 | 46.5475 | 0.2 | 0 | 4.987 | 65.1401 | 2.2 | 4.2356 | 1.0831 | 0.057851
2015-09-01 06:00 | 140.21 | 86.25 | 53.96 | 261.0813 | 8.6613 | -74.3971 | 78.0722 | 11.9278 | -76.6996 | 72.6461 | 77.8735 | 64.6875 | 0.2 | 0 | 7.0105 | 149.5715 | 1.6 | 6.2741 | 1.0749 | 0.13184
2015-09-01 07:00 | 185.01 | 107.79 | 77.22 | 297.0277 | 8.6463 | -59.3937 | 74.9314 | 15.0686 | -61.788 | 58.3108 | 156.032 | 80.8425 | 0.2 | 0 | 9.2505 | 246.125 | 2.4 | 10.0914 | 1.0596 | 0.21386
2015-09-01 08:00 | 229.81 | 129.33 | 100.48 | 328.8634 | 8.6313 | -44.3903 | 72.2095 | 17.7905 | -46.5816 | 43.9833 | 236.6311 | 96.9975 | 0.2 | 0 | 11.4905 | 345.1191 | 2.3 | 13.085 | 1.0477 | 0.29649
2015-09-01 09:00 | 274.61 | 150.87 | 123.74 | 363.6857 | 8.6163 | -29.3869 | 70.1086 | 19.8914 | -31.0608 | 29.8059 | 315.5753 | 113.1525 | 0.2 | 0 | 13.7305 | 442.4583 | 2.6 | 16.4268 | 1.0343 | 0.37526
2015-09-01 10:00 | 260.0767 | 155.9933 | 104.0833 | 287.7641 | 8.6013 | -14.3834 | 68.7956 | 21.2044 | -15.2751 | 16.318 | 276.1721 | 116.995 | 0.2 | 0 | 13.0038 | 406.1709 | 2.6 | 15.2928 | 1.0388 | 0.34599
2015-09-01 11:00 | 245.5433 | 161.1167 | 84.4267 | 229.1529 | 8.5863 | 0.61998 | 68.3812 | 21.6188 | 0.65942 | 8.4021 | 226.6934 | 120.8375 | 0.2 | 0 | 12.2772 | 359.808 | 2.2 | 13.444 | 1.0462 | 0.30868
2015-09-01 12:00 | 231.01 | 166.24 | 64.77 | 179.9369 | 8.5712 | 15.6234 | 68.9023 | 21.0977 | 16.5851 | 17.381 | 171.7209 | 124.68 | 0.2 | 0 | 11.5505 | 307.9514 | 2.2 | 11.8235 | 1.0527 | 0.26583
2015-09-01 13:00 | 205.8867 | 150.4233 | 55.4633 | 164.6548 | 8.5562 | 30.6268 | 70.3152 | 19.6848 | 32.3468 | 30.9846 | 141.1595 | 112.8175 | 0.2 | 0 | 10.2943 | 264.2713 | 2.2 | 10.4585 | 1.0582 | 0.22931
2015-09-01 14:00 | 180.7633 | 134.6067 | 46.1567 | 153.5245 | 8.5412 | 45.6303 | 72.5035 | 17.4965 | 47.8342 | 45.1889 | 108.1997 | 100.955 | 0.2 | 0 | 9.0382 | 218.1929 | 2.2 | 9.0185 | 1.0639 | 0.19036
2015-09-01 15:00 | 155.64 | 118.79 | 36.85 | 145.1865 | 8.5262 | 60.6337 | 75.2968 | 14.7032 | 63.0054 | 59.5273 | 73.6281 | 89.0925 | 0.2 | 0 | 7.782 | 170.5026 | 1.9 | 7.2282 | 1.0711 | 0.14975
2015-09-01 16:00 | 115.8867 | 88.0867 | 27.8 | 139.3377 | 8.5111 | 75.6371 | 78.4914 | 11.5086 | 77.8863 | 73.8686 | 38.7138 | 66.065 | 0.2 | 0 | 5.7943 | 110.5731 | 1.8 | 5.2554 | 1.079 | 0.097831
2015-09-01 17:00 | 76.1333 | 57.3833 | 18.75 | 132.5627 | 8.4961 | 90.6406 | 81.8687 | 8.1313 | 92.5527 | 88.1354 | 4.3133 | 43.0375 | 0.2 | 0 | 3.8067 | 51.1575 | 1.7 | 3.2987 | 1.0868 | 0.045591
2015-09-01 18:00 | 36.38 | 26.68 | 9.7 | 116.1188 | 8.4811 | 105.644 | 85.2082 | 4.7918 | 107.1052 | 102.2433 | 0 | 20.01 | 0.2 | 0 | 1.819 | 21.829 | 1.1 | 1.7822 | 1.0929 | 0.019562
2015-09-01 19:00 | 24.2533 | 17.7867 | 6.4667 | 0 | 8.466 | 120.6474 | 88.2967 | 1.7033 | 121.6443 | 116.0587 | 0 | 13.34 | 0.2 | 0 | 1.2127 | 14.5527 | 0.9 | 1.3548 | 1.0946 | 0.013062
2015-09-01 20:00 | 12.1267 | 8.8933 | 3.2333 | 0 | 8.451 | 135.6509 | 90.9362 | -0.93616 | 136.2486 | 129.3204 | 0 | 6.67 | 0.2 | 0 | 0.60633 | 7.2763 | 0.7 | 0.92739 | 1.0963 | 0.0065411
2015-09-01 21:00 | 0 | 0 | 0 | 0 | 8.4359 | 150.6543 | 92.9537 | -2.9537 | 150.96 | 141.4356 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0972 | 0
2015-09-01 22:00 | 0 | 0 | 0 | 0 | 8.4209 | 165.6578 | 94.2129 | -4.2129 | 165.7764 | 150.9198 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-09-01 23:00 | 0 | 0 | 0 | 0 | 8.4058 | 180.6612 | 94.6267 | -4.6267 | -179.3437 | 154.6191 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-09-02 | 0 | 0 | 0 | 0 | 8.3907 | -164.3353 | 94.1664 | -4.1664 | -164.4651 | 150.2859 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-09-02 01:00 | 4.2733 | 3.6367 | 0.63667 | 0 | 8.3757 | -149.3319 | 92.8658 | -2.8658 | -149.6516 | 140.4813 | 0 | 2.7275 | 0.2 | 0 | 0.21367 | 2.9412 | 0.6 | 0.69191 | 1.0972 | 0.0026463
2015-09-02 02:00 | 8.5467 | 7.2733 | 1.2733 | 0 | 8.3606 | -134.3284 | 90.8167 | -0.8167 | -134.9425 | 128.2302 | 0 | 5.455 | 0.2 | 0 | 0.42733 | 5.8823 | 0.5 | 0.68382 | 1.0973 | 0.0052927
2015-09-02 03:00 | 12.82 | 10.91 | 1.91 | 0 | 8.3455 | -119.325 | 88.1592 | 1.8408 | -120.337 | 114.9059 | 0 | 8.1825 | 0.2 | 0 | 0.641 | 8.8235 | 0.5 | 0.77573 | 1.0969 | 0.0079363
2015-09-02 04:00 | 39.18 | 33.73 | 5.45 | 63.4064 | 8.3304 | -104.3215 | 85.0691 | 4.9309 | -105.7909 | 101.0591 | 0 | 25.2975 | 0.2 | 0 | 1.959 | 27.2565 | 0.2 | 1.0518 | 1.0958 | 0.024491
2015-09-02 05:00 | 65.54 | 56.55 | 8.99 | 62.6255 | 8.3154 | -89.318 | 81.7466 | 8.2534 | -91.224 | 86.9351 | 3.3484 | 42.4125 | 0.2 | 0 | 3.277 | 49.0379 | 0.2 | 1.7324 | 1.0931 | 0.043954
2015-09-02 06:00 | 91.9 | 79.37 | 12.53 | 62.3466 | 8.3003 | -74.3146 | 78.4061 | 11.5939 | -76.5364 | 72.6621 | 18.5797 | 59.5275 | 0.2 | 0 | 4.595 | 82.7022 | -0.2 | 2.3844 | 1.0905 | 0.073951
2015-09-02 07:00 | 125.0467 | 108.88 | 16.1667 | 63.5768 | 8.2852 | -59.3111 | 75.2687 | 14.7313 | -61.6302 | 58.3238 | 33.3853 | 81.66 | 0.2 | 0 | 6.2523 | 121.2976 | -0.2 | 3.5906 | 1.0856 | 0.10798
2015-09-02 08:00 | 158.1933 | 138.39 | 19.8033 | 66.0471 | 8.2701 | -44.3076 | 72.5522 | 17.4478 | -46.4343 | 44.0024 | 47.5084 | 103.7925 | 0.2 | 0 | 7.9097 | 159.2105 | -0.1 | 4.8753 | 1.0805 | 0.14106
2015-09-02 09:00 | 191.34 | 167.9 | 23.44 | 70.0744 | 8.255 | -29.3041 | 70.4578 | 19.5422 | -30.9294 | 29.8496 | 60.778 | 125.925 | 0.2 | 0 | 9.567 | 196.27 | 0 | 6.1334 | 1.0755 | 0.17309
2015-09-02 10:00 | 190.13 | 168.8267 | 21.3033 | 59.8577 | 8.2399 | -14.3007 | 69.1514 | 20.8486 | -15.1643 | 16.4453 | 57.409 | 126.62 | 0.2 | 0 | 9.5065 | 193.5355 | 0.1 | 6.148 | 1.0754 | 0.17067
2015-09-02 11:00 | 188.92 | 169.7533 | 19.1667 | 52.8658 | 8.2248 | 0.70282 | 68.7429 | 21.2571 | 0.74638 | 8.7687 | 52.2479 | 127.315 | 0.2 | 0 | 9.446 | 189.0089 | 0.1 | 6.0065 | 1.076 | 0.16676
2015-09-02 12:00 | 187.71 | 170.68 | 17.03 | 48.1087 | 8.2097 | 15.7063 | 69.2684 | 20.7316 | 16.6475 | 17.6368 | 45.8474 | 128.01 | 0.2 | 0 | 9.3855 | 183.2429 | 0 | 5.7263 | 1.0771 | 0.16184
2015-09-02 13:00 | 163.82 | 149.7467 | 14.0733 | 42.5465 | 8.1946 | 30.7098 | 70.6841 | 19.3159 | 32.3864 | 31.1804 | 36.4002 | 112.31 | 0.2 | 0 | 8.191 | 156.9012 | 0.3 | 5.2032 | 1.0792 | 0.13885
2015-09-02 14:00 | 139.93 | 128.8133 | 11.1167 | 37.7509 | 8.1794 | 45.7133 | 72.874 | 17.126 | 47.855 | 45.3655 | 26.5231 | 96.61 | 0.2 | 0 | 6.9965 | 130.1296 | 1 | 5.0665 | 1.0797 | 0.11521
2015-09-02 15:00 | 116.04 | 107.88 | 8.16 | 32.964 | 8.1643 | 60.7168 | 75.6678 | 14.3322 | 63.0126 | 59.6993 | 16.6316 | 80.91 | 0.2 | 0 | 5.802 | 103.3436 | 1.1 | 4.3295 | 1.0827 | 0.091748
2015-09-02 16:00 | 86.62 | 78.7933 | 7.8267 | 40.5184 | 8.1492 | 75.7203 | 78.8626 | 11.1374 | 77.8858 | 74.0437 | 11.1386 | 59.095 | 0.2 | 0 | 4.331 | 74.5646 | 1 | 3.3301 | 1.0867 | 0.066443
2015-09-02 17:00 | 57.2 | 49.7067 | 7.4933 | 55.496 | 8.1341 | 90.7238 | 82.2399 | 7.7601 | 92.5504 | 88.3194 | 1.6276 | 37.28 | 0.2 | 0 | 2.86 | 41.7676 | 1.1 | 2.4052 | 1.0904 | 0.037345
2015-09-02 18:00 | 27.78 | 20.62 | 7.16 | 92.8974 | 8.1189 | 105.7273 | 85.5796 | 4.4204 | 107.1068 | 102.4419 | 0 | 15.465 | 0.2 | 0 | 1.389 | 16.854 | 0.9 | 1.4267 | 1.0943 | 0.015123
2015-09-02 19:00 | 18.52 | 13.7467 | 4.7733 | 0 | 8.1038 | 120.7308 | 88.668 | 1.332 | 121.6549 | 116.2792 | 0 | 10.31 | 0.2 | 0 | 0.926 | 11.236 | 1.1 | 1.4511 | 1.0942 | 0.010081
2015-09-02 20:00 | 9.26 | 6.8733 | 2.3867 | 0 | 8.0887 | 135.7343 | 91.3069 | -1.3069 | 136.273 | 129.5735 | 0 | 5.155 | 0.2 | 0 | 0.463 | 5.618 | 0.8 | 0.97556 | 1.0961 | 0.0050495
2015-09-02 21:00 | 0 | 0 | 0 | 0 | 8.0735 | 150.7378 | 93.323 | -3.323 | 151.0021 | 141.7361 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-09-02 22:00 | 0 | 0 | 0 | 0 | 8.0584 | 165.7413 | 94.5795 | -4.5795 | 165.8388 | 151.2764 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-09-02 23:00 | 0 | 0 | 0 | 0 | 8.0432 | 180.7448 | 94.989 | -4.989 | -179.2597 | 154.9793 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-09-03 | 0 | 0 | 0 | 0 | 8.0281 | -164.2517 | 94.5233 | -4.5233 | -164.36 | 150.5512 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-09-03 01:00 | 2.1967 | 2.1967 | 0 | 0 | 8.0129 | -149.2482 | 93.2166 | -3.2166 | -149.5274 | 140.6495 | 0 | 1.6475 | 0.2 | 0 | 0.10983 | 1.7573 | 0.2 | 0.25492 | 1.099 | 0.0015836
2015-09-03 02:00 | 4.3933 | 4.3933 | 0 | 0 | 7.9977 | -134.2447 | 91.1614 | -1.1614 | -134.8021 | 128.3353 | 0 | 3.295 | 0.2 | 0 | 0.21967 | 3.5147 | 0.1 | 0.20983 | 1.0992 | 0.0031678
2015-09-03 03:00 | 6.59 | 6.59 | 0 | 0 | 7.9826 | -119.2412 | 88.4987 | 1.5013 | -120.1842 | 114.9719 | 0 | 4.9425 | 0.2 | 0 | 0.3295 | 5.272 | 0.1 | 0.26475 | 1.0989 | 0.0047508
2015-09-03 04:00 | 22.27 | 22.27 | 0 | 0 | 7.9674 | -104.2376 | 85.4051 | 4.5949 | -105.6298 | 101.0999 | 0 | 16.7025 | 0.2 | 0 | 1.1135 | 17.816 | -0.1 | 0.45675 | 1.0982 | 0.016043
2015-09-03 05:00 | 37.95 | 37.95 | 0 | 0 | 7.9522 | -89.2341 | 82.0812 | 7.9188 | -91.0588 | 86.96 | 0 | 28.4625 | 0.2 | 0 | 1.8975 | 30.36 | 0.1 | 1.0488 | 1.0958 | 0.02728
2015-09-03 06:00 | 53.63 | 53.63 | 0 | 0 | 7.9371 | -74.2306 | 78.7419 | 11.2581 | -76.3717 | 72.6779 | 0 | 40.2225 | 0.2 | 0 | 2.6815 | 42.904 | 0.2 | 1.5408 | 1.0938 | 0.038483
2015-09-03 07:00 | 66.1933 | 65.7733 | 0.42 | 1.6898 | 7.9219 | -59.2271 | 75.608 | 14.392 | -61.4708 | 58.3374 | 0.88699 | 49.33 | 0.2 | 0 | 3.3097 | 53.5267 | 0.3 | 1.9727 | 1.0921 | 0.047935
2015-09-03 08:00 | 78.7567 | 77.9167 | 0.84 | 2.8563 | 7.9067 | -44.2235 | 72.8969 | 17.1031 | -46.2856 | 44.0232 | 2.0538 | 58.4375 | 0.2 | 0 | 3.9378 | 64.4291 | 0.2 | 2.2134 | 1.0911 | 0.057647
2015-09-03 09:00 | 91.32 | 90.06 | 1.26 | 3.8331 | 7.8915 | -29.22 | 70.809 | 19.191 | -30.7967 | 29.8967 | 3.323 | 67.545 | 0.2 | 0 | 4.566 | 75.434 | 0.4 | 2.7573 | 1.089 | 0.067359
2015-09-03 10:00 | 97.6333 | 96.4067 | 1.2267 | 3.5042 | 7.8763 | -14.2165 | 69.5094 | 20.4906 | -15.0523 | 16.5795 | 3.3585 | 72.305 | 0.2 | 0 | 4.8817 | 80.5452 | 0.9 | 3.417 | 1.0863 | 0.071749
2015-09-03 11:00 | 103.9467 | 102.7533 | 1.1933 | 3.3462 | 7.8611 | 0.78707 | 69.1068 | 20.8932 | 0.83455 | 9.1379 | 3.3037 | 77.065 | 0.2 | 0 | 5.1973 | 85.566 | 0.6 | 3.2739 | 1.0869 | 0.076262
2015-09-03 12:00 | 110.26 | 109.1 | 1.16 | 3.3336 | 7.8459 | 15.7906 | 69.6369 | 20.3631 | 16.711 | 17.899 | 3.1723 | 81.825 | 0.2 | 0 | 5.513 | 90.5103 | 0.5 | 3.3284 | 1.0867 | 0.080652
2015-09-03 13:00 | 98.8033 | 96.0667 | 2.7367 | 8.4295 | 7.8307 | 30.7942 | 71.0554 | 18.9446 | 32.4272 | 31.3813 | 7.1964 | 72.05 | 0.2 | 0 | 4.9402 | 84.1866 | 0.6 | 3.2308 | 1.0871 | 0.075044
2015-09-03 14:00 | 87.3467 | 83.0333 | 4.3133 | 14.9639 | 7.8155 | 45.7977 | 73.2468 | 16.7532 | 47.8769 | 45.546 | 10.4797 | 62.275 | 0.2 | 0 | 4.3673 | 77.1221 | 1.2 | 3.6101 | 1.0856 | 0.068651
2015-09-03 15:00 | 75.89 | 70 | 5.89 | 24.4172 | 7.8003 | 60.8012 | 76.0412 | 13.9588 | 63.0209 | 59.8745 | 12.2549 | 52.5 | 0.2 | 0 | 3.7945 | 68.5494 | 0.8 | 2.9422 | 1.0882 | 0.06117
2015-09-03 16:00 | 55.7167 | 51.5533 | 4.1633 | 22.2923 | 7.7851 | 75.8048 | 79.2362 | 10.7638 | 77.8864 | 74.2215 | 6.0617 | 38.665 | 0.2 | 0 | 2.7858 | 47.5125 | 0.8 | 2.2848 | 1.0909 | 0.0425
2015-09-03 17:00 | 35.5433 | 33.1067 | 2.4367 | 18.9536 | 7.7699 | 90.8083 | 82.6136 | 7.3864 | 92.5491 | 88.5054 | 0.49435 | 24.83 | 0.2 | 0 | 1.7772 | 27.1015 | 0.8 | 1.6469 | 1.0934 | 0.024299
2015-09-03 18:00 | 15.37 | 14.66 | 0.71 | 10.0612 | 7.7547 | 105.8119 | 85.9534 | 4.0466 | 107.1093 | 102.6422 | 0 | 10.995 | 0.2 | 0 | 0.7685 | 11.7635 | 0.7 | 1.0676 | 1.0957 | 0.010569
2015-09-03 19:00 | 10.2467 | 9.7733 | 0.47333 | 0 | 7.7394 | 120.8154 | 89.0417 | 0.95827 | 121.6666 | 116.5012 | 0 | 7.33 | 0.2 | 0 | 0.51233 | 7.8423 | 0.6 | 0.84507 | 1.0966 | 0.007052
2015-09-03 20:00 | 5.1233 | 4.8867 | 0.23667 | 0 | 7.7242 | 135.819 | 91.6801 | -1.6801 | 136.2985 | 129.8278 | 0 | 3.665 | 0.2 | 0 | 0.25617 | 3.9212 | 0.2 | 0.32254 | 1.0987 | 0.0035327
2015-09-03 21:00 | 0 | 0 | 0 | 0 | 7.709 | 150.8226 | 93.6946 | -3.6946 | 151.0454 | 142.0381 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-09-03 22:00 | 0 | 0 | 0 | 0 | 7.6937 | 165.8261 | 94.9482 | -4.9482 | 165.9027 | 151.6353 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-09-03 23:00 | 0 | 0 | 0 | 0 | 7.6785 | 180.8297 | 95.3535 | -5.3535 | -179.1741 | 155.3412 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-09-04 | 0 | 0 | 0 | 0 | 7.6633 | -164.1667 | 94.8823 | -4.8823 | -164.2532 | 150.8155 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-09-04 01:00 | 2.95 | 2.87 | 0.08 | 0 | 7.648 | -149.1632 | 93.5693 | -3.5693 | -149.4013 | 140.8156 | 0 | 2.1525 | 0.2 | 0 | 0.1475 | 2.3 | 0.3 | 0.37188 | 1.0985 | 0.0020718
2015-09-04 02:00 | 5.9 | 5.74 | 0.16 | 0 | 7.6328 | -134.1596 | 91.508 | -1.508 | -134.6599 | 128.4384 | 0 | 4.305 | 0.2 | 0 | 0.295 | 4.6 | 0.4 | 0.54375 | 1.0978 | 0.004141
2015-09-04 03:00 | 8.85 | 8.61 | 0.24 | 0 | 7.6175 | -119.156 | 88.84 | 1.16 | -120.0296 | 115.0361 | 0 | 6.4575 | 0.2 | 0 | 0.4425 | 6.9 | -0.3 | -0.084375 | 1.1003 | 0.0062257
2015-09-04 04:00 | 31.8867 | 31.5767 | 0.31 | 4.1761 | 7.6023 | -104.1525 | 85.7429 | 4.2571 | -105.4669 | 101.1396 | 0 | 23.6825 | 0.2 | 0 | 1.5943 | 25.2768 | 0.1 | 0.8899 | 1.0964 | 0.022726
2015-09-04 05:00 | 54.9233 | 54.5433 | 0.38 | 2.8799 | 7.587 | -89.1489 | 82.4177 | 7.5823 | -90.8919 | 86.9842 | 0.15152 | 40.9075 | 0.2 | 0 | 2.7462 | 43.8052 | 0.3 | 1.6689 | 1.0933 | 0.039272
2015-09-04 06:00 | 77.96 | 77.51 | 0.45 | 2.3753 | 7.5717 | -74.1453 | 79.0795 | 10.9205 | -76.2054 | 72.6936 | 0.70662 | 58.1325 | 0.2 | 0 | 3.898 | 62.7371 | 0.4 | 2.3605 | 1.0906 | 0.056103
2015-09-04 07:00 | 98.3933 | 96.0467 | 2.3467 | 9.6657 | 7.5565 | -59.1417 | 75.9492 | 14.0508 | -61.31 | 58.3516 | 5.0716 | 72.035 | 0.2 | 0 | 4.9197 | 82.0263 | 1 | 3.5633 | 1.0857 | 0.073029
2015-09-04 08:00 | 118.8267 | 114.5833 | 4.2433 | 14.7183 | 7.5412 | -44.1381 | 73.2435 | 16.7565 | -46.1355 | 44.0456 | 10.5793 | 85.9375 | 0.2 | 0 | 5.9413 | 102.4581 | 1.2 | 4.4018 | 1.0824 | 0.090938
2015-09-04 09:00 | 139.26 | 133.12 | 6.14 | 19.0158 | 7.5259 | -29.1345 | 71.1623 | 18.8377 | -30.6628 | 29.9474 | 16.4769 | 99.84 | 0.2 | 0 | 6.963 | 123.2799 | 1.5 | 5.3525 | 1.0786 | 0.10903
2015-09-04 10:00 | 142.1933 | 135.8533 | 6.34 | 18.4216 | 7.5106 | -14.131 | 69.8694 | 20.1306 | -14.9391 | 16.7209 | 17.6427 | 101.89 | 0.2 | 0 | 7.1097 | 126.6424 | 1.8 | 5.7576 | 1.077 | 0.11184
2015-09-04 11:00 | 145.1267 | 138.5867 | 6.54 | 18.651 | 7.4954 | 0.87263 | 69.4729 | 20.5271 | 0.92383 | 9.5095 | 18.3947 | 103.94 | 0.2 | 0 | 7.2563 | 129.5911 | 1.7 | 5.7497 | 1.077 | 0.11445
2015-09-04 12:00 | 148.06 | 141.32 | 6.74 | 19.7135 | 7.4801 | 15.8762 | 70.0075 | 19.9925 | 16.7757 | 18.1673 | 18.7308 | 105.99 | 0.2 | 0 | 7.403 | 132.1238 | 1.9 | 6.0289 | 1.0759 | 0.11656
2015-09-04 13:00 | 119.4167 | 114.9133 | 4.5033 | 14.1401 | 7.4648 | 30.8798 | 71.429 | 18.571 | 32.469 | 31.5871 | 12.0452 | 86.185 | 0.2 | 0 | 5.9708 | 104.201 | 2.2 | 5.4563 | 1.0782 | 0.092124
2015-09-04 14:00 | 90.7733 | 88.5067 | 2.2667 | 8.0385 | 7.4495 | 45.8834 | 73.6219 | 16.3781 | 47.8998 | 45.7303 | 5.6112 | 66.38 | 0.2 | 0 | 4.5387 | 76.5299 | 1.8 | 4.1916 | 1.0832 | 0.067978
2015-09-04 15:00 | 62.13 | 62.1 | 0.03 | 0.12774 | 7.4342 | 60.887 | 76.417 | 13.583 | 63.0302 | 60.0527 | 0.063768 | 46.575 | 0.2 | 0 | 3.1065 | 49.7453 | 2.3 | 3.8545 | 1.0846 | 0.044241
2015-09-04 16:00 | 46.46 | 46.42 | 0.04 | 0.22184 | 7.4189 | 75.8906 | 79.6121 | 10.3879 | 77.8879 | 74.4017 | 0.05965 | 34.815 | 0.2 | 0 | 2.323 | 37.1977 | 2.6 | 3.7624 | 1.085 | 0.033093
2015-09-04 17:00 | 30.79 | 30.74 | 0.05 | 0.40967 | 7.4036 | 90.8942 | 82.9897 | 7.0103 | 92.5488 | 88.6935 | 0.0093406 | 23.055 | 0.2 | 0 | 1.5395 | 24.6038 | 2.3 | 3.0689 | 1.0877 | 0.021945
2015-09-04 18:00 | 15.12 | 15.06 | 0.06 | 0.93722 | 7.3883 | 105.8978 | 86.3295 | 3.6705 | 107.1128 | 102.8441 | 0 | 11.295 | 0.2 | 0 | 0.756 | 12.051 | 2.1 | 2.4766 | 1.0901 | 0.010772
2015-09-04 19:00 | 10.08 | 10.04 | 0.04 | 0 | 7.373 | 120.9014 | 89.4177 | 0.58227 | 121.6792 | 116.7244 | 0 | 7.53 | 0.2 | 0 | 0.504 | 8.034 | 1.9 | 2.1511 | 1.0914 | 0.00719
2015-09-04 20:00 | 5.04 | 5.02 | 0.02 | 0 | 7.3577 | 135.905 | 92.0554 | -2.0554 | 136.3252 | 130.0833 | 0 | 3.765 | 0.2 | 0 | 0.252 | 4.017 | 1.2 | 1.3255 | 1.0947 | 0.0036059
2015-09-04 21:00 | 0 | 0 | 0 | 0 | 7.3424 | 150.9086 | 94.0683 | -4.0683 | 151.09 | 142.3413 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-09-04 22:00 | 0 | 0 | 0 | 0 | 7.3271 | 165.9123 | 95.319 | -5.319 | 165.968 | 151.9962 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-09-04 23:00 | 0 | 0 | 0 | 0 | 7.3117 | 180.9159 | 95.72 | -5.72 | -179.087 | 155.7047 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0968 | 0
2015-09-05 | 0 | 0 | 0 | 0 | 7.2964 | -164.0805 | 95.2431 | -5.2431 | -164.1447 | 151.0784 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-09-05 01:00 | 2.4733 | 2.44 | 0.033333 | 0 | 7.2811 | -149.0769 | 93.9238 | -3.9238 | -149.2735 | 140.9793 | 0 | 1.83 | 0.2 | 0 | 0.12367 | 1.9537 | 0.6 | 0.66105 | 1.0974 | 0.001758
2015-09-05 02:00 | 4.9467 | 4.88 | 0.066667 | 0 | 7.2657 | -134.0733 | 91.8563 | -1.8563 | -134.5159 | 128.5395 | 0 | 3.66 | 0.2 | 0 | 0.24733 | 3.9073 | 0.7 | 0.8221 | 1.0967 | 0.0035139
2015-09-05 03:00 | 7.42 | 7.32 | 0.1 | 0 | 7.2504 | -119.0696 | 89.183 | 0.81696 | -119.8733 | 115.0988 | 0 | 5.49 | 0.2 | 0 | 0.371 | 5.861 | 0.1 | 0.28316 | 1.0989 | 0.0052812
2015-09-05 04:00 | 30.0067 | 29.05 | 0.95667 | 14.0022 | 7.2351 | -104.066 | 86.0823 | 3.9177 | -105.3023 | 101.1781 | 0 | 21.7875 | 0.2 | 0 | 1.5003 | 23.2878 | 0.2 | 0.92774 | 1.0963 | 0.020935
2015-09-05 05:00 | 52.5933 | 50.78 | 1.8133 | 14.3803 | 7.2197 | -89.0624 | 82.7558 | 7.2442 | -90.7235 | 87.0077 | 0.75067 | 38.085 | 0.2 | 0 | 2.6297 | 41.4653 | 0.4 | 1.6958 | 1.0932 | 0.037171
2015-09-05 06:00 | 75.18 | 72.51 | 2.67 | 14.5402 | 7.2044 | -74.0588 | 79.4188 | 10.5812 | -76.0376 | 72.7093 | 4.3216 | 54.3825 | 0.2 | 0 | 3.759 | 62.4631 | 0.6 | 2.552 | 1.0898 | 0.055819
2015-09-05 07:00 | 105.1467 | 99.4067 | 5.74 | 24.2223 | 7.189 | -59.0551 | 76.2921 | 13.7079 | -61.1479 | 58.3665 | 12.7042 | 74.555 | 0.2 | 0 | 5.2573 | 92.5165 | 0.7 | 3.5911 | 1.0856 | 0.08236
2015-09-05 08:00 | 135.1133 | 126.3033 | 8.81 | 31.1886 | 7.1737 | -44.0515 | 73.592 | 16.408 | -45.9843 | 44.0698 | 22.4088 | 94.7275 | 0.2 | 0 | 6.7557 | 123.892 | 0.6 | 4.4716 | 1.0821 | 0.10993
2015-09-05 09:00 | 165.08 | 153.2 | 11.88 | 37.4745 | 7.1583 | -29.0479 | 71.5174 | 18.4826 | -30.5278 | 30.0017 | 32.4533 | 114.9 | 0.2 | 0 | 8.254 | 155.6073 | 0.9 | 5.7627 | 1.0769 | 0.13742
2015-09-05 10:00 | 164.81 | 156.0833 | 8.7267 | 25.8016 | 7.143 | -14.0442 | 70.2315 | 19.7685 | -14.8249 | 16.8693 | 24.6914 | 117.0625 | 0.2 | 0 | 8.2405 | 149.9944 | 0.9 | 5.5873 | 1.0777 | 0.13255
2015-09-05 11:00 | 164.54 | 158.9667 | 5.5733 | 16.1721 | 7.1276 | 0.95941 | 69.841 | 20.159 | 1.0141 | 9.8836 | 15.9321 | 119.225 | 0.2 | 0 | 8.227 | 143.3841 | 0.8 | 5.2808 | 1.0789 | 0.12685
2015-09-05 12:00 | 164.27 | 161.85 | 2.42 | 7.2072 | 7.1122 | 15.9631 | 70.3802 | 19.6198 | 16.8413 | 18.4415 | 6.837 | 121.3875 | 0.2 | 0 | 8.2135 | 136.438 | 0.7 | 4.9637 | 1.0801 | 0.12085
2015-09-05 13:00 | 144.0567 | 142.2033 | 1.8533 | 5.9353 | 7.0969 | 30.9667 | 71.8047 | 18.1953 | 32.5118 | 31.7976 | 5.0445 | 106.6525 | 0.2 | 0 | 7.2028 | 118.8998 | 1 | 4.7156 | 1.0811 | 0.10541
2015-09-05 14:00 | 123.8433 | 122.5567 | 1.2867 | 4.6677 | 7.0815 | 45.9703 | 73.9992 | 16.0008 | 47.9236 | 45.9183 | 3.2473 | 91.9175 | 0.2 | 0 | 6.1922 | 101.3569 | 1.1 | 4.2674 | 1.0829 | 0.090005
2015-09-05 15:00 | 103.63 | 102.91 | 0.72 | 3.1518 | 7.0661 | 60.974 | 76.7949 | 13.2051 | 63.0404 | 60.2339 | 1.5648 | 77.1825 | 0.2 | 0 | 5.1815 | 83.9288 | 1 | 3.6228 | 1.0855 | 0.074706
2015-09-05 16:00 | 75.48 | 74.3733 | 1.1067 | 6.3669 | 7.0507 | 75.9776 | 79.9902 | 10.0098 | 77.8903 | 74.5842 | 1.6925 | 55.78 | 0.2 | 0 | 3.774 | 61.2465 | 0.8 | 2.714 | 1.0891 | 0.054699
2015-09-05 17:00 | 47.33 | 45.8367 | 1.4933 | 12.93 | 7.0354 | 90.9813 | 83.3679 | 6.6321 | 92.5493 | 88.8835 | 0.25194 | 34.3775 | 0.2 | 0 | 2.3665 | 36.9959 | 0.9 | 2.0561 | 1.0918 | 0.033121
2015-09-05 18:00 | 19.18 | 17.3 | 1.88 | 32.7364 | 7.02 | 105.9849 | 86.7078 | 3.2922 | 107.1172 | 103.0476 | 0 | 12.975 | 0.2 | 0 | 0.959 | 13.934 | 0.7 | 1.1354 | 1.0955 | 0.012517
2015-09-05 19:00 | 12.7867 | 11.5333 | 1.2533 | 0 | 7.0046 | 120.9886 | 89.7959 | 0.2041 | 121.6928 | 116.9489 | 0 | 8.65 | 0.2 | 0 | 0.63933 | 9.2893 | 0.5 | 0.79029 | 1.0968 | 0.0083549
2015-09-05 20:00 | 6.3933 | 5.7667 | 0.62667 | 0 | 6.9892 | 135.9923 | 92.4329 | -2.4329 | 136.3529 | 130.3398 | 0 | 4.325 | 0.2 | 0 | 0.31967 | 4.6447 | 0.6 | 0.74515 | 1.097 | 0.0041781
2015-09-05 21:00 | 0 | 0 | 0 | 0 | 6.9738 | 150.9959 | 94.4442 | -4.4442 | 151.1357 | 142.6457 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-09-05 22:00 | 0 | 0 | 0 | 0 | 6.9584 | 165.9996 | 95.6919 | -5.6919 | 166.0345 | 152.3591 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-09-05 23:00 | 0 | 0 | 0 | 0 | 6.943 | 181.0032 | 96.0883 | -6.0883 | -178.9985 | 156.0698 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-09-06 | 0 | 0 | 0 | 0 | 6.9276 | -163.9931 | 95.6058 | -5.6058 | -164.0347 | 151.34 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-09-06 01:00 | 2.1167 | 2.11 | 0.0066667 | 0 | 6.9122 | -148.9894 | 94.2801 | -4.2801 | -149.144 | 141.1408 | 0 | 1.5825 | 0.2 | 0 | 0.10583 | 1.6883 | -0.3 | -0.24724 | 1.101 | 0.0015242
2015-09-06 02:00 | 4.2333 | 4.22 | 0.013333 | 0 | 6.8968 | -133.9858 | 92.2062 | -2.2062 | -134.3702 | 128.6385 | 0 | 3.165 | 0.2 | 0 | 0.21167 | 3.3767 | -0.6 | -0.49448 | 1.102 | 0.0030512
2015-09-06 03:00 | 6.35 | 6.33 | 0.02 | 0 | 6.8814 | -118.9821 | 89.5277 | 0.4723 | -119.7153 | 115.1598 | 0 | 4.7475 | 0.2 | 0 | 0.3175 | 5.065 | -0.3 | -0.14172 | 1.1006 | 0.004571
2015-09-06 04:00 | 27.3167 | 27.1767 | 0.14 | 2.2442 | 6.866 | -103.9784 | 86.4234 | 3.5766 | -105.1362 | 101.2155 | 0 | 20.3825 | 0.2 | 0 | 1.3658 | 21.7483 | -0.2 | 0.47964 | 1.0981 | 0.019583
2015-09-06 05:00 | 48.2833 | 48.0233 | 0.26 | 2.1628 | 6.8505 | -88.9747 | 83.0956 | 6.9044 | -90.5536 | 87.0308 | 0.11203 | 36.0175 | 0.2 | 0 | 2.4142 | 38.5437 | -0.2 | 1.0045 | 1.096 | 0.034639
2015-09-06 06:00 | 69.25 | 68.87 | 0.38 | 2.1375 | 6.8351 | -73.9711 | 79.7598 | 10.2402 | -75.8686 | 72.7251 | 0.63476 | 51.6525 | 0.2 | 0 | 3.4625 | 55.7498 | -0.1 | 1.6422 | 1.0934 | 0.049986
2015-09-06 07:00 | 95.0767 | 94.5 | 0.57667 | 2.4951 | 6.8197 | -58.9674 | 76.6368 | 13.3632 | -60.9845 | 58.3822 | 1.308 | 70.875 | 0.2 | 0 | 4.7538 | 76.9369 | 0.2 | 2.6043 | 1.0896 | 0.06874
2015-09-06 08:00 | 120.9033 | 120.13 | 0.77333 | 2.7958 | 6.8042 | -43.9637 | 73.9423 | 16.0577 | -45.832 | 44.0959 | 2.0079 | 90.0975 | 0.2 | 0 | 6.0452 | 98.1505 | 0.4 | 3.4672 | 1.0861 | 0.087416
2015-09-06 09:00 | 146.73 | 145.76 | 0.97 | 3.118 | 6.7888 | -28.96 | 71.8745 | 18.1255 | -30.3917 | 30.0598 | 2.6986 | 109.32 | 0.2 | 0 | 7.3365 | 119.3551 | 1 | 4.7298 | 1.0811 | 0.10581
2015-09-06 10:00 | 147.4167 | 146.7067 | 0.71 | 2.137 | 6.7734 | -13.9563 | 70.5954 | 19.4046 | -14.7098 | 17.0248 | 2.0434 | 110.03 | 0.2 | 0 | 7.3708 | 119.4442 | 1.3 | 5.0326 | 1.0799 | 0.10577
2015-09-06 11:00 | 148.1033 | 147.6533 | 0.45 | 1.3292 | 6.7579 | 1.0473 | 70.211 | 19.789 | 1.1053 | 10.2599 | 1.3079 | 110.74 | 0.2 | 0 | 7.4052 | 119.4531 | 1.6 | 5.3329 | 1.0787 | 0.10566
2015-09-06 12:00 | 148.79 | 148.6 | 0.19 | 0.57644 | 6.7425 | 16.051 | 70.7549 | 19.2451 | 16.9079 | 18.7212 | 0.54594 | 111.45 | 0.2 | 0 | 7.4395 | 119.4354 | 1.7 | 5.4324 | 1.0783 | 0.1056
2015-09-06 13:00 | 129.0767 | 128.5633 | 0.51333 | 1.6776 | 6.727 | 31.0547 | 72.1824 | 17.8176 | 32.5554 | 32.0128 | 1.4225 | 96.4225 | 0.2 | 0 | 6.4538 | 104.2988 | 2 | 5.2593 | 1.079 | 0.092278
2015-09-06 14:00 | 109.3633 | 108.5267 | 0.83667 | 3.107 | 6.7116 | 46.0584 | 74.3785 | 15.6215 | 47.9483 | 46.1098 | 2.154 | 81.395 | 0.2 | 0 | 5.4682 | 89.0172 | 1.8 | 4.5818 | 1.0817 | 0.078956
2015-09-06 15:00 | 89.65 | 88.49 | 1.16 | 5.2258 | 6.6961 | 61.0621 | 77.1749 | 12.8251 | 63.0514 | 60.4178 | 2.5798 | 66.3675 | 0.2 | 0 | 4.4825 | 73.4298 | 2.1 | 4.3947 | 1.0824 | 0.065175
2015-09-06 16:00 | 65.04 | 64.2 | 0.84 | 5.0216 | 6.6807 | 76.0658 | 80.3705 | 9.6295 | 77.8934 | 74.769 | 1.3192 | 48.15 | 0.2 | 0 | 3.252 | 52.7212 | 2.2 | 3.8475 | 1.0846 | 0.046889
2015-09-06 17:00 | 40.43 | 39.91 | 0.52 | 4.7751 | 6.6652 | 91.0695 | 83.7483 | 6.2517 | 92.5506 | 89.0753 | 0.077064 | 29.9325 | 0.2 | 0 | 2.0215 | 32.0311 | 2 | 3.001 | 1.088 | 0.028577
2015-09-06 18:00 | 15.82 | 15.62 | 0.2 | 0 | 6.6498 | 106.0732 | 87.0882 | 2.9118 | 107.1223 | 103.2524 | 0 | 11.715 | 0.2 | 0 | 0.791 | 12.506 | 2.1 | 2.4908 | 1.09 | 0.011178
2015-09-06 19:00 | 10.5467 | 10.4133 | 0.13333 | 0 | 6.6343 | 121.0769 | 90.1762 | -0.17615 | 121.7073 | 117.1744 | 0 | 7.81 | 0.2 | 0 | 0.52733 | 8.3373 | 1.8 | 2.0605 | 1.0918 | 0.0074639
2015-09-06 20:00 | 5.2733 | 5.2067 | 0.066667 | 0 | 6.6188 | 136.0806 | 92.8125 | -2.8125 | 136.3815 | 130.5971 | 0 | 3.905 | 0.2 | 0 | 0.26367 | 4.1687 | 1.2 | 1.3303 | 1.0947 | 0.0037419
2015-09-06 21:00 | 0 | 0 | 0 | 0 | 6.6034 | 151.0843 | 94.822 | -4.822 | 151.1825 | 142.9511 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.0948 | 0
2015-09-06 22:00 | 0 | 0 | 0 | 0 | 6.5879 | 166.088 | 96.0667 | -6.0667 | 166.1023 | 152.7239 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0908 | 0
2015-09-06 23:00 | 0 | 0 | 0 | 0 | 6.5724 | 181.0917 | 96.4586 | -6.4586 | -178.9086 | 156.4362 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0888 | 0
2015-09-07 | 0 | 0 | 0 | 0 | 6.5569 | -163.9046 | 95.9702 | -5.9702 | -163.9232 | 151.6 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0888 | 0
2015-09-07 01:00 | 0.97667 | 0.95333 | 0.023333 | 0 | 6.5414 | -148.9009 | 94.6381 | -4.6381 | -149.013 | 141.2999 | 0 | 0.715 | 0.2 | 0 | 0.048833 | 0.76383 | 2.9 | 2.9239 | 1.0883 | 0.00068165
2015-09-07 02:00 | 1.9533 | 1.9067 | 0.046667 | 0 | 6.526 | -133.8972 | 92.5578 | -2.5578 | -134.223 | 128.7354 | 0 | 1.43 | 0.2 | 0 | 0.097667 | 1.5277 | 3.1 | 3.1477 | 1.0874 | 0.0013622
2015-09-07 03:00 | 2.93 | 2.86 | 0.07 | 0 | 6.5105 | -118.8935 | 89.8739 | 0.12606 | -119.5558 | 115.2193 | 0 | 2.145 | 0.2 | 0 | 0.1465 | 2.2915 | 3.4 | 3.4716 | 1.0861 | 0.0020408
2015-09-07 04:00 | 14.18 | 14.0133 | 0.16667 | 2.9544 | 6.495 | -103.8897 | 86.7661 | 3.2339 | -104.9686 | 101.2519 | 0 | 10.51 | 0.2 | 0 | 0.709 | 11.219 | 3 | 3.3506 | 1.0866 | 0.0099962
2015-09-07 05:00 | 25.43 | 25.1667 | 0.26333 | 2.3039 | 6.4795 | -88.886 | 83.4369 | 6.5631 | -90.3824 | 87.0533 | 0.11844 | 18.875 | 0.2 | 0 | 1.2715 | 20.2649 | 3.2 | 3.8333 | 1.0847 | 0.018024
2015-09-07 06:00 | 36.68 | 36.32 | 0.36 | 2.0944 | 6.464 | -73.8823 | 80.1025 | 9.8975 | -75.6983 | 72.741 | 0.62139 | 27.24 | 0.2 | 0 | 1.834 | 29.6954 | 3.4 | 4.328 | 1.0827 | 0.026364
2015-09-07 07:00 | 47.55 | 47.2567 | 0.29333 | 1.3023 | 6.4485 | -58.8786 | 76.9831 | 13.0169 | -60.8201 | 58.3988 | 0.68242 | 35.4425 | 0.2 | 0 | 2.3775 | 38.5024 | 3.4 | 4.6032 | 1.0816 | 0.034148
2015-09-07 08:00 | 58.42 | 58.1933 | 0.22667 | 0.83735 | 6.433 | -43.8749 | 74.2943 | 15.7057 | -45.6787 | 44.1241 | 0.60107 | 43.645 | 0.2 | 0 | 2.921 | 47.1671 | 3.4 | 4.874 | 1.0805 | 0.041791
2015-09-07 09:00 | 69.29 | 69.13 | 0.16 | 0.52434 | 6.4175 | -28.8711 | 72.2332 | 17.7668 | -30.2548 | 30.1218 | 0.45354 | 51.8475 | 0.2 | 0 | 3.4645 | 55.7655 | 3.5 | 5.2427 | 1.079 | 0.049342
2015-09-07 10:00 | 80.89 | 75.8667 | 5.0233 | 15.3991 | 6.4019 | -13.8674 | 70.9611 | 19.0389 | -14.5938 | 17.1873 | 14.7114 | 56.9 | 0.2 | 0 | 4.0445 | 75.6559 | 3.3 | 5.6642 | 1.0773 | 0.066836
2015-09-07 11:00 | 92.49 | 82.6033 | 9.8867 | 29.7395 | 6.3864 | 1.1363 | 70.5829 | 19.4171 | 1.1974 | 10.6384 | 29.2283 | 61.9525 | 0.2 | 0 | 4.6245 | 95.8053 | 4 | 6.9939 | 1.072 | 0.084219
2015-09-07 12:00 | 104.09 | 89.34 | 14.75 | 45.6095 | 6.3709 | 16.14 | 71.1315 | 18.8685 | 16.9752 | 19.0063 | 43.123 | 67.005 | 0.2 | 0 | 5.2045 | 115.3325 | 3.9 | 7.5041 | 1.07 | 0.10119
2015-09-07 13:00 | 100.9867 | 90.62 | 10.3667 | 34.5934 | 6.3554 | 31.1438 | 72.5621 | 17.4379 | 32.5999 | 32.2324 | 29.2623 | 67.965 | 0.2 | 0 | 5.0493 | 102.2766 | 3.8 | 6.9961 | 1.072 | 0.089907
2015-09-07 14:00 | 97.8833 | 91.9 | 5.9833 | 22.762 | 6.3399 | 46.1475 | 74.7598 | 15.2402 | 47.9739 | 46.3049 | 15.7244 | 68.925 | 0.2 | 0 | 4.8942 | 89.5436 | 3.7 | 6.4982 | 1.074 | 0.07886
2015-09-07 15:00 | 94.78 | 93.18 | 1.6 | 7.4257 | 6.3243 | 61.1512 | 77.557 | 12.443 | 63.0632 | 60.6045 | 3.6448 | 69.885 | 0.2 | 0 | 4.739 | 78.2688 | 4.2 | 6.6459 | 1.0734 | 0.068892
2015-09-07 16:00 | 69.51 | 66.3 | 3.21 | 19.9757 | 6.3088 | 76.155 | 80.7527 | 9.2473 | 77.8974 | 74.9559 | 5.1849 | 49.725 | 0.2 | 0 | 3.4755 | 58.3854 | 4 | 5.8245 | 1.0767 | 0.051548
2015-09-07 17:00 | 44.24 | 39.42 | 4.82 | 47.1343 | 6.2933 | 91.1587 | 84.1306 | 5.8694 | 92.5526 | 89.2687 | 0.60158 | 29.565 | 0.2 | 0 | 2.212 | 32.3786 | 3.4 | 4.4118 | 1.0824 | 0.028737
2015-09-07 18:00 | 18.97 | 12.54 | 6.43 | 0 | 6.2777 | 106.1624 | 87.4706 | 2.5294 | 107.1282 | 103.4584 | 0 | 9.405 | 0.2 | 0 | 0.9485 | 10.3535 | 3.1 | 3.4235 | 1.0863 | 0.0092226
2015-09-07 19:00 | 12.6467 | 8.36 | 4.2867 | 0 | 6.2622 | 121.1662 | 90.5584 | -0.55838 | 121.7225 | 117.4008 | 0 | 6.27 | 0.2 | 0 | 0.63233 | 6.9023 | 2.7 | 2.9157 | 1.0883 | 0.0061599
2015-09-07 20:00 | 6.3233 | 4.18 | 2.1433 | 0 | 6.2467 | 136.1699 | 93.1939 | -3.1939 | 136.4109 | 130.8551 | 0 | 3.135 | 0.2 | 0 | 0.31617 | 3.4512 | 2.7 | 2.8078 | 1.0888 | 0.0030812
2015-09-07 21:00 | 0 | 0 | 0 | 0 | 6.2311 | 151.1737 | 95.2017 | -5.2017 | 151.2303 | 143.2572 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0908 | 0
2015-09-07 22:00 | 0 | 0 | 0 | 0 | 6.2156 | 166.1774 | 96.4433 | -6.4433 | 166.1712 | 153.0903 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0908 | 0
2015-09-07 23:00 | 0 | 0 | 0 | 0 | 6.2 | 181.1812 | 96.8306 | -6.8306 | -178.8174 | 156.8039 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0908 | 0
2015-09-08 | 0 | 0 | 0 | 0 | 6.1845 | -163.8151 | 96.3363 | -6.3363 | -163.8103 | 151.8583 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0916 | 0
2015-09-08 01:00 | 2.0367 | 1.6733 | 0.36333 | 0 | 6.1689 | -148.8113 | 94.9976 | -4.9976 | -148.8806 | 141.4565 | 0 | 1.255 | 0.2 | 0 | 0.10183 | 1.3568 | 1.9 | 1.9424 | 1.0922 | 0.0012152
2015-09-08 02:00 | 4.0733 | 3.3467 | 0.72667 | 0 | 6.1534 | -133.8076 | 92.911 | -2.911 | -134.0744 | 128.8302 | 0 | 2.51 | 0.2 | 0 | 0.20367 | 2.7137 | 1.9 | 1.9848 | 1.0921 | 0.0024301
2015-09-08 03:00 | 6.11 | 5.02 | 1.09 | 0 | 6.1378 | -118.8038 | 90.2217 | -0.22167 | -119.3949 | 115.2772 | 0 | 3.765 | 0.2 | 0 | 0.3055 | 4.0705 | 1.6 | 1.7272 | 1.0931 | 0.0036485
2015-09-08 04:00 | 30.8667 | 25.1667 | 5.7 | 0 | 6.1222 | -103.8001 | 87.1102 | 2.8898 | -104.7997 | 101.2873 | 0 | 18.875 | 0.2 | 0 | 1.5433 | 20.4183 | 1.7 | 2.3381 | 1.0906 | 0.018261
2015-09-08 05:00 | 55.6233 | 45.3133 | 10.31 | 95.1549 | 6.1067 | -88.7963 | 83.7798 | 6.2202 | -90.2099 | 87.0754 | 4.8549 | 33.985 | 0.2 | 0 | 2.7812 | 41.6211 | 1.9 | 3.2007 | 1.0872 | 0.037105
2015-09-08 06:00 | 80.38 | 65.46 | 14.92 | 89.8979 | 6.0911 | -73.7926 | 80.4466 | 9.5534 | -75.5268 | 72.757 | 26.6479 | 49.095 | 0.2 | 0 | 4.019 | 79.7619 | 2.1 | 4.5926 | 1.0816 | 0.070744
2015-09-08 07:00 | 98.8567 | 85.5633 | 13.2933 | 60.6121 | 6.0755 | -58.7888 | 77.331 | 12.669 | -60.6547 | 58.4165 | 31.745 | 64.1725 | 0.2 | 0 | 4.9428 | 100.8604 | 2.3 | 5.4519 | 1.0782 | 0.089172
2015-09-08 08:00 | 117.3333 | 105.6667 | 11.6667 | 44.0667 | 6.0599 | -43.7851 | 74.6479 | 15.3521 | -45.5245 | 44.1543 | 31.6164 | 79.25 | 0.2 | 0 | 5.8667 | 116.733 | 2.2 | 5.8479 | 1.0766 | 0.10305
2015-09-08 09:00 | 135.81 | 125.77 | 10.04 | 33.5623 | 6.0444 | -28.7813 | 72.5937 | 17.4063 | -30.117 | 30.1877 | 29.0107 | 94.3275 | 0.2 | 0 | 6.7905 | 130.1287 | 2.3 | 6.3665 | 1.0745 | 0.11466
2015-09-08 10:00 | 143.27 | 130.2133 | 13.0567 | 40.7842 | 6.0288 | -13.7775 | 71.3286 | 18.6714 | -14.4771 | 17.3568 | 38.9271 | 97.66 | 0.2 | 0 | 7.1635 | 143.7506 | 2.1 | 6.5922 | 1.0736 | 0.12655
2015-09-08 11:00 | 150.73 | 134.6567 | 16.0733 | 49.2617 | 6.0132 | 1.2262 | 70.9566 | 19.0434 | 1.2901 | 11.019 | 48.3535 | 100.9925 | 0.2 | 0 | 7.5365 | 156.8825 | 2.3 | 7.2026 | 1.0712 | 0.1378
2015-09-08 12:00 | 158.19 | 139.1 | 19.09 | 60.1942 | 5.9976 | 16.23 | 71.5099 | 18.4901 | 17.0433 | 19.2966 | 56.8125 | 104.325 | 0.2 | 0 | 7.9095 | 169.047 | 2.5 | 7.7827 | 1.0689 | 0.14817
2015-09-08 13:00 | 144.03 | 123.3033 | 20.7267 | 70.6641 | 5.982 | 31.2338 | 72.9436 | 17.0564 | 32.6451 | 32.4563 | 59.6264 | 92.4775 | 0.2 | 0 | 7.2015 | 159.3054 | 2.8 | 7.7783 | 1.0689 | 0.13963
2015-09-08 14:00 | 129.87 | 107.5067 | 22.3633 | 87.2182 | 5.9664 | 46.2375 | 75.143 | 14.857 | 48.0001 | 46.5032 | 60.0335 | 80.63 | 0.2 | 0 | 6.4935 | 147.157 | 2.5 | 7.0987 | 1.0716 | 0.12931
2015-09-08 15:00 | 115.71 | 91.71 | 24 | 114.876 | 5.9508 | 61.2413 | 77.9409 | 12.0591 | 63.0757 | 60.7938 | 56.0543 | 68.7825 | 0.2 | 0 | 5.7855 | 130.6223 | 3.6 | 7.6819 | 1.0693 | 0.11453
2015-09-08 16:00 | 83.33 | 65.08 | 18.25 | 118.4496 | 5.9352 | 76.2451 | 81.1369 | 8.8631 | 77.9019 | 75.1449 | 30.3676 | 48.81 | 0.2 | 0 | 4.1665 | 83.3441 | 2.6 | 5.2045 | 1.0792 | 0.073754
2015-09-08 17:00 | 50.95 | 38.45 | 12.5 | 130.7704 | 5.9196 | 91.2489 | 84.5149 | 5.4851 | 92.5552 | 89.4637 | 1.2241 | 28.8375 | 0.2 | 0 | 2.5475 | 32.6091 | 1.4 | 2.419 | 1.0903 | 0.029155
2015-09-08 18:00 | 18.57 | 11.82 | 6.75 | 0 | 5.904 | 106.2526 | 87.8549 | 2.1451 | 107.1348 | 103.6656 | 0 | 8.865 | 0.2 | 0 | 0.9285 | 9.7935 | 1 | 1.306 | 1.0948 | 0.0087918
2015-09-08 19:00 | 12.38 | 7.88 | 4.5 | 0 | 5.8884 | 121.2564 | 90.9425 | -0.94247 | 121.7384 | 117.628 | 0 | 5.91 | 0.2 | 0 | 0.619 | 6.529 | 0 | 0.20403 | 1.0992 | 0.0058848
2015-09-08 20:00 | 6.19 | 3.94 | 2.25 | 0 | 5.8728 | 136.2602 | 93.5773 | -3.5773 | 136.4412 | 131.1137 | 0 | 2.955 | 0.2 | 0 | 0.3095 | 3.2645 | -0.5 | -0.39798 | 1.1016 | 0.0029488
2015-09-08 21:00 | 0 | 0 | 0 | 0 | 5.8572 | 151.264 | 95.5832 | -5.5832 | 151.279 | 143.564 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-09-08 22:00 | 0 | 0 | 0 | 0 | 5.8416 | 166.2677 | 96.8216 | -6.8216 | 166.2411 | 153.4583 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-09-08 23:00 | 0 | 0 | 0 | 0 | 5.8259 | 181.2715 | 97.2042 | -7.2042 | -178.725 | 157.1728 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-09-09 | 0 | 0 | 0 | 0 | 5.8103 | -163.7247 | 96.704 | -6.704 | -163.6961 | 152.1147 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-09-09 01:00 | 1.6733 | 1.6733 | 0 | 0 | 5.7947 | -148.7209 | 95.3587 | -5.3587 | -148.7468 | 141.6107 | 0 | 1.255 | 0.2 | 0 | 0.083667 | 1.3387 | -0.2 | -0.15817 | 1.1006 | 0.0012082
2015-09-09 02:00 | 3.3467 | 3.3467 | 0 | 0 | 5.7791 | -133.7171 | 93.2656 | -3.2656 | -133.9243 | 128.923 | 0 | 2.51 | 0.2 | 0 | 0.16733 | 2.6773 | 1.1 | 1.1837 | 1.0953 | 0.0024046
2015-09-09 03:00 | 5.02 | 5.02 | 0 | 0 | 5.7634 | -118.7133 | 90.5708 | -0.57084 | -119.2326 | 115.3337 | 0 | 3.765 | 0.2 | 0 | 0.251 | 4.016 | 0.7 | 0.8255 | 1.0967 | 0.0036116
2015-09-09 04:00 | 30.8833 | 30.05 | 0.83333 | 0 | 5.7478 | -103.7095 | 87.4558 | 2.5442 | -104.6295 | 101.3218 | 0 | 22.5375 | 0.2 | 0 | 1.5442 | 24.0817 | 1.4 | 2.1526 | 1.0914 | 0.021552
2015-09-09 05:00 | 56.7467 | 55.08 | 1.6667 | 16.2802 | 5.7322 | -88.7057 | 84.1241 | 5.8759 | -90.0362 | 87.0972 | 0.82446 | 41.31 | 0.2 | 0 | 2.8373 | 44.9718 | 1.4 | 2.8054 | 1.0888 | 0.040151
2015-09-09 06:00 | 82.61 | 80.11 | 2.5 | 15.6236 | 5.7165 | -73.702 | 80.7923 | 9.2077 | -75.3544 | 72.7734 | 4.627 | 60.0825 | 0.2 | 0 | 4.1305 | 68.84 | 1.6 | 3.7512 | 1.085 | 0.061247
2015-09-09 07:00 | 131.09 | 92.35 | 38.74 | 181.5679 | 5.7009 | -58.6982 | 77.6805 | 12.3195 | -60.4884 | 58.4352 | 95.044 | 69.2625 | 0.2 | 0 | 6.5545 | 170.861 | 1.7 | 7.0394 | 1.0718 | 0.15017
2015-09-09 08:00 | 179.57 | 104.59 | 74.98 | 289.759 | 5.6852 | -43.6944 | 75.0031 | 14.9969 | -45.3695 | 44.1868 | 207.7779 | 78.4425 | 0.2 | 0 | 8.9785 | 295.1989 | 2.3 | 11.525 | 1.0539 | 0.25511
2015-09-09 09:00 | 228.05 | 116.83 | 111.22 | 379.4494 | 5.6696 | -28.6906 | 72.9558 | 17.0442 | -29.9786 | 30.2577 | 327.7563 | 87.6225 | 0.2 | 0 | 11.4025 | 426.7813 | 3.1 | 16.4369 | 1.0343 | 0.36195
2015-09-09 10:00 | 247.9733 | 92.53 | 155.4433 | 494.9953 | 5.6539 | -13.6868 | 71.6977 | 18.3023 | -14.3597 | 17.5331 | 471.9992 | 69.3975 | 0.2 | 0 | 12.3987 | 553.7954 | 2.9 | 20.2061 | 1.0192 | 0.46282
2015-09-09 11:00 | 267.8967 | 68.23 | 199.6667 | 623.7935 | 5.6383 | 1.317 | 71.332 | 18.668 | 1.3834 | 11.4015 | 611.4836 | 51.1725 | 0.2 | 0 | 13.3948 | 676.0509 | 2.9 | 24.0266 | 1.0039 | 0.55652
2015-09-09 12:00 | 287.82 | 43.93 | 243.89 | 784.6132 | 5.6226 | 16.3208 | 71.8901 | 18.1099 | 17.1119 | 19.5916 | 739.1891 | 32.9475 | 0.2 | 0 | 14.391 | 786.5276 | 2.7 | 27.279 | 0.99088 | 0.63907
2015-09-09 13:00 | 246.9567 | 42.1233 | 204.8333 | 713.9269 | 5.607 | 31.3246 | 73.3269 | 16.6731 | 32.6909 | 32.6845 | 600.8815 | 31.5925 | 0.2 | 0 | 12.3478 | 644.8219 | 4 | 24.1507 | 1.0034 | 0.53055
2015-09-09 14:00 | 206.0933 | 40.3167 | 165.7767 | 663.3544 | 5.5913 | 46.3284 | 75.528 | 14.472 | 48.0269 | 46.7047 | 454.9007 | 30.2375 | 0.2 | 0 | 10.3047 | 495.4429 | 3.2 | 18.6826 | 1.0253 | 0.41653
2015-09-09 15:00 | 165.23 | 38.51 | 126.72 | 626.2947 | 5.5757 | 61.3322 | 78.3266 | 11.6734 | 63.0887 | 60.9855 | 303.7726 | 28.8825 | 0.2 | 0 | 8.2615 | 340.9166 | 3.7 | 14.3536 | 1.0426 | 0.29146
2015-09-09 16:00 | 114.94 | 30.0433 | 84.8967 | 575.9037 | 5.56 | 76.336 | 81.5229 | 8.4771 | 77.9071 | 75.3357 | 145.7932 | 22.5325 | 0.2 | 0 | 5.747 | 174.0727 | 1.5 | 6.9398 | 1.0722 | 0.15305
2015-09-09 17:00 | 64.65 | 21.5767 | 43.0733 | 484.6332 | 5.5443 | 91.3398 | 84.9009 | 5.0991 | 92.5585 | 89.66 | 2.8757 | 16.1825 | 0.2 | 0 | 3.2325 | 22.2907 | 2.1 | 2.7966 | 1.0888 | 0.019902
2015-09-09 18:00 | 14.36 | 13.11 | 1.25 | 0 | 5.5286 | 106.3437 | 88.2409 | 1.7591 | 107.1419 | 103.8738 | 0 | 9.8325 | 0.2 | 0 | 0.718 | 10.5505 | 1.6 | 1.9297 | 1.0923 | 0.0094498
2015-09-09 19:00 | 9.5733 | 8.74 | 0.83333 | 0 | 5.513 | 121.3475 | 91.3283 | -1.3283 | 121.755 | 117.8557 | 0 | 6.555 | 0.2 | 0 | 0.47867 | 7.0337 | 1 | 1.2198 | 1.0951 | 0.0063162
2015-09-09 20:00 | 4.7867 | 4.37 | 0.41667 | 0 | 5.4973 | 136.3513 | 93.9623 | -3.9623 | 136.4722 | 131.3725 | 0 | 3.2775 | 0.2 | 0 | 0.23933 | 3.5168 | 1.1 | 1.2099 | 1.0952 | 0.0031582
2015-09-09 21:00 | 0 | 0 | 0 | 0 | 5.4816 | 151.3551 | 95.9664 | -5.9664 | 151.3285 | 143.8713 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0936 | 0
2015-09-09 22:00 | 0 | 0 | 0 | 0 | 5.4659 | 166.3589 | 97.2015 | -7.2015 | 166.3121 | 153.8277 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-09-09 23:00 | 0 | 0 | 0 | 0 | 5.4502 | 181.3627 | 97.5794 | -7.5794 | -178.6315 | 157.5427 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.096 | 0
2015-09-10 | 0 | 0 | 0 | 0 | 5.4346 | -163.6335 | 97.0732 | -7.0732 | -163.5806 | 152.3692 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-09-10 01:00 | 0.95667 | 0.95667 | 0 | 0 | 5.4189 | -148.6297 | 95.7212 | -5.7212 | -148.6117 | 141.7623 | 0 | 0.7175 | 0.2 | 0 | 0.047833 | 0.76533 | 0.5 | 0.52392 | 1.0979 | 0.00068902
2015-09-10 02:00 | 1.9133 | 1.9133 | 0 | 0 | 5.4032 | -133.6258 | 93.6216 | -3.6216 | -133.773 | 129.0136 | 0 | 1.435 | 0.2 | 0 | 0.095667 | 1.5307 | -0.1 | -0.052167 | 1.1002 | 0.0013809
2015-09-10 03:00 | 2.87 | 2.87 | 0 | 0 | 5.3875 | -118.622 | 90.9214 | -0.92138 | -119.0691 | 115.3887 | 0 | 2.1525 | 0.2 | 0 | 0.1435 | 2.296 | 0 | 0.07175 | 1.0997 | 0.0020705
2015-09-10 04:00 | 19.06 | 18.9567 | 0.10333 | 0 | 5.3718 | -103.6182 | 87.8027 | 2.1973 | -104.4582 | 101.3554 | 0 | 14.2175 | 0.2 | 0 | 0.953 | 15.1705 | 0.3 | 0.77408 | 1.0969 | 0.013645
2015-09-10 05:00 | 35.25 | 35.0433 | 0.20667 | 2.1445 | 5.3561 | -88.6144 | 84.4698 | 5.5302 | -89.8616 | 87.1187 | 0.1078 | 26.2825 | 0.2 | 0 | 1.7625 | 28.1528 | 0.9 | 1.7798 | 1.0929 | 0.025229
2015-09-10 06:00 | 51.44 | 51.13 | 0.31 | 2.0126 | 5.3404 | -73.6106 | 81.1394 | 8.8606 | -75.181 | 72.7902 | 0.59546 | 38.3475 | 0.2 | 0 | 2.572 | 41.515 | 1 | 2.2973 | 1.0908 | 0.037134
2015-09-10 07:00 | 76.52 | 75.9733 | 0.54667 | 2.6361 | 5.3247 | -58.6067 | 78.0314 | 11.9686 | -60.3213 | 58.4551 | 1.3791 | 56.98 | 0.2 | 0 | 3.826 | 62.1851 | 1.3 | 3.2433 | 1.087 | 0.055429
2015-09-10 08:00 | 101.6 | 100.8167 | 0.78333 | 3.0993 | 5.309 | -43.6029 | 75.3598 | 14.6402 | -45.2139 | 44.2216 | 2.2211 | 75.6125 | 0.2 | 0 | 5.08 | 82.9136 | 1.2 | 3.791 | 1.0848 | 0.073757
2015-09-10 09:00 | 126.68 | 125.66 | 1.02 | 3.5536 | 5.2933 | -28.5991 | 73.3195 | 16.6805 | -29.8396 | 30.3318 | 3.0671 | 94.245 | 0.2 | 0 | 6.334 | 103.6461 | 1.4 | 4.6389 | 1.0814 | 0.091912
2015-09-10 10:00 | 132.2467 | 130.2633 | 1.9833 | 6.4419 | 5.2775 | -13.5953 | 72.0685 | 17.9315 | -14.2418 | 17.7163 | 6.1364 | 97.6975 | 0.2 | 0 | 6.6123 | 110.4462 | 1.5 | 4.9514 | 1.0802 | 0.097829
2015-09-10 11:00 | 137.8133 | 134.8667 | 2.9467 | 9.3889 | 5.2618 | 1.4086 | 71.7089 | 18.2911 | 1.4773 | 11.7859 | 9.191 | 101.15 | 0.2 | 0 | 6.8907 | 117.2317 | 2 | 5.6635 | 1.0773 | 0.10357
2015-09-10 12:00 | 143.38 | 139.47 | 3.91 | 12.8407 | 5.2461 | 16.4124 | 72.2719 | 17.7281 | 17.1811 | 19.8913 | 12.0746 | 104.6025 | 0.2 | 0 | 7.169 | 123.8461 | 3.3 | 7.1702 | 1.0713 | 0.1088
2015-09-10 13:00 | 117.96 | 114.3633 | 3.5967 | 12.8238 | 5.2304 | 31.4162 | 73.7118 | 16.2882 | 32.7372 | 32.9167 | 10.7651 | 85.7725 | 0.2 | 0 | 5.898 | 102.4356 | 2.9 | 6.1011 | 1.0756 | 0.090347
2015-09-10 14:00 | 92.54 | 89.2567 | 3.2833 | 13.4913 | 5.2147 | 46.4201 | 75.9147 | 14.0853 | 48.0542 | 46.9094 | 9.2166 | 66.9425 | 0.2 | 0 | 4.627 | 80.7861 | 2.9 | 5.4246 | 1.0783 | 0.071432
2015-09-10 15:00 | 67.12 | 64.15 | 2.97 | 15.1758 | 5.1989 | 61.4239 | 78.714 | 11.286 | 63.1023 | 61.1795 | 7.3157 | 48.1125 | 0.2 | 0 | 3.356 | 58.7842 | 3.1 | 4.937 | 1.0803 | 0.052071
2015-09-10 16:00 | 47.3733 | 45.3467 | 2.0267 | 14.4022 | 5.1832 | 76.4277 | 81.9105 | 8.0895 | 77.9127 | 75.5283 | 3.5991 | 34.01 | 0.2 | 0 | 2.3687 | 39.9778 | 3.3 | 4.5493 | 1.0818 | 0.035463
2015-09-10 17:00 | 27.6267 | 26.5433 | 1.0833 | 13.1896 | 5.1675 | 91.4316 | 85.2887 | 4.7113 | 92.5622 | 89.8577 | 0.032768 | 19.9075 | 0.2 | 0 | 1.3813 | 21.3216 | 3 | 3.6663 | 1.0853 | 0.018976
2015-09-10 18:00 | 7.88 | 7.74 | 0.14 | 0 | 5.1517 | 106.4354 | 88.6287 | 1.3713 | 107.1495 | 104.0828 | 0 | 5.805 | 0.2 | 0 | 0.394 | 6.199 | 2.9 | 3.0937 | 1.0876 | 0.0055286
2015-09-10 19:00 | 5.2533 | 5.16 | 0.093333 | 0 | 5.136 | 121.4392 | 91.7158 | -1.7158 | 121.7721 | 118.084 | 0 | 3.87 | 0.2 | 0 | 0.26267 | 4.1327 | 3.7 | 3.8291 | 1.0847 | 0.0036758
2015-09-10 20:00 | 2.6267 | 2.58 | 0.046667 | 0 | 5.1203 | 136.4431 | 94.349 | -4.349 | 136.5038 | 131.6316 | 0 | 1.935 | 0.2 | 0 | 0.13133 | 2.0663 | 3.2 | 3.2646 | 1.0869 | 0.0018417
2015-09-10 21:00 | 0 | 0 | 0 | 0 | 5.1045 | 151.4469 | 96.3512 | -6.3512 | 151.3788 | 144.1788 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0888 | 0
2015-09-10 22:00 | 0 | 0 | 0 | 0 | 5.0888 | 166.4508 | 97.5831 | -7.5831 | 166.3838 | 154.1983 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0876 | 0
2015-09-10 23:00 | 0 | 0 | 0 | 0 | 5.073 | 181.4546 | 97.9561 | -7.9561 | -178.537 | 157.9135 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.4 | 3.4 | 1.0864 | 0
2015-09-11 | 0 | 0 | 0 | 0 | 5.0573 | -163.5415 | 97.4439 | -7.4439 | -163.4641 | 152.6216 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.4 | 3.4 | 1.0864 | 0
2015-09-11 01:00 | 0.94 | 0.64333 | 0.29667 | 0 | 5.0415 | -148.5377 | 96.0851 | -6.0851 | -148.4754 | 141.9113 | 0 | 0.4825 | 0.2 | 0 | 0.047 | 0.5295 | 3.7 | 3.7165 | 1.0851 | 0.00047115
2015-09-11 02:00 | 1.88 | 1.2867 | 0.59333 | 0 | 5.0258 | -133.5339 | 93.9789 | -3.9789 | -133.6205 | 129.1023 | 0 | 0.965 | 0.2 | 0 | 0.094 | 1.059 | 4.3 | 4.3331 | 1.0827 | 0.00094017
2015-09-11 03:00 | 2.82 | 1.93 | 0.89 | 0 | 5.01 | -118.53 | 91.2732 | -1.2732 | -118.9045 | 115.4422 | 0 | 1.4475 | 0.2 | 0 | 0.141 | 1.5885 | 6 | 6.0496 | 1.0758 | 0.0014013
2015-09-11 04:00 | 8.7567 | 7.76 | 0.99667 | 0 | 4.9943 | -103.5262 | 88.1509 | 1.8491 | -104.2859 | 101.3882 | 0 | 5.82 | 0.2 | 0 | 0.43783 | 6.2578 | 5.4 | 5.5956 | 1.0776 | 0.0055297
2015-09-11 05:00 | 14.6933 | 13.59 | 1.1033 | 12.2131 | 4.9785 | -88.5223 | 84.8168 | 5.1832 | -89.686 | 87.14 | 0.60939 | 10.1925 | 0.2 | 0 | 0.73467 | 11.5366 | 6.1 | 6.4605 | 1.0742 | 0.010162
2015-09-11 06:00 | 20.63 | 19.42 | 1.21 | 8.1746 | 4.9627 | -73.5185 | 81.4878 | 8.5122 | -75.0069 | 72.8074 | 2.4163 | 14.565 | 0.2 | 0 | 1.0315 | 18.0128 | 5.6 | 6.1629 | 1.0753 | 0.015883
2015-09-11 07:00 | 28.9433 | 27.4433 | 1.5 | 7.4495 | 4.947 | -58.5146 | 78.3837 | 11.6163 | -60.1535 | 58.4762 | 3.895 | 20.5825 | 0.2 | 0 | 1.4472 | 25.9246 | 4.4 | 5.2101 | 1.0792 | 0.022941
2015-09-11 08:00 | 37.2567 | 35.4667 | 1.79 | 7.2559 | 4.9312 | -43.5108 | 75.718 | 14.282 | -45.0577 | 44.2588 | 5.1967 | 26.6 | 0.2 | 0 | 1.8628 | 33.6595 | 4.3 | 5.3519 | 1.0786 | 0.02977
2015-09-11 09:00 | 45.57 | 43.49 | 2.08 | 7.4041 | 4.9154 | -28.5069 | 73.6846 | 16.3154 | -29.7002 | 30.4101 | 6.3855 | 32.6175 | 0.2 | 0 | 2.2785 | 41.2815 | 4.6 | 5.89 | 1.0764 | 0.036438
2015-09-11 10:00 | 52.1733 | 50.2833 | 1.89 | 6.2646 | 4.8996 | -13.5031 | 72.4407 | 17.5593 | -14.1236 | 17.9062 | 5.9612 | 37.7125 | 0.2 | 0 | 2.6087 | 46.2824 | 4.3 | 5.7463 | 1.077 | 0.040874
2015-09-11 11:00 | 58.7767 | 57.0767 | 1.7 | 5.5273 | 4.8839 | 1.5008 | 72.0874 | 17.9126 | 1.5715 | 12.172 | 5.403 | 42.8075 | 0.2 | 0 | 2.9388 | 51.1494 | 4.5 | 6.0984 | 1.0756 | 0.045114
2015-09-11 12:00 | 65.38 | 63.87 | 1.51 | 5.065 | 4.8681 | 16.5047 | 72.6552 | 17.3448 | 17.2507 | 20.1954 | 4.7536 | 47.9025 | 0.2 | 0 | 3.269 | 55.9251 | 4.4 | 6.1477 | 1.0754 | 0.049317
2015-09-11 13:00 | 71.19 | 53.2267 | 17.9633 | 65.5626 | 4.8523 | 31.5085 | 74.0983 | 15.9017 | 32.7839 | 33.1527 | 54.89 | 39.92 | 0.2 | 0 | 3.5595 | 98.3695 | 4.3 | 7.374 | 1.0705 | 0.08635
2015-09-11 14:00 | 77 | 42.5833 | 34.4167 | 145.3471 | 4.8365 | 46.5124 | 76.3029 | 13.6971 | 48.082 | 47.117 | 98.9093 | 31.9375 | 0.2 | 0 | 3.85 | 134.6968 | 4.3 | 8.5093 | 1.066 | 0.11774
2015-09-11 15:00 | 82.81 | 31.94 | 50.87 | 269.0895 | 4.8207 | 61.5162 | 79.1029 | 10.8971 | 63.1162 | 61.3758 | 128.9106 | 23.955 | 0.2 | 0 | 4.1405 | 157.0061 | 5.7 | 10.6064 | 1.0576 | 0.13616
2015-09-11 16:00 | 57.8 | 23.06 | 34.74 | 259.2719 | 4.805 | 76.5201 | 82.2997 | 7.7003 | 77.9188 | 75.7225 | 63.9412 | 17.295 | 0.2 | 0 | 2.89 | 84.1262 | 5.2 | 7.8289 | 1.0687 | 0.073722
2015-09-11 17:00 | 32.79 | 14.18 | 18.61 | 246.9417 | 4.7892 | 91.524 | 85.678 | 4.322 | 92.5663 | 90.0564 | 0 | 10.635 | 0.2 | 0 | 1.6395 | 12.2745 | 3.6 | 3.9836 | 1.0841 | 0.010911
2015-09-11 18:00 | 7.78 | 5.3 | 2.48 | 0 | 4.7734 | 106.5278 | 89.018 | 0.98198 | 107.1576 | 104.2925 | 0 | 3.975 | 0.2 | 0 | 0.389 | 4.364 | 3.9 | 4.0364 | 1.0839 | 0.0038786
2015-09-11 19:00 | 5.1867 | 3.5333 | 1.6533 | 0 | 4.7576 | 121.5317 | 92.1049 | -2.1049 | 121.7896 | 118.3125 | 0 | 2.65 | 0.2 | 0 | 0.25933 | 2.9093 | 4.5 | 4.5909 | 1.0816 | 0.0025804
2015-09-11 20:00 | 2.5933 | 1.7667 | 0.82667 | 0 | 4.7418 | 136.5355 | 94.7372 | -4.7372 | 136.5359 | 131.8907 | 0 | 1.325 | 0.2 | 0 | 0.12967 | 1.4547 | 5.1 | 5.1455 | 1.0794 | 0.0012876
2015-09-11 21:00 | 0 | 0 | 0 | 0 | 4.726 | 151.5394 | 96.7375 | -6.7375 | 151.4297 | 144.4865 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.7 | 4.7 | 1.0812 | 0
2015-09-11 22:00 | 0 | 0 | 0 | 0 | 4.7102 | 166.5433 | 97.966 | -7.966 | 166.4564 | 154.5701 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.5 | 5.5 | 1.078 | 0
2015-09-11 23:00 | 0 | 0 | 0 | 0 | 4.6944 | 181.5471 | 98.3342 | -8.3342 | -178.4416 | 158.2851 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.2 | 5.2 | 1.0792 | 0
2015-09-12 | 0 | 0 | 0 | 0 | 4.6786 | -163.449 | 97.8158 | -7.8158 | -163.3466 | 152.8717 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.3 | 5.3 | 1.0788 | 0
2015-09-12 01:00 | 0.89667 | 0.58 | 0.31667 | 0 | 4.6628 | -148.4451 | 96.4502 | -6.4502 | -148.3381 | 142.0577 | 0 | 0.435 | 0.2 | 0 | 0.044833 | 0.47983 | 5.5 | 5.515 | 1.0779 | 0.00042413
2015-09-12 02:00 | 1.7933 | 1.16 | 0.63333 | 0 | 4.6469 | -133.4413 | 94.3374 | -4.3374 | -133.4669 | 129.1889 | 0 | 0.87 | 0.2 | 0 | 0.089667 | 0.95967 | 5.1 | 5.13 | 1.0795 | 0.00084947
2015-09-12 03:00 | 2.69 | 1.74 | 0.95 | 0 | 4.6311 | -118.4374 | 91.6263 | -1.6263 | -118.7389 | 115.4944 | 0 | 1.305 | 0.2 | 0 | 0.1345 | 1.4395 | 5 | 5.045 | 1.0798 | 0.0012746
2015-09-12 04:00 | 22.9933 | 10.4933 | 12.5 | 0 | 4.6153 | -103.4335 | 88.5004 | 1.4996 | -104.1126 | 101.4202 | 0 | 7.87 | 0.2 | 0 | 1.1497 | 9.0197 | 2.9 | 3.1819 | 1.0873 | 0.0080416
2015-09-12 05:00 | 43.2967 | 19.2467 | 24.05 | 285.3429 | 4.5995 | -88.4296 | 85.1651 | 4.8349 | -89.5096 | 87.1611 | 14.1324 | 14.435 | 0.2 | 0 | 2.1648 | 30.7323 | 2.7 | 3.6604 | 1.0854 | 0.027352
2015-09-12 06:00 | 63.6 | 28 | 35.6 | 250.7378 | 4.5837 | -73.4258 | 81.8375 | 8.1625 | -74.8321 | 72.8251 | 74.0401 | 21 | 0.2 | 0 | 3.18 | 98.2201 | 2.7 | 5.7694 | 1.0769 | 0.086736
2015-09-12 07:00 | 70.43 | 28.7033 | 41.7267 | 213.6459 | 4.5678 | -58.4219 | 78.7373 | 11.2627 | -59.9852 | 58.4988 | 111.6336 | 21.5275 | 0.2 | 0 | 3.5215 | 136.6826 | 3.2 | 7.4713 | 1.0701 | 0.11994
2015-09-12 08:00 | 77.26 | 29.4067 | 47.8533 | 198.8835 | 4.552 | -43.418 | 76.0775 | 13.9225 | -44.9011 | 44.2984 | 142.3433 | 22.055 | 0.2 | 0 | 3.863 | 168.2613 | 3.5 | 8.7582 | 1.065 | 0.14694
2015-09-12 09:00 | 84.09 | 30.11 | 53.98 | 196.448 | 4.5362 | -28.4142 | 74.0511 | 15.9489 | -29.5604 | 30.4927 | 169.278 | 22.5825 | 0.2 | 0 | 4.2045 | 196.065 | 4.3 | 10.427 | 1.0583 | 0.17015
2015-09-12 10:00 | 88.18 | 35.54 | 52.64 | 178.157 | 4.5204 | -13.4103 | 72.8143 | 17.1857 | -14.005 | 18.1028 | 169.3384 | 26.655 | 0.2 | 0 | 4.409 | 200.4024 | 4.4 | 10.6626 | 1.0573 | 0.17375
2015-09-12 11:00 | 92.27 | 40.97 | 51.3 | 170.291 | 4.5045 | 1.5936 | 72.4674 | 17.5326 | 1.6661 | 12.5597 | 166.2159 | 30.7275 | 0.2 | 0 | 4.6135 | 201.5569 | 4.4 | 10.6987 | 1.0572 | 0.17473
2015-09-12 12:00 | 96.36 | 46.4 | 49.96 | 171.2689 | 4.4887 | 16.5975 | 73.0399 | 16.9601 | 17.3206 | 20.5036 | 160.419 | 34.8 | 0.2 | 0 | 4.818 | 200.037 | 4.7 | 10.9512 | 1.0562 | 0.17325
2015-09-12 13:00 | 93.48 | 43.6467 | 49.8333 | 186.314 | 4.4729 | 31.6014 | 74.4862 | 15.5138 | 32.831 | 33.3925 | 155.5573 | 32.735 | 0.2 | 0 | 4.674 | 192.9663 | 4.1 | 10.1302 | 1.0595 | 0.16764
2015-09-12 14:00 | 90.6 | 40.8933 | 49.7067 | 215.9504 | 4.457 | 46.6052 | 76.6925 | 13.3075 | 48.1101 | 47.3274 | 146.373 | 30.67 | 0.2 | 0 | 4.53 | 181.573 | 4.2 | 9.8742 | 1.0605 | 0.1579
2015-09-12 15:00 | 87.72 | 38.14 | 49.58 | 271.8963 | 4.4412 | 61.6091 | 79.4934 | 10.5066 | 63.1306 | 61.5742 | 129.428 | 28.605 | 0.2 | 0 | 4.386 | 162.419 | 4.9 | 9.9756 | 1.0601 | 0.14119
2015-09-12 16:00 | 61.1 | 27.1 | 34 | 267.2326 | 4.4253 | 76.613 | 82.6904 | 7.3096 | 77.9251 | 75.9182 | 65.0193 | 20.325 | 0.2 | 0 | 3.055 | 88.3993 | 5.1 | 7.8625 | 1.0686 | 0.077456
2015-09-12 17:00 | 34.48 | 16.06 | 18.42 | 268.6734 | 4.4095 | 91.6169 | 86.0688 | 3.9312 | 92.5707 | 90.2562 | 0 | 12.045 | 0.2 | 0 | 1.724 | 13.769 | 4.9 | 5.3303 | 1.0787 | 0.012179
2015-09-12 18:00 | 7.86 | 5.02 | 2.84 | 0 | 4.3936 | 106.6208 | 89.4088 | 0.5912 | 107.166 | 104.5027 | 0 | 3.765 | 0.2 | 0 | 0.393 | 4.158 | 4.6 | 4.7299 | 1.0811 | 0.003686
2015-09-12 19:00 | 5.24 | 3.3467 | 1.8933 | 0 | 4.3778 | 121.6246 | 92.4954 | -2.4954 | 121.8076 | 118.5413 | 0 | 2.51 | 0.2 | 0 | 0.262 | 2.772 | 5 | 5.0866 | 1.0797 | 0.0024541
2015-09-12 20:00 | 2.62 | 1.6733 | 0.94667 | 0 | 4.3619 | 136.6285 | 95.1268 | -5.1268 | 136.5685 | 132.1496 | 0 | 1.255 | 0.2 | 0 | 0.131 | 1.386 | 4.8 | 4.8433 | 1.0806 | 0.0012282
2015-09-12 21:00 | 0 | 0 | 0 | 0 | 4.3461 | 151.6324 | 97.1252 | -7.1252 | 151.4812 | 144.794 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.3 | 4.3 | 1.0828 | 0
2015-09-12 22:00 | 0 | 0 | 0 | 0 | 4.3302 | 166.6363 | 98.3503 | -8.3503 | 166.5297 | 154.9429 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.2 | 5.2 | 1.0792 | 0
2015-09-12 23:00 | 0 | 0 | 0 | 0 | 4.3144 | 181.6402 | 98.7136 | -8.7136 | -178.3454 | 158.6574 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.4 | 5.4 | 1.0784 | 0
2015-09-13 | 0 | 0 | 0 | 0 | 4.2985 | -163.3559 | 98.189 | -8.189 | -163.2281 | 153.1194 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.6 | 3.6 | 1.0856 | 0
2015-09-13 01:00 | 0.56333 | 0.38333 | 0.18 | 0 | 4.2826 | -148.352 | 96.8166 | -6.8166 | -148.1998 | 142.2014 | 0 | 0.2875 | 0.2 | 0 | 0.028167 | 0.31567 | 4.1 | 4.1099 | 1.0836 | 0.00028048
2015-09-13 02:00 | 1.1267 | 0.76667 | 0.36 | 0 | 4.2668 | -133.3482 | 94.6972 | -4.6972 | -133.3124 | 129.2734 | 0 | 0.575 | 0.2 | 0 | 0.056333 | 0.63133 | 5.6 | 5.6197 | 1.0775 | 0.00055783
2015-09-13 03:00 | 1.69 | 1.15 | 0.54 | 0 | 4.2509 | -118.3443 | 91.9805 | -1.9805 | -118.5723 | 115.5453 | 0 | 0.8625 | 0.2 | 0 | 0.0845 | 0.947 | 3.4 | 3.4296 | 1.0863 | 0.00084354
2015-09-13 04:00 | 18.5967 | 9.1867 | 9.41 | 0 | 4.235 | -103.3404 | 88.851 | 1.149 | -103.9385 | 101.4516 | 0 | 6.89 | 0.2 | 0 | 0.92983 | 7.8198 | 3.6 | 3.8444 | 1.0846 | 0.0069549
2015-09-13 05:00 | 35.5033 | 17.2233 | 18.28 | 233.7435 | 4.2192 | -88.3365 | 85.5146 | 4.4854 | -89.3325 | 87.1822 | 11.4909 | 12.9175 | 0.2 | 0 | 1.7752 | 26.1836 | 3.6 | 4.4182 | 1.0823 | 0.023238
2015-09-13 06:00 | 52.41 | 25.26 | 27.15 | 199.7568 | 4.2033 | -73.3326 | 82.1885 | 7.8115 | -74.6567 | 72.8435 | 58.9248 | 18.945 | 0.2 | 0 | 2.6205 | 80.4903 | 4.4 | 6.9153 | 1.0723 | 0.070777
2015-09-13 07:00 | 71.8367 | 28.7333 | 43.1033 | 227.784 | 4.1874 | -58.3287 | 79.0922 | 10.9078 | -59.8165 | 58.5227 | 118.9397 | 21.55 | 0.2 | 0 | 3.5918 | 144.0815 | 4.9 | 9.4025 | 1.0624 | 0.12552
2015-09-13 08:00 | 91.2633 | 32.2067 | 59.0567 | 251.8485 | 4.1715 | -43.3248 | 76.4383 | 13.5617 | -44.7442 | 44.3407 | 180.1211 | 24.155 | 0.2 | 0 | 4.5632 | 208.8392 | 3.8 | 10.3262 | 1.0587 | 0.1813
2015-09-13 09:00 | 110.69 | 35.68 | 75.01 | 279.261 | 4.1556 | -28.3209 | 74.4189 | 15.5811 | -29.4204 | 30.5798 | 240.4219 | 26.76 | 0.2 | 0 | 5.5345 | 272.7164 | 3.3 | 11.8224 | 1.0527 | 0.23541
2015-09-13 10:00 | 113.0867 | 38.7767 | 74.31 | 256.9402 | 4.1398 | -13.317 | 73.1893 | 16.8107 | -13.8862 | 18.3059 | 243.9373 | 29.0825 | 0.2 | 0 | 5.6543 | 278.6741 | 3.9 | 12.6086 | 1.0496 | 0.23984
2015-09-13 11:00 | 115.4833 | 41.8733 | 73.61 | 249.6125 | 4.1239 | 1.6869 | 72.8486 | 17.1514 | 1.7608 | 12.9489 | 243.2649 | 31.405 | 0.2 | 0 | 5.7742 | 280.444 | 4.3 | 13.0639 | 1.0477 | 0.24094
2015-09-13 12:00 | 117.88 | 44.97 | 72.91 | 255.5979 | 4.108 | 16.6908 | 73.426 | 16.574 | 17.3907 | 20.8157 | 238.9146 | 33.7275 | 0.2 | 0 | 5.894 | 278.5361 | 4 | 12.7043 | 1.0492 | 0.23963
2015-09-13 13:00 | 98.8767 | 41.0033 | 57.8733 | 221.8078 | 4.0921 | 31.6947 | 74.8755 | 15.1245 | 32.8783 | 33.6358 | 184.6717 | 30.7525 | 0.2 | 0 | 4.9438 | 220.368 | 4.5 | 11.3865 | 1.0545 | 0.19054
2015-09-13 14:00 | 79.8733 | 37.0367 | 42.8367 | 191.6378 | 4.0762 | 46.6986 | 77.0836 | 12.9164 | 48.1384 | 47.5405 | 129.3688 | 27.7775 | 0.2 | 0 | 3.9937 | 161.1399 | 4.1 | 9.1356 | 1.0635 | 0.14052
2015-09-13 15:00 | 60.87 | 33.07 | 27.8 | 158.2953 | 4.0603 | 61.7025 | 79.8852 | 10.1148 | 63.1451 | 61.7746 | 74.8645 | 24.8025 | 0.2 | 0 | 3.0435 | 102.7105 | 4.2 | 7.4097 | 1.0704 | 0.090149
2015-09-13 16:00 | 41.6333 | 22.9167 | 18.7167 | 155.4027 | 4.0444 | 76.7064 | 83.0825 | 6.9175 | 77.9318 | 76.1154 | 37.2916 | 17.1875 | 0.2 | 0 | 2.0817 | 56.5608 | 3.9 | 5.6675 | 1.0773 | 0.049966
2015-09-13 17:00 | 22.3967 | 12.7633 | 9.6333 | 156.0577 | 4.0285 | 91.7103 | 86.4609 | 3.5391 | 92.5754 | 90.4569 | 0 | 9.5725 | 0.2 | 0 | 1.1198 | 10.6923 | 5 | 5.3341 | 1.0787 | 0.0094574
2015-09-13 18:00 | 3.16 | 2.61 | 0.55 | 0 | 4.0126 | 106.7142 | 89.8009 | 0.19906 | 107.1746 | 104.7134 | 0 | 1.9575 | 0.2 | 0 | 0.158 | 2.1155 | 5.7 | 5.7661 | 1.0769 | 0.0018682
2015-09-13 19:00 | 2.1067 | 1.74 | 0.36667 | 0 | 3.9967 | 121.7181 | 92.8873 | -2.8873 | 121.8258 | 118.77 | 0 | 1.305 | 0.2 | 0 | 0.10533 | 1.4103 | 4.9 | 4.9441 | 1.0802 | 0.0012492
2015-09-13 20:00 | 1.0533 | 0.87 | 0.18333 | 0 | 3.9808 | 136.722 | 95.5178 | -5.5178 | 136.6014 | 132.4083 | 0 | 0.6525 | 0.2 | 0 | 0.052667 | 0.70517 | 5.7 | 5.722 | 1.0771 | 0.00062283
2015-09-13 21:00 | 0 | 0 | 0 | 0 | 3.9649 | 151.7259 | 97.5142 | -7.5142 | 151.5331 | 145.1013 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5 | 5 | 1.08 | 0
2015-09-13 22:00 | 0 | 0 | 0 | 0 | 3.949 | 166.7298 | 98.7359 | -8.7359 | 166.6036 | 155.3164 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.9 | 4.9 | 1.0804 | 0
2015-09-13 23:00 | 0 | 0 | 0 | 0 | 3.9331 | 181.7337 | 99.0943 | -9.0943 | -178.2484 | 159.0302 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5 | 5 | 1.08 | 0
2015-09-14 | 0 | 0 | 0 | 0 | 3.9172 | -163.2624 | 98.5634 | -8.5634 | -163.1088 | 153.3646 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6.2 | 6.2 | 1.0752 | 0
2015-09-14 01:00 | 0.28 | 0.28 | 0 | 0 | 3.9013 | -148.2585 | 97.1841 | -7.1841 | -148.0607 | 142.3424 | 0 | 0.21 | 0.2 | 0 | 0.014 | 0.224 | 5.5 | 5.507 | 1.078 | 0.000198
2015-09-14 02:00 | 0.56 | 0.56 | 0 | 0 | 3.8853 | -133.2546 | 95.058 | -5.058 | -133.157 | 129.356 | 0 | 0.42 | 0.2 | 0 | 0.028 | 0.448 | 6.6 | 6.614 | 1.0735 | 0.00039438
2015-09-14 03:00 | 0.84 | 0.84 | 0 | 0 | 3.8694 | -118.2507 | 92.3358 | -2.3358 | -118.4049 | 115.5948 | 0 | 0.63 | 0.2 | 0 | 0.042 | 0.672 | 6.8 | 6.821 | 1.0727 | 0.00059111
2015-09-14 04:00 | 10.2133 | 9.9967 | 0.21667 | 0 | 3.8535 | -103.2468 | 89.2027 | 0.79728 | -103.7637 | 101.4823 | 0 | 7.4975 | 0.2 | 0 | 0.51067 | 8.0082 | 5.6 | 5.8503 | 1.0766 | 0.0070697
2015-09-14 05:00 | 19.5867 | 19.1533 | 0.43333 | 6.0099 | 3.8376 | -88.2429 | 85.8652 | 4.1348 | -89.1549 | 87.2033 | 0.29324 | 14.365 | 0.2 | 0 | 0.97933 | 15.6376 | 5.3 | 5.7887 | 1.0768 | 0.013808
2015-09-14 06:00 | 28.96 | 28.31 | 0.65 | 5.0068 | 3.8217 | -73.239 | 82.5406 | 7.4594 | -74.4809 | 72.8626 | 1.4753 | 21.2325 | 0.2 | 0 | 1.448 | 24.1558 | 5.4 | 6.1549 | 1.0754 | 0.021301
2015-09-14 07:00 | 44.5333 | 42.2567 | 2.2767 | 12.4325 | 3.8057 | -58.2351 | 79.4483 | 10.5517 | -59.6475 | 58.5483 | 6.487 | 31.6925 | 0.2 | 0 | 2.2267 | 40.4062 | 6 | 7.2627 | 1.0709 | 0.035484
2015-09-14 08:00 | 60.1067 | 56.2033 | 3.9033 | 17.094 | 3.7898 | -43.2312 | 76.8003 | 13.1997 | -44.5871 | 44.3857 | 12.2162 | 42.1525 | 0.2 | 0 | 3.0053 | 57.374 | 5.8 | 7.5929 | 1.0696 | 0.050322
2015-09-14 09:00 | 75.68 | 70.15 | 5.53 | 21.0754 | 3.7739 | -28.2273 | 74.788 | 15.212 | -29.2802 | 30.6712 | 18.1271 | 52.6125 | 0.2 | 0 | 3.784 | 74.5236 | 5.5 | 7.8289 | 1.0687 | 0.065307
2015-09-14 10:00 | 76.21 | 70.3333 | 5.8767 | 20.7715 | 3.7579 | -13.2234 | 73.5655 | 16.4345 | -13.7673 | 18.5154 | 19.6963 | 52.75 | 0.2 | 0 | 3.8105 | 76.2568 | 6.7 | 9.083 | 1.0637 | 0.066512
2015-09-14 11:00 | 76.74 | 70.5167 | 6.2233 | 21.5705 | 3.742 | 1.7805 | 73.2312 | 16.7688 | 1.8557 | 13.3396 | 20.9885 | 52.8875 | 0.2 | 0 | 3.837 | 77.713 | 5.9 | 8.3285 | 1.0667 | 0.067974
2015-09-14 12:00 | 77.27 | 70.7 | 6.57 | 23.5681 | 3.7261 | 16.7844 | 73.8134 | 16.1866 | 17.4609 | 21.1315 | 21.9833 | 53.025 | 0.2 | 0 | 3.8635 | 78.8718 | 6 | 8.4647 | 1.0661 | 0.068953
2015-09-14 13:00 | 67.0267 | 62.6467 | 4.38 | 17.2217 | 3.7101 | 31.7883 | 75.2661 | 14.7339 | 32.9258 | 33.8825 | 14.2972 | 46.985 | 0.2 | 0 | 3.3513 | 64.6335 | 6 | 8.0198 | 1.0679 | 0.056599
2015-09-14 14:00 | 56.7833 | 54.5933 | 2.19 | 10.0991 | 3.6942 | 46.7922 | 77.4759 | 12.5241 | 48.1669 | 47.7561 | 6.7895 | 40.945 | 0.2 | 0 | 2.8392 | 50.5737 | 6.1 | 7.6804 | 1.0693 | 0.044343
2015-09-14 15:00 | 46.54 | 46.54 | 0 | 0 | 3.6783 | 61.7962 | 80.2783 | 9.7217 | 63.1599 | 61.9768 | 0 | 34.905 | 0.2 | 0 | 2.327 | 37.232 | 6.1 | 7.2635 | 1.0709 | 0.032696
2015-09-14 16:00 | 32.2633 | 32.24 | 0.023333 | 0.20536 | 3.6623 | 76.8001 | 83.4758 | 6.5242 | 77.9385 | 76.3138 | 0.048589 | 24.18 | 0.2 | 0 | 1.6132 | 25.8418 | 6 | 6.8076 | 1.0728 | 0.022732
2015-09-14 17:00 | 17.9867 | 17.94 | 0.046667 | 0.85042 | 3.6464 | 91.804 | 86.8543 | 3.1457 | 92.5802 | 90.6583 | 0 | 13.455 | 0.2 | 0 | 0.89933 | 14.3543 | 6 | 6.4486 | 1.0742 | 0.012644
2015-09-14 18:00 | 3.71 | 3.64 | 0.07 | 0 | 3.6304 | 106.8079 | 90.1943 | -0.19432 | 107.1834 | 104.9244 | 0 | 2.73 | 0.2 | 0 | 0.1855 | 2.9155 | 5.9 | 5.9911 | 1.076 | 0.0025725
2015-09-14 19:00 | 2.4733 | 2.4267 | 0.046667 | 0 | 3.6145 | 121.8118 | 93.2804 | -3.2804 | 121.8442 | 118.9986 | 0 | 1.82 | 0.2 | 0 | 0.12367 | 1.9437 | 6 | 6.0607 | 1.0758 | 0.0017145
2015-09-14 20:00 | 1.2367 | 1.2133 | 0.023333 | 0 | 3.5985 | 136.8157 | 95.91 | -5.91 | 136.6347 | 132.6664 | 0 | 0.91 | 0.2 | 0 | 0.061833 | 0.97183 | 5.9 | 5.9304 | 1.0763 | 0.00085769
2015-09-14 21:00 | 0 | 0 | 0 | 0 | 3.5826 | 151.8196 | 97.9044 | -7.9044 | 151.5855 | 145.4081 | 0 | 0 | 0.2 | 0 | 0 | 0 | 6 | 6 | 1.076 | 0
2015-09-14 22:00 | 0 | 0 | 0 | 0 | 3.5666 | 166.8235 | 99.1227 | -9.1227 | 166.678 | 155.6906 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.9 | 5.9 | 1.0764 | 0
2015-09-14 23:00 | 0 | 0 | 0 | 0 | 3.5506 | 181.8274 | 99.476 | -9.476 | -178.1508 | 159.4035 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5.9 | 5.9 | 1.0764 | 0
2015-09-15 | 0 | 0 | 0 | 0 | 3.5347 | -163.1686 | 98.9389 | -8.9389 | -162.9888 | 153.6072 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.8 | 4.8 | 1.0808 | 0
2015-09-15 01:00 | 0.46 | 0.32333 | 0.13667 | 0 | 3.5187 | -148.1647 | 97.5527 | -7.5527 | -147.9207 | 142.4807 | 0 | 0.2425 | 0.2 | 0 | 0.023 | 0.2655 | 3.3 | 3.3083 | 1.0868 | 0.0002366
2015-09-15 02:00 | 0.92 | 0.64667 | 0.27333 | 0 | 3.5028 | -133.1608 | 95.4199 | -5.4199 | -133.0008 | 129.4366 | 0 | 0.485 | 0.2 | 0 | 0.046 | 0.531 | 2.8 | 2.8166 | 1.0887 | 0.00047406
2015-09-15 03:00 | 1.38 | 0.97 | 0.41 | 0 | 3.4868 | -118.1569 | 92.6922 | -2.6922 | -118.2369 | 115.6432 | 0 | 0.7275 | 0.2 | 0 | 0.069 | 0.7965 | 2.4 | 2.4249 | 1.0903 | 0.00071211
2015-09-15 04:00 | 23.7667 | 13.7133 | 10.0533 | 0 | 3.4708 | -103.153 | 89.5555 | 0.4445 | -103.5883 | 101.5125 | 0 | 10.285 | 0.2 | 0 | 1.1883 | 11.4733 | 3.1 | 3.4585 | 1.0862 | 0.010219
2015-09-15 05:00 | 46.1533 | 26.4567 | 19.6967 | 298.5219 | 3.4549 | -88.1491 | 86.2168 | 3.7832 | -88.9767 | 87.2245 | 14.4553 | 19.8425 | 0.2 | 0 | 2.3077 | 36.6054 | 3.6 | 4.7439 | 1.081 | 0.032449
2015-09-15 06:00 | 68.54 | 39.2 | 29.34 | 237.1685 | 3.4389 | -73.1451 | 82.8938 | 7.1062 | -74.3047 | 72.8825 | 69.8065 | 29.4 | 0.2 | 0 | 3.427 | 102.6335 | 3.1 | 6.3073 | 1.0748 | 0.090452
2015-09-15 07:00 | 80.0133 | 59.0267 | 20.9867 | 118.5756 | 3.4229 | -58.1412 | 79.8055 | 10.1945 | -59.4782 | 58.5754 | 61.8224 | 44.27 | 0.2 | 0 | 4.0007 | 110.0931 | 3.8 | 7.2404 | 1.071 | 0.096689
2015-09-15 08:00 | 91.4867 | 78.8533 | 12.6333 | 56.8634 | 3.4069 | -43.1373 | 77.1635 | 12.8365 | -44.4299 | 44.4334 | 40.6041 | 59.14 | 0.2 | 0 | 4.5743 | 104.3184 | 3.3 | 6.56 | 1.0738 | 0.091851
2015-09-15 09:00 | 102.96 | 98.68 | 4.28 | 16.7089 | 3.391 | -28.1334 | 75.1582 | 14.8418 | -29.1401 | 30.7672 | 14.3572 | 74.01 | 0.2 | 0 | 5.148 | 93.5152 | 3.5 | 6.4223 | 1.0743 | 0.082381
2015-09-15 10:00 | 96.6667 | 93.0267 | 3.64 | 13.16 | 3.375 | -13.1295 | 73.9429 | 16.0571 | -13.6485 | 18.7312 | 12.463 | 69.77 | 0.2 | 0 | 4.8333 | 87.0663 | 3.3 | 6.0208 | 1.0759 | 0.076814
2015-09-15 11:00 | 90.3733 | 87.3733 | 3 | 10.6348 | 3.359 | 1.8744 | 73.6148 | 16.3852 | 1.9505 | 13.7315 | 10.3308 | 65.53 | 0.2 | 0 | 4.5187 | 80.3795 | 3 | 5.5119 | 1.078 | 0.071049
2015-09-15 12:00 | 84.08 | 81.72 | 2.36 | 8.6686 | 3.343 | 16.8784 | 74.2019 | 15.7981 | 17.5312 | 21.4507 | 8.0681 | 61.29 | 0.2 | 0 | 4.204 | 73.5621 | 4.5 | 6.7988 | 1.0728 | 0.064713
2015-09-15 13:00 | 89.86 | 67.2633 | 22.5967 | 91.2213 | 3.327 | 31.8823 | 75.6578 | 14.3422 | 32.9733 | 34.1324 | 75.5078 | 50.4475 | 0.2 | 0 | 4.493 | 130.4483 | 3.9 | 7.9765 | 1.0681 | 0.11425
2015-09-15 14:00 | 95.64 | 52.8067 | 42.8333 | 203.8306 | 3.3111 | 46.8862 | 77.8693 | 12.1307 | 48.1955 | 47.9742 | 136.4576 | 39.605 | 0.2 | 0 | 4.782 | 180.8446 | 4.3 | 9.9514 | 1.0602 | 0.15722
2015-09-15 15:00 | 101.42 | 38.35 | 63.07 | 389.134 | 3.2951 | 61.8901 | 80.6725 | 9.3275 | 63.1747 | 62.1807 | 181.6029 | 28.7625 | 0.2 | 0 | 5.071 | 215.4364 | 3.1 | 9.8324 | 1.0607 | 0.18738
2015-09-15 16:00 | 69.6033 | 26.85 | 42.7533 | 400.39 | 3.2791 | 76.894 | 83.8703 | 6.1297 | 77.9454 | 76.5133 | 93.379 | 20.1375 | 0.2 | 0 | 3.4802 | 116.9966 | 3 | 6.6561 | 1.0734 | 0.10298
2015-09-15 17:00 | 37.7867 | 15.35 | 22.4367 | 0 | 3.2631 | 91.8979 | 87.2489 | 2.7511 | 92.5851 | 90.8604 | 0 | 11.5125 | 0.2 | 0 | 1.8893 | 13.4018 | 1.9 | 2.3188 | 1.0907 | 0.011987
2015-09-15 18:00 | 5.97 | 3.85 | 2.12 | 0 | 3.2471 | 106.9019 | 90.5888 | -0.58885 | 107.1922 | 105.1356 | 0 | 2.8875 | 0.2 | 0 | 0.2985 | 3.186 | 1.5 | 1.5996 | 1.0936 | 0.0028571
2015-09-15 19:00 | 3.98 | 2.5667 | 1.4133 | 0 | 3.2311 | 121.9058 | 93.6746 | -3.6746 | 121.8628 | 119.2268 | 0 | 1.925 | 0.2 | 0 | 0.199 | 2.124 | 1.5 | 1.5664 | 1.0937 | 0.0019049
2015-09-15 20:00 | 1.99 | 1.2833 | 0.70667 | 0 | 3.2151 | 136.9097 | 96.3033 | -6.3033 | 136.6681 | 132.9239 | 0 | 0.9625 | 0.2 | 0 | 0.0995 | 1.062 | 0.6 | 0.63319 | 1.0975 | 0.00095572
2015-09-15 21:00 | 0 | 0 | 0 | 0 | 3.1991 | 151.9136 | 98.2957 | -8.2957 | 151.6381 | 145.7143 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-09-15 22:00 | 0 | 0 | 0 | 0 | 3.1831 | 166.9175 | 99.5105 | -9.5105 | 166.7528 | 156.0653 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-09-15 23:00 | 0 | 0 | 0 | 0 | 3.1671 | 181.9215 | 99.8589 | -9.8589 | -178.0527 | 159.777 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-09-16 | 0 | 0 | 0 | 0 | 3.1511 | -163.0746 | 99.3154 | -9.3154 | -162.8682 | 153.847 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-09-16 01:00 | 0.33667 | 0.23333 | 0.10333 | 0 | 3.1351 | -148.0707 | 97.9222 | -7.9222 | -147.7801 | 142.6162 | 0 | 0.175 | 0.2 | 0 | 0.016833 | 0.19183 | -0.3 | -0.29401 | 1.1012 | 0.00017322
2015-09-16 02:00 | 0.67333 | 0.46667 | 0.20667 | 0 | 3.1191 | -133.0668 | 95.7827 | -5.7827 | -132.844 | 129.5152 | 0 | 0.35 | 0.2 | 0 | 0.033667 | 0.38367 | -0.4 | -0.38801 | 1.1016 | 0.00034656
2015-09-16 03:00 | 1.01 | 0.7 | 0.31 | 0 | 3.1031 | -118.0629 | 93.0495 | -3.0495 | -118.0683 | 115.6903 | 0 | 0.525 | 0.2 | 0 | 0.0505 | 0.5755 | -0.6 | -0.58202 | 1.1023 | 0.0005202
2015-09-16 04:00 | 27.19 | 12.6 | 14.59 | 0 | 3.0871 | -103.0589 | 89.9092 | 0.090753 | -103.4124 | 101.5422 | 0 | 9.45 | 0.2 | 0 | 1.3595 | 10.8095 | -0.9 | -0.5622 | 1.1022 | 0.0097701
2015-09-16 05:00 | 53.37 | 24.5 | 28.87 | 482.472 | 3.0711 | -88.055 | 86.5695 | 3.4305 | -88.7982 | 87.2459 | 23.1828 | 18.375 | 0.2 | 0 | 2.6685 | 44.2263 | -0.6 | 0.78207 | 1.0969 | 0.039779
2015-09-16 06:00 | 79.55 | 36.4 | 43.15 | 367.0092 | 3.0551 | -73.0511 | 83.248 | 6.752 | -74.1284 | 72.9032 | 107.8958 | 27.3 | 0.2 | 0 | 3.9775 | 139.1733 | 0.6 | 4.9492 | 1.0802 | 0.12328
2015-09-16 07:00 | 126.6767 | 39.5967 | 87.08 | 509.7414 | 3.039 | -58.0472 | 80.1638 | 9.8362 | -59.3089 | 58.6043 | 265.5475 | 29.6975 | 0.2 | 0 | 6.3338 | 301.5789 | 1.3 | 10.7243 | 1.0571 | 0.26142
2015-09-16 08:00 | 173.8033 | 42.7933 | 131.01 | 606.6213 | 3.023 | -43.0432 | 77.5278 | 12.4722 | -44.2727 | 44.484 | 432.7913 | 32.095 | 0.2 | 0 | 8.6902 | 473.5765 | 1.5 | 16.2993 | 1.0348 | 0.40185
2015-09-16 09:00 | 220.93 | 45.99 | 174.94 | 700.0945 | 3.007 | -28.0393 | 75.5296 | 14.4704 | -29 | 30.8677 | 600.9292 | 34.4925 | 0.2 | 0 | 11.0465 | 646.4682 | 1.1 | 21.3021 | 1.0148 | 0.53794
2015-09-16 10:00 | 222.1433 | 51.4833 | 170.66 | 631.508 | 2.991 | -13.0354 | 74.3213 | 15.6787 | -13.5298 | 18.9532 | 597.2705 | 38.6125 | 0.2 | 0 | 11.1072 | 646.9901 | 1.2 | 21.4184 | 1.0143 | 0.53813
2015-09-16 11:00 | 223.3567 | 56.9767 | 166.38 | 603.6051 | 2.975 | 1.9685 | 73.9996 | 16.0004 | 2.0451 | 14.1247 | 585.3563 | 42.7325 | 0.2 | 0 | 11.1678 | 639.2567 | 1.6 | 21.5768 | 1.0137 | 0.53137
2015-09-16 12:00 | 224.57 | 62.47 | 162.1 | 610.0897 | 2.959 | 16.9724 | 74.5915 | 15.4085 | 17.6013 | 21.7732 | 566.5657 | 46.8525 | 0.2 | 0 | 11.2285 | 624.6467 | 1.9 | 21.4202 | 1.0143 | 0.51954
2015-09-16 13:00 | 173.7233 | 62.7067 | 111.0167 | 460.5248 | 2.9429 | 31.9764 | 76.0506 | 13.9494 | 33.0207 | 34.3854 | 380.0516 | 47.03 | 0.2 | 0 | 8.6862 | 435.7678 | 1.7 | 15.3177 | 1.0387 | 0.37117
2015-09-16 14:00 | 122.8767 | 62.9433 | 59.9333 | 294.6499 | 2.9269 | 46.9803 | 78.2638 | 11.7362 | 48.224 | 48.1945 | 196.4148 | 47.2075 | 0.2 | 0 | 6.1438 | 249.7661 | 1.8 | 9.6052 | 1.0616 | 0.21742
2015-09-16 15:00 | 72.03 | 63.18 | 8.85 | 56.9987 | 2.9109 | 61.9842 | 81.0677 | 8.9323 | 63.1895 | 62.3862 | 26.4195 | 47.385 | 0.2 | 0 | 3.6015 | 77.406 | 2.5 | 4.9189 | 1.0803 | 0.068571
2015-09-16 16:00 | 49.56 | 43.26 | 6.3 | 63.0547 | 2.8948 | 76.9881 | 84.2658 | 5.7342 | 77.9522 | 76.7138 | 14.491 | 32.445 | 0.2 | 0 | 2.478 | 49.414 | 1.9 | 3.4442 | 1.0862 | 0.044013
2015-09-16 17:00 | 27.09 | 23.34 | 3.75 | 0 | 2.8788 | 91.9921 | 87.6445 | 2.3555 | 92.5899 | 91.0629 | 0 | 17.505 | 0.2 | 0 | 1.3545 | 18.8595 | 1.7 | 2.2894 | 1.0908 | 0.01687
2015-09-16 18:00 | 4.62 | 3.42 | 1.2 | 0 | 2.8628 | 106.996 | 90.9844 | -0.9844 | 107.2011 | 105.3467 | 0 | 2.565 | 0.2 | 0 | 0.231 | 2.796 | 1.8 | 1.8874 | 1.0925 | 0.0025047
2015-09-16 19:00 | 3.08 | 2.28 | 0.8 | 0 | 2.8467 | 121.9999 | 94.0699 | -4.0699 | 121.8813 | 119.4547 | 0 | 1.71 | 0.2 | 0 | 0.154 | 1.864 | 1 | 1.0582 | 1.0958 | 0.0016749
2015-09-16 20:00 | 1.54 | 1.14 | 0.4 | 0 | 2.8307 | 137.0038 | 96.6976 | -6.6976 | 136.7016 | 133.1806 | 0 | 0.855 | 0.2 | 0 | 0.077 | 0.932 | 1.6 | 1.6291 | 1.0935 | 0.00083568
2015-09-16 21:00 | 0 | 0 | 0 | 0 | 2.8147 | 152.0078 | 98.688 | -8.688 | 151.6909 | 146.0196 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-09-16 22:00 | 0 | 0 | 0 | 0 | 2.7986 | 167.0117 | 99.8994 | -9.8994 | 166.8279 | 156.4403 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-09-16 23:00 | 0 | 0 | 0 | 0 | 2.7826 | 182.0156 | 100.2426 | -10.2426 | -177.9542 | 160.1508 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-09-17 | 0 | 0 | 0 | 0 | 2.7665 | -162.9805 | 99.6929 | -9.6929 | -162.7471 | 154.0839 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-09-17 01:00 | 0.2 | 0.15 | 0.05 | 0 | 2.7505 | -147.9766 | 98.2927 | -8.2927 | -147.639 | 142.749 | 0 | 0.1125 | 0.2 | 0 | 0.01 | 0.1225 | 1.1 | 1.1038 | 1.0956 | 0.00011005
2015-09-17 02:00 | 0.4 | 0.3 | 0.1 | 0 | 2.7345 | -132.9726 | 96.1465 | -6.1465 | -132.6867 | 129.592 | 0 | 0.225 | 0.2 | 0 | 0.02 | 0.245 | 1.4 | 1.4077 | 1.0944 | 0.00021986
2015-09-17 03:00 | 0.6 | 0.45 | 0.15 | 0 | 2.7184 | -117.9687 | 93.4077 | -3.4077 | -117.8991 | 115.7364 | 0 | 0.3375 | 0.2 | 0 | 0.03 | 0.3675 | 0.4 | 0.41148 | 1.0984 | 0.00033099
2015-09-17 04:00 | 24.14 | 12.48 | 11.66 | 0 | 2.7024 | -102.9648 | 90.2639 | -0.26391 | -103.2361 | 101.5715 | 0 | 9.36 | 0.2 | 0 | 1.207 | 10.567 | 0.6 | 0.93022 | 1.0963 | 0.0094992
2015-09-17 05:00 | 47.68 | 24.51 | 23.17 | 431.6635 | 2.6863 | -87.9609 | 86.9231 | 3.0769 | -88.6195 | 87.2675 | 20.5786 | 18.3825 | 0.2 | 0 | 2.384 | 41.3451 | 2.4 | 3.692 | 1.0852 | 0.036793
2015-09-17 06:00 | 71.22 | 36.54 | 34.68 | 311.2737 | 2.6703 | -72.9569 | 83.6032 | 6.3968 | -73.9519 | 72.9249 | 91.3975 | 27.405 | 0.2 | 0 | 3.561 | 122.3635 | 1.9 | 5.7239 | 1.0771 | 0.10807
2015-09-17 07:00 | 112.2767 | 44.65 | 67.6267 | 410.7302 | 2.6542 | -57.953 | 80.5231 | 9.4769 | -59.1396 | 58.635 | 213.7803 | 33.4875 | 0.2 | 0 | 5.6138 | 252.8816 | 1.5 | 9.4026 | 1.0624 | 0.2203
2015-09-17 08:00 | 153.3333 | 52.76 | 100.5733 | 479.5201 | 2.6382 | -42.9491 | 77.893 | 12.107 | -44.1157 | 44.5376 | 341.7974 | 39.57 | 0.2 | 0 | 7.6667 | 389.034 | 2.2 | 14.3573 | 1.0426 | 0.33259
2015-09-17 09:00 | 194.39 | 60.87 | 133.52 | 548.1502 | 2.6221 | -27.9452 | 75.9019 | 14.0981 | -28.8602 | 30.9728 | 469.9905 | 45.6525 | 0.2 | 0 | 9.7195 | 525.3625 | 2.2 | 18.6176 | 1.0255 | 0.4418
2015-09-17 10:00 | 202.1633 | 61.0233 | 141.14 | 534.906 | 2.606 | -12.9412 | 74.7008 | 15.2992 | -13.4113 | 19.1811 | 505.2105 | 45.7675 | 0.2 | 0 | 10.1082 | 561.0862 | 2.1 | 19.6339 | 1.0215 | 0.46997
2015-09-17 11:00 | 209.9367 | 61.1767 | 148.76 | 552.6707 | 2.59 | 2.0627 | 74.3854 | 15.6146 | 2.1396 | 14.5189 | 535.0212 | 45.8825 | 0.2 | 0 | 10.4968 | 591.4005 | 3.6 | 22.0813 | 1.0117 | 0.49061
2015-09-17 12:00 | 217.71 | 61.33 | 156.38 | 603.5021 | 2.5739 | 17.0666 | 74.9821 | 15.0179 | 17.6713 | 22.0986 | 559.1676 | 45.9975 | 0.2 | 0 | 10.8855 | 616.0506 | 3.9 | 23.1516 | 1.0074 | 0.5089
2015-09-17 13:00 | 178.1967 | 57.8133 | 120.3833 | 513.6008 | 2.5579 | 32.0705 | 76.4443 | 13.5557 | 33.068 | 34.6412 | 422.5535 | 43.36 | 0.2 | 0 | 8.9098 | 474.8234 | 4.1 | 18.9382 | 1.0242 | 0.3988
2015-09-17 14:00 | 138.6833 | 54.2967 | 84.3867 | 429.1366 | 2.5418 | 47.0745 | 78.6593 | 11.3407 | 48.2525 | 48.4169 | 284.8202 | 40.7225 | 0.2 | 0 | 6.9342 | 332.4768 | 4.1 | 14.4899 | 1.042 | 0.28409
2015-09-17 15:00 | 99.17 | 50.78 | 48.39 | 326.0081 | 2.5257 | 62.0784 | 81.4639 | 8.5361 | 63.2041 | 62.5931 | 150.0637 | 38.085 | 0.2 | 0 | 4.9585 | 193.1072 | 3 | 9.0346 | 1.0639 | 0.16846
2015-09-17 16:00 | 67.4867 | 34.76 | 32.7267 | 351.8003 | 2.5097 | 77.0823 | 84.6623 | 5.3377 | 77.9589 | 76.9151 | 79.6455 | 26.07 | 0.2 | 0 | 3.3743 | 109.0898 | 1.9 | 5.3091 | 1.0788 | 0.096499
2015-09-17 17:00 | 35.8033 | 18.74 | 17.0633 | 0 | 2.4936 | 92.0862 | 88.041 | 1.959 | 92.5947 | 91.2658 | 0 | 14.055 | 0.2 | 0 | 1.7902 | 15.8452 | 1.2 | 1.6952 | 1.0932 | 0.014204
2015-09-17 18:00 | 4.12 | 2.72 | 1.4 | 0 | 2.4775 | 107.0901 | 91.3809 | -1.3809 | 107.2099 | 105.5576 | 0 | 2.04 | 0.2 | 0 | 0.206 | 2.246 | 1.8 | 1.8702 | 1.0925 | 0.0020121
2015-09-17 19:00 | 2.7467 | 1.8133 | 0.93333 | 0 | 2.4615 | 122.0941 | 94.4661 | -4.4661 | 121.8998 | 119.6819 | 0 | 1.36 | 0.2 | 0 | 0.13733 | 1.4973 | 1.1 | 1.1468 | 1.0954 | 0.001345
2015-09-17 20:00 | 1.3733 | 0.90667 | 0.46667 | 0 | 2.4454 | 137.098 | 97.0929 | -7.0929 | 136.7352 | 133.4362 | 0 | 0.68 | 0.2 | 0 | 0.068667 | 0.74867 | 0.4 | 0.4234 | 1.0983 | 0.00067426
2015-09-17 21:00 | 0 | 0 | 0 | 0 | 2.4293 | 152.1019 | 99.0812 | -9.0812 | 151.7439 | 146.3239 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-09-17 22:00 | 0 | 0 | 0 | 0 | 2.4132 | 167.1058 | 100.2891 | -10.2891 | 166.9032 | 156.8155 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-09-17 23:00 | 0 | 0 | 0 | 0 | 2.3972 | 182.1098 | 100.6273 | -10.6273 | -177.8553 | 160.5246 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-09-18 | 0 | 0 | 0 | 0 | 2.3811 | -162.8863 | 100.0712 | -10.0712 | -162.6255 | 154.3178 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-09-18 01:00 | 0.093333 | 0.07 | 0.023333 | 0 | 2.365 | -147.8824 | 98.664 | -8.664 | -147.4974 | 142.879 | 0 | 0.0525 | 0.2 | 0 | 0.0046667 | 0.057167 | -0.3 | -0.29821 | 1.1012 | 5.162e-05
2015-09-18 02:00 | 0.18667 | 0.14 | 0.046667 | 0 | 2.3489 | -132.8785 | 96.511 | -6.511 | -132.5289 | 129.6668 | 0 | 0.105 | 0.2 | 0 | 0.0093333 | 0.11433 | -0.2 | -0.19643 | 1.1008 | 0.0001032
2015-09-18 03:00 | 0.28 | 0.21 | 0.07 | 0 | 2.3328 | -117.8746 | 93.7668 | -3.7668 | -117.7297 | 115.7814 | 0 | 0.1575 | 0.2 | 0 | 0.014 | 0.1715 | -0.6 | -0.59464 | 1.1024 | 0.00015503
2015-09-18 04:00 | 19.76 | 10.75 | 9.01 | 0 | 2.3167 | -102.8706 | 90.6194 | -0.61942 | -103.0596 | 101.6004 | 0 | 8.0625 | 0.2 | 0 | 0.988 | 9.0505 | -0.7 | -0.41717 | 1.1017 | 0.0081759
2015-09-18 05:00 | 39.24 | 21.29 | 17.95 | 0 | 2.3007 | -87.8667 | 87.2776 | 2.7224 | -88.4406 | 87.2895 | 0 | 15.9675 | 0.2 | 0 | 1.962 | 17.9295 | -0.6 | -0.039703 | 1.1002 | 0.016175
2015-09-18 06:00 | 58.72 | 31.83 | 26.89 | 255.5249 | 2.2846 | -72.8628 | 83.9593 | 6.0407 | -73.7754 | 72.9477 | 74.9312 | 23.8725 | 0.2 | 0 | 2.936 | 101.7397 | 0.4 | 3.5794 | 1.0857 | 0.090575
2015-09-18 07:00 | 92.9033 | 41.6933 | 51.21 | 323.2026 | 2.2685 | -57.8589 | 80.8833 | 9.1167 | -58.9704 | 58.6676 | 168.0662 | 31.27 | 0.2 | 0 | 4.6452 | 203.9814 | 1 | 7.3744 | 1.0705 | 0.17906
2015-09-18 08:00 | 127.0867 | 51.5567 | 75.53 | 371.1847 | 2.2524 | -42.8549 | 78.2593 | 11.7407 | -43.9589 | 44.5942 | 264.3197 | 38.6675 | 0.2 | 0 | 6.3543 | 309.3415 | 1.8 | 11.4669 | 1.0541 | 0.26739
2015-09-18 09:00 | 161.27 | 61.42 | 99.85 | 420.8481 | 2.2363 | -27.851 | 76.2752 | 13.7248 | -28.7207 | 31.0825 | 360.4246 | 46.065 | 0.2 | 0 | 8.0635 | 414.5531 | 3 | 15.9548 | 1.0362 | 0.35223
2015-09-18 10:00 | 151.49 | 67.8067 | 83.6833 | 325.0472 | 2.2202 | -12.8471 | 75.0812 | 14.9188 | -13.2932 | 19.4149 | 306.5638 | 50.855 | 0.2 | 0 | 7.5745 | 364.9933 | 3.6 | 15.006 | 1.04 | 0.31126
2015-09-18 11:00 | 141.71 | 74.1933 | 67.5167 | 257.0494 | 2.2041 | 2.1568 | 74.772 | 15.228 | 2.2337 | 14.914 | 248.3902 | 55.645 | 0.2 | 0 | 7.0855 | 311.1207 | 3.3 | 13.0225 | 1.0479 | 0.26734
2015-09-18 12:00 | 131.93 | 80.58 | 51.35 | 203.3532 | 2.188 | 17.1607 | 75.3735 | 14.6265 | 17.7409 | 22.4267 | 187.9732 | 60.435 | 0.2 | 0 | 6.5965 | 255.0047 | 2.1 | 10.0689 | 1.0597 | 0.22159
2015-09-18 13:00 | 114.8933 | 67.9367 | 46.9567 | 206.2301 | 2.1719 | 32.1647 | 76.8389 | 13.1611 | 33.115 | 34.8998 | 169.1405 | 50.9525 | 0.2 | 0 | 5.7447 | 225.8377 | 2 | 9.0574 | 1.0638 | 0.197
2015-09-18 14:00 | 97.8567 | 55.2933 | 42.5633 | 224.1865 | 2.1558 | 47.1686 | 79.0556 | 10.9444 | 48.2807 | 48.6413 | 148.1358 | 41.47 | 0.2 | 0 | 4.8928 | 194.4986 | 1.9 | 7.9781 | 1.0681 | 0.17035
2015-09-18 15:00 | 80.82 | 42.65 | 38.17 | 269.6083 | 2.1397 | 62.1725 | 81.861 | 8.139 | 63.2186 | 62.8013 | 123.2318 | 31.9875 | 0.2 | 0 | 4.041 | 159.2603 | 2.3 | 7.2769 | 1.0709 | 0.13985
2015-09-18 16:00 | 54.77 | 29.05 | 25.72 | 298.6509 | 2.1236 | 77.1764 | 85.0595 | 4.9405 | 77.9654 | 77.1172 | 66.5864 | 21.7875 | 0.2 | 0 | 2.7385 | 91.1124 | 2.3 | 5.1473 | 1.0794 | 0.080645
2015-09-18 17:00 | 28.72 | 15.45 | 13.27 | 0 | 2.1075 | 92.1803 | 88.4383 | 1.5617 | 92.5992 | 91.4688 | 0 | 11.5875 | 0.2 | 0 | 1.436 | 13.0235 | 2.3 | 2.707 | 1.0892 | 0.011632
2015-09-18 18:00 | 2.67 | 1.85 | 0.82 | 0 | 2.0914 | 107.1842 | 91.7782 | -1.7782 | 107.2184 | 105.7683 | 0 | 1.3875 | 0.2 | 0 | 0.1335 | 1.521 | 2.1 | 2.1475 | 1.0914 | 0.0013612
2015-09-18 19:00 | 1.78 | 1.2333 | 0.54667 | 0 | 2.0753 | 122.1882 | 94.8631 | -4.8631 | 121.9182 | 119.9083 | 0 | 0.925 | 0.2 | 0 | 0.089 | 1.014 | 1.6 | 1.6317 | 1.0935 | 0.0009092
2015-09-18 20:00 | 0.89 | 0.61667 | 0.27333 | 0 | 2.0592 | 137.1921 | 97.4889 | -7.4889 | 136.7686 | 133.6907 | 0 | 0.4625 | 0.2 | 0 | 0.0445 | 0.507 | 1.4 | 1.4158 | 1.0943 | 0.00045496
2015-09-18 21:00 | 0 | 0 | 0 | 0 | 2.0431 | 152.196 | 99.4753 | -9.4753 | 151.7968 | 146.6269 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-09-18 22:00 | 0 | 0 | 0 | 0 | 2.027 | 167.1999 | 100.6796 | -10.6796 | 166.9787 | 157.1907 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.0948 | 0
2015-09-18 23:00 | 0 | 0 | 0 | 0 | 2.0109 | 182.2038 | 101.0127 | -11.0127 | -177.7562 | 160.8983 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0932 | 0
2015-09-19 | 0 | 0 | 0 | 0 | 1.9948 | -162.7923 | 100.4502 | -10.4502 | -162.5037 | 154.5486 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0932 | 0
2015-09-19 01:00 | 0.023333 | 0.023333 | 0 | 0 | 1.9787 | -147.7883 | 99.036 | -9.036 | -147.3555 | 143.0062 | 0 | 0.0175 | 0.2 | 0 | 0.0011667 | 0.018667 | 1.2 | 1.2006 | 1.0952 | 1.6764e-05
2015-09-19 02:00 | 0.046667 | 0.046667 | 0 | 0 | 1.9626 | -132.7844 | 96.8764 | -6.8764 | -132.3708 | 129.7399 | 0 | 0.035 | 0.2 | 0 | 0.0023333 | 0.037333 | 1.4 | 1.4012 | 1.0944 | 3.3503e-05
2015-09-19 03:00 | 0.07 | 0.07 | 0 | 0 | 1.9464 | -117.7805 | 94.1266 | -4.1266 | -117.5599 | 115.8254 | 0 | 0.0525 | 0.2 | 0 | 0.0035 | 0.056 | 1.5 | 1.5017 | 1.094 | 5.0236e-05
2015-09-19 04:00 | 5.77 | 5.77 | 0 | 0 | 1.9303 | -102.7766 | 90.9757 | -0.97571 | -102.8829 | 101.6291 | 0 | 4.3275 | 0.2 | 0 | 0.2885 | 4.616 | 2.1 | 2.2443 | 1.091 | 0.0041297
2015-09-19 05:00 | 11.47 | 11.47 | 0 | 0 | 1.9142 | -87.7727 | 87.6329 | 2.3671 | -88.2617 | 87.3119 | 0 | 8.6025 | 0.2 | 0 | 0.5735 | 9.176 | 2.3 | 2.5867 | 1.0897 | 0.0081989
2015-09-19 06:00 | 17.17 | 17.17 | 0 | 0 | 1.8981 | -72.7688 | 84.3163 | 5.6837 | -73.599 | 72.9716 | 0 | 12.8775 | 0.2 | 0 | 0.8585 | 13.736 | 2.2 | 2.6292 | 1.0895 | 0.012271
2015-09-19 07:00 | 24.9933 | 24.9867 | 0.0066667 | 0.043796 | 1.882 | -57.7649 | 81.2444 | 8.7556 | -58.8015 | 58.7021 | 0.022752 | 18.74 | 0.2 | 0 | 1.2497 | 20.0124 | 2.2 | 2.8254 | 1.0887 | 0.017866
2015-09-19 08:00 | 32.8167 | 32.8033 | 0.013333 | 0.067611 | 1.8659 | -42.7609 | 78.6263 | 11.3737 | -43.8024 | 44.6538 | 0.048096 | 24.6025 | 0.2 | 0 | 1.6408 | 26.2914 | 2.2 | 3.0216 | 1.0879 | 0.023454
2015-09-19 09:00 | 40.64 | 40.62 | 0.02 | 0.086614 | 1.8497 | -27.757 | 76.6493 | 13.3507 | -28.5816 | 31.1969 | 0.074089 | 30.465 | 0.2 | 0 | 2.032 | 32.5711 | 2.5 | 3.5178 | 1.0859 | 0.029003
2015-09-19 10:00 | 43.8433 | 43.5767 | 0.26667 | 1.0624 | 1.8336 | -12.7531 | 75.4624 | 14.5376 | -13.1755 | 19.6544 | 1.0005 | 32.6825 | 0.2 | 0 | 2.1922 | 35.8751 | 2.6 | 3.7211 | 1.0851 | 0.031922
2015-09-19 11:00 | 47.0467 | 46.5333 | 0.51333 | 2.0042 | 1.8175 | 2.2508 | 75.1595 | 14.8405 | 2.3273 | 15.3101 | 1.9331 | 34.9 | 0.2 | 0 | 2.3523 | 39.1854 | 2.8 | 4.0245 | 1.0839 | 0.034828
2015-09-19 12:00 | 50.25 | 49.49 | 0.76 | 3.0909 | 1.8014 | 17.2547 | 75.7657 | 14.2343 | 17.8102 | 22.7574 | 2.8502 | 37.1175 | 0.2 | 0 | 2.5125 | 42.4802 | 3 | 4.3275 | 1.0827 | 0.037714
2015-09-19 13:00 | 46.5867 | 46.08 | 0.50667 | 2.293 | 1.7852 | 32.2586 | 77.2342 | 12.7658 | 33.1617 | 35.1608 | 1.8746 | 34.56 | 0.2 | 0 | 2.3293 | 38.7639 | 2.2 | 3.4114 | 1.0864 | 0.034531
2015-09-19 14:00 | 42.9233 | 42.67 | 0.25333 | 1.384 | 1.7691 | 47.2625 | 79.4526 | 10.5474 | 48.3086 | 48.8676 | 0.91037 | 32.0025 | 0.2 | 0 | 2.1462 | 35.059 | 2.6 | 3.6956 | 1.0852 | 0.031198
2015-09-19 15:00 | 39.26 | 39.26 | 0 | 0 | 1.753 | 62.2664 | 82.2587 | 7.7413 | 63.2328 | 63.0107 | 0 | 29.445 | 0.2 | 0 | 1.963 | 31.408 | 2.5 | 3.4815 | 1.0861 | 0.027971
2015-09-19 16:00 | 26.6733 | 26.62 | 0.053333 | 0.67341 | 1.7368 | 77.2704 | 85.4575 | 4.5425 | 77.9717 | 77.3199 | 0.14782 | 19.965 | 0.2 | 0 | 1.3337 | 21.4465 | 2.5 | 3.1702 | 1.0873 | 0.019122
2015-09-19 17:00 | 14.0867 | 13.98 | 0.10667 | 0 | 1.7207 | 92.2743 | 88.8363 | 1.1637 | 92.6035 | 91.6719 | 0 | 10.485 | 0.2 | 0 | 0.70433 | 11.1893 | 2.3 | 2.6497 | 1.0894 | 0.0099955
2015-09-19 18:00 | 1.5 | 1.34 | 0.16 | 0 | 1.7046 | 107.2782 | 92.1761 | -2.1761 | 107.2267 | 105.9786 | 0 | 1.005 | 0.2 | 0 | 0.075 | 1.08 | 1.9 | 1.9338 | 1.0923 | 0.00096731
2015-09-19 19:00 | 1 | 0.89333 | 0.10667 | 0 | 1.6885 | 122.2821 | 95.2607 | -5.2607 | 121.9363 | 120.1338 | 0 | 0.67 | 0.2 | 0 | 0.05 | 0.72 | 1.8 | 1.8225 | 1.0927 | 0.00064514
2015-09-19 20:00 | 0.5 | 0.44667 | 0.053333 | 0 | 1.6723 | 137.286 | 97.8857 | -7.8857 | 136.8019 | 133.9439 | 0 | 0.335 | 0.2 | 0 | 0.025 | 0.36 | 1.2 | 1.2112 | 1.0952 | 0.00032329
2015-09-19 21:00 | 0 | 0 | 0 | 0 | 1.6562 | 152.2899 | 99.87 | -9.87 | 151.8497 | 146.9285 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0968 | 0
2015-09-19 22:00 | 0 | 0 | 0 | 0 | 1.64 | 167.2938 | 101.0708 | -11.0708 | 167.0541 | 157.5656 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-09-19 23:00 | 0 | 0 | 0 | 0 | 1.6239 | 182.2977 | 101.3988 | -11.3988 | -177.657 | 161.2718 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-09-20 | 0 | 0 | 0 | 0 | 1.6078 | -162.6984 | 100.8299 | -10.8299 | -162.3816 | 154.7761 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.102 | 0
2015-09-20 01:00 | 0 | 0 | 0 | 0 | 1.5916 | -147.6945 | 99.4087 | -9.4087 | -147.2133 | 143.1306 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.102 | 0
2015-09-20 02:00 | 0 | 0 | 0 | 0 | 1.5755 | -132.6906 | 97.2423 | -7.2423 | -132.2126 | 129.8111 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-09-20 03:00 | 0 | 0 | 0 | 0 | 1.5593 | -117.6867 | 94.487 | -4.487 | -117.3901 | 115.8685 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-09-20 04:00 | 10.75 | 7.7867 | 2.9633 | 0 | 1.5432 | -102.6828 | 91.3327 | -1.3327 | -102.7062 | 101.6575 | 0 | 5.84 | 0.2 | 0 | 0.5375 | 6.3775 | -0.8 | -0.6007 | 1.1024 | 0.0057651
2015-09-20 05:00 | 21.5 | 15.5733 | 5.9267 | 0 | 1.5271 | -87.6789 | 87.9889 | 2.0111 | -88.0829 | 87.3348 | 0 | 11.68 | 0.2 | 0 | 1.075 | 12.755 | -0.3 | 0.098594 | 1.0996 | 0.011501
2015-09-20 06:00 | 32.25 | 23.36 | 8.89 | 95.7746 | 1.5109 | -72.675 | 84.674 | 5.326 | -73.4229 | 72.9967 | 28.007 | 17.52 | 0.2 | 0 | 1.6125 | 47.1395 | 0.1 | 1.5731 | 1.0937 | 0.042277
2015-09-20 07:00 | 45.0267 | 37.9533 | 7.0733 | 48.4558 | 1.4948 | -57.6711 | 81.6063 | 8.3937 | -58.633 | 58.7388 | 25.1457 | 28.465 | 0.2 | 0 | 2.2513 | 55.8621 | 0.5 | 2.2457 | 1.091 | 0.049976
2015-09-20 08:00 | 57.8033 | 52.5467 | 5.2567 | 27.5351 | 1.4786 | -42.6672 | 78.9942 | 11.0058 | -43.6465 | 44.7167 | 19.5663 | 39.41 | 0.2 | 0 | 2.8902 | 61.8665 | 1.2 | 3.1333 | 1.0875 | 0.055168
2015-09-20 09:00 | 70.58 | 67.14 | 3.44 | 15.3203 | 1.4625 | -27.6632 | 77.0242 | 12.9758 | -28.443 | 31.316 | 13.0883 | 50.355 | 0.2 | 0 | 3.529 | 66.9723 | 1.6 | 3.6929 | 1.0852 | 0.059598
2015-09-20 10:00 | 72.16 | 69.8667 | 2.2933 | 9.3776 | 1.4463 | -12.6593 | 75.8444 | 14.1556 | -13.0585 | 19.8995 | 8.8176 | 52.4 | 0.2 | 0 | 3.608 | 64.8256 | 1.6 | 3.6258 | 1.0855 | 0.057702
2015-09-20 11:00 | 73.74 | 72.5933 | 1.1467 | 4.5945 | 1.4302 | 2.3446 | 75.5477 | 14.4523 | 2.4205 | 15.7068 | 4.4229 | 54.445 | 0.2 | 0 | 3.687 | 62.5549 | 2.1 | 4.0548 | 1.0838 | 0.055593
2015-09-20 12:00 | 75.32 | 75.32 | 0 | 0 | 1.414 | 17.3485 | 76.1586 | 13.8414 | 17.8789 | 23.0905 | 0 | 56.49 | 0.2 | 0 | 3.766 | 60.256 | 2.4 | 4.283 | 1.0829 | 0.053504
2015-09-20 13:00 | 60.8467 | 60.8467 | 0 | 0 | 1.3979 | 32.3523 | 77.6302 | 12.3698 | 33.208 | 35.4242 | 0 | 45.635 | 0.2 | 0 | 3.0423 | 48.6773 | 2.4 | 3.9212 | 1.0843 | 0.043281
2015-09-20 14:00 | 46.3733 | 46.3733 | 0 | 0 | 1.3817 | 47.3562 | 79.8502 | 10.1498 | 48.3361 | 49.0955 | 0 | 34.78 | 0.2 | 0 | 2.3187 | 37.0987 | 2.2 | 3.3593 | 1.0866 | 0.033054
2015-09-20 15:00 | 31.9 | 31.9 | 0 | 0 | 1.3656 | 62.3601 | 82.6571 | 7.3429 | 63.2467 | 63.2211 | 0 | 23.925 | 0.2 | 0 | 1.595 | 25.52 | 2.2 | 2.9975 | 1.088 | 0.022768
2015-09-20 16:00 | 21.5267 | 21.52 | 0.0066667 | 0.092257 | 1.3494 | 77.364 | 85.8561 | 4.1439 | 77.9775 | 77.523 | 0.019932 | 16.14 | 0.2 | 0 | 1.0763 | 17.2363 | 2.1 | 2.6386 | 1.0894 | 0.015398
2015-09-20 17:00 | 11.1533 | 11.14 | 0.013333 | 0 | 1.3332 | 92.3679 | 89.2349 | 0.76508 | 92.6074 | 91.8749 | 0 | 8.355 | 0.2 | 0 | 0.55767 | 8.9127 | 2.1 | 2.3785 | 1.0905 | 0.0079697
2015-09-20 18:00 | 0.78 | 0.76 | 0.02 | 0 | 1.3171 | 107.3718 | 92.5747 | -2.5747 | 107.2347 | 106.1882 | 0 | 0.57 | 0.2 | 0 | 0.039 | 0.609 | 1.9 | 1.919 | 1.0923 | 0.00054548
2015-09-20 19:00 | 0.52 | 0.50667 | 0.013333 | 0 | 1.3009 | 122.3757 | 95.659 | -5.659 | 121.9541 | 120.3583 | 0 | 0.38 | 0.2 | 0 | 0.026 | 0.406 | 2.1 | 2.1127 | 1.0915 | 0.0003634
2015-09-20 20:00 | 0.26 | 0.25333 | 0.0066667 | 0 | 1.2848 | 137.3796 | 98.283 | -8.283 | 136.8348 | 134.1954 | 0 | 0.19 | 0.2 | 0 | 0.013 | 0.203 | 3.6 | 3.6063 | 1.0856 | 0.0001807
2015-09-20 21:00 | 0 | 0 | 0 | 0 | 1.2686 | 152.3835 | 100.2653 | -10.2653 | 151.9023 | 147.2284 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.8 | 3.8 | 1.0848 | 0
2015-09-20 22:00 | 0 | 0 | 0 | 0 | 1.2524 | 167.3874 | 101.4626 | -11.4626 | 167.1295 | 157.9402 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.086 | 0
2015-09-20 23:00 | 0 | 0 | 0 | 0 | 1.2363 | 182.3913 | 101.7856 | -11.7856 | -177.5577 | 161.6449 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.0892 | 0
2015-09-21 | 0 | 0 | 0 | 0 | 1.2201 | -162.6048 | 101.2103 | -11.2103 | -162.2595 | 155.0003 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0908 | 0
2015-09-21 01:00 | 0 | 0 | 0 | 0 | 1.2039 | -147.6009 | 99.7821 | -9.7821 | -147.0711 | 143.2522 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2 | 2 | 1.092 | 0
2015-09-21 02:00 | 0 | 0 | 0 | 0 | 1.1878 | -132.597 | 97.6089 | -7.6089 | -132.0542 | 129.8806 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0908 | 0
2015-09-21 03:00 | 0 | 0 | 0 | 0 | 1.1716 | -117.5931 | 94.8482 | -4.8482 | -117.2202 | 115.9107 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0924 | 0
2015-09-21 04:00 | 15.13 | 9.0533 | 6.0767 | 0 | 1.1554 | -102.5892 | 91.6904 | -1.6904 | -102.5296 | 101.6859 | 0 | 6.79 | 0.2 | 0 | 0.7565 | 7.5465 | 1.4 | 1.6358 | 1.0935 | 0.0067665
2015-09-21 05:00 | 30.26 | 18.1067 | 12.1533 | 0 | 1.1393 | -87.5854 | 88.3456 | 1.6544 | -87.9043 | 87.3582 | 0 | 13.58 | 0.2 | 0 | 1.513 | 15.093 | 1.3 | 1.7717 | 1.0929 | 0.013526
2015-09-21 06:00 | 45.39 | 27.16 | 18.23 | 210.5289 | 1.1231 | -72.5815 | 85.0325 | 4.9675 | -73.2471 | 73.0232 | 61.4713 | 20.37 | 0.2 | 0 | 2.2695 | 84.1108 | 1.2 | 3.8285 | 1.0847 | 0.074812
2015-09-21 07:00 | 67.46 | 46.9333 | 20.5267 | 146.922 | 1.1069 | -57.5776 | 81.9689 | 8.0311 | -58.4649 | 58.7775 | 76.1588 | 35.2 | 0.2 | 0 | 3.373 | 114.7318 | 0.7 | 4.2854 | 1.0829 | 0.10188
2015-09-21 08:00 | 89.53 | 66.7067 | 22.8233 | 123.6441 | 1.0908 | -42.5737 | 79.3628 | 10.6372 | -43.4911 | 44.7828 | 87.7604 | 50.03 | 0.2 | 0 | 4.4765 | 142.2669 | 1 | 5.4458 | 1.0782 | 0.12578
2015-09-21 09:00 | 111.6 | 86.48 | 25.12 | 115.1524 | 1.0746 | -27.5698 | 77.3999 | 12.6001 | -28.3052 | 31.4398 | 98.2467 | 64.86 | 0.2 | 0 | 5.58 | 168.6867 | 1.2 | 6.4715 | 1.0741 | 0.14857
2015-09-21 10:00 | 105.7667 | 87.1367 | 18.63 | 78.2528 | 1.0584 | -12.5659 | 76.2271 | 13.7729 | -12.942 | 20.1499 | 73.4634 | 65.3525 | 0.2 | 0 | 5.2883 | 144.1042 | 1.5 | 6.0033 | 1.076 | 0.12714
2015-09-21 11:00 | 99.9333 | 87.7933 | 12.14 | 49.9593 | 1.0422 | 2.438 | 75.9365 | 14.0635 | 2.5129 | 16.1042 | 47.9989 | 65.845 | 0.2 | 0 | 4.9967 | 118.8406 | 1.9 | 5.6138 | 1.0775 | 0.10501
2015-09-21 12:00 | 94.1 | 88.45 | 5.65 | 24.2947 | 1.0261 | 17.4418 | 76.5521 | 13.4479 | 17.9471 | 23.4256 | 22.2923 | 66.3375 | 0.2 | 0 | 4.705 | 93.3348 | 2.3 | 5.2167 | 1.0791 | 0.082591
2015-09-21 13:00 | 76.4967 | 72.4767 | 4.02 | 19.3776 | 1.0099 | 32.4457 | 78.0267 | 11.9733 | 33.2537 | 35.6898 | 15.7382 | 54.3575 | 0.2 | 0 | 3.8248 | 73.9206 | 2 | 4.31 | 1.0828 | 0.065631
2015-09-21 14:00 | 58.8933 | 56.5033 | 2.39 | 14.1105 | 0.99372 | 47.4496 | 80.2484 | 9.7516 | 48.3631 | 49.3249 | 9.1968 | 42.3775 | 0.2 | 0 | 2.9447 | 54.519 | 2.5 | 4.2037 | 1.0832 | 0.048424
2015-09-21 15:00 | 41.29 | 40.53 | 0.76 | 6.2861 | 0.97754 | 62.4535 | 83.0559 | 6.9441 | 63.26 | 63.4324 | 2.8115 | 30.3975 | 0.2 | 0 | 2.0645 | 35.2735 | 3.7 | 4.8023 | 1.0808 | 0.031261
2015-09-21 16:00 | 27.7033 | 27.1967 | 0.50667 | 7.7574 | 0.96137 | 77.4574 | 86.2551 | 3.7449 | 77.983 | 77.7264 | 1.6491 | 20.3975 | 0.2 | 0 | 1.3852 | 23.4317 | 3.7 | 4.4322 | 1.0823 | 0.020795
2015-09-21 17:00 | 14.1167 | 13.8633 | 0.25333 | 0 | 0.94519 | 92.4612 | 89.634 | 0.36599 | 92.6109 | 92.0777 | 0 | 10.3975 | 0.2 | 0 | 0.70583 | 11.1033 | 3.5 | 3.847 | 1.0846 | 0.0098751
2015-09-21 18:00 | 0.53 | 0.53 | 0 | 0 | 0.92901 | 107.4651 | 92.9738 | -2.9738 | 107.2422 | 106.3971 | 0 | 0.3975 | 0.2 | 0 | 0.0265 | 0.424 | 3.1 | 3.1132 | 1.0875 | 0.00037812
2015-09-21 19:00 | 0.35333 | 0.35333 | 0 | 0 | 0.91283 | 122.469 | 96.0578 | -6.0578 | 121.9715 | 120.5815 | 0 | 0.265 | 0.2 | 0 | 0.017667 | 0.28267 | 3.1 | 3.1088 | 1.0876 | 0.00025208
2015-09-21 20:00 | 0.17667 | 0.17667 | 0 | 0 | 0.89664 | 137.4729 | 98.6809 | -8.6809 | 136.8674 | 134.4453 | 0 | 0.1325 | 0.2 | 0 | 0.0088333 | 0.14133 | 1.7 | 1.7044 | 1.0932 | 0.00012669
2015-09-21 21:00 | 0 | 0 | 0 | 0 | 0.88046 | 152.4768 | 100.6612 | -10.6612 | 151.9547 | 147.5265 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0888 | 0
2015-09-21 22:00 | 0 | 0 | 0 | 0 | 0.86428 | 167.4806 | 101.855 | -11.855 | 167.2047 | 158.3142 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.4 | 3.4 | 1.0864 | 0
2015-09-21 23:00 | 0 | 0 | 0 | 0 | 0.84809 | 182.4845 | 102.1728 | -12.1728 | -177.4586 | 162.0176 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.4 | 3.4 | 1.0864 | 0
2015-09-22 | 0 | 0 | 0 | 0 | 0.83191 | -162.5116 | 101.5911 | -11.5911 | -162.1374 | 155.221 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.4 | 3.4 | 1.0864 | 0
2015-09-22 01:00 | 0 | 0 | 0 | 0 | 0.81572 | -147.5078 | 100.1559 | -10.1559 | -146.9288 | 143.371 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0872 | 0
2015-09-22 02:00 | 0 | 0 | 0 | 0 | 0.79954 | -132.5039 | 97.9761 | -7.9761 | -131.8958 | 129.9484 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0868 | 0
2015-09-22 03:00 | 0 | 0 | 0 | 0 | 0.78335 | -117.5 | 95.2098 | -5.2098 | -117.0504 | 115.9521 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0872 | 0
2015-09-22 04:00 | 4.3433 | 4.3433 | 0 | 0 | 0.76716 | -102.4961 | 92.0486 | -2.0486 | -102.3532 | 101.7142 | 0 | 3.2575 | 0.2 | 0 | 0.21717 | 3.4747 | 3.3 | 3.4086 | 1.0864 | 0.0030953
2015-09-22 05:00 | 8.6867 | 8.6867 | 0 | 0 | 0.75097 | -87.4923 | 88.703 | 1.297 | -87.726 | 87.3823 | 0 | 6.515 | 0.2 | 0 | 0.43433 | 6.9493 | 3.1 | 3.3172 | 1.0867 | 0.0061927
2015-09-22 06:00 | 13.03 | 13.03 | 0 | 0 | 0.73478 | -72.4884 | 85.3915 | 4.6085 | -73.0718 | 73.051 | 0 | 9.7725 | 0.2 | 0 | 0.6515 | 10.424 | 3.1 | 3.4257 | 1.0863 | 0.0092853
2015-09-22 07:00 | 22.3733 | 21.9167 | 0.45667 | 3.4225 | 0.71859 | -57.4845 | 82.3321 | 7.6679 | -58.2975 | 58.8185 | 1.772 | 16.4375 | 0.2 | 0 | 1.1187 | 19.3282 | 3.1 | 3.704 | 1.0852 | 0.017199
2015-09-22 08:00 | 31.7167 | 30.8033 | 0.91333 | 5.1239 | 0.7024 | -42.4807 | 79.7321 | 10.2679 | -43.3365 | 44.8521 | 3.6325 | 23.1025 | 0.2 | 0 | 1.5858 | 28.3208 | 3 | 3.885 | 1.0845 | 0.025184
2015-09-22 09:00 | 41.06 | 39.69 | 1.37 | 6.4704 | 0.68621 | -27.4768 | 77.7761 | 12.2239 | -28.168 | 31.5684 | 5.5129 | 29.7675 | 0.2 | 0 | 2.053 | 37.3334 | 2.9 | 4.0667 | 1.0837 | 0.033177
2015-09-22 10:00 | 52.5867 | 51.49 | 1.0967 | 4.7357 | 0.67002 | -12.4729 | 76.6103 | 13.3897 | -12.8264 | 20.4055 | 4.4386 | 38.6175 | 0.2 | 0 | 2.6293 | 45.6854 | 3.2 | 4.6277 | 1.0815 | 0.040515
2015-09-22 11:00 | 64.1133 | 63.29 | 0.82333 | 3.4828 | 0.65383 | 2.5309 | 76.3258 | 13.6742 | 2.6046 | 16.5021 | 3.3393 | 47.4675 | 0.2 | 0 | 3.2057 | 54.0125 | 3.3 | 4.9879 | 1.08 | 0.047836
2015-09-22 12:00 | 75.64 | 75.09 | 0.55 | 2.4351 | 0.63763 | 17.5348 | 76.9461 | 13.0539 | 18.0145 | 23.7627 | 2.2286 | 56.3175 | 0.2 | 0 | 3.782 | 62.3281 | 3.2 | 5.1478 | 1.0794 | 0.055168
2015-09-22 13:00 | 61.5667 | 60 | 1.5667 | 7.807 | 0.62144 | 32.5386 | 78.4237 | 11.5763 | 33.2987 | 35.9574 | 6.3194 | 45 | 0.2 | 0 | 3.0783 | 54.3978 | 3.3 | 4.9999 | 1.08 | 0.048175
2015-09-22 14:00 | 47.4933 | 44.91 | 2.5833 | 15.8958 | 0.60524 | 47.5425 | 80.647 | 9.353 | 48.3895 | 49.5557 | 10.3117 | 33.6825 | 0.2 | 0 | 2.3747 | 46.3689 | 3.2 | 4.649 | 1.0814 | 0.041118
2015-09-22 15:00 | 33.42 | 29.82 | 3.6 | 31.5842 | 0.58905 | 62.5464 | 83.4551 | 6.5449 | 63.2728 | 63.6444 | 14.0215 | 22.365 | 0.2 | 0 | 1.671 | 38.0575 | 2.7 | 3.8893 | 1.0844 | 0.033842
2015-09-22 16:00 | 22.3967 | 19.9933 | 2.4033 | 41.184 | 0.57285 | 77.5502 | 86.6545 | 3.3455 | 77.9878 | 77.9299 | 8.6119 | 14.995 | 0.2 | 0 | 1.1198 | 24.7267 | 3.1 | 3.8727 | 1.0845 | 0.021989
2015-09-22 17:00 | 11.3733 | 10.1667 | 1.2067 | 0 | 0.55665 | 92.5541 | 90.0335 | -0.033468 | 92.6138 | 92.2801 | 0 | 7.625 | 0.2 | 0 | 0.56867 | 8.1937 | 3.1 | 3.3561 | 1.0866 | 0.0073005
2015-09-22 18:00 | 0.35 | 0.34 | 0.01 | 0 | 0.54045 | 107.5579 | 93.3732 | -3.3732 | 107.2491 | 106.6051 | 0 | 0.255 | 0.2 | 0 | 0.0175 | 0.2725 | 2.3 | 2.3085 | 1.0908 | 0.00024373
2015-09-22 19:00 | 0.23333 | 0.22667 | 0.0066667 | 0 | 0.52426 | 122.5618 | 96.4569 | -6.4569 | 121.9883 | 120.8032 | 0 | 0.17 | 0.2 | 0 | 0.011667 | 0.18167 | 2.2 | 2.2057 | 1.0912 | 0.00016255
2015-09-22 20:00 | 0.11667 | 0.11333 | 0.0033333 | 0 | 0.50806 | 137.5656 | 99.0791 | -9.0791 | 136.8996 | 134.6933 | 0 | 0.085 | 0.2 | 0 | 0.0058333 | 0.090833 | 1.8 | 1.8028 | 1.0928 | 8.1395e-05
2015-09-22 21:00 | 0 | 0 | 0 | 0 | 0.49186 | 152.5695 | 101.0574 | -11.0574 | 152.0067 | 147.8225 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-09-22 22:00 | 0 | 0 | 0 | 0 | 0.47565 | 167.5733 | 102.2477 | -12.2477 | 167.2796 | 158.6875 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-09-22 23:00 | 0 | 0 | 0 | 0 | 0.45945 | 182.5772 | 102.5605 | -12.5605 | -177.3597 | 162.3897 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-09-23 | 0 | 0 | 0 | 0 | 0.44325 | -162.419 | 101.9724 | -11.9724 | -162.0154 | 155.4382 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0936 | 0
2015-09-23 01:00 | 0 | 0 | 0 | 0 | 0.42705 | -147.4151 | 100.5302 | -10.5302 | -146.7866 | 143.4871 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-09-23 02:00 | 0 | 0 | 0 | 0 | 0.41085 | -132.4113 | 98.3437 | -8.3437 | -131.7375 | 130.0146 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0936 | 0
2015-09-23 03:00 | 0 | 0 | 0 | 0 | 0.39464 | -117.4074 | 95.572 | -5.572 | -116.8808 | 115.9928 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0924 | 0
2015-09-23 04:00 | 11.7133 | 8.39 | 3.3233 | 0 | 0.37844 | -102.4036 | 92.4074 | -2.4074 | -102.1771 | 101.7426 | 0 | 6.2925 | 0.2 | 0 | 0.58567 | 6.8782 | 1.8 | 2.0149 | 1.0919 | 0.0061586
2015-09-23 05:00 | 23.4267 | 16.78 | 6.6467 | 0 | 0.36223 | -87.3997 | 89.0609 | 0.93914 | -87.5482 | 87.4072 | 0 | 12.585 | 0.2 | 0 | 1.1713 | 13.7563 | 2.3 | 2.7299 | 1.0891 | 0.012285
2015-09-23 06:00 | 35.14 | 25.17 | 9.97 | 134.5702 | 0.34603 | -72.3959 | 85.7512 | 4.2488 | -72.8971 | 73.0803 | 39.1642 | 18.8775 | 0.2 | 0 | 1.757 | 59.7987 | 2.2 | 4.0687 | 1.0837 | 0.05314
2015-09-23 07:00 | 59.3033 | 45.25 | 14.0533 | 110.5387 | 0.32982 | -57.392 | 82.6959 | 7.3041 | -58.1307 | 58.8618 | 57.16 | 33.9375 | 0.2 | 0 | 2.9652 | 94.0627 | 1.9 | 4.8395 | 1.0806 | 0.083351
2015-09-23 08:00 | 83.4667 | 65.33 | 18.1367 | 105.5094 | 0.31361 | -42.3882 | 80.1019 | 9.8981 | -43.1826 | 44.9249 | 74.7042 | 48.9975 | 0.2 | 0 | 4.1733 | 127.875 | 2.2 | 6.1961 | 1.0752 | 0.11274
2015-09-23 09:00 | 107.63 | 85.41 | 22.22 | 108.2314 | 0.29741 | -27.3844 | 78.1529 | 11.8471 | -28.0318 | 31.7016 | 92.0829 | 64.0575 | 0.2 | 0 | 5.3815 | 161.5219 | 1.9 | 6.9476 | 1.0722 | 0.14201
2015-09-23 10:00 | 116.48 | 95.2967 | 21.1833 | 94.1263 | 0.2812 | -12.3805 | 76.994 | 13.006 | -12.7117 | 20.6661 | 88.0695 | 71.4725 | 0.2 | 0 | 5.824 | 165.366 | 2.1 | 7.2677 | 1.0709 | 0.14522
2015-09-23 11:00 | 125.33 | 105.1833 | 20.1467 | 87.6762 | 0.26499 | 2.6233 | 76.7156 | 13.2844 | 2.6955 | 16.9004 | 83.8896 | 78.8875 | 0.2 | 0 | 6.2665 | 169.0436 | 2.3 | 7.5826 | 1.0697 | 0.14827
2015-09-23 12:00 | 134.18 | 115.07 | 19.11 | 87.1976 | 0.24878 | 17.6272 | 77.3405 | 12.6595 | 18.0812 | 24.1014 | 79.5961 | 86.3025 | 0.2 | 0 | 6.709 | 172.6076 | 2.2 | 7.594 | 1.0696 | 0.15139
2015-09-23 13:00 | 103.2 | 90.2333 | 12.9667 | 66.8815 | 0.23257 | 32.631 | 78.821 | 11.179 | 33.3431 | 36.2269 | 53.9522 | 67.675 | 0.2 | 0 | 5.16 | 126.7872 | 2.7 | 6.6621 | 1.0734 | 0.11159
2015-09-23 14:00 | 72.22 | 65.3967 | 6.8233 | 43.8394 | 0.21636 | 47.6348 | 81.0459 | 8.9541 | 48.4153 | 49.7877 | 28.3036 | 49.0475 | 0.2 | 0 | 3.611 | 80.9621 | 2.5 | 5.0301 | 1.0799 | 0.071692
2015-09-23 15:00 | 41.24 | 40.56 | 0.68 | 6.3521 | 0.20015 | 62.6387 | 83.8547 | 6.1453 | 63.285 | 63.857 | 2.7988 | 30.42 | 0.2 | 0 | 2.062 | 35.2808 | 2.8 | 3.9025 | 1.0844 | 0.031372
2015-09-23 16:00 | 27.5733 | 27.12 | 0.45333 | 0 | 0.18394 | 77.6425 | 87.0542 | 2.9458 | 77.992 | 78.1335 | 0 | 20.34 | 0.2 | 0 | 1.3787 | 21.7187 | 2.2 | 2.8787 | 1.0885 | 0.019385
2015-09-23 17:00 | 13.9067 | 13.68 | 0.22667 | 0 | 0.16773 | 92.6463 | 90.4332 | -0.43318 | 92.616 | 92.4821 | 0 | 10.26 | 0.2 | 0 | 0.69533 | 10.9553 | 2.3 | 2.6424 | 1.0894 | 0.0097868
2015-09-23 18:00 | 0.24 | 0.24 | 0 | 0 | 0.15151 | 107.6502 | 93.7729 | -3.7729 | 107.2554 | 106.8121 | 0 | 0.18 | 0.2 | 0 | 0.012 | 0.192 | 2.7 | 2.706 | 1.0892 | 0.00017148
2015-09-23 19:00 | 0.16 | 0.16 | 0 | 0 | 0.1353 | 122.654 | 96.8564 | -6.8564 | 122.0045 | 121.0235 | 0 | 0.12 | 0.2 | 0 | 0.008 | 0.128 | 3.1 | 3.104 | 1.0876 | 0.00011415
2015-09-23 20:00 | 0.08 | 0.08 | 0 | 0 | 0.11909 | 137.6578 | 99.4777 | -9.4777 | 136.9311 | 134.9392 | 0 | 0.06 | 0.2 | 0 | 0.004 | 0.064 | 3.2 | 3.202 | 1.0872 | 5.7056e-05
2015-09-23 21:00 | 0 | 0 | 0 | 0 | 0.10287 | 152.6616 | 101.4539 | -11.4539 | 152.0581 | 148.1162 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.4 | 3.4 | 1.0864 | 0
2015-09-23 22:00 | 0 | 0 | 0 | 0 | 0.086658 | 167.6655 | 102.6408 | -12.6408 | 167.3541 | 159.0598 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0844 | 0
2015-09-23 23:00 | 0 | 0 | 0 | 0 | 0.070443 | 182.6693 | 102.9485 | -12.9485 | -177.261 | 162.7611 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0876 | 0
2015-09-24 | 0 | 0 | 0 | 0 | 0.054228 | -162.3269 | 102.3541 | -12.3541 | -161.8936 | 155.6517 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.088 | 0
2015-09-24 01:00 | 0 | 0 | 0 | 0 | 0.038012 | -147.3231 | 100.9048 | -10.9048 | -146.6447 | 143.6004 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.09 | 0
2015-09-24 02:00 | 0 | 0 | 0 | 0 | 0.021795 | -132.3192 | 98.7116 | -8.7116 | -131.5796 | 130.0792 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.0892 | 0
2015-09-24 03:00 | 0 | 0 | 0 | 0 | 0.0055786 | -117.3154 | 95.9346 | -5.9346 | -116.7115 | 116.0329 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0868 | 0
2015-09-24 04:00 | 8.7733 | 7.0767 | 1.6967 | 0 | -0.010639 | -102.3116 | 92.7666 | -2.7666 | -102.0014 | 101.7711 | 0 | 5.3075 | 0.2 | 0 | 0.43867 | 5.7462 | 2.7 | 2.8796 | 1.0885 | 0.0051288
2015-09-24 05:00 | 17.5467 | 14.1533 | 3.3933 | 0 | -0.026856 | -87.3078 | 89.4192 | 0.58076 | -87.371 | 87.4329 | 0 | 10.615 | 0.2 | 0 | 0.87733 | 11.4923 | 2.6 | 2.9591 | 1.0882 | 0.010255
2015-09-24 06:00 | 26.32 | 21.23 | 5.09 | 75.0543 | -0.043075 | -72.304 | 86.1114 | 3.8886 | -72.7231 | 73.1111 | 21.8046 | 15.9225 | 0.2 | 0 | 1.316 | 39.0431 | 2.5 | 3.7201 | 1.0851 | 0.03474
2015-09-24 07:00 | 47.0733 | 40.56 | 6.5133 | 53.9071 | -0.059293 | -57.3002 | 83.0603 | 6.9397 | -57.9648 | 58.9075 | 27.8388 | 30.42 | 0.2 | 0 | 2.3537 | 60.6125 | 2.1 | 3.9941 | 1.084 | 0.053878
2015-09-24 08:00 | 67.8267 | 59.89 | 7.9367 | 47.9483 | -0.075512 | -42.2963 | 80.4722 | 9.5278 | -43.0297 | 45.001 | 33.904 | 44.9175 | 0.2 | 0 | 3.3913 | 82.2128 | 2.1 | 4.6691 | 1.0813 | 0.072897
2015-09-24 09:00 | 88.58 | 79.22 | 9.36 | 47.0701 | -0.091732 | -27.2925 | 78.5301 | 11.4699 | -27.8966 | 31.8396 | 39.9874 | 59.415 | 0.2 | 0 | 4.429 | 103.8314 | 2.4 | 5.6447 | 1.0774 | 0.091733
2015-09-24 10:00 | 90.4867 | 81.5433 | 8.9433 | 40.9278 | -0.10795 | -12.2887 | 77.3782 | 12.6218 | -12.598 | 20.9315 | 38.2269 | 61.1575 | 0.2 | 0 | 4.5243 | 103.9087 | 2 | 5.2471 | 1.079 | 0.091937
2015-09-24 11:00 | 92.3933 | 83.8667 | 8.5267 | 38.21 | -0.12417 | 2.7151 | 77.1057 | 12.8943 | 2.7854 | 17.2989 | 36.4816 | 62.9 | 0.2 | 0 | 4.6197 | 104.0013 | 1.9 | 5.15 | 1.0794 | 0.092052
2015-09-24 12:00 | 94.3 | 86.19 | 8.11 | 38.177 | -0.14039 | 17.7189 | 77.7351 | 12.2649 | 18.1469 | 24.4417 | 34.7557 | 64.6425 | 0.2 | 0 | 4.715 | 104.1132 | 2.1 | 5.3535 | 1.0786 | 0.092082
2015-09-24 13:00 | 73.26 | 67.83 | 5.43 | 29.0275 | -0.15661 | 32.7227 | 79.2185 | 10.7815 | 33.3866 | 36.4979 | 23.3346 | 50.8725 | 0.2 | 0 | 3.663 | 77.8701 | 2.5 | 4.9334 | 1.0803 | 0.068979
2015-09-24 14:00 | 52.22 | 49.47 | 2.75 | 18.4862 | -0.17284 | 47.7265 | 81.4449 | 8.5551 | 48.4403 | 50.0208 | 11.8775 | 37.1025 | 0.2 | 0 | 2.611 | 51.591 | 2 | 3.6122 | 1.0856 | 0.045924
2015-09-24 15:00 | 31.18 | 31.11 | 0.07 | 0.69921 | -0.18906 | 62.7303 | 84.2544 | 5.7456 | 63.2964 | 64.0701 | 0.30575 | 23.3325 | 0.2 | 0 | 1.559 | 25.1972 | 1.9 | 2.6874 | 1.0893 | 0.022506
2015-09-24 16:00 | 20.8067 | 20.76 | 0.046667 | 0 | -0.20528 | 77.7341 | 87.4541 | 2.5459 | 77.9955 | 78.337 | 0 | 15.57 | 0.2 | 0 | 1.0403 | 16.6103 | 1.8 | 2.3191 | 1.0907 | 0.014856
2015-09-24 17:00 | 10.4333 | 10.41 | 0.023333 | 0 | -0.2215 | 92.7379 | 90.833 | -0.83303 | 92.6176 | 92.6833 | 0 | 7.8075 | 0.2 | 0 | 0.52167 | 8.3292 | 2 | 2.2603 | 1.091 | 0.0074512
2015-09-24 18:00 | 0.06 | 0.06 | 0 | 0 | -0.23772 | 107.7417 | 94.1727 | -4.1727 | 107.261 | 107.018 | 0 | 0.045 | 0.2 | 0 | 0.003 | 0.048 | 2.2 | 2.2015 | 1.0912 | 4.2949e-05
2015-09-24 19:00 | 0.04 | 0.04 | 0 | 0 | -0.25395 | 122.7455 | 97.2559 | -7.2559 | 122.02 | 121.242 | 0 | 0.03 | 0.2 | 0 | 0.002 | 0.032 | 1.8 | 1.801 | 1.0928 | 2.8675e-05
2015-09-24 20:00 | 0.02 | 0.02 | 0 | 0 | -0.27017 | 137.7493 | 99.8764 | -9.8764 | 136.962 | 135.1829 | 0 | 0.015 | 0.2 | 0 | 0.001 | 0.016 | 1.5 | 1.5005 | 1.094 | 1.4353e-05
2015-09-24 21:00 | 0 | 0 | 0 | 0 | -0.2864 | 152.7531 | 101.8507 | -11.8507 | 152.109 | 148.4073 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-09-24 22:00 | 0 | 0 | 0 | 0 | -0.30262 | 167.7569 | 103.0341 | -13.0341 | 167.4281 | 159.431 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0944 | 0
2015-09-24 23:00 | 0 | 0 | 0 | 0 | -0.31884 | 182.7607 | 103.3368 | -13.3368 | -177.1628 | 163.1316 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.0948 | 0
2015-09-25 | 0 | 0 | 0 | 0 | -0.33507 | -162.2355 | 102.736 | -12.736 | -161.7722 | 155.8615 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.0948 | 0
2015-09-25 01:00 | 0 | 0 | 0 | 0 | -0.35129 | -147.2317 | 101.2798 | -11.2798 | -146.503 | 143.711 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0936 | 0
2015-09-25 02:00 | 0 | 0 | 0 | 0 | -0.36752 | -132.2279 | 99.08 | -9.08 | -131.4219 | 130.1423 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.0948 | 0
2015-09-25 03:00 | 0 | 0 | 0 | 0 | -0.38375 | -117.2242 | 96.2975 | -6.2975 | -116.5427 | 116.0724 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.096 | 0
2015-09-25 04:00 | 11.27 | 7.1333 | 4.1367 | 0 | -0.39997 | -102.2204 | 93.1262 | -3.1262 | -101.8263 | 101.7997 | 0 | 5.35 | 0.2 | 0 | 0.5635 | 5.9135 | 0.4 | 0.5848 | 1.0977 | 0.0053226
2015-09-25 05:00 | 22.54 | 14.2667 | 8.2733 | 0 | -0.4162 | -87.2166 | 89.778 | 0.22197 | -87.1944 | 87.4595 | 0 | 10.7 | 0.2 | 0 | 1.127 | 11.827 | -0.2 | 0.16959 | 1.0993 | 0.010661
2015-09-25 06:00 | 33.81 | 21.4 | 12.41 | 201.6672 | -0.43243 | -72.2128 | 86.472 | 3.528 | -72.5499 | 73.1435 | 58.4785 | 16.05 | 0.2 | 0 | 1.6905 | 76.219 | -0.6 | 1.7818 | 1.0929 | 0.068304
2015-09-25 07:00 | 57.2733 | 42.3933 | 14.88 | 129.9534 | -0.44865 | -57.209 | 83.4251 | 6.5749 | -57.7998 | 58.9556 | 67.0173 | 31.795 | 0.2 | 0 | 2.8637 | 101.676 | 0.7 | 3.8774 | 1.0845 | 0.090419
2015-09-25 08:00 | 80.7367 | 63.3867 | 17.35 | 109.023 | -0.46488 | -42.2053 | 80.843 | 9.157 | -42.8779 | 45.0806 | 76.9823 | 47.54 | 0.2 | 0 | 4.0368 | 128.5592 | 1.6 | 5.6175 | 1.0775 | 0.11359
2015-09-25 09:00 | 104.2 | 84.38 | 19.82 | 103.0204 | -0.48111 | -27.2015 | 78.9078 | 11.0922 | -27.7624 | 31.9822 | 87.3832 | 63.285 | 0.2 | 0 | 5.21 | 155.8782 | 0.4 | 5.2712 | 1.0789 | 0.13791
2015-09-25 10:00 | 105.6567 | 90.45 | 15.2067 | 71.7424 | -0.49734 | -12.1977 | 77.7626 | 12.2374 | -12.4853 | 21.2016 | 66.8864 | 67.8375 | 0.2 | 0 | 5.2828 | 140.0068 | 0.9 | 5.2752 | 1.0789 | 0.12386
2015-09-25 11:00 | 107.1133 | 96.52 | 10.5933 | 48.9286 | -0.51356 | 2.8061 | 77.4961 | 12.5039 | 2.8742 | 17.6977 | 46.613 | 72.39 | 0.2 | 0 | 5.3557 | 124.3586 | 1.5 | 5.3862 | 1.0785 | 0.10997
2015-09-25 12:00 | 108.57 | 102.59 | 5.98 | 29.0725 | -0.52979 | 17.8099 | 78.1299 | 11.8701 | 18.2117 | 24.7832 | 26.3949 | 76.9425 | 0.2 | 0 | 5.4285 | 108.7659 | 1.8 | 5.1989 | 1.0792 | 0.096252
2015-09-25 13:00 | 88.09 | 78.1333 | 9.9567 | 55.2409 | -0.54602 | 32.8136 | 79.6162 | 10.3838 | 33.4292 | 36.7705 | 44.2502 | 58.6 | 0.2 | 0 | 4.4045 | 107.2547 | 2.6 | 5.9517 | 1.0762 | 0.09465
2015-09-25 14:00 | 67.61 | 53.6767 | 13.9333 | 98.2142 | -0.56225 | 47.8174 | 81.8441 | 8.1559 | 48.4644 | 50.2548 | 62.7956 | 40.2575 | 0.2 | 0 | 3.3805 | 106.4336 | 2.5 | 5.826 | 1.0767 | 0.093969
2015-09-25 15:00 | 47.13 | 29.22 | 17.91 | 192.2327 | -0.57848 | 62.8212 | 84.6541 | 5.3459 | 63.307 | 64.2834 | 83.4136 | 21.915 | 0.2 | 0 | 2.3565 | 107.6851 | 2.1 | 5.4652 | 1.0781 | 0.095202
2015-09-25 16:00 | 31.44 | 19.49 | 11.95 | 0 | -0.59471 | 77.8249 | 87.8539 | 2.1461 | 77.9982 | 78.5402 | 0 | 14.6175 | 0.2 | 0 | 1.572 | 16.1895 | 2 | 2.5059 | 1.09 | 0.01447
2015-09-25 17:00 | 15.75 | 9.76 | 5.99 | 0 | -0.61094 | 92.8287 | 91.2329 | -1.2329 | 92.6183 | 92.8838 | 0 | 7.32 | 0.2 | 0 | 0.7875 | 8.1075 | 1.7 | 1.9534 | 1.0922 | 0.007261
2015-09-25 18:00 | 0.06 | 0.03 | 0.03 | 0 | -0.62717 | 107.8325 | 94.5725 | -4.5725 | 107.2658 | 107.2225 | 0 | 0.0225 | 0.2 | 0 | 0.003 | 0.0255 | 2 | 2.0008 | 1.092 | 2.2834e-05
2015-09-25 19:00 | 0.04 | 0.02 | 0.02 | 0 | -0.6434 | 122.8362 | 97.6555 | -7.6555 | 122.0347 | 121.4586 | 0 | 0.015 | 0.2 | 0 | 0.002 | 0.017 | 1.9 | 1.9005 | 1.0924 | 1.5228e-05
2015-09-25 20:00 | 0.02 | 0.01 | 0.01 | 0 | -0.65963 | 137.84 | 100.2751 | -10.2751 | 136.9922 | 135.4241 | 0 | 0.0075 | 0.2 | 0 | 0.001 | 0.0085 | 1.9 | 1.9003 | 1.0924 | 7.614e-06
2015-09-25 21:00 | 0 | 0 | 0 | 0 | -0.67586 | 152.8437 | 102.2475 | -12.2475 | 152.1592 | 148.6958 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0912 | 0
2015-09-25 22:00 | 0 | 0 | 0 | 0 | -0.69209 | 167.8475 | 103.4276 | -13.4276 | 167.5015 | 159.8007 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0916 | 0
2015-09-25 23:00 | 0 | 0 | 0 | 0 | -0.70832 | 182.8513 | 103.7252 | -13.7252 | -177.0651 | 163.5011 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0924 | 0
2015-09-26 | 0 | 0 | 0 | 0 | -0.72455 | -162.145 | 103.1181 | -13.1181 | -161.6513 | 156.0675 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0912 | 0
2015-09-26 01:00 | 0 | 0 | 0 | 0 | -0.74078 | -147.1412 | 101.6549 | -11.6549 | -146.3618 | 143.8188 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0932 | 0
2015-09-26 02:00 | 0 | 0 | 0 | 0 | -0.75701 | -132.1375 | 99.4485 | -9.4485 | -131.2648 | 130.2039 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-09-26 03:00 | 0 | 0 | 0 | 0 | -0.77324 | -117.1337 | 96.6607 | -6.6607 | -116.3744 | 116.1113 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0936 | 0
2015-09-26 04:00 | 8.4333 | 5.84 | 2.5933 | 0 | -0.78947 | -102.13 | 93.4861 | -3.4861 | -101.6518 | 101.8287 | 0 | 4.38 | 0.2 | 0 | 0.42167 | 4.8017 | 1.4 | 1.5501 | 1.0938 | 0.0043067
2015-09-26 05:00 | 16.8667 | 11.68 | 5.1867 | 0 | -0.8057 | -87.1262 | 90.1372 | -0.13717 | -87.0187 | 87.487 | 0 | 8.76 | 0.2 | 0 | 0.84333 | 9.6033 | 1.3 | 1.6001 | 1.0936 | 0.0086118
2015-09-26 06:00 | 25.3 | 17.52 | 7.78 | 140.8205 | -0.82194 | -72.1225 | 86.8329 | 3.1671 | -72.3777 | 73.1776 | 40.7542 | 13.14 | 0.2 | 0 | 1.265 | 55.1592 | 1.9 | 3.6237 | 1.0855 | 0.049098
2015-09-26 07:00 | 58.6833 | 31.2433 | 27.44 | 253.6769 | -0.83817 | -57.1187 | 83.7902 | 6.2098 | -57.6359 | 59.0062 | 130.6298 | 23.4325 | 0.2 | 0 | 2.9342 | 156.9965 | 1.8 | 6.7061 | 1.0732 | 0.13816
2015-09-26 08:00 | 92.0667 | 44.9667 | 47.1 | 308.3606 | -0.8544 | -42.115 | 81.2141 | 8.7859 | -42.7272 | 45.1638 | 217.4198 | 33.725 | 0.2 | 0 | 4.6033 | 255.7481 | 1.8 | 9.7921 | 1.0608 | 0.22247
2015-09-26 09:00 | 125.45 | 58.69 | 66.76 | 359.0942 | -0.87063 | -27.1113 | 79.2857 | 10.7143 | -27.6295 | 32.1295 | 304.0983 | 44.0175 | 0.2 | 0 | 6.2725 | 354.3883 | 2.4 | 13.4746 | 1.0461 | 0.304
2015-09-26 10:00 | 120.5633 | 72.78 | 47.7833 | 232.6404 | -0.88686 | -12.1075 | 78.1473 | 11.8527 | -12.3739 | 21.4762 | 216.4881 | 54.585 | 0.2 | 0 | 6.0282 | 277.1013 | 1.6 | 10.2594 | 1.059 | 0.24062
2015-09-26 11:00 | 115.6767 | 86.87 | 28.8067 | 137.2749 | -0.90309 | 2.8962 | 77.8866 | 12.1134 | 2.9619 | 18.0965 | 130.4846 | 65.1525 | 0.2 | 0 | 5.7838 | 201.4209 | 1.7 | 7.9944 | 1.068 | 0.1764
2015-09-26 12:00 | 110.79 | 100.96 | 9.83 | 49.4112 | -0.91933 | 17.9 | 78.5249 | 11.4751 | 18.2754 | 25.1259 | 44.7358 | 75.72 | 0.2 | 0 | 5.5395 | 125.9953 | 1.6 | 5.5374 | 1.0779 | 0.11136
2015-09-26 13:00 | 85.37 | 75.36 | 10.01 | 57.7248 | -0.93556 | 32.9037 | 80.0139 | 9.9861 | 33.4708 | 37.0443 | 46.0742 | 56.52 | 0.2 | 0 | 4.2685 | 106.8627 | 1.4 | 4.7395 | 1.081 | 0.094729
2015-09-26 14:00 | 59.95 | 49.76 | 10.19 | 75.4997 | -0.95179 | 47.9074 | 82.2433 | 7.7567 | 48.4876 | 50.4896 | 48.0343 | 37.32 | 0.2 | 0 | 2.9975 | 88.3518 | 1.2 | 3.961 | 1.0842 | 0.078545
2015-09-26 15:00 | 34.53 | 24.16 | 10.37 | 120.2728 | -0.96802 | 62.9111 | 85.0538 | 4.9462 | 63.3166 | 64.4969 | 51.7846 | 18.12 | 0.2 | 0 | 1.7265 | 71.6311 | 1.2 | 3.4385 | 1.0862 | 0.063803
2015-09-26 16:00 | 23.02 | 16.1067 | 6.9133 | 0 | -0.98426 | 77.9149 | 88.2537 | 1.7463 | 78 | 78.743 | 0 | 12.08 | 0.2 | 0 | 1.151 | 13.231 | 1.1 | 1.5135 | 1.0939 | 0.011869
2015-09-26 17:00 | 11.51 | 8.0533 | 3.4567 | 0 | -1.0005 | 92.9186 | 91.6327 | -1.6327 | 92.6181 | 93.0834 | 0 | 6.04 | 0.2 | 0 | 0.5755 | 6.6155 | 1.3 | 1.5067 | 1.094 | 0.0059345
2015-09-26 18:00 | 0 | 0 | 0 | 0 | -1.0167 | 107.9223 | 94.9723 | -4.9723 | 107.2696 | 107.4255 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0972 | 0
2015-09-26 19:00 | 0 | 0 | 0 | 0 | -1.033 | 122.9261 | 98.0551 | -8.0551 | 122.0485 | 121.6732 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-09-26 20:00 | 0 | 0 | 0 | 0 | -1.0492 | 137.9298 | 100.6739 | -10.6739 | 137.0215 | 135.6628 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-09-26 21:00 | 0 | 0 | 0 | 0 | -1.0654 | 152.9335 | 102.6444 | -12.6444 | 152.2086 | 148.9813 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-09-26 22:00 | 0 | 0 | 0 | 0 | -1.0817 | 167.9372 | 103.821 | -13.821 | 167.5741 | 160.1689 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-09-26 23:00 | 0 | 0 | 0 | 0 | -1.0979 | 182.9409 | 104.1137 | -14.1137 | -176.968 | 163.8694 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-09-27 | 0 | 0 | 0 | 0 | -1.1141 | -162.0554 | 103.5003 | -13.5003 | -161.5309 | 156.2695 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-09-27 01:00 | 0 | 0 | 0 | 0 | -1.1303 | -147.0516 | 102.0302 | -12.0302 | -146.2212 | 143.924 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-09-27 02:00 | 0 | 0 | 0 | 0 | -1.1466 | -132.0479 | 99.8172 | -9.8172 | -131.1082 | 130.2641 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-09-27 03:00 | 0 | 0 | 0 | 0 | -1.1628 | -117.0442 | 97.0241 | -7.0241 | -116.2068 | 116.1499 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.1032 | 0
2015-09-27 04:00 | 6.5133 | 6.4633 | 0.05 | 0 | -1.179 | -102.0405 | 93.8463 | -3.8463 | -101.4781 | 101.858 | 0 | 4.8475 | 0.2 | 0 | 0.32567 | 5.1732 | -0.7 | -0.53834 | 1.1022 | 0.0046753
2015-09-27 05:00 | 13.0267 | 12.9267 | 0.1 | 0 | -1.1953 | -87.0368 | 90.4966 | -0.4966 | -86.8438 | 87.5157 | 0 | 9.695 | 0.2 | 0 | 0.65133 | 10.3463 | -0.2 | 0.12332 | 1.0995 | 0.0093282
2015-09-27 06:00 | 19.54 | 19.39 | 0.15 | 0 | -1.2115 | -72.0331 | 87.1942 | 2.8058 | -72.2064 | 73.2135 | 0 | 14.5425 | 0.2 | 0 | 0.977 | 15.5195 | 0 | 0.48498 | 1.0981 | 0.013974
2015-09-27 07:00 | 49.33 | 36.11 | 13.22 | 129.8292 | -1.2277 | -57.0294 | 84.1557 | 5.8443 | -57.4732 | 59.0594 | 66.7517 | 27.0825 | 0.2 | 0 | 2.4665 | 96.3007 | -0.3 | 2.7094 | 1.0892 | 0.086007
2015-09-27 08:00 | 79.12 | 52.83 | 26.29 | 179.6565 | -1.244 | -42.0257 | 81.5854 | 8.4146 | -42.5777 | 45.2504 | 126.4799 | 39.6225 | 0.2 | 0 | 3.956 | 170.0584 | -0.2 | 5.1143 | 1.0795 | 0.15054
2015-09-27 09:00 | 108.91 | 69.55 | 39.36 | 219.3692 | -1.2602 | -27.022 | 79.6638 | 10.3362 | -27.4979 | 32.2815 | 185.4622 | 52.1625 | 0.2 | 0 | 5.4455 | 243.0702 | 0.7 | 8.2959 | 1.0668 | 0.21264
2015-09-27 10:00 | 112.5633 | 68.9133 | 43.65 | 219.5479 | -1.2764 | -12.0183 | 78.5322 | 11.4678 | -12.2638 | 21.755 | 203.911 | 51.685 | 0.2 | 0 | 5.6282 | 261.2242 | 0.2 | 8.3633 | 1.0665 | 0.22846
2015-09-27 11:00 | 116.2167 | 68.2767 | 47.94 | 235.9528 | -1.2927 | 2.9854 | 78.2772 | 11.7228 | 3.0483 | 18.4952 | 223.7659 | 51.2075 | 0.2 | 0 | 5.8108 | 280.7843 | 0.5 | 9.2745 | 1.0629 | 0.24473
2015-09-27 12:00 | 119.87 | 67.64 | 52.23 | 271.7717 | -1.3089 | 17.9891 | 78.9198 | 11.0802 | 18.3379 | 25.4695 | 245.3595 | 50.73 | 0.2 | 0 | 5.9935 | 302.083 | 1 | 10.4401 | 1.0582 | 0.26213
2015-09-27 13:00 | 90.2433 | 53.8833 | 36.36 | 218.2867 | -1.3251 | 32.9928 | 80.4116 | 9.5884 | 33.5113 | 37.3193 | 173.5968 | 40.4125 | 0.2 | 0 | 4.5122 | 218.5215 | 0.9 | 7.7288 | 1.0691 | 0.19157
2015-09-27 14:00 | 60.6167 | 40.1267 | 20.49 | 159.9983 | -1.3414 | 47.9965 | 82.6423 | 7.3577 | 48.5097 | 50.725 | 101.286 | 30.095 | 0.2 | 0 | 3.0308 | 134.4118 | 1.2 | 5.4004 | 1.0784 | 0.11886
2015-09-27 15:00 | 30.99 | 26.37 | 4.62 | 58.2806 | -1.3576 | 63.0002 | 85.4533 | 4.5467 | 63.3253 | 64.7105 | 24.897 | 19.7775 | 0.2 | 0 | 1.5495 | 46.224 | 1.6 | 3.0445 | 1.0878 | 0.041232
2015-09-27 16:00 | 20.66 | 17.58 | 3.08 | 0 | -1.3738 | 78.0038 | 88.6533 | 1.3467 | 78.0008 | 78.9453 | 0 | 13.185 | 0.2 | 0 | 1.033 | 14.218 | 1.8 | 2.2443 | 1.091 | 0.01272
2015-09-27 17:00 | 10.33 | 8.79 | 1.54 | 0 | -1.3901 | 93.0075 | 92.0323 | -2.0323 | 92.6169 | 93.2819 | 0 | 6.5925 | 0.2 | 0 | 0.5165 | 7.109 | 1.7 | 1.9222 | 1.0923 | 0.0063675
2015-09-27 18:00 | 0 | 0 | 0 | 0 | -1.4063 | 108.0112 | 95.3719 | -5.3719 | 107.2725 | 107.6269 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.09 | 0
2015-09-27 19:00 | 0 | 0 | 0 | 0 | -1.4225 | 123.0149 | 98.4544 | -8.4544 | 122.0614 | 121.8856 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0916 | 0
2015-09-27 20:00 | 0 | 0 | 0 | 0 | -1.4388 | 138.0186 | 101.0724 | -11.0724 | 137.0498 | 135.8986 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.088 | 0
2015-09-27 21:00 | 0 | 0 | 0 | 0 | -1.455 | 153.0222 | 103.0411 | -13.0411 | 152.2571 | 149.2637 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0908 | 0
2015-09-27 22:00 | 0 | 0 | 0 | 0 | -1.4712 | 168.0259 | 104.2144 | -14.2144 | 167.646 | 160.5353 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.088 | 0
2015-09-27 23:00 | 0 | 0 | 0 | 0 | -1.4874 | 183.0296 | 104.5021 | -14.5021 | -176.8717 | 164.2364 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0876 | 0
2015-09-28 | 0 | 0 | 0 | 0 | -1.5037 | -161.9667 | 103.8825 | -13.8825 | -161.4112 | 156.4676 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0888 | 0
2015-09-28 01:00 | 0 | 0 | 0 | 0 | -1.5199 | -146.9631 | 102.4056 | -12.4056 | -146.0813 | 144.0266 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.088 | 0
2015-09-28 02:00 | 0 | 0 | 0 | 0 | -1.5361 | -131.9594 | 100.186 | -10.186 | -130.9523 | 130.323 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0884 | 0
2015-09-28 03:00 | 0 | 0 | 0 | 0 | -1.5524 | -116.9557 | 97.3877 | -7.3877 | -116.0399 | 116.188 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.088 | 0
2015-09-28 04:00 | 6.1167 | 3.8067 | 2.31 | 0 | -1.5686 | -101.9521 | 94.2067 | -4.2067 | -101.3054 | 101.8877 | 0 | 2.855 | 0.2 | 0 | 0.30583 | 3.1608 | 3.1 | 3.1988 | 1.0872 | 0.0028179
2015-09-28 05:00 | 12.2333 | 7.6133 | 4.62 | 0 | -1.5848 | -86.9484 | 90.8562 | -0.85624 | -86.67 | 87.5454 | 0 | 5.71 | 0.2 | 0 | 0.61167 | 6.3217 | 3.1 | 3.2976 | 1.0868 | 0.0056338
2015-09-28 06:00 | 18.35 | 11.42 | 6.93 | 0 | -1.6011 | -71.9448 | 87.5557 | 2.4443 | -72.0364 | 73.2513 | 0 | 8.565 | 0.2 | 0 | 0.9175 | 9.4825 | 3.4 | 3.6963 | 1.0852 | 0.0084382
2015-09-28 07:00 | 40.84 | 17.2433 | 23.5967 | 247.1501 | -1.6173 | -56.9411 | 84.5213 | 5.4787 | -57.3117 | 59.1152 | 126.8656 | 12.9325 | 0.2 | 0 | 2.042 | 141.8401 | 3.9 | 8.3325 | 1.0667 | 0.12406
2015-09-28 08:00 | 63.33 | 23.0667 | 40.2633 | 287.766 | -1.6335 | -41.9374 | 81.957 | 8.043 | -42.4296 | 45.3407 | 202.2678 | 17.3 | 0.2 | 0 | 3.1665 | 222.7343 | 4.2 | 11.1604 | 1.0554 | 0.19275
2015-09-28 09:00 | 85.82 | 28.89 | 56.93 | 329.218 | -1.6497 | -26.9338 | 80.0421 | 9.9579 | -27.3676 | 32.4381 | 277.8507 | 21.6675 | 0.2 | 0 | 4.291 | 303.8092 | 4.3 | 13.794 | 1.0448 | 0.26029
2015-09-28 10:00 | 74.9633 | 35.9733 | 38.99 | 202.8301 | -1.666 | -11.9301 | 78.9171 | 11.0829 | -12.1551 | 22.0379 | 188.0105 | 26.98 | 0.2 | 0 | 3.7482 | 218.7386 | 4.7 | 11.5356 | 1.0539 | 0.18903
2015-09-28 11:00 | 64.1067 | 43.0567 | 21.05 | 107.1263 | -1.6822 | 3.0735 | 78.6678 | 11.3322 | 3.1333 | 18.8937 | 101.3544 | 32.2925 | 0.2 | 0 | 3.2053 | 136.8523 | 4.8 | 9.0766 | 1.0637 | 0.11937
2015-09-28 12:00 | 53.25 | 50.14 | 3.11 | 16.773 | -1.6984 | 18.0772 | 79.3146 | 10.6854 | 18.3991 | 25.8138 | 15.0993 | 37.605 | 0.2 | 0 | 2.6625 | 55.3668 | 4.8 | 6.5302 | 1.0739 | 0.048755
2015-09-28 13:00 | 40.37 | 38.2833 | 2.0867 | 13.064 | -1.7147 | 33.0808 | 80.809 | 9.191 | 33.5505 | 37.5952 | 10.3512 | 28.7125 | 0.2 | 0 | 2.0185 | 41.0822 | 5.8 | 7.0838 | 1.0717 | 0.036102
2015-09-28 14:00 | 27.49 | 26.4267 | 1.0633 | 8.7764 | -1.7309 | 48.0844 | 83.0411 | 6.9589 | 48.5307 | 50.9608 | 5.5278 | 19.82 | 0.2 | 0 | 1.3745 | 26.7223 | 5.6 | 6.4351 | 1.0743 | 0.02354
2015-09-28 15:00 | 14.61 | 14.57 | 0.04 | 0.55307 | -1.7471 | 63.0881 | 85.8525 | 4.1475 | 63.3329 | 64.9239 | 0.2344 | 10.9275 | 0.2 | 0 | 0.7305 | 11.8924 | 4.9 | 5.2716 | 1.0789 | 0.010521
2015-09-28 16:00 | 9.74 | 9.7133 | 0.026667 | 0 | -1.7633 | 78.0917 | 89.0526 | 0.94738 | 78.0005 | 79.1469 | 0 | 7.285 | 0.2 | 0 | 0.487 | 7.772 | 3.8 | 4.0429 | 1.0838 | 0.0069073
2015-09-28 17:00 | 4.87 | 4.8567 | 0.013333 | 0 | -1.7796 | 93.0954 | 92.4316 | -2.4316 | 92.6147 | 93.4791 | 0 | 3.6425 | 0.2 | 0 | 0.2435 | 3.886 | 3.9 | 4.0214 | 1.0839 | 0.0034539
2015-09-28 18:00 | 0 | 0 | 0 | 0 | -1.7958 | 108.099 | 95.7711 | -5.7711 | 107.2743 | 107.8266 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0816 | 0
2015-09-28 19:00 | 0 | 0 | 0 | 0 | -1.812 | 123.1026 | 98.8535 | -8.8535 | 122.0731 | 122.0957 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5 | 5 | 1.08 | 0
2015-09-28 20:00 | 0 | 0 | 0 | 0 | -1.8282 | 138.1063 | 101.4708 | -11.4708 | 137.0771 | 136.1315 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.086 | 0
2015-09-28 21:00 | 0 | 0 | 0 | 0 | -1.8445 | 153.1099 | 103.4376 | -13.4376 | 152.3046 | 149.5427 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0884 | 0
2015-09-28 22:00 | 0 | 0 | 0 | 0 | -1.8607 | 168.1135 | 104.6077 | -14.6077 | 167.7169 | 160.8997 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.086 | 0
2015-09-28 23:00 | 0 | 0 | 0 | 0 | -1.8769 | 183.1171 | 104.8905 | -14.8905 | -176.7762 | 164.602 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0844 | 0
2015-09-29 | 0 | 0 | 0 | 0 | -1.8931 | -161.8792 | 104.2646 | -14.2646 | -161.2923 | 156.6615 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0868 | 0
2015-09-29 01:00 | 0 | 0 | 0 | 0 | -1.9094 | -146.8756 | 102.7809 | -12.7809 | -145.9421 | 144.1265 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.086 | 0
2015-09-29 02:00 | 0 | 0 | 0 | 0 | -1.9256 | -131.872 | 100.5549 | -10.5549 | -130.7973 | 130.3806 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.3 | 4.3 | 1.0828 | 0
2015-09-29 03:00 | 0 | 0 | 0 | 0 | -1.9418 | -116.8684 | 97.7513 | -7.7513 | -115.874 | 116.2259 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0816 | 0
2015-09-29 04:00 | 3.03 | 3.03 | 0 | 0 | -1.958 | -101.8648 | 94.5671 | -4.5671 | -101.1336 | 101.9179 | 0 | 2.2725 | 0.2 | 0 | 0.1515 | 2.424 | 4.1 | 4.1757 | 1.0833 | 0.0021532
2015-09-29 05:00 | 6.06 | 6.06 | 0 | 0 | -1.9743 | -86.8612 | 91.216 | -1.216 | -86.4973 | 87.5764 | 0 | 4.545 | 0.2 | 0 | 0.303 | 4.848 | 4.3 | 4.4515 | 1.0822 | 0.0043021
2015-09-29 06:00 | 9.09 | 9.09 | 0 | 0 | -1.9905 | -71.8576 | 87.9174 | 2.0826 | -71.8676 | 73.2909 | 0 | 6.8175 | 0.2 | 0 | 0.4545 | 7.272 | 4 | 4.2272 | 1.0831 | 0.0064585
2015-09-29 07:00 | 20.9633 | 20.9633 | 0 | 0 | -2.0067 | -56.854 | 84.8872 | 5.1128 | -57.1516 | 59.1737 | 0 | 15.7225 | 0.2 | 0 | 1.0482 | 16.7707 | 4.2 | 4.7241 | 1.0811 | 0.014867
2015-09-29 08:00 | 32.8367 | 32.8367 | 0 | 0 | -2.0229 | -41.8503 | 82.3286 | 7.6714 | -42.283 | 45.4346 | 0 | 24.6275 | 0.2 | 0 | 1.6418 | 26.2693 | 4.3 | 5.1209 | 1.0795 | 0.023254
2015-09-29 09:00 | 44.71 | 44.71 | 0 | 0 | -2.0391 | -26.8467 | 80.4204 | 9.5796 | -27.2389 | 32.5992 | 0 | 33.5325 | 0.2 | 0 | 2.2355 | 35.768 | 4.2 | 5.3178 | 1.0787 | 0.031639
2015-09-29 10:00 | 45.8367 | 45.8367 | 0 | 0 | -2.0554 | -11.8431 | 79.3019 | 10.6981 | -12.0479 | 22.3247 | 0 | 34.3775 | 0.2 | 0 | 2.2918 | 36.6693 | 5 | 6.1459 | 1.0754 | 0.032337
2015-09-29 11:00 | 46.9633 | 46.9633 | 0 | 0 | -2.0716 | 3.1605 | 79.0583 | 10.9417 | 3.2169 | 19.292 | 0 | 35.2225 | 0.2 | 0 | 2.3482 | 37.5707 | 5.1 | 6.2741 | 1.0749 | 0.033116
2015-09-29 12:00 | 48.09 | 48.09 | 0 | 0 | -2.0878 | 18.164 | 79.7091 | 10.2909 | 18.459 | 26.1586 | 0 | 36.0675 | 0.2 | 0 | 2.4045 | 38.472 | 4.3 | 5.5023 | 1.078 | 0.034007
2015-09-29 13:00 | 36.56 | 36.56 | 0 | 0 | -2.104 | 33.1676 | 81.2062 | 8.7938 | 33.5885 | 37.8718 | 0 | 27.42 | 0.2 | 0 | 1.828 | 29.248 | 4.1 | 5.014 | 1.0799 | 0.025901
2015-09-29 14:00 | 25.03 | 25.03 | 0 | 0 | -2.1202 | 48.1712 | 83.4395 | 6.5605 | 48.5505 | 51.1969 | 0 | 18.7725 | 0.2 | 0 | 1.2515 | 20.024 | 4.2 | 4.8258 | 1.0807 | 0.017745
2015-09-29 15:00 | 13.5 | 13.5 | 0 | 0 | -2.1365 | 63.1748 | 86.2514 | 3.7486 | 63.3393 | 65.137 | 0 | 10.125 | 0.2 | 0 | 0.675 | 10.8 | 5 | 5.3375 | 1.0787 | 0.0095525
2015-09-29 16:00 | 9 | 9 | 0 | 0 | -2.1527 | 78.1784 | 89.4515 | 0.54851 | 77.9991 | 79.3477 | 0 | 6.75 | 0.2 | 0 | 0.45 | 7.2 | 4.2 | 4.425 | 1.0823 | 0.0063899
2015-09-29 17:00 | 4.5 | 4.5 | 0 | 0 | -2.1689 | 93.182 | 92.8304 | -2.8304 | 92.6113 | 93.675 | 0 | 3.375 | 0.2 | 0 | 0.225 | 3.6 | 5.9 | 6.0125 | 1.0759 | 0.0031762
2015-09-29 18:00 | 0 | 0 | 0 | 0 | -2.1851 | 108.1856 | 96.17 | -6.17 | 107.2749 | 108.0243 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5 | 4.5 | 1.082 | 0
2015-09-29 19:00 | 0 | 0 | 0 | 0 | -2.2013 | 123.1892 | 99.2522 | -9.2522 | 122.0837 | 122.3033 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.2 | 4.2 | 1.0832 | 0
2015-09-29 20:00 | 0 | 0 | 0 | 0 | -2.2175 | 138.1927 | 101.8687 | -11.8687 | 137.1032 | 136.3613 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0872 | 0
2015-09-29 21:00 | 0 | 0 | 0 | 0 | -2.2338 | 153.1963 | 103.8338 | -13.8338 | 152.351 | 149.8181 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0896 | 0
2015-09-29 22:00 | 0 | 0 | 0 | 0 | -2.25 | 168.1999 | 105.0006 | -15.0006 | 167.7868 | 161.2618 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.0892 | 0
2015-09-29 23:00 | 0 | 0 | 0 | 0 | -2.2662 | 183.2035 | 105.2786 | -15.2786 | -176.6816 | 164.966 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.8 | 3.8 | 1.0848 | 0
2015-09-30 | 0 | 0 | 0 | 0 | -2.2824 | -161.793 | 104.6466 | -14.6466 | -161.1743 | 156.8514 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0896 | 0
2015-09-30 01:00 | 0 | 0 | 0 | 0 | -2.2986 | -146.7894 | 103.1561 | -13.1561 | -145.8038 | 144.2238 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0904 | 0
2015-09-30 02:00 | 0 | 0 | 0 | 0 | -2.3148 | -131.7858 | 100.9237 | -10.9237 | -130.6432 | 130.437 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.088 | 0
2015-09-30 03:00 | 0 | 0 | 0 | 0 | -2.331 | -116.7823 | 98.115 | -8.115 | -115.7091 | 116.2636 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.4 | 3.4 | 1.0864 | 0
2015-09-30 04:00 | 3 | 2.8833 | 0.11667 | 0 | -2.3473 | -101.7787 | 94.9277 | -4.9277 | -100.9629 | 101.9487 | 0 | 2.1625 | 0.2 | 0 | 0.15 | 2.3125 | 3.8 | 3.8723 | 1.0845 | 0.0020565
2015-09-30 05:00 | 6 | 5.7667 | 0.23333 | 0 | -2.3635 | -86.7752 | 91.5759 | -1.5759 | -86.3258 | 87.6086 | 0 | 4.325 | 0.2 | 0 | 0.3 | 4.625 | 3.4 | 3.5445 | 1.0858 | 0.004118
2015-09-30 06:00 | 9 | 8.65 | 0.35 | 0 | -2.3797 | -71.7716 | 88.2791 | 1.7209 | -71.7001 | 73.3326 | 0 | 6.4875 | 0.2 | 0 | 0.45 | 6.9375 | 3.3 | 3.5168 | 1.0859 | 0.0061776
2015-09-30 07:00 | 20.9567 | 20.58 | 0.37667 | 4.5516 | -2.3959 | -56.7681 | 85.253 | 4.747 | -56.993 | 59.2349 | 2.3282 | 15.435 | 0.2 | 0 | 1.0478 | 18.811 | 2.9 | 3.4878 | 1.086 | 0.016752
2015-09-30 08:00 | 32.9133 | 32.51 | 0.40333 | 3.1744 | -2.4121 | -41.7645 | 82.7003 | 7.2997 | -42.138 | 45.5321 | 2.2237 | 24.3825 | 0.2 | 0 | 1.6457 | 28.2518 | 2.7 | 3.5829 | 1.0857 | 0.025151
2015-09-30 09:00 | 44.87 | 44.44 | 0.43 | 2.6891 | -2.4283 | -26.761 | 80.7986 | 9.2014 | -27.1118 | 32.7649 | 2.2613 | 33.33 | 0.2 | 0 | 2.2435 | 37.8348 | 2.3 | 3.4823 | 1.0861 | 0.033695
2015-09-30 10:00 | 45.94 | 45.4333 | 0.50667 | 2.83 | -2.4445 | -11.7574 | 79.6866 | 10.3134 | -11.9423 | 22.6152 | 2.6124 | 34.075 | 0.2 | 0 | 2.297 | 38.9844 | 1.7 | 2.9183 | 1.0883 | 0.034791
2015-09-30 11:00 | 47.01 | 46.4267 | 0.58333 | 3.1855 | -2.4607 | 3.2461 | 79.4485 | 10.5515 | 3.299 | 19.6898 | 2.9993 | 34.82 | 0.2 | 0 | 2.3505 | 40.1698 | 1 | 2.2553 | 1.091 | 0.035936
2015-09-30 12:00 | 48.08 | 47.42 | 0.66 | 3.8401 | -2.4769 | 18.2497 | 80.1034 | 9.8966 | 18.5173 | 26.5038 | 3.4365 | 35.565 | 0.2 | 0 | 2.404 | 41.4055 | 1 | 2.2939 | 1.0908 | 0.037036
2015-09-30 13:00 | 37.29 | 36.11 | 1.18 | 8.0804 | -2.4931 | 33.2532 | 81.6029 | 8.3971 | 33.6252 | 38.1491 | 6.3545 | 27.0825 | 0.2 | 0 | 1.8645 | 35.3015 | 0.9 | 2.0032 | 1.092 | 0.03161
2015-09-30 14:00 | 26.5 | 24.8 | 1.7 | 15.8361 | -2.5094 | 48.2568 | 83.8374 | 6.1626 | 48.569 | 51.4331 | 9.8727 | 18.6 | 0.2 | 0 | 1.325 | 29.7977 | 0 | 0.93118 | 1.0963 | 0.026786
2015-09-30 15:00 | 15.71 | 13.49 | 2.22 | 37.9873 | -2.5256 | 63.2603 | 86.6497 | 3.3503 | 63.3445 | 65.3498 | 15.8436 | 10.1175 | 0.2 | 0 | 0.7855 | 26.7466 | -1.1 | -0.26417 | 1.1011 | 0.024149
2015-09-30 16:00 | 10.4733 | 8.9933 | 1.48 | 0 | -2.5418 | 78.2638 | 89.8498 | 0.15019 | 77.9964 | 79.5475 | 0 | 6.745 | 0.2 | 0 | 0.52367 | 7.2687 | -2 | -1.7729 | 1.1071 | 0.0065986
2015-09-30 17:00 | 5.2367 | 4.4967 | 0.74 | 0 | -2.558 | 93.2673 | 93.2287 | -3.2287 | 92.6066 | 93.8695 | 0 | 3.3725 | 0.2 | 0 | 0.26183 | 3.6343 | -2.4 | -2.2864 | 1.1091 | 0.0033054
2015-09-30 18:00 | 0 | 0 | 0 | 0 | -2.5742 | 108.2709 | 96.5682 | -6.5682 | 107.2742 | 108.2201 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-09-30 19:00 | 0 | 0 | 0 | 0 | -2.5904 | 123.2744 | 99.6503 | -9.6503 | 122.093 | 122.5083 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-09-30 20:00 | 0 | 0 | 0 | 0 | -2.6066 | 138.2779 | 102.2662 | -12.2662 | 137.1281 | 136.5878 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-09-30 21:00 | 0 | 0 | 0 | 0 | -2.6228 | 153.2814 | 104.2296 | -14.2296 | 152.3963 | 150.0896 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.112 | 0
2015-09-30 22:00 | 0 | 0 | 0 | 0 | -2.639 | 168.285 | 105.3933 | -15.3933 | 167.8556 | 161.6214 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.112 | 0
2015-09-30 23:00 | 0 | 0 | 0 | 0 | -2.6552 | 183.2885 | 105.6664 | -15.6664 | -176.5882 | 165.3283 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-10-01 | 0 | 0 | 0 | 0 | -2.6714 | -161.708 | 105.0283 | -15.0283 | -161.0574 | 157.0371 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.112 | 0
2015-10-01 01:00 | 0 | 0 | 0 | 0 | -2.6876 | -146.7045 | 103.5312 | -13.5312 | -145.6665 | 144.3187 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.112 | 0
2015-10-01 02:00 | 0 | 0 | 0 | 0 | -2.7038 | -131.701 | 101.2923 | -11.2923 | -130.4901 | 130.4923 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.11 | 0
2015-10-01 03:00 | 0 | 0 | 0 | 0 | -2.72 | -116.6975 | 98.4785 | -8.4785 | -115.5452 | 116.3011 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-10-01 04:00 | 3.3667 | 2.69 | 0.67667 | 0 | -2.7362 | -101.694 | 95.2881 | -5.2881 | -100.7935 | 101.9801 | 0 | 2.0175 | 0.2 | 0 | 0.16833 | 2.1858 | -2.7 | -2.6317 | 1.1105 | 0.0019905
2015-10-01 05:00 | 6.7333 | 5.38 | 1.3533 | 0 | -2.7524 | -86.6905 | 91.9357 | -1.9357 | -86.1557 | 87.6422 | 0 | 4.035 | 0.2 | 0 | 0.33667 | 4.3717 | -3 | -2.8634 | 1.1115 | 0.0039843
2015-10-01 06:00 | 10.1 | 8.07 | 2.03 | 0 | -2.7686 | -71.687 | 88.6409 | 1.3591 | -71.5342 | 73.3762 | 0 | 6.0525 | 0.2 | 0 | 0.505 | 6.5575 | -2.9 | -2.6951 | 1.1108 | 0.0059728
2015-10-01 07:00 | 29.1733 | 20.11 | 9.0633 | 118.6459 | -2.7848 | -56.6835 | 85.6189 | 4.3811 | -56.836 | 59.299 | 60.5757 | 15.0825 | 0.2 | 0 | 1.4587 | 77.1168 | -2.5 | -0.090099 | 1.1004 | 0.069582
2015-10-01 08:00 | 48.2467 | 32.15 | 16.0967 | 133.4454 | -2.801 | -41.68 | 83.0719 | 6.9281 | -41.9946 | 45.6332 | 93.3115 | 24.1125 | 0.2 | 0 | 2.4123 | 119.8364 | -2.3 | 1.4449 | 1.0942 | 0.10752
2015-10-01 09:00 | 67.32 | 44.19 | 23.13 | 150.7956 | -2.8172 | -26.6765 | 81.1768 | 8.8232 | -26.9865 | 32.935 | 126.5609 | 33.1425 | 0.2 | 0 | 3.366 | 163.0694 | -2.2 | 2.8959 | 1.0884 | 0.14554
2015-10-01 10:00 | 76.2867 | 46.72 | 29.5667 | 171.4745 | -2.8334 | -11.673 | 80.0711 | 9.9289 | -11.8384 | 22.9092 | 157.9492 | 35.04 | 0.2 | 0 | 3.8143 | 196.8035 | -2.1 | 4.0501 | 1.0838 | 0.1749
2015-10-01 11:00 | 85.2533 | 49.25 | 36.0033 | 204.0706 | -2.8495 | 3.3305 | 79.8384 | 10.1616 | 3.3794 | 20.0871 | 191.6573 | 36.9375 | 0.2 | 0 | 4.2627 | 232.8575 | -2.7 | 4.5768 | 1.0817 | 0.20654
2015-10-01 12:00 | 94.22 | 51.78 | 42.44 | 257.0641 | -2.8657 | 18.3339 | 80.4972 | 9.5028 | 18.5742 | 26.8492 | 229.3522 | 38.835 | 0.2 | 0 | 4.711 | 272.8982 | -2.5 | 6.0281 | 1.0759 | 0.24076
2015-10-01 13:00 | 68.8533 | 38.9267 | 29.9267 | 215.0096 | -2.8819 | 33.3374 | 81.9992 | 8.0008 | 33.6604 | 38.4268 | 168.4391 | 29.195 | 0.2 | 0 | 3.4427 | 201.0768 | -2.2 | 4.0836 | 1.0837 | 0.17868
2015-10-01 14:00 | 43.4867 | 26.0733 | 17.4133 | 173.3502 | -2.8981 | 48.3409 | 84.2348 | 5.7652 | 48.5861 | 51.6694 | 107.5116 | 19.555 | 0.2 | 0 | 2.1743 | 129.2409 | -2.6 | 1.4388 | 1.0942 | 0.11597
2015-10-01 15:00 | 18.12 | 13.22 | 4.9 | 0 | -2.9143 | 63.3444 | 87.0474 | 2.9526 | 63.3483 | 65.562 | 0 | 9.915 | 0.2 | 0 | 0.906 | 10.821 | -2.1 | -1.7618 | 1.107 | 0.0098231
2015-10-01 16:00 | 12.08 | 8.8133 | 3.2667 | 0 | -2.9305 | 78.3478 | 90.2475 | -0.24748 | 77.9924 | 79.7463 | 0 | 6.61 | 0.2 | 0 | 0.604 | 7.214 | -2.3 | -2.0746 | 1.1083 | 0.0065561
2015-10-01 17:00 | 6.04 | 4.4067 | 1.6333 | 0 | -2.9467 | 93.3513 | 93.6263 | -3.6263 | 92.6007 | 94.0623 | 0 | 3.305 | 0.2 | 0 | 0.302 | 3.607 | -2.5 | -2.3873 | 1.1095 | 0.0032818
2015-10-01 18:00 | 0 | 0 | 0 | 0 | -2.9629 | 108.3548 | 96.9659 | -6.9659 | 107.2723 | 108.4136 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.3 | -3.3 | 1.1132 | 0
2015-10-01 19:00 | 0 | 0 | 0 | 0 | -2.9791 | 123.3582 | 100.0478 | -10.0478 | 122.101 | 122.7105 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.8 | -2.8 | 1.1112 | 0
2015-10-01 20:00 | 0 | 0 | 0 | 0 | -2.9952 | 138.3617 | 102.6631 | -12.6631 | 137.1517 | 136.8108 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.8 | -2.8 | 1.1112 | 0
2015-10-01 21:00 | 0 | 0 | 0 | 0 | -3.0114 | 153.3652 | 104.6249 | -14.6249 | 152.4402 | 150.3571 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-10-01 22:00 | 0 | 0 | 0 | 0 | -3.0276 | 168.3686 | 105.7854 | -15.7854 | 167.9232 | 161.9782 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.112 | 0
2015-10-01 23:00 | 0 | 0 | 0 | 0 | -3.0438 | 183.3721 | 106.0539 | -16.0539 | -176.4959 | 165.6887 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-10-02 | 0 | 0 | 0 | 0 | -3.06 | -161.6245 | 105.4097 | -15.4097 | -160.9415 | 157.2185 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-10-02 01:00 | 0 | 0 | 0 | 0 | -3.0762 | -146.621 | 103.9059 | -13.9059 | -145.5304 | 144.411 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-10-02 02:00 | 0 | 0 | 0 | 0 | -3.0923 | -131.6176 | 101.6608 | -11.6608 | -130.3382 | 130.5465 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-10-02 03:00 | 0 | 0 | 0 | 0 | -3.1085 | -116.6141 | 98.8419 | -8.8419 | -115.3827 | 116.3386 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-10-02 04:00 | 2.03 | 1.9233 | 0.10667 | 0 | -3.1247 | -101.6107 | 95.6485 | -5.6485 | -100.6254 | 102.0123 | 0 | 1.4425 | 0.2 | 0 | 0.1015 | 1.544 | -2.1 | -2.0518 | 1.1082 | 0.0014031
2015-10-02 05:00 | 4.06 | 3.8467 | 0.21333 | 0 | -3.1409 | -86.6073 | 92.2955 | -2.2955 | -85.9871 | 87.6772 | 0 | 2.885 | 0.2 | 0 | 0.203 | 3.088 | -2 | -1.9035 | 1.1076 | 0.0028047
2015-10-02 06:00 | 6.09 | 5.77 | 0.32 | 0 | -3.1571 | -71.6038 | 89.0026 | 0.99745 | -71.3699 | 73.422 | 0 | 4.3275 | 0.2 | 0 | 0.3045 | 4.632 | -2.2 | -2.0553 | 1.1082 | 0.0042093
2015-10-02 07:00 | 16.79 | 15.4233 | 1.3667 | 19.5175 | -3.1732 | -56.6004 | 85.9847 | 4.0153 | -56.6807 | 59.3658 | 9.9452 | 11.5675 | 0.2 | 0 | 0.8395 | 22.3522 | -1.9 | -1.2015 | 1.1048 | 0.02025
2015-10-02 08:00 | 27.49 | 25.0767 | 2.4133 | 21.1353 | -3.1894 | -41.597 | 83.4434 | 6.5566 | -41.853 | 45.738 | 14.7512 | 18.8075 | 0.2 | 0 | 1.3745 | 34.9332 | -1.9 | -0.80834 | 1.1032 | 0.031602
2015-10-02 09:00 | 38.19 | 34.73 | 3.46 | 23.559 | -3.2056 | -26.5935 | 81.5547 | 8.4453 | -26.8629 | 33.1095 | 19.7337 | 26.0475 | 0.2 | 0 | 1.9095 | 47.6907 | -2 | -0.50967 | 1.102 | 0.043097
2015-10-02 10:00 | 40.3867 | 36.0833 | 4.3033 | 25.9522 | -3.2218 | -11.5901 | 80.4553 | 9.5447 | -11.7363 | 23.2064 | 23.8524 | 27.0625 | 0.2 | 0 | 2.0193 | 52.9343 | -2.1 | -0.4458 | 1.1018 | 0.047824
2015-10-02 11:00 | 42.5833 | 37.4367 | 5.1467 | 30.3225 | -3.2379 | 3.4133 | 80.2278 | 9.7722 | 3.4581 | 20.4838 | 28.4052 | 28.0775 | 0.2 | 0 | 2.1292 | 58.6119 | -2.3 | -0.46838 | 1.1019 | 0.052958
2015-10-02 12:00 | 44.78 | 38.79 | 5.99 | 37.8346 | -3.2541 | 18.4167 | 80.8906 | 9.1094 | 18.6294 | 27.1946 | 33.6523 | 29.0925 | 0.2 | 0 | 2.239 | 64.9838 | -2.3 | -0.26926 | 1.1011 | 0.058673
2015-10-02 13:00 | 33 | 28.7633 | 4.2367 | 32.0119 | -3.2703 | 33.4202 | 82.3948 | 7.6052 | 33.694 | 38.7047 | 24.9814 | 21.5725 | 0.2 | 0 | 1.65 | 48.2039 | -2.2 | -0.69363 | 1.1028 | 0.04359
2015-10-02 14:00 | 21.22 | 18.7367 | 2.4833 | 26.5425 | -3.2864 | 48.4236 | 84.6315 | 5.3685 | 48.6017 | 51.9054 | 16.3757 | 14.0525 | 0.2 | 0 | 1.061 | 31.4892 | -3 | -2.016 | 1.1081 | 0.028611
2015-10-02 15:00 | 9.44 | 8.71 | 0.73 | 0 | -3.3026 | 63.427 | 87.4443 | 2.5557 | 63.3507 | 65.7735 | 0 | 6.5325 | 0.2 | 0 | 0.472 | 7.0045 | -3.5 | -3.2811 | 1.1131 | 0.0063934
2015-10-02 16:00 | 6.2933 | 5.8067 | 0.48667 | 0 | -3.3188 | 78.4304 | 90.6444 | -0.64438 | 77.9871 | 79.9438 | 0 | 4.355 | 0.2 | 0 | 0.31467 | 4.6697 | -3.7 | -3.5541 | 1.1142 | 0.0042665
2015-10-02 17:00 | 3.1467 | 2.9033 | 0.24333 | 0 | -3.3349 | 93.4338 | 94.0231 | -4.0231 | 92.5933 | 94.2534 | 0 | 2.1775 | 0.2 | 0 | 0.15733 | 2.3348 | -3.7 | -3.627 | 1.1145 | 0.0021338
2015-10-02 18:00 | 0 | 0 | 0 | 0 | -3.3511 | 108.4372 | 97.3627 | -7.3627 | 107.2689 | 108.6049 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.9 | -3.9 | 1.1156 | 0
2015-10-02 19:00 | 0 | 0 | 0 | 0 | -3.3673 | 123.4406 | 100.4446 | -10.4446 | 122.1075 | 122.9097 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.1 | -4.1 | 1.1164 | 0
2015-10-02 20:00 | 0 | 0 | 0 | 0 | -3.3834 | 138.444 | 103.0593 | -13.0593 | 137.1738 | 137.0301 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1184 | 0
2015-10-02 21:00 | 0 | 0 | 0 | 0 | -3.3996 | 153.4474 | 105.0195 | -15.0195 | 152.4827 | 150.6204 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.7 | -4.7 | 1.1188 | 0
2015-10-02 22:00 | 0 | 0 | 0 | 0 | -3.4158 | 168.4508 | 106.177 | -16.177 | 167.9894 | 162.332 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.9 | -4.9 | 1.1196 | 0
2015-10-02 23:00 | 0 | 0 | 0 | 0 | -3.4319 | 183.4542 | 106.4408 | -16.4408 | -176.4049 | 166.047 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.2 | -5.2 | 1.1208 | 0
2015-10-03 | 0 | 0 | 0 | 0 | -3.4481 | -161.5424 | 105.7907 | -15.7907 | -160.8269 | 157.3956 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.6 | -5.6 | 1.1224 | 0
2015-10-03 01:00 | 0 | 0 | 0 | 0 | -3.4642 | -146.5391 | 104.2803 | -14.2803 | -145.3955 | 144.501 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.2 | -5.2 | 1.1208 | 0
2015-10-03 02:00 | 0 | 0 | 0 | 0 | -3.4804 | -131.5357 | 102.0289 | -12.0289 | -130.1875 | 130.5997 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.2 | -5.2 | 1.1208 | 0
2015-10-03 03:00 | 0 | 0 | 0 | 0 | -3.4966 | -116.5323 | 99.2051 | -9.2051 | -115.2215 | 116.3761 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.5 | -6.5 | 1.126 | 0
2015-10-03 04:00 | 4.0233 | 2.65 | 1.3733 | 0 | -3.5127 | -101.5289 | 96.0087 | -6.0087 | -100.4588 | 102.0452 | 0 | 1.9875 | 0.2 | 0 | 0.20117 | 2.1887 | -5.8 | -5.7316 | 1.1229 | 0.0020153
2015-10-03 05:00 | 8.0467 | 5.3 | 2.7467 | 0 | -3.5289 | -86.5256 | 92.6552 | -2.6552 | -85.82 | 87.7136 | 0 | 3.975 | 0.2 | 0 | 0.40233 | 4.3773 | -4.9 | -4.7632 | 1.1191 | 0.0040167
2015-10-03 06:00 | 12.07 | 7.95 | 4.12 | 0 | -3.545 | -71.5222 | 89.3641 | 0.6359 | -71.2072 | 73.4699 | 0 | 5.9625 | 0.2 | 0 | 0.6035 | 6.566 | -4.4 | -4.1948 | 1.1168 | 0.0060129
2015-10-03 07:00 | 35.3 | 20.2667 | 15.0333 | 236.1671 | -3.5612 | -56.5188 | 86.3503 | 3.6497 | -56.5272 | 59.4356 | 120.0926 | 15.2 | 0.2 | 0 | 1.765 | 137.0576 | -4 | 0.28305 | 1.0989 | 0.1235
2015-10-03 08:00 | 58.53 | 32.5833 | 25.9467 | 240.8149 | -3.5773 | -41.5155 | 83.8146 | 6.1854 | -41.7133 | 45.8465 | 167.7475 | 24.4375 | 0.2 | 0 | 2.9265 | 195.1115 | -4 | 2.0972 | 1.0916 | 0.17465
2015-10-03 09:00 | 81.76 | 44.9 | 36.86 | 262.6417 | -3.5935 | -26.5121 | 81.9323 | 8.0677 | -26.7413 | 33.2883 | 219.5472 | 33.675 | 0.2 | 0 | 4.088 | 257.3102 | -3.2 | 4.8409 | 1.0806 | 0.22801
2015-10-03 10:00 | 85.9567 | 45.9367 | 40.02 | 251.3679 | -3.6096 | -11.5087 | 80.839 | 9.161 | -11.636 | 23.5068 | 230.5076 | 34.4525 | 0.2 | 0 | 4.2978 | 269.2579 | -3 | 5.4143 | 1.0783 | 0.23809
2015-10-03 11:00 | 90.1533 | 46.9733 | 43.18 | 264.8471 | -3.6258 | 3.4946 | 80.6168 | 9.3832 | 3.535 | 20.8797 | 247.4548 | 35.23 | 0.2 | 0 | 4.5077 | 287.1925 | -2.9 | 6.0748 | 1.0757 | 0.25333
2015-10-03 12:00 | 94.35 | 48.01 | 46.34 | 305.7735 | -3.6419 | 18.498 | 81.2832 | 8.7168 | 18.6829 | 27.5398 | 271.1264 | 36.0075 | 0.2 | 0 | 4.7175 | 311.8514 | -2.5 | 7.2454 | 1.071 | 0.27388
2015-10-03 13:00 | 67.3333 | 35.3567 | 31.9767 | 254.7705 | -3.6581 | 33.5013 | 82.7897 | 7.2103 | 33.726 | 38.9828 | 198.042 | 26.5175 | 0.2 | 0 | 3.3667 | 227.9262 | -2.5 | 4.6227 | 1.0815 | 0.20213
2015-10-03 14:00 | 40.3167 | 22.7033 | 17.6133 | 203.2011 | -3.6742 | 48.5047 | 85.0274 | 4.9726 | 48.6159 | 52.1412 | 124.7082 | 17.0275 | 0.2 | 0 | 2.0158 | 143.7515 | -2.7 | 1.7922 | 1.0928 | 0.12882
2015-10-03 15:00 | 13.3 | 10.05 | 3.25 | 0 | -3.6904 | 63.508 | 87.8404 | 2.1596 | 63.3516 | 65.9841 | 0 | 7.5375 | 0.2 | 0 | 0.665 | 8.2025 | -2.3 | -2.0437 | 1.1082 | 0.0074536
2015-10-03 16:00 | 8.8667 | 6.7 | 2.1667 | 0 | -3.7065 | 78.5114 | 91.0404 | -1.0404 | 77.9802 | 80.14 | 0 | 5.025 | 0.2 | 0 | 0.44333 | 5.4683 | -2.6 | -2.4291 | 1.1097 | 0.004976
2015-10-03 17:00 | 4.4333 | 3.35 | 1.0833 | 0 | -3.7227 | 93.5147 | 94.419 | -4.419 | 92.5844 | 94.4425 | 0 | 2.5125 | 0.2 | 0 | 0.22167 | 2.7342 | -2.5 | -2.4146 | 1.1097 | 0.0024879
2015-10-03 18:00 | 0 | 0 | 0 | 0 | -3.7388 | 108.518 | 97.7587 | -7.7587 | 107.2639 | 108.7937 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-10-03 19:00 | 0 | 0 | 0 | 0 | -3.7549 | 123.5214 | 100.8405 | -10.8405 | 122.1125 | 123.1059 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.8 | -2.8 | 1.1112 | 0
2015-10-03 20:00 | 0 | 0 | 0 | 0 | -3.7711 | 138.5247 | 103.4547 | -13.4547 | 137.1944 | 137.2457 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.8 | -2.8 | 1.1112 | 0
2015-10-03 21:00 | 0 | 0 | 0 | 0 | -3.7872 | 153.528 | 105.4134 | -15.4134 | 152.5237 | 150.8792 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-10-03 22:00 | 0 | 0 | 0 | 0 | -3.8033 | 168.5313 | 106.5679 | -16.5679 | 168.0541 | 162.6824 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-10-03 23:00 | 0 | 0 | 0 | 0 | -3.8195 | 183.5347 | 106.8272 | -16.8272 | -176.3152 | 166.403 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-10-04 | 0 | 0 | 0 | 0 | -3.8356 | -161.462 | 106.1712 | -16.1712 | -160.7137 | 157.5684 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-10-04 01:00 | 0 | 0 | 0 | 0 | -3.8517 | -146.4587 | 104.6543 | -14.6543 | -145.2619 | 144.5885 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-10-04 02:00 | 0 | 0 | 0 | 0 | -3.8679 | -131.4554 | 102.3967 | -12.3967 | -130.0383 | 130.6521 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-10-04 03:00 | 0 | 0 | 0 | 0 | -3.884 | -116.4521 | 99.568 | -9.568 | -115.0617 | 116.4137 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.112 | 0
2015-10-04 04:00 | 3.5033 | 2.2767 | 1.2267 | 0 | -3.9001 | -101.4488 | 96.3687 | -6.3687 | -100.2937 | 102.0791 | 0 | 1.7075 | 0.2 | 0 | 0.17517 | 1.8827 | -2.6 | -2.5412 | 1.1102 | 0.0017139
2015-10-04 05:00 | 7.0067 | 4.5533 | 2.4533 | 0 | -3.9163 | -86.4455 | 93.0146 | -3.0146 | -85.6547 | 87.7517 | 0 | 3.415 | 0.2 | 0 | 0.35033 | 3.7653 | -3.1 | -2.9823 | 1.1119 | 0.0034332
2015-10-04 06:00 | 10.51 | 6.83 | 3.68 | 0 | -3.9324 | -71.4422 | 89.7254 | 0.27456 | -71.0464 | 73.52 | 0 | 5.1225 | 0.2 | 0 | 0.5255 | 5.648 | -2.3 | -2.1235 | 1.1085 | 0.0051338
2015-10-04 07:00 | 32.39 | 18.3967 | 13.9933 | 244.2542 | -3.9485 | -56.4389 | 86.7157 | 3.2843 | -56.3757 | 59.5082 | 123.9382 | 13.7975 | 0.2 | 0 | 1.6195 | 139.3552 | -2.1 | 2.2548 | 1.091 | 0.12467
2015-10-04 08:00 | 54.27 | 29.9633 | 24.3067 | 239.9321 | -3.9646 | -41.4356 | 84.1856 | 5.8144 | -41.5756 | 45.9587 | 166.7952 | 22.4725 | 0.2 | 0 | 2.7135 | 191.9812 | -1.9 | 4.0994 | 1.0836 | 0.17059
2015-10-04 09:00 | 76.15 | 41.53 | 34.62 | 258.7018 | -3.9808 | -26.4323 | 82.3095 | 7.6905 | -26.6216 | 33.4714 | 215.799 | 31.1475 | 0.2 | 0 | 3.8075 | 250.754 | -1.6 | 6.2361 | 1.0751 | 0.22105
2015-10-04 10:00 | 77.6933 | 42.26 | 35.4333 | 232.1948 | -3.9969 | -11.429 | 81.2223 | 8.7777 | -11.5378 | 23.8101 | 212.4323 | 31.695 | 0.2 | 0 | 3.8847 | 248.012 | -1.7 | 6.0504 | 1.0758 | 0.21878
2015-10-04 11:00 | 79.2367 | 42.99 | 36.2467 | 231.8344 | -4.013 | 3.5743 | 81.0051 | 8.9949 | 3.61 | 21.2747 | 216.0353 | 32.2425 | 0.2 | 0 | 3.9618 | 252.2396 | -1.7 | 6.1825 | 1.0753 | 0.22241
2015-10-04 12:00 | 80.78 | 43.72 | 37.06 | 255.9658 | -4.0291 | 18.5776 | 81.6752 | 8.3248 | 18.7346 | 27.8846 | 226.2459 | 32.79 | 0.2 | 0 | 4.039 | 263.0749 | -1.8 | 6.4211 | 1.0743 | 0.23175
2015-10-04 13:00 | 58.5367 | 32.4467 | 26.09 | 219.8249 | -4.0452 | 33.5808 | 83.1838 | 6.8162 | 33.7563 | 39.2607 | 170.2047 | 24.335 | 0.2 | 0 | 2.9268 | 197.4666 | -2.3 | 3.8708 | 1.0845 | 0.17561
2015-10-04 14:00 | 36.2933 | 21.1733 | 15.12 | 189.4509 | -4.0614 | 48.5841 | 85.4224 | 4.5776 | 48.6283 | 52.3765 | 115.6541 | 15.88 | 0.2 | 0 | 1.8147 | 133.3488 | -2.2 | 1.9671 | 1.0921 | 0.11942
2015-10-04 15:00 | 14.05 | 9.9 | 4.15 | 0 | -4.0775 | 63.5874 | 88.2356 | 1.7644 | 63.351 | 66.1938 | 0 | 7.425 | 0.2 | 0 | 0.7025 | 8.1275 | -1.9 | -1.646 | 1.1066 | 0.0073749
2015-10-04 16:00 | 9.3667 | 6.6 | 2.7667 | 0 | -4.0936 | 78.5907 | 91.4354 | -1.4354 | 77.9718 | 80.3347 | 0 | 4.95 | 0.2 | 0 | 0.46833 | 5.4183 | -1.7 | -1.5307 | 1.1061 | 0.0049145
2015-10-04 17:00 | 4.6833 | 3.3 | 1.3833 | 0 | -4.1097 | 93.5939 | 94.8139 | -4.8139 | 92.574 | 94.6297 | 0 | 2.475 | 0.2 | 0 | 0.23417 | 2.7092 | -1.9 | -1.8153 | 1.1073 | 0.0024598
2015-10-04 18:00 | 0 | 0 | 0 | 0 | -4.1258 | 108.5972 | 98.1536 | -8.1536 | 107.2574 | 108.9799 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-10-04 19:00 | 0 | 0 | 0 | 0 | -4.1419 | 123.6004 | 101.2355 | -11.2355 | 122.1159 | 123.2988 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-10-04 20:00 | 0 | 0 | 0 | 0 | -4.158 | 138.6037 | 103.8492 | -13.8492 | 137.2134 | 137.4573 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-10-04 21:00 | 0 | 0 | 0 | 0 | -4.1741 | 153.607 | 105.8064 | -15.8064 | 152.5632 | 151.1333 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-10-04 22:00 | 0 | 0 | 0 | 0 | -4.1903 | 168.6102 | 106.9581 | -16.9581 | 168.1173 | 163.0293 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.1084 | 0
2015-10-04 23:00 | 0 | 0 | 0 | 0 | -4.2064 | 183.6135 | 107.2129 | -17.2129 | -176.2271 | 166.7567 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-10-05 | 0 | 0 | 0 | 0 | -4.2225 | -161.3833 | 106.5511 | -16.5511 | -160.6019 | 157.7368 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.2 | -2.2 | 1.1088 | 0
2015-10-05 01:00 | 0 | 0 | 0 | 0 | -4.2386 | -146.3801 | 105.0278 | -15.0278 | -145.1298 | 144.6738 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.112 | 0
2015-10-05 02:00 | 0 | 0 | 0 | 0 | -4.2547 | -131.3768 | 102.7641 | -12.7641 | -129.8905 | 130.7035 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-10-05 03:00 | 0 | 0 | 0 | 0 | -4.2708 | -116.3736 | 99.9305 | -9.9305 | -114.9035 | 116.4514 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.2 | -4.2 | 1.1168 | 0
2015-10-05 04:00 | 2.92 | 2.0467 | 0.87333 | 0 | -4.2869 | -101.3704 | 96.7283 | -6.7283 | -100.1303 | 102.1138 | 0 | 1.535 | 0.2 | 0 | 0.146 | 1.681 | -3.8 | -3.7475 | 1.115 | 0.0015369
2015-10-05 05:00 | 5.84 | 4.0933 | 1.7467 | 0 | -4.303 | -86.3671 | 93.3737 | -3.3737 | -85.4911 | 87.7913 | 0 | 3.07 | 0.2 | 0 | 0.292 | 3.362 | -3.3 | -3.1949 | 1.1128 | 0.0030678
2015-10-05 06:00 | 8.76 | 6.14 | 2.62 | 0 | -4.3191 | -71.3639 | 90.0865 | -0.086476 | -70.8875 | 73.5724 | 0 | 4.605 | 0.2 | 0 | 0.438 | 5.043 | -4.4 | -4.2424 | 1.117 | 0.004619
2015-10-05 07:00 | 34.0833 | 17.72 | 16.3633 | 0 | -4.3351 | -56.3607 | 87.0808 | 2.9192 | -56.2261 | 59.5838 | 0 | 13.29 | 0.2 | 0 | 1.7042 | 14.9942 | -4.4 | -3.9314 | 1.1157 | 0.013718
2015-10-05 08:00 | 59.4067 | 29.3 | 30.1067 | 317.3458 | -4.3512 | -41.3575 | 84.5562 | 5.4438 | -41.44 | 46.0745 | 220.1498 | 21.975 | 0.2 | 0 | 2.9703 | 245.0952 | -4.5 | 3.1592 | 1.0874 | 0.21854
2015-10-05 09:00 | 84.73 | 40.88 | 43.85 | 344.4527 | -4.3673 | -26.3542 | 82.6862 | 7.3138 | -26.5041 | 33.6586 | 286.7067 | 30.66 | 0.2 | 0 | 4.2365 | 321.6032 | -3.3 | 6.7501 | 1.073 | 0.28297
2015-10-05 10:00 | 86.9267 | 41.8767 | 45.05 | 308.5652 | -4.3834 | -11.351 | 81.6049 | 8.3951 | -11.4416 | 24.1161 | 281.6334 | 31.4075 | 0.2 | 0 | 4.3463 | 317.3872 | -3.3 | 6.6184 | 1.0735 | 0.27939
2015-10-05 11:00 | 89.1233 | 42.8733 | 46.25 | 309.029 | -4.3995 | 3.6522 | 81.3926 | 8.6074 | 3.6829 | 21.6687 | 287.1912 | 32.155 | 0.2 | 0 | 4.4562 | 323.8024 | -2.4 | 7.7188 | 1.0691 | 0.28387
2015-10-05 12:00 | 91.32 | 43.87 | 47.45 | 343.7714 | -4.4156 | 18.6554 | 82.0663 | 7.9337 | 18.7844 | 28.229 | 302.8847 | 32.9025 | 0.2 | 0 | 4.566 | 340.3532 | -2.6 | 8.036 | 1.0679 | 0.29803
2015-10-05 13:00 | 64.76 | 32.1033 | 32.6567 | 291.9165 | -4.4317 | 33.6586 | 83.5769 | 6.4231 | 33.7849 | 39.5385 | 225.1253 | 24.0775 | 0.2 | 0 | 3.238 | 252.4408 | -2.2 | 5.6888 | 1.0772 | 0.22299
2015-10-05 14:00 | 38.2 | 20.3367 | 17.8633 | 244.8573 | -4.4478 | 48.6618 | 85.8163 | 4.1837 | 48.6391 | 52.6112 | 148.6825 | 15.2525 | 0.2 | 0 | 1.91 | 165.845 | -1.9 | 3.2827 | 1.0869 | 0.14781
2015-10-05 15:00 | 11.64 | 8.57 | 3.07 | 0 | -4.4639 | 63.665 | 88.6296 | 1.3704 | 63.3486 | 66.4024 | 0 | 6.4275 | 0.2 | 0 | 0.582 | 7.0095 | -2.2 | -1.981 | 1.1079 | 0.0063681
2015-10-05 16:00 | 7.76 | 5.7133 | 2.0467 | 0 | -4.4799 | 78.6682 | 91.8292 | -1.8292 | 77.9617 | 80.5277 | 0 | 4.285 | 0.2 | 0 | 0.388 | 4.673 | -1.9 | -1.754 | 1.107 | 0.0042419
2015-10-05 17:00 | 3.88 | 2.8567 | 1.0233 | 0 | -4.496 | 93.6714 | 95.2077 | -5.2077 | 92.5619 | 94.8147 | 0 | 2.1425 | 0.2 | 0 | 0.194 | 2.3365 | -2.3 | -2.227 | 1.1089 | 0.0021246
2015-10-05 18:00 | 0 | 0 | 0 | 0 | -4.5121 | 108.6746 | 98.5474 | -8.5474 | 107.2493 | 109.1634 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.2 | -2.2 | 1.1088 | 0
2015-10-05 19:00 | 0 | 0 | 0 | 0 | -4.5282 | 123.6777 | 101.6293 | -11.6293 | 122.1176 | 123.4884 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-10-05 20:00 | 0 | 0 | 0 | 0 | -4.5442 | 138.6809 | 104.2427 | -14.2427 | 137.2307 | 137.6648 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.1084 | 0
2015-10-05 21:00 | 0 | 0 | 0 | 0 | -4.5603 | 153.6841 | 106.1985 | -16.1985 | 152.6009 | 151.3825 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.1064 | 0
2015-10-05 22:00 | 0 | 0 | 0 | 0 | -4.5764 | 168.6873 | 107.3474 | -17.3474 | 168.1789 | 163.3724 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-10-05 23:00 | 0 | 0 | 0 | 0 | -4.5925 | 183.6904 | 107.5978 | -17.5978 | -176.1405 | 167.1079 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-10-06 | 0 | 0 | 0 | 0 | -4.6085 | -161.3064 | 106.9303 | -16.9303 | -160.4916 | 157.9008 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-10-06 01:00 | 0 | 0 | 0 | 0 | -4.6246 | -146.3032 | 105.4006 | -15.4006 | -144.9992 | 144.7568 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-10-06 02:00 | 0 | 0 | 0 | 0 | -4.6407 | -131.3001 | 103.1309 | -13.1309 | -129.7444 | 130.7542 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.1032 | 0
2015-10-06 03:00 | 0 | 0 | 0 | 0 | -4.6567 | -116.2969 | 100.2925 | -10.2925 | -114.747 | 116.4894 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.1048 | 0
2015-10-06 04:00 | 1.07 | 1.0333 | 0.036667 | 0 | -4.6728 | -101.2937 | 97.0875 | -7.0875 | -99.9687 | 102.1496 | 0 | 0.775 | 0.2 | 0 | 0.0535 | 0.8285 | -0.9 | -0.87411 | 1.1035 | 0.00074968
2015-10-06 05:00 | 2.14 | 2.0667 | 0.073333 | 0 | -4.6889 | -86.2906 | 93.7324 | -3.7324 | -85.3295 | 87.8326 | 0 | 1.55 | 0.2 | 0 | 0.107 | 1.657 | -0.6 | -0.54822 | 1.1022 | 0.0014976
2015-10-06 06:00 | 3.21 | 3.1 | 0.11 | 0 | -4.7049 | -71.2874 | 90.4471 | -0.44714 | -70.7306 | 73.6271 | 0 | 2.325 | 0.2 | 0 | 0.1605 | 2.4855 | -1 | -0.92233 | 1.1037 | 0.0022494
2015-10-06 07:00 | 14.26 | 12.13 | 2.13 | 0 | -4.721 | -56.2843 | 87.4454 | 2.5546 | -56.0787 | 59.6624 | 0 | 9.0975 | 0.2 | 0 | 0.713 | 9.8105 | -1.1 | -0.79342 | 1.1032 | 0.0088746
2015-10-06 08:00 | 25.31 | 21.16 | 4.15 | 46.9253 | -4.737 | -41.2812 | 84.9262 | 5.0738 | -41.3065 | 46.194 | 32.4826 | 15.87 | 0.2 | 0 | 1.2655 | 49.6181 | -0.8 | 0.75057 | 1.097 | 0.044633
2015-10-06 09:00 | 36.36 | 30.19 | 6.17 | 51.0806 | -4.7531 | -26.278 | 83.0623 | 6.9377 | -26.3887 | 33.8499 | 42.4224 | 22.6425 | 0.2 | 0 | 1.818 | 66.8829 | -0.8 | 1.2901 | 1.0948 | 0.060045
2015-10-06 10:00 | 35.0433 | 29.9667 | 5.0767 | 36.4178 | -4.7691 | -11.2749 | 81.9868 | 8.0132 | -11.3476 | 24.4247 | 33.1587 | 22.475 | 0.2 | 0 | 1.7522 | 57.3858 | -0.6 | 1.1933 | 1.0952 | 0.051537
2015-10-06 11:00 | 33.7267 | 29.7433 | 3.9833 | 27.8584 | -4.7852 | 3.7282 | 81.7794 | 8.2206 | 3.7539 | 22.0616 | 25.8186 | 22.3075 | 0.2 | 0 | 1.6863 | 49.8125 | -0.5 | 1.0566 | 1.0958 | 0.044758
2015-10-06 12:00 | 32.41 | 29.52 | 2.89 | 22.0139 | -4.8012 | 18.7314 | 82.4564 | 7.5436 | 18.8323 | 28.5727 | 19.3329 | 22.14 | 0.2 | 0 | 1.6205 | 43.0934 | -0.3 | 1.0467 | 1.0958 | 0.038722
2015-10-06 13:00 | 23.38 | 21.4367 | 1.9433 | 18.496 | -4.8173 | 33.7345 | 83.9689 | 6.0311 | 33.8116 | 39.8158 | 14.2069 | 16.0775 | 0.2 | 0 | 1.169 | 31.4534 | -0.3 | 0.68292 | 1.0973 | 0.028301
2015-10-06 14:00 | 14.35 | 13.3533 | 0.99667 | 15.0747 | -4.8333 | 48.7376 | 86.2091 | 3.7909 | 48.6482 | 52.8451 | 9.1047 | 10.015 | 0.2 | 0 | 0.7175 | 19.8372 | -0.5 | 0.11991 | 1.0995 | 0.017885
2015-10-06 15:00 | 5.32 | 5.27 | 0.05 | 0 | -4.8494 | 63.7407 | 89.0225 | 0.97755 | 63.3446 | 66.6097 | 0 | 3.9525 | 0.2 | 0 | 0.266 | 4.2185 | -0.6 | -0.46817 | 1.1019 | 0.0038116
2015-10-06 16:00 | 3.5467 | 3.5133 | 0.033333 | 0 | -4.8654 | 78.7439 | 92.2219 | -2.2219 | 77.9499 | 80.719 | 0 | 2.635 | 0.2 | 0 | 0.17733 | 2.8123 | -0.6 | -0.51211 | 1.102 | 0.0025414
2015-10-06 17:00 | 1.7733 | 1.7567 | 0.016667 | 0 | -4.8815 | 93.747 | 95.6002 | -5.6002 | 92.5481 | 94.9974 | 0 | 1.3175 | 0.2 | 0 | 0.088667 | 1.4062 | -0.5 | -0.45606 | 1.1018 | 0.0012705
2015-10-06 18:00 | 0 | 0 | 0 | 0 | -4.8975 | 108.7501 | 98.94 | -8.94 | 107.2393 | 109.3441 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.102 | 0
2015-10-06 19:00 | 0 | 0 | 0 | 0 | -4.9135 | 123.7532 | 102.022 | -12.022 | 122.1176 | 123.6745 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-10-06 20:00 | 0 | 0 | 0 | 0 | -4.9296 | 138.7563 | 104.635 | -14.635 | 137.2462 | 137.868 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-10-06 21:00 | 0 | 0 | 0 | 0 | -4.9456 | 153.7594 | 106.5895 | -16.5895 | 152.6369 | 151.6265 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-10-06 22:00 | 0 | 0 | 0 | 0 | -4.9617 | 168.7625 | 107.7357 | -17.7357 | 168.2387 | 163.7112 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-10-06 23:00 | 0 | 0 | 0 | 0 | -4.9777 | 183.7656 | 107.9818 | -17.9818 | -176.0557 | 167.4562 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-10-07 | 0 | 0 | 0 | 0 | -4.9937 | -161.2313 | 107.3087 | -17.3087 | -160.3831 | 158.0605 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-10-07 01:00 | 0 | 0 | 0 | 0 | -5.0097 | -146.2283 | 105.7728 | -15.7728 | -144.8704 | 144.8377 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-10-07 02:00 | 0 | 0 | 0 | 0 | -5.0258 | -131.2252 | 103.4971 | -13.4971 | -129.5999 | 130.8043 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0924 | 0
2015-10-07 03:00 | 0 | 0 | 0 | 0 | -5.0418 | -116.2221 | 100.6541 | -10.6541 | -114.5923 | 116.5277 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-10-07 04:00 | 1.6167 | 1.2567 | 0.36 | 0 | -5.0578 | -101.219 | 97.4462 | -7.4462 | -99.809 | 102.1865 | 0 | 0.9425 | 0.2 | 0 | 0.080833 | 1.0233 | 0.2 | 0.23198 | 1.0991 | 0.00092227
2015-10-07 05:00 | 3.2333 | 2.5133 | 0.72 | 0 | -5.0738 | -86.216 | 94.0907 | -4.0907 | -85.1698 | 87.8757 | 0 | 1.885 | 0.2 | 0 | 0.16167 | 2.0467 | 0.2 | 0.26396 | 1.0989 | 0.0018443
2015-10-07 06:00 | 4.85 | 3.77 | 1.08 | 0 | -5.0899 | -71.2129 | 90.8073 | -0.80735 | -70.5758 | 73.6842 | 0 | 2.8275 | 0.2 | 0 | 0.2425 | 3.07 | 1.2 | 1.2959 | 1.0948 | 0.0027561
2015-10-07 07:00 | 26.93 | 14.7367 | 12.1933 | 0 | -5.1059 | -56.2098 | 87.8096 | 2.1904 | -55.9334 | 59.744 | 0 | 11.0525 | 0.2 | 0 | 1.3465 | 12.399 | 2.2 | 2.5875 | 1.0897 | 0.011079
2015-10-07 08:00 | 49.01 | 25.7033 | 23.3067 | 284.1833 | -5.1219 | -41.2068 | 85.2957 | 4.7043 | -41.1754 | 46.3171 | 196.2758 | 19.2775 | 0.2 | 0 | 2.4505 | 218.0038 | 2.3 | 9.1126 | 1.0635 | 0.19012
2015-10-07 09:00 | 71.09 | 36.67 | 34.42 | 301.1849 | -5.1379 | -26.2037 | 83.4378 | 6.5622 | -26.2757 | 34.0452 | 249.5607 | 27.5025 | 0.2 | 0 | 3.5545 | 280.6177 | 1.1 | 9.8693 | 1.0605 | 0.24403
2015-10-07 10:00 | 71.31 | 37.2367 | 34.0733 | 256.5562 | -5.1539 | -11.2007 | 82.368 | 7.632 | -11.2558 | 24.7355 | 233.0169 | 27.9275 | 0.2 | 0 | 3.5655 | 264.5099 | 1.8 | 10.0659 | 1.0597 | 0.22985
2015-10-07 11:00 | 71.53 | 37.8033 | 33.7267 | 247.413 | -5.1699 | 3.8024 | 82.1652 | 7.8348 | 3.8226 | 22.4533 | 228.6569 | 28.3525 | 0.2 | 0 | 3.5765 | 260.5859 | 3 | 11.1433 | 1.0554 | 0.22552
2015-10-07 12:00 | 71.75 | 38.37 | 33.38 | 268.014 | -5.1859 | 18.8054 | 82.8455 | 7.1545 | 18.8781 | 28.9155 | 234.6017 | 28.7775 | 0.2 | 0 | 3.5875 | 266.9667 | 2.9 | 11.2427 | 1.055 | 0.23096
2015-10-07 13:00 | 50.81 | 27.7267 | 23.0833 | 234.8717 | -5.202 | 33.8085 | 84.3598 | 5.6402 | 33.8363 | 40.0925 | 179.6782 | 20.795 | 0.2 | 0 | 2.5405 | 203.0137 | 3.1 | 9.4442 | 1.0622 | 0.17683
2015-10-07 14:00 | 29.87 | 17.0833 | 12.7867 | 215.6459 | -5.218 | 48.8115 | 86.6007 | 3.3993 | 48.6554 | 53.0781 | 129.5441 | 12.8125 | 0.2 | 0 | 1.4935 | 143.8501 | 2.8 | 7.2953 | 1.0708 | 0.12631
2015-10-07 15:00 | 8.93 | 6.44 | 2.49 | 0 | -5.234 | 63.8145 | 89.414 | 0.58604 | 63.3388 | 66.8156 | 0 | 4.83 | 0.2 | 0 | 0.4465 | 5.2765 | 3.3 | 3.4649 | 1.0861 | 0.0046994
2015-10-07 16:00 | 5.9533 | 4.2933 | 1.66 | 0 | -5.25 | 78.8176 | 92.6131 | -2.6131 | 77.9364 | 80.9084 | 0 | 3.22 | 0.2 | 0 | 0.29767 | 3.5177 | 3.1 | 3.2099 | 1.0872 | 0.0031359
2015-10-07 17:00 | 2.9767 | 2.1467 | 0.83 | 0 | -5.266 | 93.8206 | 95.9914 | -5.9914 | 92.5325 | 95.1778 | 0 | 1.61 | 0.2 | 0 | 0.14883 | 1.7588 | 3.1 | 3.155 | 1.0874 | 0.0015683
2015-10-07 18:00 | 0 | 0 | 0 | 0 | -5.282 | 108.8236 | 99.3312 | -9.3312 | 107.2276 | 109.5218 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0876 | 0
2015-10-07 19:00 | 0 | 0 | 0 | 0 | -5.298 | 123.8267 | 102.4133 | -12.4133 | 122.1156 | 123.857 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0904 | 0
2015-10-07 20:00 | 0 | 0 | 0 | 0 | -5.314 | 138.8297 | 105.026 | -15.026 | 137.2598 | 138.0667 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0916 | 0
2015-10-07 21:00 | 0 | 0 | 0 | 0 | -5.33 | 153.8327 | 106.9794 | -16.9794 | 152.671 | 151.8653 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-10-07 22:00 | 0 | 0 | 0 | 0 | -5.3459 | 168.8357 | 108.1229 | -18.1229 | 168.2967 | 164.0456 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-10-07 23:00 | 0 | 0 | 0 | 0 | -5.3619 | 183.8387 | 108.3649 | -18.3649 | -175.9727 | 167.8017 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-10-08 | 0 | 0 | 0 | 0 | -5.3779 | -161.1583 | 107.6862 | -17.6862 | -160.2763 | 158.2156 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0924 | 0
2015-10-08 01:00 | 0 | 0 | 0 | 0 | -5.3939 | -146.1553 | 106.1442 | -16.1442 | -144.7433 | 144.9164 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0928 | 0
2015-10-08 02:00 | 0 | 0 | 0 | 0 | -5.4099 | -131.1523 | 103.8627 | -13.8627 | -129.4573 | 130.8537 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0912 | 0
2015-10-08 03:00 | 0 | 0 | 0 | 0 | -5.4259 | -116.1493 | 101.0149 | -11.0149 | -114.4395 | 116.5664 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0908 | 0
2015-10-08 04:00 | 1.31 | 1 | 0.31 | 0 | -5.4419 | -101.1463 | 97.8044 | -7.8044 | -99.6513 | 102.2245 | 0 | 0.75 | 0.2 | 0 | 0.0655 | 0.8155 | 2.7 | 2.7255 | 1.0891 | 0.00072829
2015-10-08 05:00 | 2.62 | 2 | 0.62 | 0 | -5.4578 | -86.1433 | 94.4485 | -4.4485 | -85.0123 | 87.9205 | 0 | 1.5 | 0.2 | 0 | 0.131 | 1.631 | 2.8 | 2.851 | 1.0886 | 0.0014559
2015-10-08 06:00 | 3.93 | 3 | 0.93 | 0 | -5.4738 | -71.1403 | 91.167 | -1.167 | -70.4232 | 73.7437 | 0 | 2.25 | 0.2 | 0 | 0.1965 | 2.4465 | 2.8 | 2.8765 | 1.0885 | 0.0021837
2015-10-08 07:00 | 17.5567 | 12.22 | 5.3367 | 0 | -5.4898 | -56.1374 | 88.1731 | 1.8269 | -55.7905 | 59.8285 | 0 | 9.165 | 0.2 | 0 | 0.87783 | 10.0428 | 2.7 | 3.0138 | 1.0879 | 0.0089594
2015-10-08 08:00 | 31.1833 | 21.44 | 9.7433 | 128.8881 | -5.5058 | -41.1344 | 85.6646 | 4.3354 | -41.0465 | 46.4439 | 88.8123 | 16.08 | 0.2 | 0 | 1.5592 | 106.4514 | 2.7 | 6.0266 | 1.0759 | 0.093915
2015-10-08 09:00 | 44.81 | 30.66 | 14.15 | 131.2824 | -5.5217 | -26.1314 | 83.8125 | 6.1875 | -26.1649 | 34.2443 | 108.524 | 22.995 | 0.2 | 0 | 2.2405 | 133.7595 | 2.9 | 7.08 | 1.0717 | 0.11754
2015-10-08 10:00 | 49.5467 | 32.4133 | 17.1333 | 135.731 | -5.5377 | -11.1285 | 82.7482 | 7.2518 | -11.1663 | 25.0485 | 122.9654 | 24.31 | 0.2 | 0 | 2.4773 | 149.7528 | 3.3 | 7.9798 | 1.0681 | 0.13116
2015-10-08 11:00 | 54.2833 | 34.1667 | 20.1167 | 155.1477 | -5.5537 | 3.8745 | 82.55 | 7.45 | 3.8892 | 22.8436 | 142.9791 | 25.625 | 0.2 | 0 | 2.7142 | 171.3183 | 3.5 | 8.8537 | 1.0646 | 0.14955
2015-10-08 12:00 | 59.02 | 35.92 | 23.1 | 196.0528 | -5.5696 | 18.8775 | 83.2334 | 6.7666 | 18.9218 | 29.2573 | 171.043 | 26.94 | 0.2 | 0 | 2.951 | 200.934 | 3.4 | 9.6792 | 1.0613 | 0.17486
2015-10-08 13:00 | 42.0767 | 25.8733 | 16.2033 | 177.0635 | -5.5856 | 33.8804 | 84.7494 | 5.2506 | 33.8591 | 40.3685 | 134.9037 | 19.405 | 0.2 | 0 | 2.1038 | 156.4126 | 3.9 | 8.7879 | 1.0648 | 0.13658
2015-10-08 14:00 | 25.1333 | 15.8267 | 9.3067 | 177.2844 | -5.6016 | 48.8834 | 86.9908 | 3.0092 | 48.6606 | 53.3101 | 105.9246 | 11.87 | 0.2 | 0 | 1.2567 | 119.0513 | 3.5 | 7.2204 | 1.0711 | 0.10456
2015-10-08 15:00 | 8.19 | 5.78 | 2.41 | 0 | -5.6175 | 63.8863 | 89.804 | 0.19598 | 63.3312 | 67.0201 | 0 | 4.335 | 0.2 | 0 | 0.4095 | 4.7445 | 3.2 | 3.3483 | 1.0866 | 0.0042274
2015-10-08 16:00 | 5.46 | 3.8533 | 1.6067 | 0 | -5.6335 | 78.8893 | 93.0029 | -3.0029 | 77.921 | 81.0958 | 0 | 2.89 | 0.2 | 0 | 0.273 | 3.163 | 3.5 | 3.5988 | 1.0856 | 0.0028157
2015-10-08 17:00 | 2.73 | 1.9267 | 0.80333 | 0 | -5.6494 | 93.8922 | 96.381 | -6.381 | 92.515 | 95.3556 | 0 | 1.445 | 0.2 | 0 | 0.1365 | 1.5815 | 3.3 | 3.3494 | 1.0866 | 0.0014091
2015-10-08 18:00 | 0 | 0 | 0 | 0 | -5.6654 | 108.8952 | 99.7209 | -9.7209 | 107.2139 | 109.6964 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0872 | 0
2015-10-08 19:00 | 0 | 0 | 0 | 0 | -5.6813 | 123.8981 | 102.8032 | -12.8032 | 122.1117 | 124.0358 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.086 | 0
2015-10-08 20:00 | 0 | 0 | 0 | 0 | -5.6973 | 138.901 | 105.4157 | -15.4157 | 137.2714 | 138.2609 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.4 | 3.4 | 1.0864 | 0
2015-10-08 21:00 | 0 | 0 | 0 | 0 | -5.7132 | 153.9039 | 107.3679 | -17.3679 | 152.7031 | 152.0984 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0868 | 0
2015-10-08 22:00 | 0 | 0 | 0 | 0 | -5.7292 | 168.9069 | 108.509 | -18.509 | 168.3527 | 164.3752 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0868 | 0
2015-10-08 23:00 | 0 | 0 | 0 | 0 | -5.7451 | 183.9098 | 108.7468 | -18.7468 | -175.8916 | 168.144 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0868 | 0
2015-10-09 | 0 | 0 | 0 | 0 | -5.761 | -161.0873 | 108.0628 | -18.0628 | -160.1714 | 158.3664 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0884 | 0
2015-10-09 01:00 | 0 | 0 | 0 | 0 | -5.777 | -146.0844 | 106.5147 | -16.5147 | -144.6181 | 144.993 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0924 | 0
2015-10-09 02:00 | 0 | 0 | 0 | 0 | -5.7929 | -131.0815 | 104.2274 | -14.2274 | -129.3166 | 130.9025 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0916 | 0
2015-10-09 03:00 | 0 | 0 | 0 | 0 | -5.8089 | -116.0786 | 101.3751 | -11.3751 | -114.2887 | 116.6055 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.088 | 0
2015-10-09 04:00 | 1.4467 | 0.96 | 0.48667 | 0 | -5.8248 | -101.0757 | 98.162 | -8.162 | -99.4957 | 102.2637 | 0 | 0.72 | 0.2 | 0 | 0.072333 | 0.79233 | 1.5 | 1.5248 | 1.0939 | 0.00071072
2015-10-09 05:00 | 2.8933 | 1.92 | 0.97333 | 0 | -5.8407 | -86.0728 | 94.8057 | -4.8057 | -84.8569 | 87.9672 | 0 | 1.44 | 0.2 | 0 | 0.14467 | 1.5847 | 1.4 | 1.4495 | 1.0942 | 0.0014218
2015-10-09 06:00 | 4.34 | 2.88 | 1.46 | 0 | -5.8566 | -71.0699 | 91.5261 | -1.5261 | -70.273 | 73.8056 | 0 | 2.16 | 0.2 | 0 | 0.217 | 2.377 | 2.2 | 2.2743 | 1.0909 | 0.0021263
2015-10-09 07:00 | 26.2333 | 12.17 | 14.0633 | 0 | -5.8726 | -56.067 | 88.536 | 1.464 | -55.65 | 59.9162 | 0 | 9.1275 | 0.2 | 0 | 1.3117 | 10.4392 | 2.1 | 2.4262 | 1.0903 | 0.0093331
2015-10-09 08:00 | 48.1267 | 21.46 | 26.6667 | 385.4247 | -5.8885 | -41.0641 | 86.0327 | 3.9673 | -40.9201 | 46.5742 | 264.9466 | 16.095 | 0.2 | 0 | 2.4063 | 283.4479 | 2.1 | 10.9577 | 1.0562 | 0.24548
2015-10-09 09:00 | 70.02 | 30.75 | 39.27 | 387.6818 | -5.9044 | -26.0612 | 84.1863 | 5.8137 | -26.0567 | 34.4472 | 319.7011 | 23.0625 | 0.2 | 0 | 3.501 | 346.2646 | 2.9 | 13.7208 | 1.0451 | 0.29675
2015-10-09 10:00 | 72.0767 | 31.4433 | 40.6333 | 339.5688 | -5.9203 | -11.0583 | 83.1274 | 6.8726 | -11.0792 | 25.3634 | 306.8374 | 23.5825 | 0.2 | 0 | 3.6038 | 334.0237 | 2.3 | 12.7382 | 1.049 | 0.28733
2015-10-09 11:00 | 74.1333 | 32.1367 | 41.9967 | 341.3821 | -5.9363 | 3.9445 | 82.9336 | 7.0664 | 3.9534 | 23.2325 | 313.7001 | 24.1025 | 0.2 | 0 | 3.7067 | 341.5093 | 3.2 | 13.8722 | 1.0445 | 0.2925
2015-10-09 12:00 | 76.19 | 32.83 | 43.36 | 390.2021 | -5.9522 | 18.9474 | 83.62 | 6.38 | 18.9633 | 29.598 | 339.2855 | 24.6225 | 0.2 | 0 | 3.8095 | 367.7175 | 3 | 14.4912 | 1.042 | 0.3142
2015-10-09 13:00 | 53.4733 | 23.5533 | 29.92 | 352.9871 | -5.9681 | 33.9503 | 85.1376 | 4.8624 | 33.8798 | 40.6436 | 267.8381 | 17.665 | 0.2 | 0 | 2.6737 | 288.1767 | 3.3 | 12.3055 | 1.0508 | 0.2483
2015-10-09 14:00 | 30.7567 | 14.2767 | 16.48 | 0 | -5.984 | 48.9531 | 87.3795 | 2.6205 | 48.6639 | 53.5408 | 0 | 10.7075 | 0.2 | 0 | 1.5378 | 12.2453 | 3.2 | 3.5827 | 1.0857 | 0.010901
2015-10-09 15:00 | 8.04 | 5 | 3.04 | 0 | -5.9999 | 63.956 | 90.1925 | -0.19253 | 63.3216 | 67.2228 | 0 | 3.75 | 0.2 | 0 | 0.402 | 4.152 | 2.9 | 3.0297 | 1.0879 | 0.0037038
2015-10-09 16:00 | 5.36 | 3.3333 | 2.0267 | 0 | -6.0158 | 78.9588 | 93.3911 | -3.3911 | 77.9037 | 81.2811 | 0 | 2.5 | 0.2 | 0 | 0.268 | 2.768 | 3.4 | 3.4865 | 1.0861 | 0.0024651
2015-10-09 17:00 | 2.68 | 1.6667 | 1.0133 | 0 | -6.0317 | 93.9617 | 96.769 | -6.769 | 92.4956 | 95.5308 | 0 | 1.25 | 0.2 | 0 | 0.134 | 1.384 | 3.7 | 3.7433 | 1.085 | 0.0012314
2015-10-09 18:00 | 0 | 0 | 0 | 0 | -6.0476 | 108.9645 | 100.1091 | -10.1091 | 107.1983 | 109.8679 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0868 | 0
2015-10-09 19:00 | 0 | 0 | 0 | 0 | -6.0635 | 123.9674 | 103.1915 | -13.1915 | 122.1059 | 124.2107 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.2 | 4.2 | 1.0832 | 0
2015-10-09 20:00 | 0 | 0 | 0 | 0 | -6.0794 | 138.9702 | 105.8039 | -15.8039 | 137.281 | 138.4504 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.3 | 4.3 | 1.0828 | 0
2015-10-09 21:00 | 0 | 0 | 0 | 0 | -6.0953 | 153.9731 | 107.7551 | -17.7551 | 152.7332 | 152.3259 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.084 | 0
2015-10-09 22:00 | 0 | 0 | 0 | 0 | -6.1112 | 168.9759 | 108.8938 | -18.8938 | 168.4067 | 164.6996 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.2 | 4.2 | 1.0832 | 0
2015-10-09 23:00 | 0 | 0 | 0 | 0 | -6.1271 | 183.9787 | 109.1277 | -19.1277 | -175.8125 | 168.483 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.7 | 4.7 | 1.0812 | 0
2015-10-10 | 0 | 0 | 0 | 0 | -6.143 | -161.0185 | 108.4383 | -18.4383 | -160.0685 | 158.5127 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.9 | 4.9 | 1.0804 | 0
2015-10-10 01:00 | 0 | 0 | 0 | 0 | -6.1589 | -146.0156 | 106.8843 | -16.8843 | -144.4949 | 145.0677 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.9 | 4.9 | 1.0804 | 0
2015-10-10 02:00 | 0 | 0 | 0 | 0 | -6.1748 | -131.0128 | 104.5913 | -14.5913 | -129.178 | 130.9509 | 0 | 0 | 0.2 | 0 | 0 | 0 | 5 | 5 | 1.08 | 0
2015-10-10 03:00 | 0 | 0 | 0 | 0 | -6.1906 | -116.01 | 101.7346 | -11.7346 | -114.14 | 116.6451 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5 | 4.5 | 1.082 | 0
2015-10-10 04:00 | 1.09 | 0.74667 | 0.34333 | 0 | -6.2065 | -101.0072 | 98.5188 | -8.5188 | -99.3423 | 102.3041 | 0 | 0.56 | 0.2 | 0 | 0.0545 | 0.6145 | 5.1 | 5.1192 | 1.0795 | 0.00054396
2015-10-10 05:00 | 2.18 | 1.4933 | 0.68667 | 0 | -6.2224 | -86.0044 | 95.1621 | -5.1621 | -84.7039 | 88.0157 | 0 | 1.12 | 0.2 | 0 | 0.109 | 1.229 | 3.2 | 3.2384 | 1.087 | 0.0010955
2015-10-10 06:00 | 3.27 | 2.24 | 1.03 | 0 | -6.2383 | -71.0016 | 91.8844 | -1.8844 | -70.1251 | 73.8699 | 0 | 1.68 | 0.2 | 0 | 0.1635 | 1.8435 | 4.1 | 4.1576 | 1.0834 | 0.0016377
2015-10-10 07:00 | 19.9 | 10.9933 | 8.9067 | 0 | -6.2541 | -55.9988 | 88.8982 | 1.1018 | -55.5119 | 60.0068 | 0 | 8.245 | 0.2 | 0 | 0.995 | 9.24 | 4.1 | 4.3887 | 1.0824 | 0.0082015
2015-10-10 08:00 | 36.53 | 19.7467 | 16.7833 | 267.2843 | -6.27 | -40.996 | 86.3999 | 3.6001 | -40.7963 | 46.7081 | 183.2811 | 14.81 | 0.2 | 0 | 1.8265 | 199.9176 | 1.9 | 8.1474 | 1.0674 | 0.17498
2015-10-10 09:00 | 53.16 | 28.5 | 24.66 | 260.0763 | -6.2859 | -25.9932 | 84.5591 | 5.4409 | -25.9509 | 34.6537 | 213.9398 | 21.375 | 0.2 | 0 | 2.658 | 237.9728 | 1.9 | 9.3367 | 1.0627 | 0.20736
2015-10-10 10:00 | 54.7933 | 29.6667 | 25.1267 | 222.1495 | -6.3017 | -10.9904 | 83.5055 | 6.4945 | -10.9946 | 25.6801 | 200.2073 | 22.25 | 0.2 | 0 | 2.7397 | 225.197 | 4.6 | 11.6374 | 1.0535 | 0.19453
2015-10-10 11:00 | 56.4267 | 30.8333 | 25.5933 | 219.8856 | -6.3176 | 4.0124 | 83.316 | 6.684 | 4.0153 | 23.6197 | 201.4647 | 23.125 | 0.2 | 0 | 2.8213 | 227.411 | 2.8 | 9.9066 | 1.0604 | 0.19774
2015-10-10 12:00 | 58.06 | 32 | 26.06 | 249.5273 | -6.3335 | 19.0151 | 84.0052 | 5.9948 | 19.0025 | 29.9374 | 216.2333 | 24 | 0.2 | 0 | 2.903 | 243.1363 | 4.2 | 11.798 | 1.0528 | 0.2099
2015-10-10 13:00 | 40.28 | 22.4967 | 17.7833 | 227.8875 | -6.3493 | 34.0179 | 85.5243 | 4.4757 | 33.8983 | 40.9177 | 172.2035 | 16.8725 | 0.2 | 0 | 2.014 | 191.09 | 4.3 | 10.2716 | 1.0589 | 0.16593
2015-10-10 14:00 | 22.5 | 12.9933 | 9.5067 | 0 | -6.3652 | 49.0207 | 87.7666 | 2.2334 | 48.6652 | 53.7703 | 0 | 9.745 | 0.2 | 0 | 1.125 | 10.87 | 4.1 | 4.4397 | 1.0822 | 0.0096464
2015-10-10 15:00 | 4.72 | 3.49 | 1.23 | 0 | -6.381 | 64.0234 | 90.5794 | -0.57935 | 63.31 | 67.4238 | 0 | 2.6175 | 0.2 | 0 | 0.236 | 2.8535 | 4.6 | 4.6892 | 1.0812 | 0.00253
2015-10-10 16:00 | 3.1467 | 2.3267 | 0.82 | 0 | -6.3969 | 79.0262 | 93.7775 | -3.7775 | 77.8845 | 81.4642 | 0 | 1.745 | 0.2 | 0 | 0.15733 | 1.9023 | 3.9 | 3.9594 | 1.0842 | 0.0016912
2015-10-10 17:00 | 1.5733 | 1.1633 | 0.41 | 0 | -6.4127 | 94.029 | 97.1553 | -7.1553 | 92.4743 | 95.7032 | 0 | 0.8725 | 0.2 | 0 | 0.078667 | 0.95117 | 3.4 | 3.4297 | 1.0863 | 0.00084725
2015-10-10 18:00 | 0 | 0 | 0 | 0 | -6.4286 | 109.0317 | 100.4955 | -10.4955 | 107.1807 | 110.036 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0872 | 0
2015-10-10 19:00 | 0 | 0 | 0 | 0 | -6.4444 | 124.0345 | 103.5781 | -13.5781 | 122.0979 | 124.3816 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0844 | 0
2015-10-10 20:00 | 0 | 0 | 0 | 0 | -6.4603 | 139.0372 | 106.1905 | -16.1905 | 137.2885 | 138.635 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0868 | 0
2015-10-10 21:00 | 0 | 0 | 0 | 0 | -6.4761 | 154.04 | 108.1408 | -18.1408 | 152.7611 | 152.5473 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.086 | 0
2015-10-10 22:00 | 0 | 0 | 0 | 0 | -6.492 | 169.0427 | 109.2771 | -19.2771 | 168.4586 | 165.0186 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0888 | 0
2015-10-10 23:00 | 0 | 0 | 0 | 0 | -6.5078 | 184.0454 | 109.5072 | -19.5072 | -175.7355 | 168.8185 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.2 | 4.2 | 1.0832 | 0
2015-10-11 | 0 | 0 | 0 | 0 | -6.5236 | -160.9518 | 108.8127 | -18.8127 | -159.9677 | 158.6545 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0888 | 0
2015-10-11 01:00 | 0 | 0 | 0 | 0 | -6.5395 | -145.9491 | 107.2528 | -17.2528 | -144.3738 | 145.1405 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0888 | 0
2015-10-11 02:00 | 0 | 0 | 0 | 0 | -6.5553 | -130.9464 | 104.9543 | -14.9543 | -129.0415 | 130.9989 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0924 | 0
2015-10-11 03:00 | 0 | 0 | 0 | 0 | -6.5711 | -115.9437 | 102.0931 | -12.0931 | -113.9935 | 116.6854 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0908 | 0
2015-10-11 04:00 | 0.73667 | 0.53667 | 0.2 | 0 | -6.5869 | -100.941 | 98.8748 | -8.8748 | -99.1912 | 102.3459 | 0 | 0.4025 | 0.2 | 0 | 0.036833 | 0.43933 | 2.4 | 2.4137 | 1.0903 | 0.0003928
2015-10-11 05:00 | 1.4733 | 1.0733 | 0.4 | 0 | -6.6028 | -85.9382 | 95.5178 | -5.5178 | -84.5533 | 88.0662 | 0 | 0.805 | 0.2 | 0 | 0.073667 | 0.87867 | 2.7 | 2.7275 | 1.0891 | 0.0007847
2015-10-11 06:00 | 2.21 | 1.61 | 0.6 | 0 | -6.6186 | -70.9355 | 92.242 | -2.242 | -69.9798 | 73.9367 | 0 | 1.2075 | 0.2 | 0 | 0.1105 | 1.318 | 2.3 | 2.3412 | 1.0906 | 0.0011787
2015-10-11 07:00 | 17.8033 | 10.4333 | 7.37 | 0 | -6.6344 | -55.9328 | 89.2595 | 0.74051 | -55.3765 | 60.1005 | 0 | 7.825 | 0.2 | 0 | 0.89017 | 8.7152 | 3.1 | 3.3723 | 1.0865 | 0.0077647
2015-10-11 08:00 | 33.3967 | 19.2567 | 14.14 | 250.6642 | -6.6502 | -40.9301 | 86.7662 | 3.2338 | -40.6751 | 46.8454 | 171.4465 | 14.4425 | 0.2 | 0 | 1.6698 | 187.5588 | 3 | 8.8612 | 1.0646 | 0.16373
2015-10-11 09:00 | 48.99 | 28.08 | 20.91 | 236.6543 | -6.666 | -25.9274 | 84.9309 | 5.0691 | -25.8478 | 34.8637 | 194.1782 | 21.06 | 0.2 | 0 | 2.4495 | 217.6877 | 3.2 | 10.0027 | 1.06 | 0.18921
2015-10-11 10:00 | 49.2733 | 28.8 | 20.4733 | 192.1143 | -6.6818 | -10.9248 | 83.8825 | 6.1175 | -10.9126 | 25.9983 | 172.6737 | 21.6 | 0.2 | 0 | 2.4637 | 196.7374 | 3 | 9.148 | 1.0634 | 0.17155
2015-10-11 11:00 | 49.5567 | 29.52 | 20.0367 | 182.5056 | -6.6976 | 4.0779 | 83.697 | 6.303 | 4.0747 | 24.0053 | 166.7203 | 22.14 | 0.2 | 0 | 2.4778 | 191.3382 | 2.9 | 8.8793 | 1.0645 | 0.16701
2015-10-11 12:00 | 49.84 | 30.24 | 19.6 | 200.4615 | -6.7134 | 19.0806 | 84.389 | 5.611 | 19.0395 | 30.2753 | 173.1212 | 22.68 | 0.2 | 0 | 2.492 | 198.2932 | 2.8 | 8.9967 | 1.064 | 0.17301
2015-10-11 13:00 | 33.8733 | 20.7733 | 13.1 | 183.6441 | -6.7292 | 34.0833 | 85.9094 | 4.0906 | 33.9147 | 41.1905 | 138.1965 | 15.58 | 0.2 | 0 | 1.6937 | 155.4702 | 2.8 | 7.6584 | 1.0694 | 0.13633
2015-10-11 14:00 | 17.9067 | 11.3067 | 6.6 | 0 | -6.745 | 49.086 | 88.1519 | 1.8481 | 48.6643 | 53.9982 | 0 | 8.48 | 0.2 | 0 | 0.89533 | 9.3753 | 2.3 | 2.593 | 1.0896 | 0.0083768
2015-10-11 15:00 | 1.94 | 1.84 | 0.1 | 0 | -6.7608 | 64.0886 | 90.9644 | -0.96438 | 63.2964 | 67.6229 | 0 | 1.38 | 0.2 | 0 | 0.097 | 1.477 | 2.1 | 2.1462 | 1.0914 | 0.0013219
2015-10-11 16:00 | 1.2933 | 1.2267 | 0.066667 | 0 | -6.7766 | 79.0913 | 94.1621 | -4.1621 | 77.8632 | 81.6448 | 0 | 0.92 | 0.2 | 0 | 0.064667 | 0.98467 | 2.1 | 2.1308 | 1.0915 | 0.00088129
2015-10-11 17:00 | 0.64667 | 0.61333 | 0.033333 | 0 | -6.7924 | 94.094 | 97.5397 | -7.5397 | 92.4508 | 95.8727 | 0 | 0.46 | 0.2 | 0 | 0.032333 | 0.49233 | 1.6 | 1.6154 | 1.0935 | 0.00044148
2015-10-11 18:00 | 0 | 0 | 0 | 0 | -6.8082 | 109.0966 | 100.88 | -10.88 | 107.1609 | 110.2007 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-10-11 19:00 | 0 | 0 | 0 | 0 | -6.824 | 124.0993 | 103.963 | -13.963 | 122.0877 | 124.5484 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0944 | 0
2015-10-11 20:00 | 0 | 0 | 0 | 0 | -6.8398 | 139.1019 | 106.5753 | -16.5753 | 137.2937 | 138.8147 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-10-11 21:00 | 0 | 0 | 0 | 0 | -6.8556 | 154.1046 | 108.5248 | -18.5248 | 152.7868 | 152.7627 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-10-11 22:00 | 0 | 0 | 0 | 0 | -6.8713 | 169.1072 | 109.659 | -19.659 | 168.5082 | 165.3317 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-10-11 23:00 | 0 | 0 | 0 | 0 | -6.8871 | 184.1098 | 109.8854 | -19.8854 | -175.6607 | 169.1502 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-10-12 | 0 | 0 | 0 | 0 | -6.9029 | -160.8875 | 109.1858 | -19.1858 | -159.8691 | 158.7919 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.096 | 0
2015-10-12 01:00 | 0 | 0 | 0 | 0 | -6.9187 | -145.8849 | 107.6202 | -17.6202 | -144.2549 | 145.2115 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0944 | 0
2015-10-12 02:00 | 0 | 0 | 0 | 0 | -6.9344 | -130.8823 | 105.3162 | -15.3162 | -128.9073 | 131.0465 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-10-12 03:00 | 0 | 0 | 0 | 0 | -6.9502 | -115.8797 | 102.4508 | -12.4508 | -113.8494 | 116.7262 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-10-12 04:00 | 0.57333 | 0.4 | 0.17333 | 0 | -6.9659 | -100.8771 | 99.2299 | -9.2299 | -99.0426 | 102.389 | 0 | 0.3 | 0.2 | 0 | 0.028667 | 0.32867 | 0 | 0.010271 | 1.1 | 0.00029645
2015-10-12 05:00 | 1.1467 | 0.8 | 0.34667 | 0 | -6.9817 | -85.8744 | 95.8726 | -5.8726 | -84.4052 | 88.1186 | 0 | 0.6 | 0.2 | 0 | 0.057333 | 0.65733 | -0.9 | -0.87946 | 1.1035 | 0.00059481
2015-10-12 06:00 | 1.72 | 1.2 | 0.52 | 0 | -6.9975 | -70.8718 | 92.5986 | -2.5986 | -69.837 | 74.0061 | 0 | 0.9 | 0.2 | 0 | 0.086 | 0.986 | -0.1 | -0.069188 | 1.1003 | 0.0008896
2015-10-12 07:00 | 11.7567 | 8.1767 | 3.58 | 0 | -7.0132 | -55.8692 | 89.6199 | 0.38014 | -55.2437 | 60.1972 | 0 | 6.1325 | 0.2 | 0 | 0.58783 | 6.7203 | -0.5 | -0.28999 | 1.1012 | 0.0060681
2015-10-12 08:00 | 21.7933 | 15.1533 | 6.64 | 0 | -7.029 | -40.8666 | 87.1315 | 2.8685 | -40.5565 | 46.9863 | 0 | 11.365 | 0.2 | 0 | 1.0897 | 12.4547 | -0.2 | 0.18921 | 1.0992 | 0.011226
2015-10-12 09:00 | 31.83 | 22.13 | 9.7 | 118.4203 | -7.0447 | -25.864 | 85.3015 | 4.6985 | -25.7474 | 35.0771 | 96.9128 | 16.5975 | 0.2 | 0 | 1.5915 | 115.1018 | -0.3 | 3.2969 | 1.0868 | 0.10258
2015-10-12 10:00 | 31.78 | 22.4767 | 9.3033 | 92.9886 | -7.0605 | -10.8614 | 84.2581 | 5.7419 | -10.8331 | 26.3179 | 83.3501 | 16.8575 | 0.2 | 0 | 1.589 | 101.7966 | -0.8 | 2.3811 | 1.0905 | 0.091026
2015-10-12 11:00 | 31.73 | 22.8233 | 8.9067 | 86.305 | -7.0762 | 4.1411 | 84.0765 | 5.9235 | 4.1316 | 24.389 | 78.6034 | 17.1175 | 0.2 | 0 | 1.5865 | 97.3074 | -0.4 | 2.6409 | 1.0894 | 0.086928
2015-10-12 12:00 | 31.68 | 23.17 | 8.51 | 93.378 | -7.092 | 19.1437 | 84.7711 | 5.2289 | 19.074 | 30.6115 | 80.3648 | 17.3775 | 0.2 | 0 | 1.584 | 99.3263 | 0.1 | 3.2039 | 1.0872 | 0.088548
2015-10-12 13:00 | 21.8 | 16.0433 | 5.7567 | 89.0315 | -7.1077 | 34.1463 | 86.2927 | 3.7073 | 33.9288 | 41.462 | 66.7197 | 12.0325 | 0.2 | 0 | 1.09 | 79.8422 | -0.3 | 2.1951 | 1.0912 | 0.071443
2015-10-12 14:00 | 11.92 | 8.9167 | 3.0033 | 0 | -7.1234 | 49.1489 | 88.5354 | 1.4646 | 48.6613 | 54.2246 | 0 | 6.6875 | 0.2 | 0 | 0.596 | 7.2835 | -0.2 | 0.027609 | 1.0999 | 0.0065691
2015-10-12 15:00 | 2.04 | 1.79 | 0.25 | 0 | -7.1392 | 64.1514 | 91.3475 | -1.3475 | 63.2806 | 67.82 | 0 | 1.3425 | 0.2 | 0 | 0.102 | 1.4445 | 0 | 0.045141 | 1.0998 | 0.0013027
2015-10-12 16:00 | 1.36 | 1.1933 | 0.16667 | 0 | -7.1549 | 79.154 | 94.5448 | -4.5448 | 77.8398 | 81.823 | 0 | 0.895 | 0.2 | 0 | 0.068 | 0.963 | -0.2 | -0.16991 | 1.1007 | 0.00086916
2015-10-12 17:00 | 0.68 | 0.59667 | 0.083333 | 0 | -7.1706 | 94.1566 | 97.9221 | -7.9221 | 92.4253 | 96.0393 | 0 | 0.4475 | 0.2 | 0 | 0.034 | 0.4815 | 0 | 0.015047 | 1.0999 | 0.00043429
2015-10-12 18:00 | 0 | 0 | 0 | 0 | -7.1863 | 109.1591 | 101.2626 | -11.2626 | 107.1389 | 110.3618 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-10-12 19:00 | 0 | 0 | 0 | 0 | -7.2021 | 124.1617 | 104.3459 | -14.3459 | 122.0754 | 124.7109 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-10-12 20:00 | 0 | 0 | 0 | 0 | -7.2178 | 139.1642 | 106.9583 | -16.9583 | 137.2967 | 138.9892 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-10-12 21:00 | 0 | 0 | 0 | 0 | -7.2335 | 154.1668 | 108.9071 | -18.9071 | 152.8102 | 152.9717 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-10-12 22:00 | 0 | 0 | 0 | 0 | -7.2492 | 169.1693 | 110.0393 | -20.0393 | 168.5555 | 165.6386 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-10-12 23:00 | 0 | 0 | 0 | 0 | -7.2649 | 184.1718 | 110.2621 | -20.2621 | -175.5882 | 169.4778 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-10-13 | 0 | 0 | 0 | 0 | -7.2806 | -160.8256 | 109.5576 | -19.5576 | -159.7728 | 158.925 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-10-13 01:00 | 0 | 0 | 0 | 0 | -7.2963 | -145.8231 | 107.9864 | -17.9864 | -144.1383 | 145.2807 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-10-13 02:00 | 0 | 0 | 0 | 0 | -7.312 | -130.8206 | 105.6771 | -15.6771 | -128.7754 | 131.094 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-10-13 03:00 | 0 | 0 | 0 | 0 | -7.3277 | -115.8181 | 102.8073 | -12.8073 | -113.7076 | 116.7678 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-10-13 04:00 | 0.34 | 0.24333 | 0.096667 | 0 | -7.3434 | -100.8156 | 99.5841 | -9.5841 | -98.8964 | 102.4336 | 0 | 0.1825 | 0.2 | 0 | 0.017 | 0.1995 | -0.3 | -0.29377 | 1.1012 | 0.00018014
2015-10-13 05:00 | 0.68 | 0.48667 | 0.19333 | 0 | -7.3591 | -85.813 | 96.2265 | -6.2265 | -84.2596 | 88.1731 | 0 | 0.365 | 0.2 | 0 | 0.034 | 0.399 | -0.2 | -0.18753 | 1.1008 | 0.00036014
2015-10-13 06:00 | 1.02 | 0.73 | 0.29 | 0 | -7.3748 | -70.8105 | 92.9543 | -2.9543 | -69.697 | 74.078 | 0 | 0.5475 | 0.2 | 0 | 0.051 | 0.5985 | -1.2 | -1.1813 | 1.1047 | 0.00054217
2015-10-13 07:00 | 11.66 | 7.73 | 3.93 | 0 | -7.3905 | -55.808 | 89.9792 | 0.020805 | -55.1136 | 60.2969 | 0 | 5.7975 | 0.2 | 0 | 0.583 | 6.3805 | -1.9 | -1.7006 | 1.1068 | 0.0057908
2015-10-13 08:00 | 22.3 | 14.73 | 7.57 | 0 | -7.4062 | -40.8055 | 87.4956 | 2.5044 | -40.4408 | 47.1305 | 0 | 11.0475 | 0.2 | 0 | 1.115 | 12.1625 | -1.9 | -1.5199 | 1.1061 | 0.011031
2015-10-13 09:00 | 32.94 | 21.73 | 11.21 | 148.5062 | -7.4219 | -25.8031 | 85.6709 | 4.3291 | -25.6497 | 35.2938 | 121.2108 | 16.2975 | 0.2 | 0 | 1.647 | 139.1553 | -1.7 | 2.6486 | 1.0894 | 0.12431
2015-10-13 10:00 | 35.32 | 22.9967 | 12.3233 | 131.7326 | -7.4376 | -10.8006 | 84.6322 | 5.3678 | -10.7563 | 26.6386 | 117.7494 | 17.2475 | 0.2 | 0 | 1.766 | 136.7629 | -1.6 | 2.6738 | 1.0893 | 0.12216
2015-10-13 11:00 | 37.7 | 24.2633 | 13.4367 | 139.044 | -7.4532 | 4.2019 | 84.4545 | 5.5455 | 4.186 | 24.7708 | 126.2507 | 18.1975 | 0.2 | 0 | 1.885 | 146.3332 | -1.5 | 3.0729 | 1.0877 | 0.13052
2015-10-13 12:00 | 40.08 | 25.53 | 14.55 | 172.1455 | -7.4689 | 19.2044 | 85.1515 | 4.8485 | 19.1062 | 30.9461 | 147.6409 | 19.1475 | 0.2 | 0 | 2.004 | 168.7924 | -1.2 | 4.0748 | 1.0837 | 0.14999
2015-10-13 13:00 | 27.46 | 17.5767 | 9.8833 | 170.363 | -7.4846 | 34.2069 | 86.6742 | 3.3258 | 33.9406 | 41.7321 | 127.1361 | 13.1825 | 0.2 | 0 | 1.373 | 141.6916 | -1.6 | 2.8279 | 1.0887 | 0.12649
2015-10-13 14:00 | 14.84 | 9.6233 | 5.2167 | 0 | -7.5003 | 49.2093 | 88.9169 | 1.0831 | 48.6561 | 54.4492 | 0 | 7.2175 | 0.2 | 0 | 0.742 | 7.9595 | -1.8 | -1.5513 | 1.1062 | 0.00722
2015-10-13 15:00 | 2.22 | 1.67 | 0.55 | 0 | -7.5159 | 64.2118 | 91.7286 | -1.7286 | 63.2627 | 68.0149 | 0 | 1.2525 | 0.2 | 0 | 0.111 | 1.3635 | -3 | -2.9574 | 1.1118 | 0.0012431
2015-10-13 16:00 | 1.48 | 1.1133 | 0.36667 | 0 | -7.5316 | 79.2143 | 94.9253 | -4.9253 | 77.8143 | 81.9985 | 0 | 0.835 | 0.2 | 0 | 0.074 | 0.909 | -2.8 | -2.7716 | 1.1111 | 0.00082818
2015-10-13 17:00 | 0.74 | 0.55667 | 0.18333 | 0 | -7.5472 | 94.2167 | 98.3025 | -8.3025 | 92.3975 | 96.2028 | 0 | 0.4175 | 0.2 | 0 | 0.037 | 0.4545 | -2.7 | -2.6858 | 1.1107 | 0.00041396
2015-10-13 18:00 | 0 | 0 | 0 | 0 | -7.5629 | 109.2192 | 101.6431 | -11.6431 | 107.1148 | 110.5193 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.8 | -2.8 | 1.1112 | 0
2015-10-13 19:00 | 0 | 0 | 0 | 0 | -7.5786 | 124.2216 | 104.7268 | -14.7268 | 122.0607 | 124.8692 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1144 | 0
2015-10-13 20:00 | 0 | 0 | 0 | 0 | -7.5942 | 139.2241 | 107.3394 | -17.3394 | 137.2973 | 139.1585 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-10-13 21:00 | 0 | 0 | 0 | 0 | -7.6099 | 154.2265 | 109.2876 | -19.2876 | 152.8312 | 153.1742 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.8 | -3.8 | 1.1152 | 0
2015-10-13 22:00 | 0 | 0 | 0 | 0 | -7.6255 | 169.2289 | 110.4179 | -20.4179 | 168.6004 | 165.9389 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-10-13 23:00 | 0 | 0 | 0 | 0 | -7.6411 | 184.2314 | 110.6372 | -20.6372 | -175.5181 | 169.8013 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-10-14 | 0 | 0 | 0 | 0 | -7.6568 | -160.7662 | 109.9279 | -19.9279 | -159.6789 | 159.0536 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-10-14 01:00 | 0 | 0 | 0 | 0 | -7.6724 | -145.7638 | 108.3513 | -18.3513 | -144.0241 | 145.3482 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-10-14 02:00 | 0 | 0 | 0 | 0 | -7.688 | -130.7614 | 106.0367 | -16.0367 | -128.6459 | 131.1412 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.1084 | 0
2015-10-14 03:00 | 0 | 0 | 0 | 0 | -7.7037 | -115.7589 | 103.1628 | -13.1628 | -113.5684 | 116.8102 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-10-14 04:00 | 0.15667 | 0.13333 | 0.023333 | 0 | -7.7193 | -100.7565 | 99.9372 | -9.9372 | -98.7528 | 102.4796 | 0 | 0.1 | 0.2 | 0 | 0.0078333 | 0.10783 | -1.1 | -1.0966 | 1.1044 | 9.7654e-05
2015-10-14 05:00 | 0.31333 | 0.26667 | 0.046667 | 0 | -7.7349 | -85.7541 | 96.5793 | -6.5793 | -84.1168 | 88.2296 | 0 | 0.2 | 0.2 | 0 | 0.015667 | 0.21567 | -0.5 | -0.49326 | 1.102 | 0.00019488
2015-10-14 06:00 | 0.47 | 0.4 | 0.07 | 0 | -7.7506 | -70.7517 | 93.309 | -3.309 | -69.5597 | 74.1525 | 0 | 0.3 | 0.2 | 0 | 0.0235 | 0.3235 | -0.4 | -0.38989 | 1.1016 | 0.00029221
2015-10-14 07:00 | 5.3633 | 5.3167 | 0.046667 | 0 | -7.7662 | -55.7493 | 90.3374 | -0.33741 | -54.9864 | 60.3997 | 0 | 3.9875 | 0.2 | 0 | 0.26817 | 4.2557 | -0.2 | -0.06701 | 1.1003 | 0.0038395
2015-10-14 08:00 | 10.2567 | 10.2333 | 0.023333 | 0 | -7.7818 | -40.7469 | 87.8586 | 2.1414 | -40.3278 | 47.2781 | 0 | 7.675 | 0.2 | 0 | 0.51283 | 8.1878 | 0.4 | 0.65587 | 1.0974 | 0.0073678
2015-10-14 09:00 | 15.15 | 15.15 | 0 | 0 | -7.7974 | -25.7446 | 86.0389 | 3.9611 | -25.5548 | 35.5136 | 0 | 11.3625 | 0.2 | 0 | 0.7575 | 12.12 | 0.2 | 0.57875 | 1.0977 | 0.010909
2015-10-14 10:00 | 15.6633 | 15.6633 | 0 | 0 | -7.813 | -10.7422 | 85.0049 | 4.9951 | -10.6823 | 26.9604 | 0 | 11.7475 | 0.2 | 0 | 0.78317 | 12.5307 | 0.3 | 0.69158 | 1.0972 | 0.011274
2015-10-14 11:00 | 16.1767 | 16.1767 | 0 | 0 | -7.8286 | 4.2602 | 84.8308 | 5.1692 | 4.2377 | 25.1506 | 0 | 12.1325 | 0.2 | 0 | 0.80883 | 12.9413 | 0.2 | 0.60442 | 1.0976 | 0.011647
2015-10-14 12:00 | 16.69 | 16.69 | 0 | 0 | -7.8442 | 19.2626 | 85.53 | 4.47 | 19.1358 | 31.2787 | 0 | 12.5175 | 0.2 | 0 | 0.8345 | 13.352 | 0.6 | 1.0172 | 1.0959 | 0.011999
2015-10-14 13:00 | 11.37 | 11.37 | 0 | 0 | -7.8598 | 34.2649 | 87.0537 | 2.9463 | 33.95 | 42.0004 | 0 | 8.5275 | 0.2 | 0 | 0.5685 | 9.096 | 1.3 | 1.5842 | 1.0937 | 0.0081573
2015-10-14 14:00 | 6.05 | 6.05 | 0 | 0 | -7.8754 | 49.2673 | 89.2964 | 0.7036 | 48.6486 | 54.6719 | 0 | 4.5375 | 0.2 | 0 | 0.3025 | 4.84 | 0.9 | 1.0513 | 1.0958 | 0.004349
2015-10-14 15:00 | 0.73 | 0.73 | 0 | 0 | -7.891 | 64.2697 | 92.1075 | -2.1075 | 63.2426 | 68.2076 | 0 | 0.5475 | 0.2 | 0 | 0.0365 | 0.584 | 0.7 | 0.71825 | 1.0971 | 0.00052539
2015-10-14 16:00 | 0.48667 | 0.48667 | 0 | 0 | -7.9066 | 79.272 | 95.3037 | -5.3037 | 77.7865 | 82.1714 | 0 | 0.365 | 0.2 | 0 | 0.024333 | 0.38933 | 1.2 | 1.2122 | 1.0952 | 0.00034963
2015-10-14 17:00 | 0.24333 | 0.24333 | 0 | 0 | -7.9222 | 94.2744 | 98.6806 | -8.6806 | 92.3676 | 96.3631 | 0 | 0.1825 | 0.2 | 0 | 0.012167 | 0.19467 | 1.7 | 1.7061 | 1.0932 | 0.0001745
2015-10-14 18:00 | 0 | 0 | 0 | 0 | -7.9378 | 109.2767 | 102.0214 | -12.0214 | 107.0883 | 110.6731 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0924 | 0
2015-10-14 19:00 | 0 | 0 | 0 | 0 | -7.9533 | 124.2791 | 105.1055 | -15.1055 | 122.0436 | 125.023 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0924 | 0
2015-10-14 20:00 | 0 | 0 | 0 | 0 | -7.9689 | 139.2814 | 107.7184 | -17.7184 | 137.2955 | 139.3224 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.096 | 0
2015-10-14 21:00 | 0 | 0 | 0 | 0 | -7.9845 | 154.2837 | 109.6661 | -19.6661 | 152.8497 | 153.3701 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-10-14 22:00 | 0 | 0 | 0 | 0 | -8.0001 | 169.2861 | 110.7946 | -20.7946 | 168.6428 | 166.2322 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-10-14 23:00 | 0 | 0 | 0 | 0 | -8.0156 | 184.2884 | 111.0106 | -21.0106 | -175.4505 | 170.1203 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-10-15 | 0 | 0 | 0 | 0 | -8.0312 | -160.7093 | 110.2967 | -20.2967 | -159.5875 | 159.178 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-10-15 01:00 | 0 | 0 | 0 | 0 | -8.0468 | -145.707 | 108.7147 | -18.7147 | -143.9125 | 145.4141 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-10-15 02:00 | 0 | 0 | 0 | 0 | -8.0623 | -130.7047 | 106.395 | -16.395 | -128.519 | 131.1884 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-10-15 03:00 | 0 | 0 | 0 | 0 | -8.0779 | -115.7024 | 103.5171 | -13.5171 | -113.4318 | 116.8534 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-10-15 04:00 | 0.05 | 0.05 | 0 | 0 | -8.0934 | -100.7001 | 100.2891 | -10.2891 | -98.6119 | 102.5271 | 0 | 0.0375 | 0.2 | 0 | 0.0025 | 0.04 | 1.1 | 1.1013 | 1.0956 | 3.5936e-05
2015-10-15 05:00 | 0.1 | 0.1 | 0 | 0 | -8.109 | -85.6978 | 96.931 | -6.931 | -83.9768 | 88.2882 | 0 | 0.075 | 0.2 | 0 | 0.005 | 0.08 | 1.1 | 1.1025 | 1.0956 | 7.1871e-05
2015-10-15 06:00 | 0.15 | 0.15 | 0 | 0 | -8.1245 | -70.6955 | 93.6625 | -3.6625 | -69.4253 | 74.2295 | 0 | 0.1125 | 0.2 | 0 | 0.0075 | 0.12 | 0.9 | 0.90375 | 1.0964 | 0.00010788
2015-10-15 07:00 | 4.6233 | 4.6233 | 0 | 0 | -8.1401 | -55.6932 | 90.6944 | -0.69441 | -54.8621 | 60.5054 | 0 | 3.4675 | 0.2 | 0 | 0.23117 | 3.6987 | 1 | 1.1156 | 1.0955 | 0.0033227
2015-10-15 08:00 | 9.0967 | 9.0967 | 0 | 0 | -8.1556 | -40.6909 | 88.2202 | 1.7798 | -40.2179 | 47.429 | 0 | 6.8225 | 0.2 | 0 | 0.45483 | 7.2773 | 0.7 | 0.92742 | 1.0963 | 0.006542
2015-10-15 09:00 | 13.57 | 13.57 | 0 | 0 | -8.1712 | -25.6886 | 86.4054 | 3.5946 | -25.4628 | 35.7363 | 0 | 10.1775 | 0.2 | 0 | 0.6785 | 10.856 | 0.6 | 0.93925 | 1.0962 | 0.0097587
2015-10-15 10:00 | 14.1133 | 14.1033 | 0.01 | 0.12404 | -8.1867 | -10.6864 | 85.3759 | 4.6241 | -10.6111 | 27.2829 | 0.11024 | 10.5775 | 0.2 | 0 | 0.70567 | 11.3934 | 0.3 | 0.65604 | 1.0974 | 0.010252
2015-10-15 11:00 | 14.6567 | 14.6367 | 0.02 | 0.23927 | -8.2022 | 4.3159 | 85.2053 | 4.7947 | 4.2867 | 25.5282 | 0.21591 | 10.9775 | 0.2 | 0 | 0.73283 | 11.9262 | 0 | 0.3727 | 1.0985 | 0.010743
2015-10-15 12:00 | 15.2 | 15.17 | 0.03 | 0.42028 | -8.2177 | 19.3182 | 85.9066 | 4.0934 | 19.1628 | 31.6092 | 0.35792 | 11.3775 | 0.2 | 0 | 0.76 | 12.4954 | 0 | 0.39048 | 1.0984 | 0.011255
2015-10-15 13:00 | 10.31 | 10.2867 | 0.023333 | 0 | -8.2333 | 34.3204 | 87.4311 | 2.5689 | 33.957 | 42.267 | 0 | 7.715 | 0.2 | 0 | 0.5155 | 8.2305 | -0.1 | 0.1572 | 1.0994 | 0.0074197
2015-10-15 14:00 | 5.42 | 5.4033 | 0.016667 | 0 | -8.2488 | 49.3227 | 89.6737 | 0.32634 | 48.6388 | 54.8926 | 0 | 4.0525 | 0.2 | 0 | 0.271 | 4.3235 | 0.5 | 0.63511 | 1.0975 | 0.0038908
2015-10-15 15:00 | 0.53 | 0.52 | 0.01 | 0 | -8.2643 | 64.3249 | 92.4841 | -2.4841 | 63.2203 | 68.3978 | 0 | 0.39 | 0.2 | 0 | 0.0265 | 0.4165 | 0.9 | 0.91302 | 1.0963 | 0.00037444
2015-10-15 16:00 | 0.35333 | 0.34667 | 0.0066667 | 0 | -8.2798 | 79.3272 | 95.6797 | -5.6797 | 77.7565 | 82.3414 | 0 | 0.26 | 0.2 | 0 | 0.017667 | 0.27767 | 1.3 | 1.3087 | 1.0948 | 0.00024926
2015-10-15 17:00 | 0.17667 | 0.17333 | 0.0033333 | 0 | -8.2953 | 94.3294 | 99.0563 | -9.0563 | 92.3353 | 96.5201 | 0 | 0.13 | 0.2 | 0 | 0.0088333 | 0.13883 | 1.6 | 1.6043 | 1.0936 | 0.0001245
2015-10-15 18:00 | 0 | 0 | 0 | 0 | -8.3108 | 109.3317 | 102.3974 | -12.3974 | 107.0595 | 110.823 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-10-15 19:00 | 0 | 0 | 0 | 0 | -8.3263 | 124.3339 | 105.482 | -15.482 | 122.0242 | 125.1723 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0968 | 0
2015-10-15 20:00 | 0 | 0 | 0 | 0 | -8.3418 | 139.3361 | 108.0952 | -18.0952 | 137.2912 | 139.4809 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-10-15 21:00 | 0 | 0 | 0 | 0 | -8.3573 | 154.3383 | 110.0426 | -20.0426 | 152.8657 | 153.5591 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-10-15 22:00 | 0 | 0 | 0 | 0 | -8.3728 | 169.3406 | 111.1694 | -21.1694 | 168.6827 | 166.5181 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-10-15 23:00 | 0 | 0 | 0 | 0 | -8.3883 | 184.3428 | 111.3822 | -21.3822 | -175.3855 | 170.4344 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-10-16 | 0 | 0 | 0 | 0 | -8.4038 | -160.655 | 110.6639 | -20.6639 | -159.4986 | 159.298 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.0948 | 0
2015-10-16 01:00 | 0 | 0 | 0 | 0 | -8.4193 | -145.6528 | 109.0767 | -19.0767 | -143.8034 | 145.4785 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-10-16 02:00 | 0 | 0 | 0 | 0 | -8.4348 | -130.6506 | 106.7519 | -16.7519 | -128.3947 | 131.2355 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-10-16 03:00 | 0 | 0 | 0 | 0 | -8.4503 | -115.6484 | 103.87 | -13.87 | -113.2979 | 116.8975 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-10-16 04:00 | 0.03 | 0.026667 | 0.0033333 | 0 | -8.4657 | -100.6462 | 100.6398 | -10.6398 | -98.4738 | 102.5762 | 0 | 0.02 | 0.2 | 0 | 0.0015 | 0.0215 | 1.9 | 1.9007 | 1.0924 | 1.9259e-05
2015-10-16 05:00 | 0.06 | 0.053333 | 0.0066667 | 0 | -8.4812 | -85.6441 | 97.2815 | -7.2815 | -83.8396 | 88.3489 | 0 | 0.04 | 0.2 | 0 | 0.003 | 0.043 | 2.3 | 2.3013 | 1.0908 | 3.8461e-05
2015-10-16 06:00 | 0.09 | 0.08 | 0.01 | 0 | -8.4967 | -70.6419 | 94.0148 | -4.0148 | -69.2938 | 74.3091 | 0 | 0.06 | 0.2 | 0 | 0.0045 | 0.0645 | 1.9 | 1.902 | 1.0924 | 5.7777e-05
2015-10-16 07:00 | 6.4133 | 4.8933 | 1.52 | 0 | -8.5121 | -55.6397 | 91.0501 | -1.0501 | -54.7408 | 60.6141 | 0 | 3.67 | 0.2 | 0 | 0.32067 | 3.9907 | 1.6 | 1.7247 | 1.0931 | 0.003577
2015-10-16 08:00 | 12.7367 | 9.7067 | 3.03 | 0 | -8.5276 | -40.6375 | 88.5803 | 1.4197 | -40.1109 | 47.5831 | 0 | 7.28 | 0.2 | 0 | 0.63683 | 7.9168 | 1.2 | 1.4474 | 1.0942 | 0.0071034
2015-10-16 09:00 | 19.06 | 14.52 | 4.54 | 80.5856 | -8.5431 | -25.6354 | 86.7704 | 3.2296 | -25.3738 | 35.962 | 65.2266 | 10.89 | 0.2 | 0 | 0.953 | 77.0696 | 1.1 | 3.5084 | 1.086 | 0.06863
2015-10-16 10:00 | 22.42 | 15.9867 | 6.4333 | 86.7122 | -8.5585 | -10.6332 | 85.7452 | 4.2548 | -10.5428 | 27.606 | 76.8405 | 11.99 | 0.2 | 0 | 1.121 | 89.9515 | 1.1 | 3.911 | 1.0844 | 0.079982
2015-10-16 11:00 | 25.78 | 17.4533 | 8.3267 | 107.9923 | -8.574 | 4.369 | 85.5779 | 4.4221 | 4.333 | 25.9034 | 97.1425 | 13.09 | 0.2 | 0 | 1.289 | 111.5215 | 1.2 | 4.685 | 1.0813 | 0.098879
2015-10-16 12:00 | 29.14 | 18.92 | 10.22 | 157.5699 | -8.5894 | 19.3711 | 86.2812 | 3.7188 | 19.1873 | 31.9376 | 133.7177 | 14.19 | 0.2 | 0 | 1.457 | 149.3647 | 1.2 | 5.8676 | 1.0765 | 0.13185
2015-10-16 13:00 | 19.6433 | 12.7767 | 6.8667 | 0 | -8.6048 | 34.3733 | 87.8063 | 2.1937 | 33.9615 | 42.5316 | 0 | 9.5825 | 0.2 | 0 | 0.98217 | 10.5647 | 1.1 | 1.4301 | 1.0943 | 0.0094798
2015-10-16 14:00 | 10.1467 | 6.6333 | 3.5133 | 0 | -8.6203 | 49.3754 | 90.0486 | -0.048599 | 48.6266 | 55.1111 | 0 | 4.975 | 0.2 | 0 | 0.50733 | 5.4823 | 1.2 | 1.3713 | 1.0945 | 0.0049204
2015-10-16 15:00 | 0.65 | 0.49 | 0.16 | 0 | -8.6357 | 64.3775 | 92.8583 | -2.8583 | 63.1956 | 68.5856 | 0 | 0.3675 | 0.2 | 0 | 0.0325 | 0.4 | 1.4 | 1.4125 | 1.0943 | 0.00035895
2015-10-16 16:00 | 0.43333 | 0.32667 | 0.10667 | 0 | -8.6512 | 79.3797 | 96.0533 | -6.0533 | 77.7242 | 82.5085 | 0 | 0.245 | 0.2 | 0 | 0.021667 | 0.26667 | 1.3 | 1.3083 | 1.0948 | 0.00023939
2015-10-16 17:00 | 0.21667 | 0.16333 | 0.053333 | 0 | -8.6666 | 94.3818 | 99.4296 | -9.4296 | 92.3007 | 96.6737 | 0 | 0.1225 | 0.2 | 0 | 0.010833 | 0.13333 | 0.8 | 0.80417 | 1.0968 | 0.00011991
2015-10-16 18:00 | 0 | 0 | 0 | 0 | -8.682 | 109.3839 | 102.7709 | -12.7709 | 107.0283 | 110.969 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-10-16 19:00 | 0 | 0 | 0 | 0 | -8.6974 | 124.386 | 105.856 | -15.856 | 122.0022 | 125.317 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-10-16 20:00 | 0 | 0 | 0 | 0 | -8.7129 | 139.3882 | 108.4697 | -18.4697 | 137.2843 | 139.6338 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-10-16 21:00 | 0 | 0 | 0 | 0 | -8.7283 | 154.3903 | 110.4168 | -20.4168 | 152.879 | 153.7411 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-10-16 22:00 | 0 | 0 | 0 | 0 | -8.7437 | 169.3924 | 111.5422 | -21.5422 | 168.7198 | 166.7961 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-10-16 23:00 | 0 | 0 | 0 | 0 | -8.7591 | 184.3945 | 111.752 | -21.752 | -175.3232 | 170.7435 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-10-17 | 0 | 0 | 0 | 0 | -8.7745 | -160.6034 | 111.0293 | -21.0293 | -159.4125 | 159.4138 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-10-17 01:00 | 0 | 0 | 0 | 0 | -8.7899 | -145.6013 | 109.437 | -19.437 | -143.697 | 145.5415 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-10-17 02:00 | 0 | 0 | 0 | 0 | -8.8053 | -130.5993 | 107.1074 | -17.1074 | -128.2732 | 131.2826 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-10-17 03:00 | 0 | 0 | 0 | 0 | -8.8207 | -115.5972 | 104.2216 | -14.2216 | -113.1668 | 116.9426 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-10-17 04:00 | 0.0033333 | 0.0033333 | 0 | 0 | -8.8361 | -100.5951 | 100.9892 | -10.9892 | -98.3386 | 102.627 | 0 | 0.0025 | 0.2 | 0 | 0.00016667 | 0.0026667 | -1.7 | -1.6999 | 1.1068 | 2.4202e-06
2015-10-17 05:00 | 0.0066667 | 0.0066667 | 0 | 0 | -8.8515 | -85.593 | 97.6307 | -7.6307 | -83.7054 | 88.4117 | 0 | 0.005 | 0.2 | 0 | 0.00033333 | 0.0053333 | -2.7 | -2.6998 | 1.1108 | 4.8579e-06
2015-10-17 06:00 | 0.01 | 0.01 | 0 | 0 | -8.8668 | -70.591 | 94.3657 | -4.3657 | -69.1653 | 74.3912 | 0 | 0.0075 | 0.2 | 0 | 0.0005 | 0.008 | -2.6 | -2.5997 | 1.1104 | 7.2842e-06
2015-10-17 07:00 | 6.1067 | 4.53 | 1.5767 | 0 | -8.8822 | -55.5889 | 91.4044 | -1.4044 | -54.6225 | 60.7258 | 0 | 3.3975 | 0.2 | 0 | 0.30533 | 3.7028 | -2.8 | -2.6843 | 1.1107 | 0.0033726
2015-10-17 08:00 | 12.2033 | 9.05 | 3.1533 | 0 | -8.8976 | -40.5868 | 88.939 | 1.061 | -40.007 | 47.7404 | 0 | 6.7875 | 0.2 | 0 | 0.61017 | 7.3977 | -2.4 | -2.1688 | 1.1087 | 0.0067253
2015-10-17 09:00 | 18.3 | 13.57 | 4.73 | 0 | -8.913 | -25.5848 | 87.1337 | 2.8663 | -25.2879 | 36.1903 | 0 | 10.1775 | 0.2 | 0 | 0.915 | 11.0925 | -0.6 | -0.25336 | 1.101 | 0.010015
2015-10-17 10:00 | 19.7733 | 14.3733 | 5.4 | 79.6521 | -8.9283 | -10.5827 | 86.1127 | 3.8873 | -10.4774 | 27.9296 | 70.3745 | 10.78 | 0.2 | 0 | 0.98867 | 82.1432 | -1 | 1.567 | 1.0937 | 0.073671
2015-10-17 11:00 | 21.2467 | 15.1767 | 6.07 | 85.9111 | -8.9437 | 4.4193 | 85.9484 | 4.0516 | 4.3764 | 26.2763 | 77.0338 | 11.3825 | 0.2 | 0 | 1.0623 | 89.4787 | -1.3 | 1.4962 | 1.094 | 0.080271
2015-10-17 12:00 | 22.72 | 15.98 | 6.74 | 115.463 | -8.9591 | 19.4213 | 86.6535 | 3.3465 | 19.2091 | 32.2636 | 97.6356 | 11.985 | 0.2 | 0 | 1.136 | 110.7566 | -1.4 | 2.0611 | 1.0918 | 0.099154
2015-10-17 13:00 | 15.2367 | 10.73 | 4.5067 | 0 | -8.9744 | 34.4234 | 88.1792 | 1.8208 | 33.9635 | 42.7941 | 0 | 8.0475 | 0.2 | 0 | 0.76183 | 8.8093 | -1.1 | -0.82471 | 1.1033 | 0.0079698
2015-10-17 14:00 | 7.7533 | 5.48 | 2.2733 | 0 | -8.9898 | 49.4254 | 90.4211 | -0.4211 | 48.612 | 55.3274 | 0 | 4.11 | 0.2 | 0 | 0.38767 | 4.4977 | -1.4 | -1.2594 | 1.105 | 0.0040755
2015-10-17 15:00 | 0.27 | 0.23 | 0.04 | 0 | -9.0051 | 64.4274 | 93.23 | -3.23 | 63.1686 | 68.7707 | 0 | 0.1725 | 0.2 | 0 | 0.0135 | 0.186 | -1.3 | -1.2942 | 1.1052 | 0.00016856
2015-10-17 16:00 | 0.18 | 0.15333 | 0.026667 | 0 | -9.0205 | 79.4294 | 96.4243 | -6.4243 | 77.6896 | 82.6726 | 0 | 0.115 | 0.2 | 0 | 0.009 | 0.124 | -1.4 | -1.3961 | 1.1056 | 0.00011242
2015-10-17 17:00 | 0.09 | 0.076667 | 0.013333 | 0 | -9.0358 | 94.4314 | 99.8003 | -9.8003 | 92.2638 | 96.8238 | 0 | 0.0575 | 0.2 | 0 | 0.0045 | 0.062 | -1.1 | -1.0981 | 1.1044 | 5.6147e-05
2015-10-17 18:00 | 0 | 0 | 0 | 0 | -9.0512 | 109.4335 | 103.1418 | -13.1418 | 106.9946 | 111.111 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-10-17 19:00 | 0 | 0 | 0 | 0 | -9.0665 | 124.4355 | 106.2276 | -16.2276 | 121.9777 | 125.457 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-10-17 20:00 | 0 | 0 | 0 | 0 | -9.0818 | 139.4375 | 108.8418 | -18.8418 | 137.2748 | 139.7811 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-10-17 21:00 | 0 | 0 | 0 | 0 | -9.0972 | 154.4395 | 110.7888 | -20.7888 | 152.8896 | 153.9159 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-10-17 22:00 | 0 | 0 | 0 | 0 | -9.1125 | 169.4414 | 111.9128 | -21.9128 | 168.7543 | 167.066 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-10-17 23:00 | 0 | 0 | 0 | 0 | -9.1278 | 184.4434 | 112.1197 | -22.1197 | -175.2636 | 171.0473 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-10-18 | 0 | 0 | 0 | 0 | -9.1431 | -160.5546 | 111.3928 | -21.3928 | -159.3291 | 159.5254 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-10-18 01:00 | 0 | 0 | 0 | 0 | -9.1584 | -145.5526 | 109.7957 | -19.7957 | -143.5935 | 145.6032 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-10-18 02:00 | 0 | 0 | 0 | 0 | -9.1738 | -130.5507 | 107.4612 | -17.4612 | -128.1545 | 131.3299 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-10-18 03:00 | 0 | 0 | 0 | 0 | -9.1891 | -115.5487 | 104.5717 | -14.5717 | -113.0386 | 116.9886 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-10-18 04:00 | 0 | 0 | 0 | 0 | -9.2044 | -100.5467 | 101.3372 | -11.3372 | -98.2063 | 102.6793 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-10-18 05:00 | 0 | 0 | 0 | 0 | -9.2197 | -85.5448 | 97.9784 | -7.9784 | -83.5742 | 88.4766 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0972 | 0
2015-10-18 06:00 | 0 | 0 | 0 | 0 | -9.235 | -70.5428 | 94.7152 | -4.7152 | -69.0399 | 74.476 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-10-18 07:00 | 3.05 | 3.05 | 0 | 0 | -9.2502 | -55.5409 | 91.7571 | -1.7571 | -54.5074 | 60.8404 | 0 | 2.2875 | 0.2 | 0 | 0.1525 | 2.44 | 1.2 | 1.2763 | 1.0949 | 0.0021907
2015-10-18 08:00 | 6.1 | 6.1 | 0 | 0 | -9.2655 | -40.5389 | 89.296 | 0.70402 | -39.9062 | 47.9007 | 0 | 4.575 | 0.2 | 0 | 0.305 | 4.88 | 1.4 | 1.5525 | 1.0938 | 0.0043769
2015-10-18 09:00 | 9.15 | 9.15 | 0 | 0 | -9.2808 | -25.537 | 87.4952 | 2.5048 | -25.205 | 36.4212 | 0 | 6.8625 | 0.2 | 0 | 0.4575 | 7.32 | 1.3 | 1.5288 | 1.0939 | 0.0065659
2015-10-18 10:00 | 9.59 | 9.5767 | 0.013333 | 0.21705 | -9.2961 | -10.5351 | 86.4781 | 3.5219 | -10.4151 | 28.2534 | 0.19119 | 7.1825 | 0.2 | 0 | 0.4795 | 7.8532 | 1 | 1.2454 | 1.095 | 0.0070515
2015-10-18 11:00 | 10.03 | 10.0033 | 0.026667 | 0.41512 | -9.3114 | 4.4669 | 86.3169 | 3.6831 | 4.417 | 26.6467 | 0.37103 | 7.5025 | 0.2 | 0 | 0.5015 | 8.375 | 1.6 | 1.8617 | 1.0926 | 0.0075031
2015-10-18 12:00 | 10.47 | 10.43 | 0.04 | 0 | -9.3266 | 19.4688 | 87.0236 | 2.9764 | 19.2282 | 32.5872 | 0 | 7.8225 | 0.2 | 0 | 0.5235 | 8.346 | 1.4 | 1.6608 | 1.0934 | 0.0074826
2015-10-18 13:00 | 6.9933 | 6.9667 | 0.026667 | 0 | -9.3419 | 34.4707 | 88.5497 | 1.4503 | 33.963 | 43.0544 | 0 | 5.225 | 0.2 | 0 | 0.34967 | 5.5747 | 1.2 | 1.3742 | 1.0945 | 0.0050032
2015-10-18 14:00 | 3.5167 | 3.5033 | 0.013333 | 0 | -9.3572 | 49.4726 | 90.791 | -0.79105 | 48.595 | 55.5413 | 0 | 2.6275 | 0.2 | 0 | 0.17583 | 2.8033 | 1.4 | 1.4876 | 1.094 | 0.0025149
2015-10-18 15:00 | 0.04 | 0.04 | 0 | 0 | -9.3724 | 64.4745 | 93.5991 | -3.5991 | 63.1392 | 68.9531 | 0 | 0.03 | 0.2 | 0 | 0.002 | 0.032 | 1.2 | 1.201 | 1.0952 | 2.8738e-05
2015-10-18 16:00 | 0.026667 | 0.026667 | 0 | 0 | -9.3877 | 79.4764 | 96.7926 | -6.7926 | 77.6526 | 82.8336 | 0 | 0.02 | 0.2 | 0 | 0.0013333 | 0.021333 | 0.8 | 0.80067 | 1.0968 | 1.9187e-05
2015-10-18 17:00 | 0.013333 | 0.013333 | 0 | 0 | -9.403 | 94.4783 | 100.1683 | -10.1683 | 92.2244 | 96.9703 | 0 | 0.01 | 0.2 | 0 | 0.00066667 | 0.010667 | 1.2 | 1.2003 | 1.0952 | 9.5793e-06
2015-10-18 18:00 | 0 | 0 | 0 | 0 | -9.4182 | 109.4802 | 103.5101 | -13.5101 | 106.9585 | 111.2488 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2 | 2 | 1.092 | 0
2015-10-18 19:00 | 0 | 0 | 0 | 0 | -9.4334 | 124.4821 | 106.5965 | -16.5965 | 121.9506 | 125.5922 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0904 | 0
2015-10-18 20:00 | 0 | 0 | 0 | 0 | -9.4487 | 139.484 | 109.2113 | -19.2113 | 137.2626 | 139.9226 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0896 | 0
2015-10-18 21:00 | 0 | 0 | 0 | 0 | -9.4639 | 154.4858 | 111.1583 | -21.1583 | 152.8975 | 154.0835 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0888 | 0
2015-10-18 22:00 | 0 | 0 | 0 | 0 | -9.4792 | 169.4877 | 112.2811 | -22.2811 | 168.7859 | 167.3272 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0904 | 0
2015-10-18 23:00 | 0 | 0 | 0 | 0 | -9.4944 | 184.4896 | 112.4854 | -22.4854 | -175.2069 | 171.3453 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0876 | 0
2015-10-19 | 0 | 0 | 0 | 0 | -9.5096 | -160.5086 | 111.7544 | -21.7544 | -159.2486 | 159.6328 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0852 | 0
2015-10-19 01:00 | 0 | 0 | 0 | 0 | -9.5248 | -145.5067 | 110.1525 | -20.1525 | -143.4928 | 145.6636 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.084 | 0
2015-10-19 02:00 | 0 | 0 | 0 | 0 | -9.5401 | -130.5049 | 107.8134 | -17.8134 | -128.0387 | 131.3773 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.088 | 0
2015-10-19 03:00 | 0 | 0 | 0 | 0 | -9.5553 | -115.503 | 104.9202 | -14.9202 | -112.9133 | 117.0357 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0904 | 0
2015-10-19 04:00 | 0 | 0 | 0 | 0 | -9.5705 | -100.5012 | 101.6836 | -11.6836 | -98.0771 | 102.7334 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0888 | 0
2015-10-19 05:00 | 0 | 0 | 0 | 0 | -9.5857 | -85.4993 | 98.3247 | -8.3247 | -83.4461 | 88.5438 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.0892 | 0
2015-10-19 06:00 | 0 | 0 | 0 | 0 | -9.6009 | -70.4975 | 95.0631 | -5.0631 | -68.9177 | 74.5633 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0884 | 0
2015-10-19 07:00 | 4.8767 | 3.56 | 1.3167 | 0 | -9.6161 | -55.4957 | 92.1083 | -2.1083 | -54.3955 | 60.9578 | 0 | 2.67 | 0.2 | 0 | 0.24383 | 2.9138 | 2.6 | 2.6911 | 1.0892 | 0.0026026
2015-10-19 08:00 | 9.7533 | 7.12 | 2.6333 | 0 | -9.6313 | -40.4939 | 89.6513 | 0.34873 | -39.8086 | 48.064 | 0 | 5.34 | 0.2 | 0 | 0.48767 | 5.8277 | 2.5 | 2.6821 | 1.0893 | 0.0052053
2015-10-19 09:00 | 14.63 | 10.68 | 3.95 | 0 | -9.6465 | -25.492 | 87.8548 | 2.1452 | -25.1252 | 36.6544 | 0 | 8.01 | 0.2 | 0 | 0.7315 | 8.7415 | 2.1 | 2.3732 | 1.0905 | 0.0078168
2015-10-19 10:00 | 14.4467 | 10.7467 | 3.7 | 67.1541 | -9.6617 | -10.4902 | 86.8416 | 3.1584 | -10.3557 | 28.5772 | 58.973 | 8.06 | 0.2 | 0 | 0.72233 | 67.7553 | 1.8 | 3.9174 | 1.0843 | 0.060245
2015-10-19 11:00 | 14.2633 | 10.8133 | 3.45 | 59.6271 | -9.6768 | 4.5116 | 86.683 | 3.317 | 4.4547 | 27.0144 | 53.1213 | 8.11 | 0.2 | 0 | 0.71317 | 61.9445 | 3 | 4.9358 | 1.0803 | 0.054871
2015-10-19 12:00 | 14.08 | 10.88 | 3.2 | 0 | -9.692 | 19.5134 | 87.3912 | 2.6088 | 19.2445 | 32.9081 | 0 | 8.16 | 0.2 | 0 | 0.704 | 8.864 | 3.1 | 3.377 | 1.0865 | 0.0078971
2015-10-19 13:00 | 9.3967 | 7.2633 | 2.1333 | 0 | -9.7072 | 34.5152 | 88.9175 | 1.0825 | 33.9598 | 43.3124 | 0 | 5.4475 | 0.2 | 0 | 0.46983 | 5.9173 | 2.2 | 2.3849 | 1.0905 | 0.0052911
2015-10-19 14:00 | 4.7133 | 3.6467 | 1.0667 | 0 | -9.7224 | 49.517 | 91.1583 | -1.1583 | 48.5754 | 55.7526 | 0 | 2.735 | 0.2 | 0 | 0.23567 | 2.9707 | 2.7 | 2.7928 | 1.0888 | 0.0026523
2015-10-19 15:00 | 0.03 | 0.03 | 0 | 0 | -9.7375 | 64.5187 | 93.9654 | -3.9654 | 63.1073 | 69.1326 | 0 | 0.0225 | 0.2 | 0 | 0.0015 | 0.024 | 2.4 | 2.4007 | 1.0904 | 2.1459e-05
2015-10-19 16:00 | 0.02 | 0.02 | 0 | 0 | -9.7527 | 79.5205 | 97.158 | -7.158 | 77.6132 | 82.9913 | 0 | 0.015 | 0.2 | 0 | 0.001 | 0.016 | 1.7 | 1.7005 | 1.0932 | 1.4343e-05
2015-10-19 17:00 | 0.01 | 0.01 | 0 | 0 | -9.7678 | 94.5223 | 100.5335 | -10.5335 | 92.1826 | 97.1132 | 0 | 0.0075 | 0.2 | 0 | 0.0005 | 0.008 | 2.3 | 2.3003 | 1.0908 | 7.1556e-06
2015-10-19 18:00 | 0 | 0 | 0 | 0 | -9.783 | 109.5241 | 103.8755 | -13.8755 | 106.9197 | 111.3825 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-10-19 19:00 | 0 | 0 | 0 | 0 | -9.7981 | 124.5258 | 106.9626 | -16.9626 | 121.9209 | 125.7226 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-10-19 20:00 | 0 | 0 | 0 | 0 | -9.8133 | 139.5276 | 109.5782 | -19.5782 | 137.2476 | 140.0583 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-10-19 21:00 | 0 | 0 | 0 | 0 | -9.8284 | 154.5293 | 111.5253 | -21.5253 | 152.9025 | 154.2436 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.096 | 0
2015-10-19 22:00 | 0 | 0 | 0 | 0 | -9.8436 | 169.5311 | 112.6471 | -22.6471 | 168.8146 | 167.5793 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-10-19 23:00 | 0 | 0 | 0 | 0 | -9.8587 | 184.5328 | 112.8488 | -22.8488 | -175.1531 | 171.6373 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-10-20 | 0 | 0 | 0 | 0 | -9.8738 | -160.4654 | 112.114 | -22.114 | -159.171 | 159.7362 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.1048 | 0
2015-10-20 01:00 | 0 | 0 | 0 | 0 | -9.889 | -145.4637 | 110.5074 | -20.5074 | -143.395 | 145.7228 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.1056 | 0
2015-10-20 02:00 | 0 | 0 | 0 | 0 | -9.9041 | -130.462 | 108.1639 | -18.1639 | -127.926 | 131.425 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.1064 | 0
2015-10-20 03:00 | 0 | 0 | 0 | 0 | -9.9192 | -115.4602 | 105.2671 | -15.2671 | -112.7911 | 117.0839 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-10-20 04:00 | 0 | 0 | 0 | 0 | -9.9343 | -100.4585 | 102.0285 | -12.0285 | -97.951 | 102.7891 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-10-20 05:00 | 0 | 0 | 0 | 0 | -9.9494 | -85.4568 | 98.6694 | -8.6694 | -83.3212 | 88.6131 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-10-20 06:00 | 0 | 0 | 0 | 0 | -9.9645 | -70.4551 | 95.4095 | -5.4095 | -68.7988 | 74.6531 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-10-20 07:00 | 2.9467 | 2.4267 | 0.52 | 0 | -9.9796 | -55.4534 | 92.4577 | -2.4577 | -54.2868 | 61.0781 | 0 | 1.82 | 0.2 | 0 | 0.14733 | 1.9673 | -2 | -1.9385 | 1.1078 | 0.001787
2015-10-20 08:00 | 5.8933 | 4.8533 | 1.04 | 0 | -9.9947 | -40.4517 | 90.0047 | -0.0047085 | -39.7143 | 48.2301 | 0 | 3.64 | 0.2 | 0 | 0.29467 | 3.9347 | -2.2 | -2.077 | 1.1083 | 0.0035759
2015-10-20 09:00 | 8.84 | 7.28 | 1.56 | 0 | -10.0098 | -25.45 | 88.2124 | 1.7876 | -25.0487 | 36.8899 | 0 | 5.46 | 0.2 | 0 | 0.442 | 5.902 | -2.1 | -1.9156 | 1.1077 | 0.0053607
2015-10-20 10:00 | 9.6467 | 7.8267 | 1.82 | 0 | -10.0249 | -10.4483 | 87.2028 | 2.7972 | -10.2994 | 28.901 | 0 | 5.87 | 0.2 | 0 | 0.48233 | 6.3523 | -2.2 | -2.0015 | 1.108 | 0.0057715
2015-10-20 11:00 | 10.4533 | 8.3733 | 2.08 | 0 | -10.04 | 4.5534 | 87.0469 | 2.9531 | 4.4895 | 27.3793 | 0 | 6.28 | 0.2 | 0 | 0.52267 | 6.8027 | -2.9 | -2.6874 | 1.1107 | 0.006196
2015-10-20 12:00 | 11.26 | 8.92 | 2.34 | 0 | -10.0551 | 19.5551 | 87.7563 | 2.2437 | 19.2581 | 33.2263 | 0 | 6.69 | 0.2 | 0 | 0.563 | 7.253 | -3.2 | -2.9733 | 1.1119 | 0.0066129
2015-10-20 13:00 | 7.5067 | 5.9467 | 1.56 | 0 | -10.0701 | 34.5567 | 89.2827 | 0.71726 | 33.954 | 43.5678 | 0 | 4.46 | 0.2 | 0 | 0.37533 | 4.8353 | -3.7 | -3.5489 | 1.1142 | 0.0044178
2015-10-20 14:00 | 3.7533 | 2.9733 | 0.78 | 0 | -10.0852 | 49.5584 | 91.5228 | -1.5228 | 48.5534 | 55.9614 | 0 | 2.23 | 0.2 | 0 | 0.18767 | 2.4177 | -3.4 | -3.3244 | 1.1133 | 0.0022071
2015-10-20 15:00 | 0 | 0 | 0 | 0 | -10.1003 | 64.5601 | 94.3288 | -4.3288 | 63.073 | 69.3092 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-10-20 16:00 | 0 | 0 | 0 | 0 | -10.1153 | 79.5617 | 97.5206 | -7.5206 | 77.5713 | 83.1457 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.3 | -3.3 | 1.1132 | 0
2015-10-20 17:00 | 0 | 0 | 0 | 0 | -10.1304 | 94.5634 | 100.8956 | -10.8956 | 92.1382 | 97.2523 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-10-20 18:00 | 0 | 0 | 0 | 0 | -10.1454 | 109.565 | 104.238 | -14.238 | 106.8785 | 111.5119 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.112 | 0
2015-10-20 19:00 | 0 | 0 | 0 | 0 | -10.1605 | 124.5667 | 107.3259 | -17.3259 | 121.8884 | 125.848 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.112 | 0
2015-10-20 20:00 | 0 | 0 | 0 | 0 | -10.1755 | 139.5683 | 109.9423 | -19.9423 | 137.2299 | 140.1881 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.8 | -2.8 | 1.1112 | 0
2015-10-20 21:00 | 0 | 0 | 0 | 0 | -10.1906 | 154.5699 | 111.8896 | -21.8896 | 152.9046 | 154.3962 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-10-20 22:00 | 0 | 0 | 0 | 0 | -10.2056 | 169.5716 | 113.0105 | -23.0105 | 168.8404 | 167.8219 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.3 | -3.3 | 1.1132 | 0
2015-10-20 23:00 | 0 | 0 | 0 | 0 | -10.2207 | 184.5732 | 113.2099 | -23.2099 | -175.1023 | 171.9229 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.3 | -3.3 | 1.1132 | 0
2015-10-21 | 0 | 0 | 0 | 0 | -10.2357 | -160.4252 | 112.4714 | -22.4714 | -159.0964 | 159.8356 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.3 | -3.3 | 1.1132 | 0
2015-10-21 01:00 | 0 | 0 | 0 | 0 | -10.2507 | -145.4236 | 110.8604 | -20.8604 | -143.3004 | 145.7808 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-10-21 02:00 | 0 | 0 | 0 | 0 | -10.2657 | -130.422 | 108.5124 | -18.5124 | -127.8163 | 131.473 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.9 | -3.9 | 1.1156 | 0
2015-10-21 03:00 | 0 | 0 | 0 | 0 | -10.2807 | -115.4204 | 105.6122 | -15.6122 | -112.6721 | 117.1333 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-10-21 04:00 | 0 | 0 | 0 | 0 | -10.2957 | -100.4188 | 102.3716 | -12.3716 | -97.8282 | 102.8466 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1144 | 0
2015-10-21 05:00 | 0 | 0 | 0 | 0 | -10.3108 | -85.4172 | 99.0124 | -9.0124 | -83.1996 | 88.6846 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-10-21 06:00 | 0 | 0 | 0 | 0 | -10.3258 | -70.4156 | 95.7541 | -5.7541 | -68.6831 | 74.7455 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-10-21 07:00 | 1.7267 | 1.7267 | 0 | 0 | -10.3408 | -55.414 | 92.8054 | -2.8054 | -54.1815 | 61.2012 | 0 | 1.295 | 0.2 | 0 | 0.086333 | 1.3813 | -3.1 | -3.0568 | 1.1122 | 0.0012598
2015-10-21 08:00 | 3.4533 | 3.4533 | 0 | 0 | -10.3557 | -40.4125 | 90.3562 | -0.35621 | -39.6233 | 48.3991 | 0 | 2.59 | 0.2 | 0 | 0.17267 | 2.7627 | -3.2 | -3.1137 | 1.1125 | 0.0025201
2015-10-21 09:00 | 5.18 | 5.18 | 0 | 0 | -10.3707 | -25.4109 | 88.5679 | 1.4321 | -24.9754 | 37.1275 | 0 | 3.885 | 0.2 | 0 | 0.259 | 4.144 | -3.2 | -3.0705 | 1.1123 | 0.0037796
2015-10-21 10:00 | 5.4567 | 5.4567 | 0 | 0 | -10.3857 | -10.4093 | 87.5618 | 2.4382 | -10.2463 | 29.2244 | 0 | 4.0925 | 0.2 | 0 | 0.27283 | 4.3653 | -3.5 | -3.3636 | 1.1135 | 0.0039857
2015-10-21 11:00 | 5.7333 | 5.7333 | 0 | 0 | -10.4007 | 4.5922 | 87.4082 | 2.5918 | 4.5213 | 27.7414 | 0 | 4.3 | 0.2 | 0 | 0.28667 | 4.5867 | -3 | -2.8567 | 1.1114 | 0.0041801
2015-10-21 12:00 | 6.01 | 6.01 | 0 | 0 | -10.4157 | 19.5938 | 88.1188 | 1.8812 | 19.2689 | 33.5417 | 0 | 4.5075 | 0.2 | 0 | 0.3005 | 4.808 | -2.8 | -2.6498 | 1.1106 | 0.0043786
2015-10-21 13:00 | 4.0067 | 4.0067 | 0 | 0 | -10.4306 | 34.5953 | 89.6452 | 0.35485 | 33.9456 | 43.8207 | 0 | 3.005 | 0.2 | 0 | 0.20033 | 3.2053 | -2.8 | -2.6998 | 1.1108 | 0.0029196
2015-10-21 14:00 | 2.0033 | 2.0033 | 0 | 0 | -10.4456 | 49.5969 | 91.8843 | -1.8843 | 48.5288 | 56.1674 | 0 | 1.5025 | 0.2 | 0 | 0.10017 | 1.6027 | -2.5 | -2.4499 | 1.1098 | 0.0014585
2015-10-21 15:00 | 0 | 0 | 0 | 0 | -10.4606 | 64.5984 | 94.6892 | -4.6892 | 63.0363 | 69.4828 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-10-21 16:00 | 0 | 0 | 0 | 0 | -10.4755 | 79.6 | 97.8801 | -7.8801 | 77.5269 | 83.2967 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-10-21 17:00 | 0 | 0 | 0 | 0 | -10.4905 | 94.6015 | 101.2548 | -11.2548 | 92.0913 | 97.3876 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-10-21 18:00 | 0 | 0 | 0 | 0 | -10.5054 | 109.603 | 104.5974 | -14.5974 | 106.8346 | 111.637 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-10-21 19:00 | 0 | 0 | 0 | 0 | -10.5204 | 124.6045 | 107.6861 | -17.6861 | 121.8533 | 125.9685 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-10-21 20:00 | 0 | 0 | 0 | 0 | -10.5353 | 139.606 | 110.3034 | -20.3034 | 137.2092 | 140.312 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.1048 | 0
2015-10-21 21:00 | 0 | 0 | 0 | 0 | -10.5503 | 154.6075 | 112.2512 | -22.2512 | 152.9038 | 154.5412 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-10-21 22:00 | 0 | 0 | 0 | 0 | -10.5652 | 169.609 | 113.3714 | -23.3714 | 168.8631 | 168.0544 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-10-21 23:00 | 0 | 0 | 0 | 0 | -10.5801 | 184.6105 | 113.5686 | -23.5686 | -175.0546 | 172.2016 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-10-22 | 0 | 0 | 0 | 0 | -10.595 | -160.388 | 112.8266 | -22.8266 | -159.025 | 159.9312 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-10-22 01:00 | 0 | 0 | 0 | 0 | -10.61 | -145.3865 | 111.2112 | -21.2112 | -143.2088 | 145.8379 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-10-22 02:00 | 0 | 0 | 0 | 0 | -10.6249 | -130.385 | 108.859 | -18.859 | -127.7098 | 131.5214 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.1032 | 0
2015-10-22 03:00 | 0 | 0 | 0 | 0 | -10.6398 | -115.3835 | 105.9554 | -15.9554 | -112.5563 | 117.1838 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-10-22 04:00 | 0 | 0 | 0 | 0 | -10.6547 | -100.3821 | 102.7129 | -12.7129 | -97.7086 | 102.9058 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0972 | 0
2015-10-22 05:00 | 0 | 0 | 0 | 0 | -10.6696 | -85.3806 | 99.3536 | -9.3536 | -83.0813 | 88.7582 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0968 | 0
2015-10-22 06:00 | 0 | 0 | 0 | 0 | -10.6845 | -70.3791 | 96.0969 | -6.0969 | -68.5709 | 74.8404 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-10-22 07:00 | 1.4167 | 1.4167 | 0 | 0 | -10.6994 | -55.3777 | 93.1511 | -3.1511 | -54.0796 | 61.327 | 0 | 1.0625 | 0.2 | 0 | 0.070833 | 1.1333 | 0 | 0.035417 | 1.0999 | 0.0010221
2015-10-22 08:00 | 2.8333 | 2.8333 | 0 | 0 | -10.7143 | -40.3762 | 90.7057 | -0.70566 | -39.5357 | 48.5708 | 0 | 2.125 | 0.2 | 0 | 0.14167 | 2.2667 | 0.1 | 0.17083 | 1.0993 | 0.0020433
2015-10-22 09:00 | 4.25 | 4.25 | 0 | 0 | -10.7291 | -25.3748 | 88.9212 | 1.0788 | -24.9054 | 37.367 | 0 | 3.1875 | 0.2 | 0 | 0.2125 | 3.4 | 0.2 | 0.30625 | 1.0988 | 0.0030634
2015-10-22 10:00 | 4.4533 | 4.4533 | 0 | 0 | -10.744 | -10.3734 | 87.9183 | 2.0817 | -10.1964 | 29.5474 | 0 | 3.34 | 0.2 | 0 | 0.22267 | 3.5627 | -0.2 | -0.088667 | 1.1004 | 0.0032146
2015-10-22 11:00 | 4.6567 | 4.6567 | 0 | 0 | -10.7589 | 4.6281 | 87.767 | 2.233 | 4.55 | 28.1005 | 0 | 3.4925 | 0.2 | 0 | 0.23283 | 3.7253 | -0.2 | -0.083583 | 1.1003 | 0.0033613
2015-10-22 12:00 | 4.86 | 4.86 | 0 | 0 | -10.7737 | 19.6295 | 88.4785 | 1.5215 | 19.2768 | 33.854 | 0 | 3.645 | 0.2 | 0 | 0.243 | 3.888 | -0.6 | -0.4785 | 1.1019 | 0.0035131
2015-10-22 13:00 | 3.24 | 3.24 | 0 | 0 | -10.7886 | 34.6309 | 90.0046 | -0.0046454 | 33.9344 | 44.0708 | 0 | 2.43 | 0.2 | 0 | 0.162 | 2.592 | -0.5 | -0.419 | 1.1017 | 0.0023415
2015-10-22 14:00 | 1.62 | 1.62 | 0 | 0 | -10.8035 | 49.6323 | 92.2429 | -2.2429 | 48.5016 | 56.3705 | 0 | 1.215 | 0.2 | 0 | 0.081 | 1.296 | -0.7 | -0.6595 | 1.1026 | 0.0011718
2015-10-22 15:00 | 0 | 0 | 0 | 0 | -10.8183 | 64.6338 | 95.0465 | -5.0465 | 62.997 | 69.6532 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-10-22 16:00 | 0 | 0 | 0 | 0 | -10.8332 | 79.6352 | 98.2364 | -8.2364 | 77.4801 | 83.4442 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-10-22 17:00 | 0 | 0 | 0 | 0 | -10.848 | 94.6366 | 101.6107 | -11.6107 | 92.0419 | 97.5191 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-10-22 18:00 | 0 | 0 | 0 | 0 | -10.8629 | 109.638 | 104.9536 | -14.9536 | 106.788 | 111.7577 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.102 | 0
2015-10-22 19:00 | 0 | 0 | 0 | 0 | -10.8777 | 124.6393 | 108.0433 | -18.0433 | 121.8153 | 126.0839 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-10-22 20:00 | 0 | 0 | 0 | 0 | -10.8925 | 139.6407 | 110.6616 | -20.6616 | 137.1857 | 140.4298 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-10-22 21:00 | 0 | 0 | 0 | 0 | -10.9073 | 154.6421 | 112.6099 | -22.6099 | 152.9 | 154.6785 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-10-22 22:00 | 0 | 0 | 0 | 0 | -10.9222 | 169.6435 | 113.7295 | -23.7295 | 168.8827 | 168.2766 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-10-22 23:00 | 0 | 0 | 0 | 0 | -10.937 | 184.6449 | 113.9247 | -23.9247 | -175.01 | 172.4731 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-10-23 | 0 | 0 | 0 | 0 | -10.9518 | -160.3538 | 113.1793 | -23.1793 | -158.9567 | 160.0229 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-10-23 01:00 | 0 | 0 | 0 | 0 | -10.9666 | -145.3524 | 111.5599 | -21.5599 | -143.1205 | 145.8941 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-10-23 02:00 | 0 | 0 | 0 | 0 | -10.9814 | -130.3511 | 109.2036 | -19.2036 | -127.6066 | 131.5701 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-10-23 03:00 | 0 | 0 | 0 | 0 | -10.9962 | -115.3497 | 106.2967 | -16.2967 | -112.4438 | 117.2356 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-10-23 04:00 | 0 | 0 | 0 | 0 | -11.011 | -100.3484 | 103.0524 | -13.0524 | -97.5923 | 102.9669 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-10-23 05:00 | 0 | 0 | 0 | 0 | -11.0258 | -85.347 | 99.6929 | -9.6929 | -82.9665 | 88.8341 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-10-23 06:00 | 0 | 0 | 0 | 0 | -11.0406 | -70.3457 | 96.4377 | -6.4377 | -68.4621 | 74.9379 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-10-23 07:00 | 1.12 | 1.06 | 0.06 | 0 | -11.0553 | -55.3444 | 93.4948 | -3.4948 | -53.9812 | 61.4555 | 0 | 0.795 | 0.2 | 0 | 0.056 | 0.851 | -0.3 | -0.27341 | 1.1011 | 0.00076837
2015-10-23 08:00 | 2.24 | 2.12 | 0.12 | 0 | -11.0701 | -40.3431 | 91.053 | -1.053 | -39.4515 | 48.745 | 0 | 1.59 | 0.2 | 0 | 0.112 | 1.702 | 0.1 | 0.15319 | 1.0994 | 0.0015343
2015-10-23 09:00 | 3.36 | 3.18 | 0.18 | 0 | -11.0849 | -25.3418 | 89.2721 | 0.72789 | -24.8387 | 37.6083 | 0 | 2.385 | 0.2 | 0 | 0.168 | 2.553 | 0.2 | 0.27978 | 1.0989 | 0.0023005
2015-10-23 10:00 | 3.5667 | 3.36 | 0.20667 | 0 | -11.0997 | -10.3404 | 88.2724 | 1.7276 | -10.1496 | 29.8698 | 0 | 2.52 | 0.2 | 0 | 0.17833 | 2.6983 | 0.9 | 0.98432 | 1.0961 | 0.0024252
2015-10-23 11:00 | 3.7733 | 3.54 | 0.23333 | 0 | -11.1144 | 4.6609 | 88.123 | 1.877 | 4.5757 | 28.4565 | 0 | 2.655 | 0.2 | 0 | 0.18867 | 2.8437 | 1.4 | 1.4889 | 1.094 | 0.0025511
2015-10-23 12:00 | 3.98 | 3.72 | 0.26 | 0 | -11.1292 | 19.6622 | 88.8353 | 1.1647 | 19.2818 | 34.1633 | 0 | 2.79 | 0.2 | 0 | 0.199 | 2.989 | 2.3 | 2.3934 | 1.0904 | 0.0026726
2015-10-23 13:00 | 2.6533 | 2.48 | 0.17333 | 0 | -11.1439 | 34.6634 | 90.3611 | -0.36111 | 33.9205 | 44.318 | 0 | 1.86 | 0.2 | 0 | 0.13267 | 1.9927 | 2 | 2.0623 | 1.0918 | 0.0017839
2015-10-23 14:00 | 1.3267 | 1.24 | 0.086667 | 0 | -11.1587 | 49.6647 | 92.5982 | -2.5982 | 48.4718 | 56.5706 | 0 | 0.93 | 0.2 | 0 | 0.066333 | 0.99633 | 2.3 | 2.3311 | 1.0907 | 0.00089107
2015-10-23 15:00 | 0 | 0 | 0 | 0 | -11.1734 | 64.666 | 95.4006 | -5.4006 | 62.9551 | 69.8204 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0916 | 0
2015-10-23 16:00 | 0 | 0 | 0 | 0 | -11.1881 | 79.6673 | 98.5894 | -8.5894 | 77.4307 | 83.5881 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0928 | 0
2015-10-23 17:00 | 0 | 0 | 0 | 0 | -11.2029 | 94.6686 | 101.9632 | -11.9632 | 91.9899 | 97.6465 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0936 | 0
2015-10-23 18:00 | 0 | 0 | 0 | 0 | -11.2176 | 109.6698 | 105.3065 | -15.3065 | 106.7388 | 111.874 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-10-23 19:00 | 0 | 0 | 0 | 0 | -11.2323 | 124.6711 | 108.3971 | -18.3971 | 121.7746 | 126.1942 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-10-23 20:00 | 0 | 0 | 0 | 0 | -11.247 | 139.6723 | 111.0166 | -21.0166 | 137.1593 | 140.5416 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-10-23 21:00 | 0 | 0 | 0 | 0 | -11.2617 | 154.6736 | 112.9656 | -22.9656 | 152.893 | 154.8079 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-10-23 22:00 | 0 | 0 | 0 | 0 | -11.2764 | 169.6748 | 114.0848 | -24.0848 | 168.8992 | 168.488 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-10-23 23:00 | 0 | 0 | 0 | 0 | -11.2911 | 184.6761 | 114.2782 | -24.2782 | -174.9686 | 172.7368 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-10-24 | 0 | 0 | 0 | 0 | -11.3058 | -160.3227 | 113.5296 | -23.5296 | -158.8917 | 160.1109 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-10-24 01:00 | 0 | 0 | 0 | 0 | -11.3205 | -145.3215 | 111.9062 | -21.9062 | -143.0355 | 145.9494 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-10-24 02:00 | 0 | 0 | 0 | 0 | -11.3352 | -130.3202 | 109.5459 | -19.5459 | -127.5067 | 131.6194 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-10-24 03:00 | 0 | 0 | 0 | 0 | -11.3499 | -115.319 | 106.6359 | -16.6359 | -112.3348 | 117.2887 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-10-24 04:00 | 0 | 0 | 0 | 0 | -11.3646 | -100.3178 | 103.3898 | -13.3898 | -97.4796 | 103.0297 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-10-24 05:00 | 0 | 0 | 0 | 0 | -11.3792 | -85.3166 | 100.0302 | -10.0302 | -82.8551 | 88.9122 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-10-24 06:00 | 0 | 0 | 0 | 0 | -11.3939 | -70.3154 | 96.7765 | -6.7765 | -68.3568 | 75.0378 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.3 | -3.3 | 1.1132 | 0
2015-10-24 07:00 | 0.83333 | 0.83333 | 0 | 0 | -11.4086 | -55.3142 | 93.8364 | -3.8364 | -53.8862 | 61.5866 | 0 | 0.625 | 0.2 | 0 | 0.041667 | 0.66667 | -3.2 | -3.1792 | 1.1127 | 0.00060829
2015-10-24 08:00 | 1.6667 | 1.6667 | 0 | 0 | -11.4232 | -40.313 | 91.398 | -1.398 | -39.3708 | 48.9217 | 0 | 1.25 | 0.2 | 0 | 0.083333 | 1.3333 | -3.5 | -3.4583 | 1.1138 | 0.0012178
2015-10-24 09:00 | 2.5 | 2.5 | 0 | 0 | -11.4379 | -25.3118 | 89.6206 | 0.37937 | -24.7754 | 37.8512 | 0 | 1.875 | 0.2 | 0 | 0.125 | 2 | -2.6 | -2.5375 | 1.1101 | 0.0018206
2015-10-24 10:00 | 2.68 | 2.6733 | 0.0066667 | 0 | -11.4525 | -10.3106 | 88.6238 | 1.3762 | -10.1061 | 30.1913 | 0 | 2.005 | 0.2 | 0 | 0.134 | 2.139 | -1.4 | -1.3332 | 1.1053 | 0.0019387
2015-10-24 11:00 | 2.86 | 2.8467 | 0.013333 | 0 | -11.4672 | 4.6905 | 88.4763 | 1.5237 | 4.5983 | 28.8093 | 0 | 2.135 | 0.2 | 0 | 0.143 | 2.278 | 0.4 | 0.47119 | 1.0981 | 0.0020512
2015-10-24 12:00 | 3.04 | 3.02 | 0.02 | 0 | -11.4818 | 19.6917 | 89.1892 | 0.81085 | 19.2839 | 34.4692 | 0 | 2.265 | 0.2 | 0 | 0.152 | 2.417 | 0.2 | 0.27553 | 1.0989 | 0.0021779
2015-10-24 13:00 | 2.0267 | 2.0133 | 0.013333 | 0 | -11.4964 | 34.6929 | 90.7144 | -0.71442 | 33.9039 | 44.5622 | 0 | 1.51 | 0.2 | 0 | 0.10133 | 1.6113 | 0.6 | 0.65035 | 1.0974 | 0.00145
2015-10-24 14:00 | 1.0133 | 1.0067 | 0.0066667 | 0 | -11.5111 | 49.694 | 92.9503 | -2.9503 | 48.4393 | 56.7676 | 0 | 0.755 | 0.2 | 0 | 0.050667 | 0.80567 | -0.4 | -0.37482 | 1.1015 | 0.0007277
2015-10-24 15:00 | 0 | 0 | 0 | 0 | -11.5257 | 64.6952 | 95.7512 | -5.7512 | 62.9107 | 69.9842 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-10-24 16:00 | 0 | 0 | 0 | 0 | -11.5403 | 79.6963 | 98.9389 | -8.9389 | 77.3787 | 83.7284 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-10-24 17:00 | 0 | 0 | 0 | 0 | -11.5549 | 94.6975 | 102.3124 | -12.3124 | 91.9353 | 97.7699 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-10-24 18:00 | 0 | 0 | 0 | 0 | -11.5695 | 109.6986 | 105.656 | -15.656 | 106.6868 | 111.9857 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-10-24 19:00 | 0 | 0 | 0 | 0 | -11.5841 | 124.6997 | 108.7476 | -18.7476 | 121.731 | 126.2994 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-10-24 20:00 | 0 | 0 | 0 | 0 | -11.5987 | 139.7008 | 111.3683 | -21.3683 | 137.1298 | 140.6473 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0972 | 0
2015-10-24 21:00 | 0 | 0 | 0 | 0 | -11.6133 | 154.702 | 113.3181 | -23.3181 | 152.883 | 154.9295 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-10-24 22:00 | 0 | 0 | 0 | 0 | -11.6279 | 169.7031 | 114.4371 | -24.4371 | 168.9124 | 168.688 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0968 | 0
2015-10-24 23:00 | 0 | 0 | 0 | 0 | -11.6425 | 184.7042 | 114.6289 | -24.6289 | -174.9306 | 172.9924 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.0948 | 0
2015-10-25 | 0 | 0 | 0 | 0 | -11.6571 | -160.2947 | 113.8774 | -23.8774 | -158.83 | 160.1953 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-10-25 01:00 | 0 | 0 | 0 | 0 | -11.6716 | -145.2936 | 112.2502 | -22.2502 | -142.9539 | 146.0039 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0924 | 0
2015-10-25 02:00 | 0 | 0 | 0 | 0 | -11.6862 | -130.2925 | 109.886 | -19.886 | -127.4103 | 131.6692 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0912 | 0
2015-10-25 03:00 | 0 | 0 | 0 | 0 | -11.7007 | -115.2914 | 106.9729 | -16.9729 | -112.2291 | 117.343 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2 | 2 | 1.092 | 0
2015-10-25 04:00 | 0 | 0 | 0 | 0 | -11.7153 | -100.2904 | 103.7252 | -13.7252 | -97.3703 | 103.0943 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0924 | 0
2015-10-25 05:00 | 0 | 0 | 0 | 0 | -11.7299 | -85.2893 | 100.3655 | -10.3655 | -82.7473 | 88.9924 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0928 | 0
2015-10-25 06:00 | 0 | 0 | 0 | 0 | -11.7444 | -70.2882 | 97.1132 | -7.1132 | -68.2551 | 75.1401 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-10-25 07:00 | 1.0067 | 0.8 | 0.20667 | 0 | -11.7589 | -55.2872 | 94.1757 | -4.1757 | -53.7949 | 61.7203 | 0 | 0.6 | 0.2 | 0 | 0.050333 | 0.65033 | 0.3 | 0.32032 | 1.0987 | 0.00058592
2015-10-25 08:00 | 2.0133 | 1.6 | 0.41333 | 0 | -11.7735 | -40.2861 | 91.7406 | -1.7406 | -39.2935 | 49.1008 | 0 | 1.2 | 0.2 | 0 | 0.10067 | 1.3007 | 0.6 | 0.64065 | 1.0974 | 0.0011705
2015-10-25 09:00 | 3.02 | 2.4 | 0.62 | 0 | -11.788 | -25.285 | 89.9666 | 0.033411 | -24.7156 | 38.0954 | 0 | 1.8 | 0.2 | 0 | 0.151 | 1.951 | 0.5 | 0.56097 | 1.0978 | 0.0017562
2015-10-25 10:00 | 3.3333 | 2.6133 | 0.72 | 0 | -11.8025 | -10.284 | 88.9724 | 1.0276 | -10.0659 | 30.5118 | 0 | 1.96 | 0.2 | 0 | 0.16667 | 2.1267 | 0.3 | 0.36646 | 1.0985 | 0.0019157
2015-10-25 11:00 | 3.6467 | 2.8267 | 0.82 | 0 | -11.817 | 4.717 | 88.8266 | 1.1734 | 4.6178 | 29.1588 | 0 | 2.12 | 0.2 | 0 | 0.18233 | 2.3023 | 0.3 | 0.37195 | 1.0985 | 0.0020739
2015-10-25 12:00 | 3.96 | 3.04 | 0.92 | 0 | -11.8316 | 19.7181 | 89.5399 | 0.46014 | 19.283 | 34.7719 | 0 | 2.28 | 0.2 | 0 | 0.198 | 2.478 | -0.1 | -0.022562 | 1.1001 | 0.0022353
2015-10-25 13:00 | 2.64 | 2.0267 | 0.61333 | 0 | -11.8461 | 34.7191 | 91.0645 | -1.0645 | 33.8845 | 44.8033 | 0 | 1.52 | 0.2 | 0 | 0.132 | 1.652 | -0.5 | -0.44838 | 1.1018 | 0.0014925
2015-10-25 14:00 | 1.32 | 1.0133 | 0.30667 | 0 | -11.8606 | 49.7201 | 93.299 | -3.299 | 48.4043 | 56.9615 | 0 | 0.76 | 0.2 | 0 | 0.066 | 0.826 | -0.2 | -0.17419 | 1.1007 | 0.00074552
2015-10-25 15:00 | 0 | 0 | 0 | 0 | -11.8751 | 64.7212 | 96.0984 | -6.0984 | 62.8638 | 70.1446 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-10-25 16:00 | 0 | 0 | 0 | 0 | -11.8896 | 79.7222 | 99.2849 | -9.2849 | 77.3242 | 83.8649 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-10-25 17:00 | 0 | 0 | 0 | 0 | -11.9041 | 94.7232 | 102.6579 | -12.6579 | 91.8781 | 97.8892 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-10-25 18:00 | 0 | 0 | 0 | 0 | -11.9185 | 109.7242 | 106.002 | -16.002 | 106.6322 | 112.0929 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-10-25 19:00 | 0 | 0 | 0 | 0 | -11.933 | 124.7252 | 109.0946 | -19.0946 | 121.6846 | 126.3994 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-10-25 20:00 | 0 | 0 | 0 | 0 | -11.9475 | 139.7262 | 111.7167 | -21.7167 | 137.0974 | 140.7468 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-10-25 21:00 | 0 | 0 | 0 | 0 | -11.9619 | 154.7271 | 113.6674 | -23.6674 | 152.8698 | 155.0432 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-10-25 22:00 | 0 | 0 | 0 | 0 | -11.9764 | 169.7281 | 114.7864 | -24.7864 | 168.9224 | 168.8765 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-10-25 23:00 | 0 | 0 | 0 | 0 | -11.9909 | 184.7291 | 114.9767 | -24.9767 | -174.8959 | 173.2392 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-10-26 | 0 | 0 | 0 | 0 | -12.0053 | -160.2699 | 114.2224 | -24.2224 | -158.7718 | 160.2761 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-10-26 01:00 | 0 | 0 | 0 | 0 | -12.0198 | -145.269 | 112.5916 | -22.5916 | -142.8757 | 146.0578 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.1032 | 0
2015-10-26 02:00 | 0 | 0 | 0 | 0 | -12.0342 | -130.268 | 110.2238 | -20.2238 | -127.3173 | 131.7196 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-10-26 03:00 | 0 | 0 | 0 | 0 | -12.0486 | -115.2671 | 107.3077 | -17.3077 | -112.127 | 117.3987 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-10-26 04:00 | 0 | 0 | 0 | 0 | -12.0631 | -100.2661 | 104.0583 | -14.0583 | -97.2646 | 103.1608 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-10-26 05:00 | 0 | 0 | 0 | 0 | -12.0775 | -85.2652 | 100.6985 | -10.6985 | -82.6431 | 89.0748 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-10-26 06:00 | 0 | 0 | 0 | 0 | -12.0919 | -70.2642 | 97.4476 | -7.4476 | -68.157 | 75.2448 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-10-26 07:00 | 0.43667 | 0.4 | 0.036667 | 0 | -12.1063 | -55.2633 | 94.5127 | -4.5127 | -53.7071 | 61.8564 | 0 | 0.3 | 0.2 | 0 | 0.021833 | 0.32183 | -3.3 | -3.2899 | 1.1132 | 0.00029377
2015-10-26 08:00 | 0.87333 | 0.8 | 0.073333 | 0 | -12.1207 | -40.2624 | 92.0808 | -2.0808 | -39.2199 | 49.2821 | 0 | 0.6 | 0.2 | 0 | 0.043667 | 0.64367 | -3.6 | -3.5799 | 1.1143 | 0.00058815
2015-10-26 09:00 | 1.31 | 1.2 | 0.11 | 0 | -12.1351 | -25.2615 | 90.3099 | -0.30989 | -24.6592 | 38.341 | 0 | 0.9 | 0.2 | 0 | 0.0655 | 0.9655 | -3.6 | -3.5698 | 1.1143 | 0.00088219
2015-10-26 10:00 | 1.4567 | 1.31 | 0.14667 | 0 | -12.1495 | -10.2605 | 89.3182 | 0.68177 | -10.029 | 30.8312 | 0 | 0.9825 | 0.2 | 0 | 0.072833 | 1.0553 | -3.4 | -3.367 | 1.1135 | 0.00096357
2015-10-26 11:00 | 1.6033 | 1.42 | 0.18333 | 0 | -12.1639 | 4.7404 | 89.1738 | 0.8262 | 4.6342 | 29.5048 | 0 | 1.065 | 0.2 | 0 | 0.080167 | 1.1452 | -4.4 | -4.3642 | 1.1175 | 0.0010493
2015-10-26 12:00 | 1.75 | 1.53 | 0.22 | 0 | -12.1783 | 19.7413 | 89.8873 | 0.11267 | 19.2792 | 35.071 | 0 | 1.1475 | 0.2 | 0 | 0.0875 | 1.235 | -4.8 | -4.7614 | 1.119 | 0.0011333
2015-10-26 13:00 | 1.1667 | 1.02 | 0.14667 | 0 | -12.1927 | 34.7422 | 91.4111 | -1.4111 | 33.8623 | 45.0412 | 0 | 0.765 | 0.2 | 0 | 0.058333 | 0.82333 | -5.1 | -5.0743 | 1.1203 | 0.00075635
2015-10-26 14:00 | 0.58333 | 0.51 | 0.073333 | 0 | -12.2071 | 49.7431 | 93.6442 | -3.6442 | 48.3665 | 57.152 | 0 | 0.3825 | 0.2 | 0 | 0.029167 | 0.41167 | -4.7 | -4.6871 | 1.1187 | 0.00037765
2015-10-26 15:00 | 0 | 0 | 0 | 0 | -12.2214 | 64.7439 | 96.442 | -6.442 | 62.8142 | 70.3015 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1184 | 0
2015-10-26 16:00 | 0 | 0 | 0 | 0 | -12.2358 | 79.7448 | 99.6273 | -9.6273 | 77.2671 | 83.9976 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-10-26 17:00 | 0 | 0 | 0 | 0 | -12.2502 | 94.7457 | 102.9998 | -12.9998 | 91.8183 | 98.0043 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.5 | -4.5 | 1.118 | 0
2015-10-26 18:00 | 0 | 0 | 0 | 0 | -12.2645 | 109.7466 | 106.3442 | -16.3442 | 106.5748 | 112.1955 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-10-26 19:00 | 0 | 0 | 0 | 0 | -12.2789 | 124.7474 | 109.438 | -19.438 | 121.6352 | 126.4942 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.7 | -4.7 | 1.1188 | 0
2015-10-26 20:00 | 0 | 0 | 0 | 0 | -12.2932 | 139.7483 | 112.0615 | -22.0615 | 137.0618 | 140.8402 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.2 | -5.2 | 1.1208 | 0
2015-10-26 21:00 | 0 | 0 | 0 | 0 | -12.3075 | 154.7491 | 114.0134 | -24.0134 | 152.8534 | 155.149 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-10-26 22:00 | 0 | 0 | 0 | 0 | -12.3219 | 169.75 | 115.1325 | -25.1325 | 168.9291 | 169.0529 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.3 | -4.3 | 1.1172 | 0
2015-10-26 23:00 | 0 | 0 | 0 | 0 | -12.3362 | 184.7508 | 115.3216 | -25.3216 | -174.8646 | 173.4767 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.8 | -4.8 | 1.1192 | 0
2015-10-27 | 0 | 0 | 0 | 0 | -12.3505 | -160.2484 | 114.5646 | -24.5646 | -158.717 | 160.3536 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1184 | 0
2015-10-27 01:00 | 0 | 0 | 0 | 0 | -12.3648 | -145.2475 | 112.9304 | -22.9304 | -142.801 | 146.1111 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.4 | -5.4 | 1.1216 | 0
2015-10-27 02:00 | 0 | 0 | 0 | 0 | -12.3792 | -130.2467 | 110.559 | -20.559 | -127.2279 | 131.7707 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.3 | -5.3 | 1.1212 | 0
2015-10-27 03:00 | 0 | 0 | 0 | 0 | -12.3935 | -115.2459 | 107.6401 | -17.6401 | -112.0285 | 117.4558 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.4 | -5.4 | 1.1216 | 0
2015-10-27 04:00 | 0 | 0 | 0 | 0 | -12.4078 | -100.2451 | 104.3891 | -14.3891 | -97.1625 | 103.2291 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.6 | -5.6 | 1.1224 | 0
2015-10-27 05:00 | 0 | 0 | 0 | 0 | -12.422 | -85.2443 | 101.0293 | -11.0293 | -82.5425 | 89.1594 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.8 | -5.8 | 1.1232 | 0
2015-10-27 06:00 | 0 | 0 | 0 | 0 | -12.4363 | -70.2435 | 97.7797 | -7.7797 | -68.0626 | 75.3519 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.6 | -5.6 | 1.1224 | 0
2015-10-27 07:00 | 0.26667 | 0.23333 | 0.033333 | 0 | -12.4506 | -55.2427 | 94.8472 | -4.8472 | -53.623 | 61.995 | 0 | 0.175 | 0.2 | 0 | 0.013333 | 0.18833 | -6 | -5.9941 | 1.124 | 0.00017358
2015-10-27 08:00 | 0.53333 | 0.46667 | 0.066667 | 0 | -12.4649 | -40.2419 | 92.4183 | -2.4183 | -39.1498 | 49.4656 | 0 | 0.35 | 0.2 | 0 | 0.026667 | 0.37667 | -6.8 | -6.7882 | 1.1272 | 0.00034814
2015-10-27 09:00 | 0.8 | 0.7 | 0.1 | 0 | -12.4792 | -25.2411 | 90.6504 | -0.65041 | -24.6063 | 38.5876 | 0 | 0.525 | 0.2 | 0 | 0.04 | 0.565 | -7.4 | -7.3823 | 1.1295 | 0.00052331
2015-10-27 10:00 | 0.79667 | 0.73 | 0.066667 | 0 | -12.4934 | -10.2403 | 89.6611 | 0.33895 | -9.9955 | 31.1492 | 0 | 0.5475 | 0.2 | 0 | 0.039833 | 0.58733 | -7.3 | -7.2816 | 1.1291 | 0.0005438
2015-10-27 11:00 | 0.79333 | 0.76 | 0.033333 | 0 | -12.5077 | 4.7605 | 89.5179 | 0.48213 | 4.6474 | 29.8473 | 0 | 0.57 | 0.2 | 0 | 0.039667 | 0.60967 | -7.3 | -7.2809 | 1.1291 | 0.00056448
2015-10-27 12:00 | 0.79 | 0.79 | 0 | 0 | -12.5219 | 19.7612 | 90.2315 | -0.23145 | 19.2725 | 35.3665 | 0 | 0.5925 | 0.2 | 0 | 0.0395 | 0.632 | -6.9 | -6.8803 | 1.1275 | 0.00058433
2015-10-27 13:00 | 0.52667 | 0.52667 | 0 | 0 | -12.5362 | 34.762 | 91.7542 | -1.7542 | 33.8373 | 45.2757 | 0 | 0.395 | 0.2 | 0 | 0.026333 | 0.42133 | -6.5 | -6.4868 | 1.1259 | 0.00038901
2015-10-27 14:00 | 0.26333 | 0.26333 | 0 | 0 | -12.5504 | 49.7627 | 93.9857 | -3.9857 | 48.3262 | 57.3392 | 0 | 0.1975 | 0.2 | 0 | 0.013167 | 0.21067 | -6 | -5.9934 | 1.124 | 0.00019416
2015-10-27 15:00 | 0 | 0 | 0 | 0 | -12.5647 | 64.7635 | 96.7818 | -6.7818 | 62.7621 | 70.4548 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.8 | -5.8 | 1.1232 | 0
2015-10-27 16:00 | 0 | 0 | 0 | 0 | -12.5789 | 79.7642 | 99.9658 | -9.9658 | 77.2075 | 84.1265 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.1 | -6.1 | 1.1244 | 0
2015-10-27 17:00 | 0 | 0 | 0 | 0 | -12.5931 | 94.765 | 103.3378 | -13.3378 | 91.7558 | 98.1153 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.3 | -5.3 | 1.1212 | 0
2015-10-27 18:00 | 0 | 0 | 0 | 0 | -12.6074 | 109.7657 | 106.6827 | -16.6827 | 106.5146 | 112.2935 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.2 | -5.2 | 1.1208 | 0
2015-10-27 19:00 | 0 | 0 | 0 | 0 | -12.6216 | 124.7664 | 109.7777 | -19.7777 | 121.583 | 126.5838 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.5 | -5.5 | 1.122 | 0
2015-10-27 20:00 | 0 | 0 | 0 | 0 | -12.6358 | 139.7671 | 112.4027 | -22.4027 | 137.0233 | 140.9274 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.4 | -5.4 | 1.1216 | 0
2015-10-27 21:00 | 0 | 0 | 0 | 0 | -12.65 | 154.7679 | 114.3558 | -24.3558 | 152.8338 | 155.2467 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.2 | -5.2 | 1.1208 | 0
2015-10-27 22:00 | 0 | 0 | 0 | 0 | -12.6642 | 169.7686 | 115.4752 | -25.4752 | 168.9323 | 169.2169 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-10-27 23:00 | 0 | 0 | 0 | 0 | -12.6784 | 184.7693 | 115.6633 | -25.6633 | -174.8368 | 173.7044 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.9 | -4.9 | 1.1196 | 0
2015-10-28 | 0 | 0 | 0 | 0 | -12.6926 | -160.23 | 114.904 | -24.904 | -158.6658 | 160.4278 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.5 | -5.5 | 1.122 | 0
2015-10-28 01:00 | 0 | 0 | 0 | 0 | -12.7067 | -145.2293 | 113.2664 | -23.2664 | -142.73 | 146.1638 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.5 | -5.5 | 1.122 | 0
2015-10-28 02:00 | 0 | 0 | 0 | 0 | -12.7209 | -130.2286 | 110.8917 | -20.8917 | -127.1421 | 131.8225 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.4 | -5.4 | 1.1216 | 0
2015-10-28 03:00 | 0 | 0 | 0 | 0 | -12.7351 | -115.228 | 107.9701 | -17.9701 | -111.9337 | 117.5143 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.2 | -6.2 | 1.1248 | 0
2015-10-28 04:00 | 0 | 0 | 0 | 0 | -12.7492 | -100.2273 | 104.7175 | -14.7175 | -97.0642 | 103.2993 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7 | -7 | 1.128 | 0
2015-10-28 05:00 | 0 | 0 | 0 | 0 | -12.7634 | -85.2266 | 101.3576 | -11.3576 | -82.4457 | 89.2462 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8 | -8 | 1.132 | 0
2015-10-28 06:00 | 0 | 0 | 0 | 0 | -12.7776 | -70.226 | 98.1094 | -8.1094 | -67.9719 | 75.4613 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.2 | -7.2 | 1.1288 | 0
2015-10-28 07:00 | 0.14 | 0.11333 | 0.026667 | 0 | -12.7917 | -55.2253 | 95.1792 | -5.1792 | -53.5426 | 62.1358 | 0 | 0.085 | 0.2 | 0 | 0.007 | 0.092 | -7.5 | -7.4971 | 1.13 | 8.5246e-05
2015-10-28 08:00 | 0.28 | 0.22667 | 0.053333 | 0 | -12.8058 | -40.2246 | 92.7532 | -2.7532 | -39.0834 | 49.651 | 0 | 0.17 | 0.2 | 0 | 0.014 | 0.184 | -8.6 | -8.5942 | 1.1344 | 0.00017115
2015-10-28 09:00 | 0.42 | 0.34 | 0.08 | 0 | -12.82 | -25.224 | 90.988 | -0.98803 | -24.5569 | 38.8351 | 0 | 0.255 | 0.2 | 0 | 0.021 | 0.276 | -8.2 | -8.1914 | 1.1328 | 0.00025637
2015-10-28 10:00 | 0.48333 | 0.39667 | 0.086667 | 0 | -12.8341 | -10.2234 | 90.0008 | -0.0007894 | -9.9653 | 31.4657 | 0 | 0.2975 | 0.2 | 0 | 0.024167 | 0.32167 | -8.8 | -8.7899 | 1.1352 | 0.00029942
2015-10-28 11:00 | 0.54667 | 0.45333 | 0.093333 | 0 | -12.8482 | 4.7773 | 89.8587 | 0.14134 | 4.6574 | 30.1861 | 0 | 0.34 | 0.2 | 0 | 0.027333 | 0.36733 | -9.6 | -9.5885 | 1.1384 | 0.00034289
2015-10-28 12:00 | 0.61 | 0.51 | 0.1 | 0 | -12.8623 | 19.7779 | 90.5721 | -0.5721 | 19.2628 | 35.6583 | 0 | 0.3825 | 0.2 | 0 | 0.0305 | 0.413 | -9.9 | -9.8871 | 1.1395 | 0.00038592
2015-10-28 13:00 | 0.40667 | 0.34 | 0.066667 | 0 | -12.8765 | 34.7785 | 92.0937 | -2.0937 | 33.8095 | 45.5067 | 0 | 0.255 | 0.2 | 0 | 0.020333 | 0.27533 | -10.1 | -10.0914 | 1.1404 | 0.00025746
2015-10-28 14:00 | 0.20333 | 0.17 | 0.033333 | 0 | -12.8906 | 49.7792 | 94.3235 | -4.3235 | 48.2831 | 57.5228 | 0 | 0.1275 | 0.2 | 0 | 0.010167 | 0.13767 | -9.1 | -9.0957 | 1.1364 | 0.00012828
2015-10-28 15:00 | 0 | 0 | 0 | 0 | -12.9047 | 64.7798 | 97.1178 | -7.1178 | 62.7073 | 70.6044 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.8 | -9.8 | 1.1392 | 0
2015-10-28 16:00 | 0 | 0 | 0 | 0 | -12.9188 | 79.7804 | 100.3005 | -10.3005 | 77.1452 | 84.2514 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.5 | -9.5 | 1.138 | 0
2015-10-28 17:00 | 0 | 0 | 0 | 0 | -12.9328 | 94.781 | 103.672 | -13.672 | 91.6906 | 98.2219 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.4 | -9.4 | 1.1376 | 0
2015-10-28 18:00 | 0 | 0 | 0 | 0 | -12.9469 | 109.7816 | 107.0172 | -17.0172 | 106.4517 | 112.3867 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.6 | -9.6 | 1.1384 | 0
2015-10-28 19:00 | 0 | 0 | 0 | 0 | -12.961 | 124.7822 | 110.1135 | -20.1135 | 121.5278 | 126.6681 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.1 | -9.1 | 1.1364 | 0
2015-10-28 20:00 | 0 | 0 | 0 | 0 | -12.9751 | 139.7827 | 112.7401 | -22.7401 | 136.9816 | 141.0084 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.5 | -8.5 | 1.134 | 0
2015-10-28 21:00 | 0 | 0 | 0 | 0 | -12.9891 | 154.7833 | 114.6947 | -24.6947 | 152.8109 | 155.3365 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.8 | -7.8 | 1.1312 | 0
2015-10-28 22:00 | 0 | 0 | 0 | 0 | -13.0032 | 169.7839 | 115.8146 | -25.8146 | 168.9322 | 169.3682 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8 | -8 | 1.132 | 0
2015-10-28 23:00 | 0 | 0 | 0 | 0 | -13.0172 | 184.7845 | 116.0018 | -26.0018 | -174.8125 | 173.9217 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.6 | -7.6 | 1.1304 | 0
2015-10-29 | 0 | 0 | 0 | 0 | -13.0313 | -160.215 | 115.2403 | -25.2403 | -158.6181 | 160.4988 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.3 | -7.3 | 1.1292 | 0
2015-10-29 01:00 | 0 | 0 | 0 | 0 | -13.0453 | -145.2144 | 113.5996 | -23.5996 | -142.6626 | 146.2162 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.8 | -6.8 | 1.1272 | 0
2015-10-29 02:00 | 0 | 0 | 0 | 0 | -13.0594 | -130.2139 | 111.2217 | -21.2217 | -127.06 | 131.875 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.2 | -6.2 | 1.1248 | 0
2015-10-29 03:00 | 0 | 0 | 0 | 0 | -13.0734 | -115.2133 | 108.2975 | -18.2975 | -111.8426 | 117.5742 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.4 | -5.4 | 1.1216 | 0
2015-10-29 04:00 | 0 | 0 | 0 | 0 | -13.0874 | -100.2128 | 105.0434 | -15.0434 | -96.9696 | 103.3713 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-10-29 05:00 | 0 | 0 | 0 | 0 | -13.1014 | -85.2123 | 101.6834 | -11.6834 | -82.3527 | 89.335 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.7 | -4.7 | 1.1188 | 0
2015-10-29 06:00 | 0 | 0 | 0 | 0 | -13.1154 | -70.2117 | 98.4364 | -8.4364 | -67.885 | 75.573 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-10-29 07:00 | 0.013333 | 0.013333 | 0 | 0 | -13.1295 | -55.2112 | 95.5085 | -5.5085 | -53.466 | 62.2789 | 0 | 0.01 | 0.2 | 0 | 0.00066667 | 0.010667 | -4.9 | -4.8997 | 1.1196 | 9.7928e-06
2015-10-29 08:00 | 0.026667 | 0.026667 | 0 | 0 | -13.1435 | -40.2107 | 93.0852 | -3.0852 | -39.0207 | 49.8384 | 0 | 0.02 | 0.2 | 0 | 0.0013333 | 0.021333 | -3.3 | -3.2993 | 1.1132 | 1.9474e-05
2015-10-29 09:00 | 0.04 | 0.04 | 0 | 0 | -13.1574 | -25.2102 | 91.3226 | -1.3226 | -24.5111 | 39.0834 | 0 | 0.03 | 0.2 | 0 | 0.002 | 0.032 | -1.3 | -1.299 | 1.1052 | 2.9e-05
2015-10-29 10:00 | 0.043333 | 0.043333 | 0 | 0 | -13.1714 | -10.2097 | 90.3373 | -0.33732 | -9.9385 | 31.7806 | 0 | 0.0325 | 0.2 | 0 | 0.0021667 | 0.034667 | -1.4 | -1.3989 | 1.1056 | 3.1428e-05
2015-10-29 11:00 | 0.046667 | 0.046667 | 0 | 0 | -13.1854 | 4.7908 | 90.196 | -0.19603 | 4.6643 | 30.5212 | 0 | 0.035 | 0.2 | 0 | 0.0023333 | 0.037333 | -1.5 | -1.4988 | 1.106 | 3.3858e-05
2015-10-29 12:00 | 0.05 | 0.05 | 0 | 0 | -13.1994 | 19.7913 | 90.9092 | -0.90916 | 19.25 | 35.9462 | 0 | 0.0375 | 0.2 | 0 | 0.0025 | 0.04 | -1.6 | -1.5987 | 1.1064 | 3.629e-05
2015-10-29 13:00 | 0.033333 | 0.033333 | 0 | 0 | -13.2134 | 34.7918 | 92.4295 | -2.4295 | 33.7789 | 45.7341 | 0 | 0.025 | 0.2 | 0 | 0.0016667 | 0.026667 | -1.1 | -1.0992 | 1.1044 | 2.4149e-05
2015-10-29 14:00 | 0.016667 | 0.016667 | 0 | 0 | -13.2273 | 49.7923 | 94.6574 | -4.6574 | 48.2374 | 57.7029 | 0 | 0.0125 | 0.2 | 0 | 0.00083333 | 0.013333 | -1.1 | -1.0996 | 1.1044 | 1.2075e-05
2015-10-29 15:00 | 0 | 0 | 0 | 0 | -13.2413 | 64.7927 | 97.4499 | -7.4499 | 62.65 | 70.7503 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-10-29 16:00 | 0 | 0 | 0 | 0 | -13.2552 | 79.7932 | 100.6311 | -10.6311 | 77.0804 | 84.3724 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-10-29 17:00 | 0 | 0 | 0 | 0 | -13.2692 | 94.7937 | 104.002 | -14.002 | 91.6229 | 98.3243 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.1048 | 0
2015-10-29 18:00 | 0 | 0 | 0 | 0 | -13.2831 | 109.7941 | 107.3478 | -17.3478 | 106.3861 | 112.4753 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-10-29 19:00 | 0 | 0 | 0 | 0 | -13.297 | 124.7946 | 110.4453 | -20.4453 | 121.4698 | 126.7471 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-10-29 20:00 | 0 | 0 | 0 | 0 | -13.311 | 139.795 | 113.0737 | -23.0737 | 136.9368 | 141.0832 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.1056 | 0
2015-10-29 21:00 | 0 | 0 | 0 | 0 | -13.3249 | 154.7955 | 115.0298 | -25.0298 | 152.7847 | 155.4184 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-10-29 22:00 | 0 | 0 | 0 | 0 | -13.3388 | 169.7959 | 116.1504 | -26.1504 | 168.9286 | 169.5065 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-10-29 23:00 | 0 | 0 | 0 | 0 | -13.3527 | 184.7963 | 116.3369 | -26.3369 | -174.7917 | 174.1278 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-10-30 | 0 | 0 | 0 | 0 | -13.3666 | -160.2032 | 115.5734 | -25.5734 | -158.5741 | 160.5668 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-10-30 01:00 | 0 | 0 | 0 | 0 | -13.3805 | -145.2028 | 113.9299 | -23.9299 | -142.5988 | 146.2681 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-10-30 02:00 | 0 | 0 | 0 | 0 | -13.3944 | -130.2024 | 111.5489 | -21.5489 | -126.9817 | 131.9283 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-10-30 03:00 | 0 | 0 | 0 | 0 | -13.4083 | -115.202 | 108.6221 | -18.6221 | -111.7554 | 117.6355 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-10-30 04:00 | 0 | 0 | 0 | 0 | -13.4222 | -100.2016 | 105.3667 | -15.3667 | -96.8789 | 103.4451 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-10-30 05:00 | 0 | 0 | 0 | 0 | -13.436 | -85.2012 | 102.0066 | -12.0066 | -82.2635 | 89.4259 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-10-30 06:00 | 0 | 0 | 0 | 0 | -13.4499 | -70.2008 | 98.7608 | -8.7608 | -67.8019 | 75.6869 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0972 | 0
2015-10-30 07:00 | 0.013333 | 0.01 | 0.0033333 | 0 | -13.4638 | -55.2005 | 95.8351 | -5.8351 | -53.3931 | 62.4242 | 0 | 0.0075 | 0.2 | 0 | 0.00066667 | 0.0081667 | 0.7 | 0.70026 | 1.0972 | 7.3476e-06
2015-10-30 08:00 | 0.026667 | 0.02 | 0.0066667 | 0 | -13.4776 | -40.2001 | 93.4143 | -3.4143 | -38.9616 | 50.0275 | 0 | 0.015 | 0.2 | 0 | 0.0013333 | 0.016333 | 2.1 | 2.1005 | 1.0916 | 1.462e-05
2015-10-30 09:00 | 0.04 | 0.03 | 0.01 | 0 | -13.4915 | -25.1997 | 91.6541 | -1.6541 | -24.4688 | 39.3323 | 0 | 0.0225 | 0.2 | 0 | 0.002 | 0.0245 | 2 | 2.0008 | 1.092 | 2.1938e-05
2015-10-30 10:00 | 0.046667 | 0.033333 | 0.013333 | 0 | -13.5053 | -10.1993 | 90.6705 | -0.67052 | -9.9151 | 32.0937 | 0 | 0.025 | 0.2 | 0 | 0.0023333 | 0.027333 | 2 | 2.0009 | 1.092 | 2.4475e-05
2015-10-30 11:00 | 0.053333 | 0.036667 | 0.016667 | 0 | -13.5191 | 4.801 | 90.5299 | -0.52989 | 4.6679 | 30.8523 | 0 | 0.0275 | 0.2 | 0 | 0.0026667 | 0.030167 | 1.7 | 1.7009 | 1.0932 | 2.7042e-05
2015-10-30 12:00 | 0.06 | 0.04 | 0.02 | 0 | -13.533 | 19.8014 | 91.2425 | -1.2425 | 19.2343 | 36.2302 | 0 | 0.03 | 0.2 | 0 | 0.003 | 0.033 | 2.4 | 2.401 | 1.0904 | 2.9506e-05
2015-10-30 13:00 | 0.04 | 0.026667 | 0.013333 | 0 | -13.5468 | 34.8017 | 92.7614 | -2.7614 | 33.7455 | 45.9579 | 0 | 0.02 | 0.2 | 0 | 0.002 | 0.022 | 2.4 | 2.4007 | 1.0904 | 1.9671e-05
2015-10-30 14:00 | 0.02 | 0.013333 | 0.0066667 | 0 | -13.5606 | 49.8021 | 94.9873 | -4.9873 | 48.189 | 57.8793 | 0 | 0.01 | 0.2 | 0 | 0.001 | 0.011 | 2 | 2.0003 | 1.092 | 9.8498e-06
2015-10-30 15:00 | 0 | 0 | 0 | 0 | -13.5744 | 64.8024 | 97.7778 | -7.7778 | 62.5901 | 70.8923 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0928 | 0
2015-10-30 16:00 | 0 | 0 | 0 | 0 | -13.5882 | 79.8027 | 100.9576 | -10.9576 | 77.013 | 84.4892 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0908 | 0
2015-10-30 17:00 | 0 | 0 | 0 | 0 | -13.602 | 94.803 | 104.3279 | -14.3279 | 91.5525 | 98.4223 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0872 | 0
2015-10-30 18:00 | 0 | 0 | 0 | 0 | -13.6158 | 109.8034 | 107.6741 | -17.6741 | 106.3176 | 112.5591 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0884 | 0
2015-10-30 19:00 | 0 | 0 | 0 | 0 | -13.6296 | 124.8037 | 110.773 | -20.773 | 121.4087 | 126.8208 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0928 | 0
2015-10-30 20:00 | 0 | 0 | 0 | 0 | -13.6434 | 139.804 | 113.4033 | -23.4033 | 136.8888 | 141.1519 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0932 | 0
2015-10-30 21:00 | 0 | 0 | 0 | 0 | -13.6571 | 154.8043 | 115.3611 | -25.3611 | 152.7551 | 155.4922 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.088 | 0
2015-10-30 22:00 | 0 | 0 | 0 | 0 | -13.6709 | 169.8046 | 116.4825 | -26.4825 | 168.9215 | 169.6316 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0912 | 0
2015-10-30 23:00 | 0 | 0 | 0 | 0 | -13.6847 | 184.8049 | 116.6686 | -26.6686 | -174.7746 | 174.3222 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0912 | 0
2015-10-31 | 0 | 0 | 0 | 0 | -13.6984 | -160.1949 | 115.9033 | -25.9033 | -158.5339 | 160.6319 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0908 | 0
2015-10-31 01:00 | 0 | 0 | 0 | 0 | -13.7122 | -145.1946 | 114.2571 | -24.2571 | -142.5389 | 146.3199 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0932 | 0
2015-10-31 02:00 | 0 | 0 | 0 | 0 | -13.7259 | -130.1943 | 111.8732 | -21.8732 | -126.9072 | 131.9825 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0932 | 0
2015-10-31 03:00 | 0 | 0 | 0 | 0 | -13.7396 | -115.194 | 108.944 | -18.944 | -111.6719 | 117.6983 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2 | 2 | 1.092 | 0
2015-10-31 04:00 | 0 | 0 | 0 | 0 | -13.7534 | -100.1938 | 105.6872 | -15.6872 | -96.792 | 103.5208 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2 | 2 | 1.092 | 0
2015-10-31 05:00 | 0 | 0 | 0 | 0 | -13.7671 | -85.1935 | 102.3271 | -12.3271 | -82.1782 | 89.5189 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0944 | 0
2015-10-31 06:00 | 0 | 0 | 0 | 0 | -13.7808 | -70.1933 | 99.0824 | -9.0824 | -67.7227 | 75.8029 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.096 | 0
2015-10-31 07:00 | 0.0066667 | 0.0033333 | 0.0033333 | 0 | -13.7945 | -55.193 | 96.1587 | -6.1587 | -53.324 | 62.5715 | 0 | 0.0025 | 0.2 | 0 | 0.00033333 | 0.0028333 | 0.8 | 0.80009 | 1.0968 | 2.5482e-06
2015-10-31 08:00 | 0.013333 | 0.0066667 | 0.0066667 | 0 | -13.8082 | -40.1928 | 93.7403 | -3.7403 | -38.9063 | 50.2182 | 0 | 0.005 | 0.2 | 0 | 0.00066667 | 0.0056667 | 1.2 | 1.2002 | 1.0952 | 5.089e-06
2015-10-31 09:00 | 0.02 | 0.01 | 0.01 | 0 | -13.8219 | -25.1926 | 91.9824 | -1.9824 | -24.4301 | 39.5815 | 0 | 0.0075 | 0.2 | 0 | 0.001 | 0.0085 | 1 | 1.0003 | 1.096 | 7.6391e-06
2015-10-31 10:00 | 0.023333 | 0.013333 | 0.01 | 0 | -13.8356 | -10.1923 | 91.0003 | -1.0003 | -9.8951 | 32.4047 | 0 | 0.01 | 0.2 | 0 | 0.0011667 | 0.011167 | 1.3 | 1.3003 | 1.0948 | 1.0025e-05
2015-10-31 11:00 | 0.026667 | 0.016667 | 0.01 | 0 | -13.8493 | 4.8079 | 90.8601 | -0.8601 | 4.6683 | 31.1795 | 0 | 0.0125 | 0.2 | 0 | 0.0013333 | 0.013833 | 1.9 | 1.9004 | 1.0924 | 1.2391e-05
2015-10-31 12:00 | 0.03 | 0.02 | 0.01 | 0 | -13.863 | 19.8081 | 91.572 | -1.572 | 19.2156 | 36.5101 | 0 | 0.015 | 0.2 | 0 | 0.0015 | 0.0165 | 1.6 | 1.6005 | 1.0936 | 1.4796e-05
2015-10-31 13:00 | 0.02 | 0.013333 | 0.0066667 | 0 | -13.8766 | 34.8083 | 93.0893 | -3.0893 | 33.7093 | 46.1778 | 0 | 0.01 | 0.2 | 0 | 0.001 | 0.011 | 1.4 | 1.4003 | 1.0944 | 9.8715e-06
2015-10-31 14:00 | 0.01 | 0.0066667 | 0.0033333 | 0 | -13.8903 | 49.8085 | 95.3131 | -5.3131 | 48.1379 | 58.0519 | 0 | 0.005 | 0.2 | 0 | 0.0005 | 0.0055 | 1.4 | 1.4002 | 1.0944 | 4.9357e-06
2015-10-31 15:00 | 0 | 0 | 0 | 0 | -13.904 | 64.8087 | 98.1015 | -8.1015 | 62.5276 | 71.0305 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-10-31 16:00 | 0 | 0 | 0 | 0 | -13.9176 | 79.8089 | 101.2798 | -11.2798 | 76.943 | 84.602 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0932 | 0
2015-10-31 17:00 | 0 | 0 | 0 | 0 | -13.9312 | 94.8091 | 104.6495 | -14.6495 | 91.4794 | 98.5159 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0928 | 0
2015-10-31 18:00 | 0 | 0 | 0 | 0 | -13.9449 | 109.8092 | 107.9962 | -17.9962 | 106.2464 | 112.6382 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-10-31 19:00 | 0 | 0 | 0 | 0 | -13.9585 | 124.8094 | 111.0965 | -21.0965 | 121.3448 | 126.8893 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2 | 2 | 1.092 | 0
2015-10-31 20:00 | 0 | 0 | 0 | 0 | -13.9721 | 139.8096 | 113.7287 | -23.7287 | 136.8377 | 141.2144 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0896 | 0
2015-10-31 21:00 | 0 | 0 | 0 | 0 | -13.9858 | 154.8097 | 115.6884 | -25.6884 | 152.7222 | 155.5582 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0916 | 0
2015-10-31 22:00 | 0 | 0 | 0 | 0 | -13.9994 | 169.8099 | 116.8109 | -26.8109 | 168.9108 | 169.7434 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0928 | 0
2015-10-31 23:00 | 0 | 0 | 0 | 0 | -14.013 | 184.81 | 116.9967 | -26.9967 | -174.7612 | 174.5042 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0912 | 0
2015-11-01 | 0 | 0 | 0 | 0 | -14.0266 | -160.1898 | 116.2299 | -26.2299 | -158.4974 | 160.6943 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0912 | 0
2015-11-01 01:00 | 0 | 0 | 0 | 0 | -14.0402 | -145.1897 | 114.5811 | -24.5811 | -142.4828 | 146.3714 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.0892 | 0
2015-11-01 02:00 | 0 | 0 | 0 | 0 | -14.0538 | -130.1895 | 112.1945 | -22.1945 | -126.8366 | 132.0376 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0944 | 0
2015-11-01 03:00 | 0 | 0 | 0 | 0 | -14.0673 | -115.1894 | 109.263 | -19.263 | -111.5924 | 117.7625 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0944 | 0
2015-11-01 04:00 | 0 | 0 | 0 | 0 | -14.0809 | -100.1893 | 106.0049 | -16.0049 | -96.709 | 103.5983 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0888 | 0
2015-11-01 05:00 | 0 | 0 | 0 | 0 | -14.0945 | -85.1892 | 102.6447 | -12.6447 | -82.0969 | 89.614 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0852 | 0
2015-11-01 06:00 | 0 | 0 | 0 | 0 | -14.108 | -70.1891 | 99.4011 | -9.4011 | -67.6474 | 75.9211 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0852 | 0
2015-11-01 07:00 | 0 | 0 | 0 | 0 | -14.1216 | -55.189 | 96.4793 | -6.4793 | -53.2588 | 62.7208 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.084 | 0
2015-11-01 08:00 | 0 | 0 | 0 | 0 | -14.1351 | -40.1889 | 94.0632 | -4.0632 | -38.8547 | 50.4104 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0852 | 0
2015-11-01 09:00 | 0 | 0 | 0 | 0 | -14.1487 | -25.1888 | 92.3073 | -2.3073 | -24.3951 | 39.831 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.6 | 3.6 | 1.0856 | 0
2015-11-01 10:00 | 0 | 0 | 0 | 0 | -14.1622 | -10.1887 | 91.3265 | -1.3265 | -9.8786 | 32.7137 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0888 | 0
2015-11-01 11:00 | 0 | 0 | 0 | 0 | -14.1757 | 4.8114 | 91.1865 | -1.1865 | 4.6655 | 31.5026 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.09 | 0
2015-11-01 12:00 | 0 | 0 | 0 | 0 | -14.1892 | 19.8114 | 91.8976 | -1.8976 | 19.1939 | 36.7859 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.088 | 0
2015-11-01 13:00 | 0 | 0 | 0 | 0 | -14.2028 | 34.8115 | 93.4131 | -3.4131 | 33.6702 | 46.3939 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.0892 | 0
2015-11-01 14:00 | 0 | 0 | 0 | 0 | -14.2163 | 49.8116 | 95.6347 | -5.6347 | 48.0842 | 58.2206 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.088 | 0
2015-11-01 15:00 | 0 | 0 | 0 | 0 | -14.2298 | 64.8116 | 98.4209 | -8.4209 | 62.4625 | 71.1646 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.4 | 3.4 | 1.0864 | 0
2015-11-01 16:00 | 0 | 0 | 0 | 0 | -14.2433 | 79.8117 | 101.5976 | -11.5976 | 76.8704 | 84.7106 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.088 | 0
2015-11-01 17:00 | 0 | 0 | 0 | 0 | -14.2567 | 94.8117 | 104.9667 | -14.9667 | 91.4037 | 98.6052 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0884 | 0
2015-11-01 18:00 | 0 | 0 | 0 | 0 | -14.2702 | 109.8117 | 108.3139 | -18.3139 | 106.1725 | 112.7125 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0876 | 0
2015-11-01 19:00 | 0 | 0 | 0 | 0 | -14.2837 | 124.8118 | 111.4157 | -21.4157 | 121.2778 | 126.9525 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0944 | 0
2015-11-01 20:00 | 0 | 0 | 0 | 0 | -14.2972 | 139.8118 | 114.05 | -24.05 | 136.7835 | 141.2709 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0868 | 0
2015-11-01 21:00 | 0 | 0 | 0 | 0 | -14.3106 | 154.8118 | 116.0116 | -26.0116 | 152.686 | 155.6163 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0936 | 0
2015-11-01 22:00 | 0 | 0 | 0 | 0 | -14.3241 | 169.8118 | 117.1354 | -27.1354 | 168.8966 | 169.8416 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-11-01 23:00 | 0 | 0 | 0 | 0 | -14.3375 | 184.8118 | 117.3212 | -27.3212 | -174.7515 | 174.6732 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.0948 | 0
2015-11-02 | 0 | 0 | 0 | 0 | -14.351 | -160.1882 | 116.553 | -26.553 | -158.4647 | 160.7539 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-11-02 01:00 | 0 | 0 | 0 | 0 | -14.3644 | -145.1882 | 114.9019 | -24.9019 | -142.4306 | 146.4228 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0944 | 0
2015-11-02 02:00 | 0 | 0 | 0 | 0 | -14.3778 | -130.1882 | 112.5126 | -22.5126 | -126.7699 | 132.0936 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.096 | 0
2015-11-02 03:00 | 0 | 0 | 0 | 0 | -14.3912 | -115.1882 | 109.579 | -19.579 | -111.5168 | 117.8283 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-11-02 04:00 | 0 | 0 | 0 | 0 | -14.4047 | -100.1882 | 106.3197 | -16.3197 | -96.6301 | 103.6777 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-11-02 05:00 | 0 | 0 | 0 | 0 | -14.4181 | -85.1882 | 102.9594 | -12.9594 | -82.0195 | 89.711 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-11-02 06:00 | 0 | 0 | 0 | 0 | -14.4315 | -70.1883 | 99.7168 | -9.7168 | -67.5761 | 76.0413 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-11-02 07:00 | 0 | 0 | 0 | 0 | -14.4449 | -55.1883 | 96.7968 | -6.7968 | -53.1975 | 62.872 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-11-02 08:00 | 0 | 0 | 0 | 0 | -14.4582 | -40.1884 | 94.3828 | -4.3828 | -38.8069 | 50.6039 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-11-02 09:00 | 0 | 0 | 0 | 0 | -14.4716 | -25.1884 | 92.6287 | -2.6287 | -24.3637 | 40.0806 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-11-02 10:00 | 0 | 0 | 0 | 0 | -14.485 | -10.1885 | 91.649 | -1.649 | -9.8654 | 33.0203 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-11-02 11:00 | 0 | 0 | 0 | 0 | -14.4984 | 4.8115 | 91.5091 | -1.5091 | 4.6595 | 31.8214 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.096 | 0
2015-11-02 12:00 | 0 | 0 | 0 | 0 | -14.5117 | 19.8114 | 92.2191 | -2.2191 | 19.1692 | 37.0574 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-11-02 13:00 | 0 | 0 | 0 | 0 | -14.5251 | 34.8113 | 93.7327 | -3.7327 | 33.6284 | 46.6059 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-11-02 14:00 | 0 | 0 | 0 | 0 | -14.5384 | 49.8113 | 95.9519 | -5.9519 | 48.0278 | 58.3854 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.096 | 0
2015-11-02 15:00 | 0 | 0 | 0 | 0 | -14.5518 | 64.8112 | 98.7359 | -8.7359 | 62.3948 | 71.2947 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-11-02 16:00 | 0 | 0 | 0 | 0 | -14.5651 | 79.8111 | 101.9109 | -11.9109 | 76.7953 | 84.815 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-11-02 17:00 | 0 | 0 | 0 | 0 | -14.5784 | 94.811 | 105.2794 | -15.2794 | 91.3254 | 98.6899 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-11-02 18:00 | 0 | 0 | 0 | 0 | -14.5917 | 109.8109 | 108.627 | -18.627 | 106.0958 | 112.782 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-11-02 19:00 | 0 | 0 | 0 | 0 | -14.605 | 124.8108 | 111.7304 | -21.7304 | 121.208 | 127.0104 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-11-02 20:00 | 0 | 0 | 0 | 0 | -14.6183 | 139.8106 | 114.3668 | -24.3668 | 136.7261 | 141.3212 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-11-02 21:00 | 0 | 0 | 0 | 0 | -14.6316 | 154.8105 | 116.3306 | -26.3306 | 152.6463 | 155.6667 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-11-02 22:00 | 0 | 0 | 0 | 0 | -14.6449 | 169.8104 | 117.4558 | -27.4558 | 168.8789 | 169.9263 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-11-02 23:00 | 0 | 0 | 0 | 0 | -14.6582 | 184.8103 | 117.6418 | -27.6418 | -174.7455 | 174.8284 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-11-03 | 0 | 0 | 0 | 0 | -14.6715 | -160.1899 | 116.8724 | -26.8724 | -158.4358 | 160.8111 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-11-03 01:00 | 0 | 0 | 0 | 0 | -14.6848 | -145.19 | 115.2193 | -25.2193 | -142.3823 | 146.4741 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.102 | 0
2015-11-03 02:00 | 0 | 0 | 0 | 0 | -14.698 | -130.1902 | 112.8275 | -22.8275 | -126.7072 | 132.1506 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-11-03 03:00 | 0 | 0 | 0 | 0 | -14.7113 | -115.1903 | 109.8919 | -19.8919 | -111.4453 | 117.8956 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-11-03 04:00 | 0 | 0 | 0 | 0 | -14.7245 | -100.1905 | 106.6314 | -16.6314 | -96.5551 | 103.7588 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-11-03 05:00 | 0 | 0 | 0 | 0 | -14.7378 | -85.1907 | 103.271 | -13.271 | -81.9461 | 89.81 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-11-03 06:00 | 0 | 0 | 0 | 0 | -14.751 | -70.1908 | 100.0294 | -10.0294 | -67.5087 | 76.1634 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.1056 | 0
2015-11-03 07:00 | 0 | 0 | 0 | 0 | -14.7642 | -55.191 | 97.111 | -7.111 | -53.1401 | 63.025 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-11-03 08:00 | 0 | 0 | 0 | 0 | -14.7774 | -40.1912 | 94.699 | -4.699 | -38.7629 | 50.7987 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.1064 | 0
2015-11-03 09:00 | 0 | 0 | 0 | 0 | -14.7907 | -25.1914 | 92.9465 | -2.9465 | -24.3359 | 40.33 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-11-03 10:00 | 0 | 0 | 0 | 0 | -14.8039 | -10.1916 | 91.9677 | -1.9677 | -9.8557 | 33.3245 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.1064 | 0
2015-11-03 11:00 | 0 | 0 | 0 | 0 | -14.8171 | 4.8082 | 91.8277 | -1.8277 | 4.6503 | 32.136 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.1064 | 0
2015-11-03 12:00 | 0 | 0 | 0 | 0 | -14.8303 | 19.808 | 92.5365 | -2.5365 | 19.1415 | 37.3244 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-11-03 13:00 | 0 | 0 | 0 | 0 | -14.8434 | 34.8078 | 94.048 | -4.048 | 33.5838 | 46.8139 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-11-03 14:00 | 0 | 0 | 0 | 0 | -14.8566 | 49.8075 | 96.2647 | -6.2647 | 47.9688 | 58.5462 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-11-03 15:00 | 0 | 0 | 0 | 0 | -14.8698 | 64.8073 | 99.0463 | -9.0463 | 62.3247 | 71.4208 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-11-03 16:00 | 0 | 0 | 0 | 0 | -14.8829 | 79.8071 | 102.2196 | -12.2196 | 76.7177 | 84.9151 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.1064 | 0
2015-11-03 17:00 | 0 | 0 | 0 | 0 | -14.8961 | 94.8068 | 105.5874 | -15.5874 | 91.2446 | 98.7702 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-11-03 18:00 | 0 | 0 | 0 | 0 | -14.9093 | 109.8066 | 108.9355 | -18.9355 | 106.0163 | 112.8468 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-11-03 19:00 | 0 | 0 | 0 | 0 | -14.9224 | 124.8063 | 112.0405 | -22.0405 | 121.1352 | 127.063 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-11-03 20:00 | 0 | 0 | 0 | 0 | -14.9355 | 139.8061 | 114.6793 | -24.6793 | 136.6655 | 141.3655 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-11-03 21:00 | 0 | 0 | 0 | 0 | -14.9487 | 154.8058 | 116.6453 | -26.6453 | 152.6033 | 155.7093 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-11-03 22:00 | 0 | 0 | 0 | 0 | -14.9618 | 169.8055 | 117.7722 | -27.7722 | 168.8575 | 169.9973 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.2 | -2.2 | 1.1088 | 0
2015-11-03 23:00 | 0 | 0 | 0 | 0 | -14.9749 | 184.8053 | 117.9585 | -27.9585 | -174.7433 | 174.9695 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-11-04 | 0 | 0 | 0 | 0 | -14.988 | -160.195 | 117.1882 | -27.1882 | -158.4109 | 160.8659 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.11 | 0
2015-11-04 01:00 | 0 | 0 | 0 | 0 | -15.0011 | -145.1953 | 115.5331 | -25.5331 | -142.338 | 146.5256 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-11-04 02:00 | 0 | 0 | 0 | 0 | -15.0142 | -130.1956 | 113.1391 | -23.1391 | -126.6485 | 132.2085 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-11-04 03:00 | 0 | 0 | 0 | 0 | -15.0273 | -115.1959 | 110.2015 | -20.2015 | -111.3778 | 117.9643 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-11-04 04:00 | 0 | 0 | 0 | 0 | -15.0404 | -100.1962 | 106.9399 | -16.9399 | -96.4842 | 103.8417 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-11-04 05:00 | 0 | 0 | 0 | 0 | -15.0534 | -85.1965 | 103.5794 | -13.5794 | -81.8767 | 89.9109 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.3 | -3.3 | 1.1132 | 0
2015-11-04 06:00 | 0 | 0 | 0 | 0 | -15.0665 | -70.1968 | 100.3387 | -10.3387 | -67.4453 | 76.2875 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.3 | -3.3 | 1.1132 | 0
2015-11-04 07:00 | 0 | 0 | 0 | 0 | -15.0796 | -55.1971 | 97.4219 | -7.4219 | -53.0866 | 63.1796 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1144 | 0
2015-11-04 08:00 | 0 | 0 | 0 | 0 | -15.0926 | -40.1975 | 95.0116 | -5.0116 | -38.7227 | 50.9945 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-11-04 09:00 | 0 | 0 | 0 | 0 | -15.1056 | -25.1978 | 93.2607 | -3.2607 | -24.3117 | 40.5791 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.3 | -4.3 | 1.1172 | 0
2015-11-04 10:00 | 0 | 0 | 0 | 0 | -15.1187 | -10.1982 | 92.2826 | -2.2826 | -9.8495 | 33.626 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.7 | -4.7 | 1.1188 | 0
2015-11-04 11:00 | 0 | 0 | 0 | 0 | -15.1317 | 4.8015 | 92.1422 | -2.1422 | 4.6379 | 32.4461 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.7 | -4.7 | 1.1188 | 0
2015-11-04 12:00 | 0 | 0 | 0 | 0 | -15.1447 | 19.8011 | 92.8495 | -2.8495 | 19.1108 | 37.587 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.8 | -4.8 | 1.1192 | 0
2015-11-04 13:00 | 0 | 0 | 0 | 0 | -15.1577 | 34.8008 | 94.3588 | -4.3588 | 33.5364 | 47.0176 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.2 | -5.2 | 1.1208 | 0
2015-11-04 14:00 | 0 | 0 | 0 | 0 | -15.1707 | 49.8004 | 96.5729 | -6.5729 | 47.9072 | 58.7028 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.3 | -5.3 | 1.1212 | 0
2015-11-04 15:00 | 0 | 0 | 0 | 0 | -15.1837 | 64.8001 | 99.352 | -9.352 | 62.252 | 71.5426 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.9 | -5.9 | 1.1236 | 0
2015-11-04 16:00 | 0 | 0 | 0 | 0 | -15.1967 | 79.7997 | 102.5236 | -12.5236 | 76.6376 | 85.011 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.1 | -6.1 | 1.1244 | 0
2015-11-04 17:00 | 0 | 0 | 0 | 0 | -15.2097 | 94.7993 | 105.8906 | -15.8906 | 91.1611 | 98.846 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.1 | -6.1 | 1.1244 | 0
2015-11-04 18:00 | 0 | 0 | 0 | 0 | -15.2227 | 109.7989 | 109.2393 | -19.2393 | 105.9342 | 112.9067 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.5 | -6.5 | 1.126 | 0
2015-11-04 19:00 | 0 | 0 | 0 | 0 | -15.2357 | 124.7985 | 112.346 | -22.346 | 121.0596 | 127.1105 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.8 | -6.8 | 1.1272 | 0
2015-11-04 20:00 | 0 | 0 | 0 | 0 | -15.2486 | 139.7981 | 114.9871 | -24.9871 | 136.6018 | 141.4038 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.3 | -7.3 | 1.1292 | 0
2015-11-04 21:00 | 0 | 0 | 0 | 0 | -15.2616 | 154.7977 | 116.9556 | -26.9556 | 152.5568 | 155.7443 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.6 | -7.6 | 1.1304 | 0
2015-11-04 22:00 | 0 | 0 | 0 | 0 | -15.2745 | 169.7973 | 118.0842 | -28.0842 | 168.8325 | 170.0549 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.7 | -7.7 | 1.1308 | 0
2015-11-04 23:00 | 0 | 0 | 0 | 0 | -15.2875 | 184.7969 | 118.2712 | -28.2712 | -174.7449 | 175.0958 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.2 | -8.2 | 1.1328 | 0
2015-11-05 | 0 | 0 | 0 | 0 | -15.3004 | -160.2035 | 117.5002 | -27.5002 | -158.3899 | 160.9185 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.7 | -8.7 | 1.1348 | 0
2015-11-05 01:00 | 0 | 0 | 0 | 0 | -15.3133 | -145.204 | 115.8433 | -25.8433 | -142.2977 | 146.5771 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.3 | -9.3 | 1.1372 | 0
2015-11-05 02:00 | 0 | 0 | 0 | 0 | -15.3263 | -130.2044 | 113.4472 | -23.4472 | -126.5939 | 132.2676 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.2 | -9.2 | 1.1368 | 0
2015-11-05 03:00 | 0 | 0 | 0 | 0 | -15.3392 | -115.2049 | 110.5078 | -20.5078 | -111.3144 | 118.0346 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.5 | -9.5 | 1.138 | 0
2015-11-05 04:00 | 0 | 0 | 0 | 0 | -15.3521 | -100.2053 | 107.2451 | -17.2451 | -96.4174 | 103.9264 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.4 | -9.4 | 1.1376 | 0
2015-11-05 05:00 | 0 | 0 | 0 | 0 | -15.365 | -85.2058 | 103.8845 | -13.8845 | -81.8115 | 90.0137 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.1 | -9.1 | 1.1364 | 0
2015-11-05 06:00 | 0 | 0 | 0 | 0 | -15.3779 | -70.2062 | 100.6447 | -10.6447 | -67.386 | 76.4133 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.1 | -9.1 | 1.1364 | 0
2015-11-05 07:00 | 0 | 0 | 0 | 0 | -15.3907 | -55.2067 | 97.7293 | -7.7293 | -53.0371 | 63.3358 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.5 | -9.5 | 1.138 | 0
2015-11-05 08:00 | 0 | 0 | 0 | 0 | -15.4036 | -40.2072 | 95.3207 | -5.3207 | -38.6864 | 51.1912 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10 | -10 | 1.14 | 0
2015-11-05 09:00 | 0 | 0 | 0 | 0 | -15.4165 | -25.2076 | 93.571 | -3.571 | -24.2912 | 40.8278 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.9 | -9.9 | 1.1396 | 0
2015-11-05 10:00 | 0 | 0 | 0 | 0 | -15.4293 | -10.2081 | 92.5934 | -2.5934 | -9.8467 | 33.9248 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.2 | -9.2 | 1.1368 | 0
2015-11-05 11:00 | 0 | 0 | 0 | 0 | -15.4422 | 4.7914 | 92.4524 | -2.4524 | 4.6223 | 32.7517 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.5 | -9.5 | 1.138 | 0
2015-11-05 12:00 | 0 | 0 | 0 | 0 | -15.455 | 19.7909 | 93.1582 | -3.1582 | 19.0772 | 37.845 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.6 | -10.6 | 1.1424 | 0
2015-11-05 13:00 | 0 | 0 | 0 | 0 | -15.4679 | 34.7904 | 94.665 | -4.665 | 33.4863 | 47.2171 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.8 | -10.8 | 1.1432 | 0
2015-11-05 14:00 | 0 | 0 | 0 | 0 | -15.4807 | 49.7899 | 96.8764 | -6.8764 | 47.843 | 58.8553 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.7 | -11.7 | 1.1468 | 0
2015-11-05 15:00 | 0 | 0 | 0 | 0 | -15.4935 | 64.7894 | 99.653 | -9.653 | 62.1768 | 71.6603 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.2 | -11.2 | 1.1448 | 0
2015-11-05 16:00 | 0 | 0 | 0 | 0 | -15.5063 | 79.7889 | 102.8227 | -12.8227 | 76.555 | 85.1025 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11 | -11 | 1.144 | 0
2015-11-05 17:00 | 0 | 0 | 0 | 0 | -15.5191 | 94.7883 | 106.189 | -16.189 | 91.0752 | 98.9173 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.1 | -11.1 | 1.1444 | 0
2015-11-05 18:00 | 0 | 0 | 0 | 0 | -15.5319 | 109.7878 | 109.5382 | -19.5382 | 105.8494 | 112.9619 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.4 | -11.4 | 1.1456 | 0
2015-11-05 19:00 | 0 | 0 | 0 | 0 | -15.5447 | 124.7873 | 112.6466 | -22.6466 | 120.981 | 127.1527 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.5 | -10.5 | 1.142 | 0
2015-11-05 20:00 | 0 | 0 | 0 | 0 | -15.5575 | 139.7867 | 115.2902 | -25.2902 | 136.535 | 141.4362 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.1 | -10.1 | 1.1404 | 0
2015-11-05 21:00 | 0 | 0 | 0 | 0 | -15.5703 | 154.7862 | 117.2613 | -27.2613 | 152.507 | 155.7718 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.5 | -11.5 | 1.146 | 0
2015-11-05 22:00 | 0 | 0 | 0 | 0 | -15.5831 | 169.7856 | 118.3919 | -28.3919 | 168.8038 | 170.0991 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.7 | -11.7 | 1.1468 | 0
2015-11-05 23:00 | 0 | 0 | 0 | 0 | -15.5958 | 184.7851 | 118.5798 | -28.5798 | -174.7504 | 175.2069 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.9 | -9.9 | 1.1396 | 0
2015-11-06 | 0 | 0 | 0 | 0 | -15.6086 | -160.2155 | 117.8082 | -27.8082 | -158.3729 | 160.9691 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10 | -10 | 1.14 | 0
2015-11-06 01:00 | 0 | 0 | 0 | 0 | -15.6213 | -145.2161 | 116.1498 | -26.1498 | -142.2615 | 146.6288 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10 | -10 | 1.14 | 0
2015-11-06 02:00 | 0 | 0 | 0 | 0 | -15.6341 | -130.2166 | 113.7518 | -23.7518 | -126.5434 | 132.3277 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.6 | -10.6 | 1.1424 | 0
2015-11-06 03:00 | 0 | 0 | 0 | 0 | -15.6468 | -115.2172 | 110.8106 | -20.8106 | -111.2551 | 118.1064 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.1 | -10.1 | 1.1404 | 0
2015-11-06 04:00 | 0 | 0 | 0 | 0 | -15.6595 | -100.2178 | 107.5469 | -17.5469 | -96.3548 | 104.0128 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.6 | -10.6 | 1.1424 | 0
2015-11-06 05:00 | 0 | 0 | 0 | 0 | -15.6722 | -85.2184 | 104.1863 | -14.1863 | -81.7503 | 90.1183 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.4 | -10.4 | 1.1416 | 0
2015-11-06 06:00 | 0 | 0 | 0 | 0 | -15.685 | -70.219 | 100.9472 | -10.9472 | -67.3307 | 76.5409 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.9 | -10.9 | 1.1436 | 0
2015-11-06 07:00 | 0 | 0 | 0 | 0 | -15.6977 | -55.2196 | 98.0332 | -8.0332 | -52.9915 | 63.4934 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.9 | -9.9 | 1.1396 | 0
2015-11-06 08:00 | 0 | 0 | 0 | 0 | -15.7104 | -40.2202 | 95.6259 | -5.6259 | -38.6538 | 51.3887 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.5 | -8.5 | 1.134 | 0
2015-11-06 09:00 | 0 | 0 | 0 | 0 | -15.723 | -25.2209 | 93.8773 | -3.8773 | -24.2743 | 41.0758 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.4 | -8.4 | 1.1336 | 0
2015-11-06 10:00 | 0 | 0 | 0 | 0 | -15.7357 | -10.2215 | 92.9 | -2.9 | -9.8473 | 34.2207 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.5 | -8.5 | 1.134 | 0
2015-11-06 11:00 | 0 | 0 | 0 | 0 | -15.7484 | 4.7779 | 92.7583 | -2.7583 | 4.6035 | 33.0526 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8 | -8 | 1.132 | 0
2015-11-06 12:00 | 0 | 0 | 0 | 0 | -15.7611 | 19.7772 | 93.4623 | -3.4623 | 19.0406 | 38.0983 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.4 | -8.4 | 1.1336 | 0
2015-11-06 13:00 | 0 | 0 | 0 | 0 | -15.7737 | 34.7766 | 94.9666 | -4.9666 | 33.4335 | 47.4121 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.4 | -8.4 | 1.1336 | 0
2015-11-06 14:00 | 0 | 0 | 0 | 0 | -15.7864 | 49.776 | 97.175 | -7.175 | 47.7762 | 59.0035 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.5 | -8.5 | 1.134 | 0
2015-11-06 15:00 | 0 | 0 | 0 | 0 | -15.799 | 64.7753 | 99.949 | -9.949 | 62.0991 | 71.7737 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.8 | -8.8 | 1.1352 | 0
2015-11-06 16:00 | 0 | 0 | 0 | 0 | -15.8116 | 79.7746 | 103.1168 | -13.1168 | 76.4699 | 85.1897 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8 | -8 | 1.132 | 0
2015-11-06 17:00 | 0 | 0 | 0 | 0 | -15.8243 | 94.774 | 106.4824 | -16.4824 | 90.9867 | 98.9841 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.4 | -8.4 | 1.1336 | 0
2015-11-06 18:00 | 0 | 0 | 0 | 0 | -15.8369 | 109.7733 | 109.8322 | -19.8322 | 105.762 | 113.0123 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.3 | -7.3 | 1.1292 | 0
2015-11-06 19:00 | 0 | 0 | 0 | 0 | -15.8495 | 124.7726 | 112.9423 | -22.9423 | 120.8996 | 127.1898 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.8 | -6.8 | 1.1272 | 0
2015-11-06 20:00 | 0 | 0 | 0 | 0 | -15.8621 | 139.7719 | 115.5884 | -25.5884 | 136.465 | 141.4627 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.8 | -6.8 | 1.1272 | 0
2015-11-06 21:00 | 0 | 0 | 0 | 0 | -15.8747 | 154.7712 | 117.5624 | -27.5624 | 152.4538 | 155.792 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.6 | -6.6 | 1.1264 | 0
2015-11-06 22:00 | 0 | 0 | 0 | 0 | -15.8873 | 169.7706 | 118.6952 | -28.6952 | 168.7716 | 170.1301 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.2 | -6.2 | 1.1248 | 0
2015-11-06 23:00 | 0 | 0 | 0 | 0 | -15.8998 | 184.7698 | 118.884 | -28.884 | -174.7596 | 175.3024 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.1 | -6.1 | 1.1244 | 0
2015-11-07 | 0 | 0 | 0 | 0 | -15.9124 | -160.2309 | 118.1122 | -28.1122 | -158.3598 | 161.0177 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.3 | -5.3 | 1.1212 | 0
2015-11-07 01:00 | 0 | 0 | 0 | 0 | -15.925 | -145.2316 | 116.4525 | -26.4525 | -142.2294 | 146.6807 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6 | -6 | 1.124 | 0
2015-11-07 02:00 | 0 | 0 | 0 | 0 | -15.9375 | -130.2323 | 114.0526 | -24.0526 | -126.497 | 132.3888 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.2 | -5.2 | 1.1208 | 0
2015-11-07 03:00 | 0 | 0 | 0 | 0 | -15.9501 | -115.233 | 111.1099 | -21.1099 | -111.2001 | 118.1797 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.6 | -5.6 | 1.1224 | 0
2015-11-07 04:00 | 0 | 0 | 0 | 0 | -15.9626 | -100.2338 | 107.8453 | -17.8453 | -96.2963 | 104.101 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-11-07 05:00 | 0 | 0 | 0 | 0 | -15.9752 | -85.2345 | 104.4845 | -14.4845 | -81.6933 | 90.2246 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.8 | -4.8 | 1.1192 | 0
2015-11-07 06:00 | 0 | 0 | 0 | 0 | -15.9877 | -70.2352 | 101.2461 | -11.2461 | -67.2795 | 76.6702 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.9 | -3.9 | 1.1156 | 0
2015-11-07 07:00 | 0 | 0 | 0 | 0 | -16.0002 | -55.236 | 98.3333 | -8.3333 | -52.95 | 63.6524 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-11-07 08:00 | 0 | 0 | 0 | 0 | -16.0127 | -40.2367 | 95.9274 | -5.9274 | -38.6251 | 51.5868 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.1084 | 0
2015-11-07 09:00 | 0 | 0 | 0 | 0 | -16.0252 | -25.2375 | 94.1796 | -4.1796 | -24.2611 | 41.3231 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-11-07 10:00 | 0 | 0 | 0 | 0 | -16.0377 | -10.2383 | 93.2024 | -3.2024 | -9.8513 | 34.5136 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-11-07 11:00 | 0 | 0 | 0 | 0 | -16.0502 | 4.761 | 93.0598 | -3.0598 | 4.5815 | 33.3489 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1144 | 0
2015-11-07 12:00 | 0 | 0 | 0 | 0 | -16.0627 | 19.7602 | 93.7618 | -3.7618 | 19.0011 | 38.3468 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-11-07 13:00 | 0 | 0 | 0 | 0 | -16.0751 | 34.7594 | 95.2634 | -5.2634 | 33.3779 | 47.6027 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-11-07 14:00 | 0 | 0 | 0 | 0 | -16.0876 | 49.7586 | 97.4688 | -7.4688 | 47.707 | 59.1474 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-11-07 15:00 | 0 | 0 | 0 | 0 | -16.1 | 64.7578 | 100.24 | -10.24 | 62.0191 | 71.8828 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-11-07 16:00 | 0 | 0 | 0 | 0 | -16.1125 | 79.757 | 103.4059 | -13.4059 | 76.3825 | 85.2725 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.7 | -3.7 | 1.1148 | 0
2015-11-07 17:00 | 0 | 0 | 0 | 0 | -16.1249 | 94.7562 | 106.7707 | -16.7707 | 90.8958 | 99.0464 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.8 | -3.8 | 1.1152 | 0
2015-11-07 18:00 | 0 | 0 | 0 | 0 | -16.1374 | 109.7554 | 110.121 | -20.121 | 105.6719 | 113.058 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-11-07 19:00 | 0 | 0 | 0 | 0 | -16.1498 | 124.7546 | 113.2329 | -23.2329 | 120.8154 | 127.2218 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.11 | 0
2015-11-07 20:00 | 0 | 0 | 0 | 0 | -16.1622 | 139.7537 | 115.8818 | -25.8818 | 136.392 | 141.4834 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-11-07 21:00 | 0 | 0 | 0 | 0 | -16.1746 | 154.7529 | 117.8586 | -27.8586 | 152.3972 | 155.8049 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-11-07 22:00 | 0 | 0 | 0 | 0 | -16.187 | 169.7521 | 118.9938 | -28.9938 | 168.7356 | 170.1483 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-11-07 23:00 | 0 | 0 | 0 | 0 | -16.1994 | 184.7512 | 119.1839 | -29.1839 | -174.7728 | 175.3824 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-11-08 | 0 | 0 | 0 | 0 | -16.2118 | -160.2496 | 118.412 | -28.412 | -158.3508 | 161.0646 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-11-08 01:00 | 0 | 0 | 0 | 0 | -16.2242 | -145.2505 | 116.7511 | -26.7511 | -142.2014 | 146.733 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-11-08 02:00 | 0 | 0 | 0 | 0 | -16.2365 | -130.2514 | 114.3497 | -24.3497 | -126.4549 | 132.4512 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-11-08 03:00 | 0 | 0 | 0 | 0 | -16.2489 | -115.2522 | 111.4055 | -21.4055 | -111.1492 | 118.2546 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-11-08 04:00 | 0 | 0 | 0 | 0 | -16.2612 | -100.2531 | 108.14 | -18.14 | -96.2421 | 104.1908 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0968 | 0
2015-11-08 05:00 | 0 | 0 | 0 | 0 | -16.2736 | -85.254 | 104.7791 | -14.7791 | -81.6405 | 90.3327 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.096 | 0
2015-11-08 06:00 | 0 | 0 | 0 | 0 | -16.2859 | -70.2549 | 101.5414 | -11.5414 | -67.2324 | 76.8011 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-11-08 07:00 | 0 | 0 | 0 | 0 | -16.2982 | -55.2557 | 98.6296 | -8.6296 | -52.9124 | 63.8126 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0944 | 0
2015-11-08 08:00 | 0 | 0 | 0 | 0 | -16.3106 | -40.2566 | 96.2248 | -6.2248 | -38.6003 | 51.7854 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2 | 2 | 1.092 | 0
2015-11-08 09:00 | 0 | 0 | 0 | 0 | -16.3229 | -25.2575 | 94.4778 | -4.4778 | -24.2515 | 41.5693 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.0892 | 0
2015-11-08 10:00 | 0 | 0 | 0 | 0 | -16.3352 | -10.2585 | 93.5004 | -3.5004 | -9.8587 | 34.8032 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.09 | 0
2015-11-08 11:00 | 0 | 0 | 0 | 0 | -16.3475 | 4.7406 | 93.3566 | -3.3566 | 4.5564 | 33.6403 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.09 | 0
2015-11-08 12:00 | 0 | 0 | 0 | 0 | -16.3598 | 19.7397 | 94.0565 | -4.0565 | 18.9587 | 38.5905 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0904 | 0
2015-11-08 13:00 | 0 | 0 | 0 | 0 | -16.372 | 34.7388 | 95.5552 | -5.5552 | 33.3197 | 47.7888 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0928 | 0
2015-11-08 14:00 | 0 | 0 | 0 | 0 | -16.3843 | 49.7378 | 97.7576 | -7.7576 | 47.6352 | 59.287 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0916 | 0
2015-11-08 15:00 | 0 | 0 | 0 | 0 | -16.3966 | 64.7369 | 100.5259 | -10.5259 | 61.9366 | 71.9875 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0968 | 0
2015-11-08 16:00 | 0 | 0 | 0 | 0 | -16.4088 | 79.736 | 103.6898 | -13.6898 | 76.2927 | 85.3509 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0932 | 0
2015-11-08 17:00 | 0 | 0 | 0 | 0 | -16.4211 | 94.735 | 107.0537 | -17.0537 | 90.8024 | 99.1041 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.088 | 0
2015-11-08 18:00 | 0 | 0 | 0 | 0 | -16.4333 | 109.7341 | 110.4046 | -20.4046 | 105.5793 | 113.0989 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0904 | 0
2015-11-08 19:00 | 0 | 0 | 0 | 0 | -16.4455 | 124.7331 | 113.5184 | -23.5184 | 120.7284 | 127.2486 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0896 | 0
2015-11-08 20:00 | 0 | 0 | 0 | 0 | -16.4578 | 139.7321 | 116.1701 | -26.1701 | 136.3158 | 141.4985 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.0892 | 0
2015-11-08 21:00 | 0 | 0 | 0 | 0 | -16.47 | 154.7312 | 118.1499 | -28.1499 | 152.3372 | 155.8108 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0884 | 0
2015-11-08 22:00 | 0 | 0 | 0 | 0 | -16.4822 | 169.7302 | 119.2877 | -29.2877 | 168.6961 | 170.1538 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0912 | 0
2015-11-08 23:00 | 0 | 0 | 0 | 0 | -16.4944 | 184.7292 | 119.4792 | -29.4792 | -174.7898 | 175.4466 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0884 | 0
2015-11-09 | 0 | 0 | 0 | 0 | -16.5066 | -160.2718 | 118.7075 | -28.7075 | -158.3458 | 161.1098 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0876 | 0
2015-11-09 01:00 | 0 | 0 | 0 | 0 | -16.5187 | -145.2728 | 117.0457 | -27.0457 | -142.1775 | 146.7857 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.088 | 0
2015-11-09 02:00 | 0 | 0 | 0 | 0 | -16.5309 | -130.2738 | 114.6429 | -24.6429 | -126.417 | 132.5147 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.086 | 0
2015-11-09 03:00 | 0 | 0 | 0 | 0 | -16.5431 | -115.2748 | 111.6973 | -21.6973 | -111.1026 | 118.3309 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0876 | 0
2015-11-09 04:00 | 0 | 0 | 0 | 0 | -16.5552 | -100.2758 | 108.4309 | -18.4309 | -96.192 | 104.2823 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0876 | 0
2015-11-09 05:00 | 0 | 0 | 0 | 0 | -16.5674 | -85.2769 | 105.07 | -15.07 | -81.5919 | 90.4424 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0852 | 0
2015-11-09 06:00 | 0 | 0 | 0 | 0 | -16.5795 | -70.2779 | 101.8328 | -11.8328 | -67.1894 | 76.9334 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0868 | 0
2015-11-09 07:00 | 0 | 0 | 0 | 0 | -16.5917 | -55.2789 | 98.922 | -8.922 | -52.8788 | 63.9739 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0868 | 0
2015-11-09 08:00 | 0 | 0 | 0 | 0 | -16.6038 | -40.28 | 96.5181 | -6.5181 | -38.5792 | 51.9843 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.088 | 0
2015-11-09 09:00 | 0 | 0 | 0 | 0 | -16.6159 | -25.281 | 94.7716 | -4.7716 | -24.2456 | 41.8145 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.09 | 0
2015-11-09 10:00 | 0 | 0 | 0 | 0 | -16.628 | -10.282 | 93.7939 | -3.7939 | -9.8695 | 35.0895 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-11-09 11:00 | 0 | 0 | 0 | 0 | -16.6401 | 4.7169 | 93.6488 | -3.6488 | 4.5281 | 33.9267 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0904 | 0
2015-11-09 12:00 | 0 | 0 | 0 | 0 | -16.6522 | 19.7158 | 94.3463 | -4.3463 | 18.9135 | 38.8291 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0908 | 0
2015-11-09 13:00 | 0 | 0 | 0 | 0 | -16.6643 | 34.7148 | 95.8421 | -5.8421 | 33.2588 | 47.9702 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.0892 | 0
2015-11-09 14:00 | 0 | 0 | 0 | 0 | -16.6764 | 49.7137 | 98.0412 | -8.0412 | 47.5609 | 59.422 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0888 | 0
2015-11-09 15:00 | 0 | 0 | 0 | 0 | -16.6884 | 64.7126 | 100.8066 | -10.8066 | 61.8518 | 72.0879 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0916 | 0
2015-11-09 16:00 | 0 | 0 | 0 | 0 | -16.7005 | 79.7115 | 103.9684 | -13.9684 | 76.2006 | 85.4249 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0912 | 0
2015-11-09 17:00 | 0 | 0 | 0 | 0 | -16.7125 | 94.7104 | 107.3315 | -17.3315 | 90.7066 | 99.1573 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.0892 | 0
2015-11-09 18:00 | 0 | 0 | 0 | 0 | -16.7246 | 109.7093 | 110.683 | -20.683 | 105.4841 | 113.1351 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.09 | 0
2015-11-09 19:00 | 0 | 0 | 0 | 0 | -16.7366 | 124.7082 | 113.7987 | -23.7987 | 120.6386 | 127.2705 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.086 | 0
2015-11-09 20:00 | 0 | 0 | 0 | 0 | -16.7486 | 139.7071 | 116.4532 | -26.4532 | 136.2367 | 141.5079 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0868 | 0
2015-11-09 21:00 | 0 | 0 | 0 | 0 | -16.7607 | 154.706 | 118.4362 | -28.4362 | 152.2739 | 155.8097 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0868 | 0
2015-11-09 22:00 | 0 | 0 | 0 | 0 | -16.7727 | 169.7049 | 119.5767 | -29.5767 | 168.6529 | 170.1471 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0888 | 0
2015-11-09 23:00 | 0 | 0 | 0 | 0 | -16.7847 | 184.7038 | 119.77 | -29.77 | -174.8107 | 175.4952 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0876 | 0
2015-11-10 | 0 | 0 | 0 | 0 | -16.7967 | -160.2974 | 118.9986 | -28.9986 | -158.3449 | 161.1536 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0888 | 0
2015-11-10 01:00 | 0 | 0 | 0 | 0 | -16.8086 | -145.2985 | 117.3362 | -27.3362 | -142.1579 | 146.8389 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.0892 | 0
2015-11-10 02:00 | 0 | 0 | 0 | 0 | -16.8206 | -130.2997 | 114.932 | -24.932 | -126.3833 | 132.5793 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0888 | 0
2015-11-10 03:00 | 0 | 0 | 0 | 0 | -16.8326 | -115.3008 | 111.9852 | -21.9852 | -111.0602 | 118.4087 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0884 | 0
2015-11-10 04:00 | 0 | 0 | 0 | 0 | -16.8445 | -100.302 | 108.718 | -18.718 | -96.1463 | 104.3754 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0904 | 0
2015-11-10 05:00 | 0 | 0 | 0 | 0 | -16.8565 | -85.3031 | 105.357 | -15.357 | -81.5475 | 90.5537 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0908 | 0
2015-11-10 06:00 | 0 | 0 | 0 | 0 | -16.8684 | -70.3043 | 102.1203 | -12.1203 | -67.1506 | 77.0672 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0916 | 0
2015-11-10 07:00 | 0 | 0 | 0 | 0 | -16.8804 | -55.3055 | 99.2104 | -9.2104 | -52.8492 | 64.1362 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2 | 2 | 1.092 | 0
2015-11-10 08:00 | 0 | 0 | 0 | 0 | -16.8923 | -40.3066 | 96.8073 | -6.8073 | -38.562 | 52.1834 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.0892 | 0
2015-11-10 09:00 | 0 | 0 | 0 | 0 | -16.9042 | -25.3078 | 95.061 | -5.061 | -24.2433 | 42.0583 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.09 | 0
2015-11-10 10:00 | 0 | 0 | 0 | 0 | -16.9161 | -10.309 | 94.0828 | -4.0828 | -9.8837 | 35.3723 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0904 | 0
2015-11-10 11:00 | 0 | 0 | 0 | 0 | -16.928 | 4.6898 | 93.9362 | -3.9362 | 4.4968 | 34.2082 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0896 | 0
2015-11-10 12:00 | 0 | 0 | 0 | 0 | -16.9399 | 19.6886 | 94.6312 | -4.6312 | 18.8653 | 39.0627 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0888 | 0
2015-11-10 13:00 | 0 | 0 | 0 | 0 | -16.9518 | 34.6874 | 96.1238 | -6.1238 | 33.1954 | 48.1468 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0896 | 0
2015-11-10 14:00 | 0 | 0 | 0 | 0 | -16.9637 | 49.6862 | 98.3195 | -8.3195 | 47.4843 | 59.5525 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0896 | 0
2015-11-10 15:00 | 0 | 0 | 0 | 0 | -16.9755 | 64.6849 | 101.082 | -11.082 | 61.7647 | 72.1837 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.09 | 0
2015-11-10 16:00 | 0 | 0 | 0 | 0 | -16.9874 | 79.6837 | 104.2416 | -14.2416 | 76.1062 | 85.4944 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0888 | 0
2015-11-10 17:00 | 0 | 0 | 0 | 0 | -16.9992 | 94.6825 | 107.6038 | -17.6038 | 90.6086 | 99.206 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0888 | 0
2015-11-10 18:00 | 0 | 0 | 0 | 0 | -17.0111 | 109.6812 | 110.9558 | -20.9558 | 105.3865 | 113.1667 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0872 | 0
2015-11-10 19:00 | 0 | 0 | 0 | 0 | -17.0229 | 124.68 | 114.0735 | -24.0735 | 120.5461 | 127.2874 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0884 | 0
2015-11-10 20:00 | 0 | 0 | 0 | 0 | -17.0347 | 139.6787 | 116.731 | -26.731 | 136.1545 | 141.5119 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.088 | 0
2015-11-10 21:00 | 0 | 0 | 0 | 0 | -17.0465 | 154.6775 | 118.7174 | -28.7174 | 152.2073 | 155.8018 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0884 | 0
2015-11-10 22:00 | 0 | 0 | 0 | 0 | -17.0583 | 169.6762 | 119.8608 | -29.8608 | 168.606 | 170.1287 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0896 | 0
2015-11-10 23:00 | 0 | 0 | 0 | 0 | -17.0701 | 184.675 | 120.056 | -30.056 | -174.8355 | 175.5287 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0908 | 0
2015-11-11 | 0 | 0 | 0 | 0 | -17.0819 | -160.3263 | 119.2852 | -29.2852 | -158.3481 | 161.1961 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0872 | 0
2015-11-11 01:00 | 0 | 0 | 0 | 0 | -17.0937 | -145.3276 | 117.6223 | -27.6223 | -142.1424 | 146.8926 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0944 | 0
2015-11-11 02:00 | 0 | 0 | 0 | 0 | -17.1055 | -130.3289 | 115.217 | -25.217 | -126.3539 | 132.6452 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0896 | 0
2015-11-11 03:00 | 0 | 0 | 0 | 0 | -17.1172 | -115.3302 | 112.269 | -22.269 | -111.0222 | 118.488 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0932 | 0
2015-11-11 04:00 | 0 | 0 | 0 | 0 | -17.129 | -100.3315 | 109.0012 | -19.0012 | -96.1048 | 104.4701 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0888 | 0
2015-11-11 05:00 | 0 | 0 | 0 | 0 | -17.1408 | -85.3328 | 105.64 | -15.64 | -81.5073 | 90.6666 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0844 | 0
2015-11-11 06:00 | 0 | 0 | 0 | 0 | -17.1525 | -70.3341 | 102.4038 | -12.4038 | -67.1158 | 77.2023 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0872 | 0
2015-11-11 07:00 | 0 | 0 | 0 | 0 | -17.1642 | -55.3354 | 99.4945 | -9.4945 | -52.8236 | 64.2994 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0884 | 0
2015-11-11 08:00 | 0 | 0 | 0 | 0 | -17.1759 | -40.3367 | 97.0921 | -7.0921 | -38.5487 | 52.3826 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.0892 | 0
2015-11-11 09:00 | 0 | 0 | 0 | 0 | -17.1877 | -25.338 | 95.346 | -5.346 | -24.2446 | 42.3006 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.0892 | 0
2015-11-11 10:00 | 0 | 0 | 0 | 0 | -17.1994 | -10.3394 | 94.367 | -4.367 | -9.9013 | 35.6515 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0908 | 0
2015-11-11 11:00 | 0 | 0 | 0 | 0 | -17.211 | 4.6593 | 94.2186 | -4.2186 | 4.4623 | 34.4845 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.2 | 3.2 | 1.0872 | 0
2015-11-11 12:00 | 0 | 0 | 0 | 0 | -17.2227 | 19.658 | 94.911 | -4.911 | 18.8144 | 39.2911 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.088 | 0
2015-11-11 13:00 | 0 | 0 | 0 | 0 | -17.2344 | 34.6566 | 96.4002 | -6.4002 | 33.1293 | 48.3187 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0912 | 0
2015-11-11 14:00 | 0 | 0 | 0 | 0 | -17.2461 | 49.6553 | 98.5925 | -8.5925 | 47.4052 | 59.6785 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2 | 2 | 1.092 | 0
2015-11-11 15:00 | 0 | 0 | 0 | 0 | -17.2577 | 64.6539 | 101.3518 | -11.3518 | 61.6753 | 72.2752 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2 | 2 | 1.092 | 0
2015-11-11 16:00 | 0 | 0 | 0 | 0 | -17.2694 | 79.6525 | 104.5093 | -14.5093 | 76.0095 | 85.5594 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0908 | 0
2015-11-11 17:00 | 0 | 0 | 0 | 0 | -17.281 | 94.6512 | 107.8706 | -17.8706 | 90.5082 | 99.2501 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0924 | 0
2015-11-11 18:00 | 0 | 0 | 0 | 0 | -17.2927 | 109.6498 | 111.2232 | -21.2232 | 105.2864 | 113.1935 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0928 | 0
2015-11-11 19:00 | 0 | 0 | 0 | 0 | -17.3043 | 124.6484 | 114.3429 | -24.3429 | 120.4509 | 127.2994 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0916 | 0
2015-11-11 20:00 | 0 | 0 | 0 | 0 | -17.3159 | 139.647 | 117.0034 | -27.0034 | 136.0694 | 141.5104 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2 | 2 | 1.092 | 0
2015-11-11 21:00 | 0 | 0 | 0 | 0 | -17.3275 | 154.6456 | 118.9933 | -28.9933 | 152.1374 | 155.7874 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-11-11 22:00 | 0 | 0 | 0 | 0 | -17.3391 | 169.6442 | 120.1399 | -30.1399 | 168.5556 | 170.099 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0944 | 0
2015-11-11 23:00 | 0 | 0 | 0 | 0 | -17.3507 | 184.6428 | 120.3371 | -30.3371 | -174.8641 | 175.5474 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.0948 | 0
2015-11-12 | 0 | 0 | 0 | 0 | -17.3623 | -160.3586 | 119.5672 | -29.5672 | -158.3553 | 161.2374 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.0948 | 0
2015-11-12 01:00 | 0 | 0 | 0 | 0 | -17.3739 | -145.36 | 117.9039 | -27.9039 | -142.1312 | 146.9469 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-11-12 02:00 | 0 | 0 | 0 | 0 | -17.3854 | -130.3615 | 115.4978 | -25.4978 | -126.3287 | 132.7122 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-11-12 03:00 | 0 | 0 | 0 | 0 | -17.397 | -115.3629 | 112.5488 | -22.5488 | -110.9884 | 118.5688 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-11-12 04:00 | 0 | 0 | 0 | 0 | -17.4085 | -100.3643 | 109.2803 | -19.2803 | -96.0676 | 104.5663 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0932 | 0
2015-11-12 05:00 | 0 | 0 | 0 | 0 | -17.4201 | -85.3658 | 105.919 | -15.919 | -81.4713 | 90.7809 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0936 | 0
2015-11-12 06:00 | 0 | 0 | 0 | 0 | -17.4316 | -70.3672 | 102.6831 | -12.6831 | -67.0853 | 77.3386 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0924 | 0
2015-11-12 07:00 | 0 | 0 | 0 | 0 | -17.4431 | -55.3687 | 99.7744 | -9.7744 | -52.802 | 64.4633 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.09 | 0
2015-11-12 08:00 | 0 | 0 | 0 | 0 | -17.4546 | -40.3701 | 97.3724 | -7.3724 | -38.5391 | 52.5816 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.0892 | 0
2015-11-12 09:00 | 0 | 0 | 0 | 0 | -17.4661 | -25.3716 | 95.6262 | -5.6262 | -24.2494 | 42.5414 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-11-12 10:00 | 0 | 0 | 0 | 0 | -17.4776 | -10.3731 | 94.6464 | -4.6464 | -9.9222 | 35.9269 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-11-12 11:00 | 0 | 0 | 0 | 0 | -17.4891 | 4.6255 | 94.496 | -4.496 | 4.4249 | 34.7555 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-11-12 12:00 | 0 | 0 | 0 | 0 | -17.5006 | 19.624 | 95.1856 | -5.1856 | 18.7608 | 39.5143 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-11-12 13:00 | 0 | 0 | 0 | 0 | -17.5121 | 34.6225 | 96.6714 | -6.6714 | 33.0608 | 48.4856 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-11-12 14:00 | 0 | 0 | 0 | 0 | -17.5235 | 49.621 | 98.86 | -8.86 | 47.3239 | 59.7998 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0968 | 0
2015-11-12 15:00 | 0 | 0 | 0 | 0 | -17.535 | 64.6195 | 101.6162 | -11.6162 | 61.5837 | 72.3621 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.096 | 0
2015-11-12 16:00 | 0 | 0 | 0 | 0 | -17.5464 | 79.618 | 104.7713 | -14.7713 | 75.9107 | 85.62 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-11-12 17:00 | 0 | 0 | 0 | 0 | -17.5578 | 94.6165 | 108.1317 | -18.1317 | 90.4056 | 99.2898 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.0948 | 0
2015-11-12 18:00 | 0 | 0 | 0 | 0 | -17.5693 | 109.615 | 111.4849 | -21.4849 | 105.184 | 113.2158 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-11-12 19:00 | 0 | 0 | 0 | 0 | -17.5807 | 124.6134 | 114.6067 | -24.6067 | 120.3532 | 127.3065 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-11-12 20:00 | 0 | 0 | 0 | 0 | -17.5921 | 139.6119 | 117.2704 | -27.2704 | 135.9814 | 141.5036 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0968 | 0
2015-11-12 21:00 | 0 | 0 | 0 | 0 | -17.6035 | 154.6104 | 119.2639 | -29.2639 | 152.0642 | 155.7666 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-11-12 22:00 | 0 | 0 | 0 | 0 | -17.6149 | 169.6088 | 120.4137 | -30.4137 | 168.5016 | 170.0586 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-11-12 23:00 | 0 | 0 | 0 | 0 | -17.6262 | 184.6073 | 120.6133 | -30.6133 | -174.8966 | 175.552 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-11-13 | 0 | 0 | 0 | 0 | -17.6376 | -160.3943 | 119.8444 | -29.8444 | -158.3667 | 161.2777 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-11-13 01:00 | 0 | 0 | 0 | 0 | -17.649 | -145.3958 | 118.1811 | -28.1811 | -142.1242 | 147.0018 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-11-13 02:00 | 0 | 0 | 0 | 0 | -17.6603 | -130.3974 | 115.7741 | -25.7741 | -126.3079 | 132.7805 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-11-13 03:00 | 0 | 0 | 0 | 0 | -17.6717 | -115.3989 | 112.8243 | -22.8243 | -110.959 | 118.6511 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-11-13 04:00 | 0 | 0 | 0 | 0 | -17.683 | -100.4005 | 109.5552 | -19.5552 | -96.0347 | 104.6641 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-11-13 05:00 | 0 | 0 | 0 | 0 | -17.6943 | -85.4021 | 106.1937 | -16.1937 | -81.4396 | 90.8966 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-11-13 06:00 | 0 | 0 | 0 | 0 | -17.7056 | -70.4037 | 102.9581 | -12.9581 | -67.0588 | 77.476 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-11-13 07:00 | 0 | 0 | 0 | 0 | -17.7169 | -55.4053 | 100.0499 | -10.0499 | -52.7844 | 64.6279 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-11-13 08:00 | 0 | 0 | 0 | 0 | -17.7282 | -40.4069 | 97.6482 | -7.6482 | -38.5334 | 52.7803 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-11-13 09:00 | 0 | 0 | 0 | 0 | -17.7395 | -25.4085 | 95.9018 | -5.9018 | -24.2579 | 42.7803 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-11-13 10:00 | 0 | 0 | 0 | 0 | -17.7508 | -10.4101 | 94.9208 | -4.9208 | -9.9464 | 36.1985 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-11-13 11:00 | 0 | 0 | 0 | 0 | -17.7621 | 4.5883 | 94.7683 | -4.7683 | 4.3844 | 35.0213 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-11-13 12:00 | 0 | 0 | 0 | 0 | -17.7733 | 19.5867 | 95.4548 | -5.4548 | 18.7043 | 39.7321 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-11-13 13:00 | 0 | 0 | 0 | 0 | -17.7846 | 34.5851 | 96.937 | -6.937 | 32.9897 | 48.6477 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-11-13 14:00 | 0 | 0 | 0 | 0 | -17.7958 | 49.5834 | 99.122 | -9.122 | 47.2402 | 59.9164 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-11-13 15:00 | 0 | 0 | 0 | 0 | -17.8071 | 64.5818 | 101.8749 | -11.8749 | 61.49 | 72.4444 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-11-13 16:00 | 0 | 0 | 0 | 0 | -17.8183 | 79.5801 | 105.0277 | -15.0277 | 75.8098 | 85.6761 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-11-13 17:00 | 0 | 0 | 0 | 0 | -17.8295 | 94.5785 | 108.3871 | -18.3871 | 90.3009 | 99.3249 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-11-13 18:00 | 0 | 0 | 0 | 0 | -17.8407 | 109.5768 | 111.7409 | -21.7409 | 105.0792 | 113.2335 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-11-13 19:00 | 0 | 0 | 0 | 0 | -17.8519 | 124.5752 | 114.8647 | -24.8647 | 120.2528 | 127.3089 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-11-13 20:00 | 0 | 0 | 0 | 0 | -17.8631 | 139.5735 | 117.5317 | -27.5317 | 135.8905 | 141.4917 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.1056 | 0
2015-11-13 21:00 | 0 | 0 | 0 | 0 | -17.8743 | 154.5718 | 119.5289 | -29.5289 | 151.9878 | 155.7397 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-11-13 22:00 | 0 | 0 | 0 | 0 | -17.8855 | 169.5702 | 120.6823 | -30.6823 | 168.444 | 170.0079 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-11-13 23:00 | 0 | 0 | 0 | 0 | -17.8966 | 184.5685 | 120.8844 | -30.8844 | -174.933 | 175.5434 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.102 | 0
2015-11-14 | 0 | 0 | 0 | 0 | -17.9078 | -160.4332 | 120.1168 | -30.1168 | -158.3821 | 161.3172 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-11-14 01:00 | 0 | 0 | 0 | 0 | -17.9189 | -145.4349 | 118.4536 | -28.4536 | -142.1214 | 147.0575 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.1032 | 0
2015-11-14 02:00 | 0 | 0 | 0 | 0 | -17.9301 | -130.4366 | 116.0461 | -26.0461 | -126.2915 | 132.8501 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-11-14 03:00 | 0 | 0 | 0 | 0 | -17.9412 | -115.4383 | 113.0954 | -23.0954 | -110.934 | 118.7348 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.1064 | 0
2015-11-14 04:00 | 0 | 0 | 0 | 0 | -17.9523 | -100.44 | 109.8257 | -19.8257 | -96.0061 | 104.7632 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.1056 | 0
2015-11-14 05:00 | 0 | 0 | 0 | 0 | -17.9634 | -85.4417 | 106.4642 | -16.4642 | -81.4121 | 91.0136 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-11-14 06:00 | 0 | 0 | 0 | 0 | -17.9745 | -70.4435 | 103.2287 | -13.2287 | -67.0366 | 77.6144 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-11-14 07:00 | 0 | 0 | 0 | 0 | -17.9856 | -55.4452 | 100.3209 | -10.3209 | -52.7708 | 64.7929 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-11-14 08:00 | 0 | 0 | 0 | 0 | -17.9967 | -40.4469 | 97.9193 | -7.9193 | -38.5315 | 52.9787 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-11-14 09:00 | 0 | 0 | 0 | 0 | -18.0077 | -25.4487 | 96.1724 | -6.1724 | -24.2699 | 43.0173 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-11-14 10:00 | 0 | 0 | 0 | 0 | -18.0188 | -10.4504 | 95.1901 | -5.1901 | -9.9738 | 36.466 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-11-14 11:00 | 0 | 0 | 0 | 0 | -18.0299 | 4.5478 | 95.0354 | -5.0354 | 4.3409 | 35.2816 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.1056 | 0
2015-11-14 12:00 | 0 | 0 | 0 | 0 | -18.0409 | 19.5461 | 95.7187 | -5.7187 | 18.6452 | 39.9445 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.1056 | 0
2015-11-14 13:00 | 0 | 0 | 0 | 0 | -18.0519 | 34.5443 | 97.1971 | -7.1971 | 32.9163 | 48.8046 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.1084 | 0
2015-11-14 14:00 | 0 | 0 | 0 | 0 | -18.063 | 49.5426 | 99.3783 | -9.3783 | 47.1544 | 60.0283 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-11-14 15:00 | 0 | 0 | 0 | 0 | -18.074 | 64.5408 | 102.1278 | -12.1278 | 61.3942 | 72.5222 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-11-14 16:00 | 0 | 0 | 0 | 0 | -18.085 | 79.539 | 105.2782 | -15.2782 | 75.7069 | 85.7277 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-11-14 17:00 | 0 | 0 | 0 | 0 | -18.096 | 94.5372 | 108.6367 | -18.6367 | 90.194 | 99.3556 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.1064 | 0
2015-11-14 18:00 | 0 | 0 | 0 | 0 | -18.107 | 109.5354 | 111.9911 | -21.9911 | 104.9722 | 113.2467 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-11-14 19:00 | 0 | 0 | 0 | 0 | -18.1179 | 124.5336 | 115.117 | -25.117 | 120.15 | 127.3065 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-11-14 20:00 | 0 | 0 | 0 | 0 | -18.1289 | 139.5318 | 117.7873 | -27.7873 | 135.7968 | 141.4746 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-11-14 21:00 | 0 | 0 | 0 | 0 | -18.1399 | 154.53 | 119.7884 | -29.7884 | 151.9083 | 155.7067 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-11-14 22:00 | 0 | 0 | 0 | 0 | -18.1508 | 169.5282 | 120.9454 | -30.9454 | 168.3829 | 169.9476 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-11-14 23:00 | 0 | 0 | 0 | 0 | -18.1618 | 184.5264 | 121.1503 | -31.1503 | -174.9733 | 175.5224 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-11-15 | 0 | 0 | 0 | 0 | -18.1727 | -160.4754 | 120.3842 | -30.3842 | -158.4016 | 161.3559 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-11-15 01:00 | 0 | 0 | 0 | 0 | -18.1836 | -145.4773 | 118.7213 | -28.7213 | -142.1229 | 147.1139 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-11-15 02:00 | 0 | 0 | 0 | 0 | -18.1945 | -130.4791 | 116.3134 | -26.3134 | -126.2793 | 132.9209 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-11-15 03:00 | 0 | 0 | 0 | 0 | -18.2054 | -115.4809 | 113.3621 | -23.3621 | -110.9133 | 118.8199 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-11-15 04:00 | 0 | 0 | 0 | 0 | -18.2163 | -100.4828 | 110.0919 | -20.0919 | -95.9819 | 104.8638 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-11-15 05:00 | 0 | 0 | 0 | 0 | -18.2272 | -85.4846 | 106.7302 | -16.7302 | -81.3889 | 91.1319 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-11-15 06:00 | 0 | 0 | 0 | 0 | -18.2381 | -70.4865 | 103.4949 | -13.4949 | -67.0184 | 77.7538 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0968 | 0
2015-11-15 07:00 | 0 | 0 | 0 | 0 | -18.2489 | -55.4884 | 100.5873 | -10.5873 | -52.7612 | 64.9584 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.0948 | 0
2015-11-15 08:00 | 0 | 0 | 0 | 0 | -18.2598 | -40.4902 | 98.1856 | -8.1856 | -38.5333 | 53.1764 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0928 | 0
2015-11-15 09:00 | 0 | 0 | 0 | 0 | -18.2706 | -25.4921 | 96.4381 | -6.4381 | -24.2855 | 43.2521 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0916 | 0
2015-11-15 10:00 | 0 | 0 | 0 | 0 | -18.2815 | -10.494 | 95.4543 | -5.4543 | -10.0045 | 36.7293 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0916 | 0
2015-11-15 11:00 | 0 | 0 | 0 | 0 | -18.2923 | 4.5041 | 95.297 | -5.297 | 4.2945 | 35.5364 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-11-15 12:00 | 0 | 0 | 0 | 0 | -18.3031 | 19.5022 | 95.977 | -5.977 | 18.5835 | 40.1513 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-11-15 13:00 | 0 | 0 | 0 | 0 | -18.3139 | 34.5003 | 97.4516 | -7.4516 | 32.8405 | 48.9565 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0932 | 0
2015-11-15 14:00 | 0 | 0 | 0 | 0 | -18.3247 | 49.4984 | 99.6288 | -9.6288 | 47.0663 | 60.1354 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-11-15 15:00 | 0 | 0 | 0 | 0 | -18.3355 | 64.4965 | 102.3749 | -12.3749 | 61.2963 | 72.5954 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0936 | 0
2015-11-15 16:00 | 0 | 0 | 0 | 0 | -18.3463 | 79.4946 | 105.5229 | -15.5229 | 75.602 | 85.7748 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0924 | 0
2015-11-15 17:00 | 0 | 0 | 0 | 0 | -18.3571 | 94.4927 | 108.8803 | -18.8803 | 90.0852 | 99.3819 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0932 | 0
2015-11-15 18:00 | 0 | 0 | 0 | 0 | -18.3678 | 109.4908 | 112.2353 | -22.2353 | 104.863 | 113.2553 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-11-15 19:00 | 0 | 0 | 0 | 0 | -18.3786 | 124.4888 | 115.3634 | -25.3634 | 120.0448 | 127.2996 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-11-15 20:00 | 0 | 0 | 0 | 0 | -18.3893 | 139.4869 | 118.037 | -28.037 | 135.7003 | 141.4527 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-11-15 21:00 | 0 | 0 | 0 | 0 | -18.4001 | 154.4849 | 120.0422 | -30.0422 | 151.8256 | 155.668 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-11-15 22:00 | 0 | 0 | 0 | 0 | -18.4108 | 169.483 | 121.203 | -31.203 | 168.3182 | 169.8783 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.0948 | 0
2015-11-15 23:00 | 0 | 0 | 0 | 0 | -18.4215 | 184.481 | 121.4109 | -31.4109 | -175.0174 | 175.4901 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-11-16 | 0 | 0 | 0 | 0 | -18.4322 | -160.5209 | 120.6465 | -30.6465 | -158.4252 | 161.3942 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.096 | 0
2015-11-16 01:00 | 0 | 0 | 0 | 0 | -18.4429 | -145.5229 | 118.9842 | -28.9842 | -142.1287 | 147.1712 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-11-16 02:00 | 0 | 0 | 0 | 0 | -18.4536 | -130.5249 | 116.576 | -26.576 | -126.2715 | 132.993 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-11-16 03:00 | 0 | 0 | 0 | 0 | -18.4643 | -115.5268 | 113.6241 | -23.6241 | -110.8969 | 118.9064 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-11-16 04:00 | 0 | 0 | 0 | 0 | -18.4749 | -100.5288 | 110.3535 | -20.3535 | -95.962 | 104.9658 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-11-16 05:00 | 0 | 0 | 0 | 0 | -18.4856 | -85.5308 | 106.9916 | -16.9916 | -81.37 | 91.2514 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-11-16 06:00 | 0 | 0 | 0 | 0 | -18.4963 | -70.5328 | 103.7564 | -13.7564 | -67.0044 | 77.8941 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-11-16 07:00 | 0 | 0 | 0 | 0 | -18.5069 | -55.5348 | 100.8489 | -10.8489 | -52.7556 | 65.124 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-11-16 08:00 | 0 | 0 | 0 | 0 | -18.5175 | -40.5368 | 98.4471 | -8.4471 | -38.5389 | 53.3735 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-11-16 09:00 | 0 | 0 | 0 | 0 | -18.5281 | -25.5388 | 96.6987 | -6.6987 | -24.3045 | 43.4847 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-11-16 10:00 | 0 | 0 | 0 | 0 | -18.5388 | -10.5408 | 95.7131 | -5.7131 | -10.0385 | 36.9884 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.1048 | 0
2015-11-16 11:00 | 0 | 0 | 0 | 0 | -18.5494 | 4.4572 | 95.5532 | -5.5532 | 4.2451 | 35.7856 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-11-16 12:00 | 0 | 0 | 0 | 0 | -18.5599 | 19.4551 | 96.2297 | -6.2297 | 18.5192 | 40.3526 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.8 | -2.8 | 1.1112 | 0
2015-11-16 13:00 | 0 | 0 | 0 | 0 | -18.5705 | 34.4531 | 97.7002 | -7.7002 | 32.7623 | 49.1032 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-11-16 14:00 | 0 | 0 | 0 | 0 | -18.5811 | 49.4511 | 99.8734 | -9.8734 | 46.9762 | 60.2377 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-11-16 15:00 | 0 | 0 | 0 | 0 | -18.5917 | 64.449 | 102.616 | -12.616 | 61.1965 | 72.664 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-11-16 16:00 | 0 | 0 | 0 | 0 | -18.6022 | 79.447 | 105.7615 | -15.7615 | 75.4951 | 85.8175 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-11-16 17:00 | 0 | 0 | 0 | 0 | -18.6128 | 94.4449 | 109.1178 | -19.1178 | 89.9743 | 99.4037 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-11-16 18:00 | 0 | 0 | 0 | 0 | -18.6233 | 109.4429 | 112.4734 | -22.4734 | 104.7517 | 113.2596 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.2 | -4.2 | 1.1168 | 0
2015-11-16 19:00 | 0 | 0 | 0 | 0 | -18.6338 | 124.4408 | 115.6037 | -25.6037 | 119.9372 | 127.2881 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1144 | 0
2015-11-16 20:00 | 0 | 0 | 0 | 0 | -18.6443 | 139.4387 | 118.2809 | -28.2809 | 135.6011 | 141.4259 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.4 | -2.4 | 1.1096 | 0
2015-11-16 21:00 | 0 | 0 | 0 | 0 | -18.6548 | 154.4366 | 120.2902 | -30.2902 | 151.7398 | 155.6237 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.1084 | 0
2015-11-16 22:00 | 0 | 0 | 0 | 0 | -18.6653 | 169.4346 | 121.455 | -31.455 | 168.2501 | 169.8006 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1144 | 0
2015-11-16 23:00 | 0 | 0 | 0 | 0 | -18.6758 | 184.4325 | 121.6661 | -31.6661 | -175.0652 | 175.4475 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.3 | -4.3 | 1.1172 | 0
2015-11-17 | 0 | 0 | 0 | 0 | -18.6863 | -160.5696 | 120.9036 | -30.9036 | -158.4529 | 161.432 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.3 | -4.3 | 1.1172 | 0
2015-11-17 01:00 | 0 | 0 | 0 | 0 | -18.6967 | -145.5717 | 119.242 | -29.242 | -142.1386 | 147.2294 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.1 | -5.1 | 1.1204 | 0
2015-11-17 02:00 | 0 | 0 | 0 | 0 | -18.7072 | -130.5738 | 116.8338 | -26.8338 | -126.268 | 133.0664 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1184 | 0
2015-11-17 03:00 | 0 | 0 | 0 | 0 | -18.7176 | -115.5759 | 113.8815 | -23.8815 | -110.885 | 118.9943 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.11 | 0
2015-11-17 04:00 | 0 | 0 | 0 | 0 | -18.7281 | -100.578 | 110.6105 | -20.6105 | -95.9464 | 105.0691 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.3 | -3.3 | 1.1132 | 0
2015-11-17 05:00 | 0 | 0 | 0 | 0 | -18.7385 | -85.5802 | 107.2484 | -17.2484 | -81.3553 | 91.3719 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-11-17 06:00 | 0 | 0 | 0 | 0 | -18.7489 | -70.5823 | 104.0132 | -14.0132 | -66.9945 | 78.035 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1144 | 0
2015-11-17 07:00 | 0 | 0 | 0 | 0 | -18.7593 | -55.5844 | 101.1057 | -11.1057 | -52.7539 | 65.2899 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-11-17 08:00 | 0 | 0 | 0 | 0 | -18.7697 | -40.5866 | 98.7035 | -8.7035 | -38.5482 | 53.5697 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-11-17 09:00 | 0 | 0 | 0 | 0 | -18.7801 | -25.5887 | 96.9541 | -6.9541 | -24.327 | 43.7148 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-11-17 10:00 | 0 | 0 | 0 | 0 | -18.7905 | -10.5908 | 95.9666 | -5.9666 | -10.0755 | 37.243 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-11-17 11:00 | 0 | 0 | 0 | 0 | -18.8009 | 4.407 | 95.8039 | -5.8039 | 4.193 | 36.0291 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.1064 | 0
2015-11-17 12:00 | 0 | 0 | 0 | 0 | -18.8112 | 19.4048 | 96.4767 | -6.4767 | 18.4523 | 40.5483 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-11-17 13:00 | 0 | 0 | 0 | 0 | -18.8216 | 34.4027 | 97.943 | -7.943 | 32.6819 | 49.2447 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.2 | -2.2 | 1.1088 | 0
2015-11-17 14:00 | 0 | 0 | 0 | 0 | -18.8319 | 49.4005 | 100.112 | -10.112 | 46.884 | 60.335 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-11-17 15:00 | 0 | 0 | 0 | 0 | -18.8422 | 64.3983 | 102.851 | -12.851 | 61.0948 | 72.7279 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-11-17 16:00 | 0 | 0 | 0 | 0 | -18.8526 | 79.3961 | 105.994 | -15.994 | 75.3865 | 85.8556 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.8 | -3.8 | 1.1152 | 0
2015-11-17 17:00 | 0 | 0 | 0 | 0 | -18.8629 | 94.394 | 109.3492 | -19.3492 | 89.8616 | 99.4211 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1184 | 0
2015-11-17 18:00 | 0 | 0 | 0 | 0 | -18.8732 | 109.3918 | 112.7054 | -22.7054 | 104.6384 | 113.2594 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.2 | -6.2 | 1.1248 | 0
2015-11-17 19:00 | 0 | 0 | 0 | 0 | -18.8835 | 124.3896 | 115.838 | -25.838 | 119.8273 | 127.2721 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.8 | -4.8 | 1.1192 | 0
2015-11-17 20:00 | 0 | 0 | 0 | 0 | -18.8937 | 139.3874 | 118.5187 | -28.5187 | 135.4993 | 141.3944 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.7 | -4.7 | 1.1188 | 0
2015-11-17 21:00 | 0 | 0 | 0 | 0 | -18.904 | 154.3852 | 120.5322 | -30.5322 | 151.651 | 155.5741 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.8 | -4.8 | 1.1192 | 0
2015-11-17 22:00 | 0 | 0 | 0 | 0 | -18.9143 | 169.3829 | 121.7013 | -31.7013 | 168.1786 | 169.7151 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1184 | 0
2015-11-17 23:00 | 0 | 0 | 0 | 0 | -18.9245 | 184.3807 | 121.9158 | -31.9158 | -175.1169 | 175.3958 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1184 | 0
2015-11-18 | 0 | 0 | 0 | 0 | -18.9347 | -160.6215 | 121.1555 | -31.1555 | -158.4847 | 161.4696 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.3 | -5.3 | 1.1212 | 0
2015-11-18 01:00 | 0 | 0 | 0 | 0 | -18.945 | -145.6237 | 119.4948 | -29.4948 | -142.1529 | 147.2885 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.4 | -7.4 | 1.1296 | 0
2015-11-18 02:00 | 0 | 0 | 0 | 0 | -18.9552 | -130.626 | 117.0866 | -27.0866 | -126.2689 | 133.141 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.8 | -7.8 | 1.1312 | 0
2015-11-18 03:00 | 0 | 0 | 0 | 0 | -18.9654 | -115.6282 | 114.1341 | -24.1341 | -110.8774 | 119.0836 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.2 | -6.2 | 1.1248 | 0
2015-11-18 04:00 | 0 | 0 | 0 | 0 | -18.9756 | -100.6304 | 110.8627 | -20.8627 | -95.9352 | 105.1736 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.9 | -5.9 | 1.1236 | 0
2015-11-18 05:00 | 0 | 0 | 0 | 0 | -18.9858 | -85.6327 | 107.5005 | -17.5005 | -81.3449 | 91.4935 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-11-18 06:00 | 0 | 0 | 0 | 0 | -18.996 | -70.635 | 104.2652 | -14.2652 | -66.9888 | 78.1766 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.7 | -4.7 | 1.1188 | 0
2015-11-18 07:00 | 0 | 0 | 0 | 0 | -19.0062 | -55.6372 | 101.3575 | -11.3575 | -52.7562 | 65.4557 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.7 | -3.7 | 1.1148 | 0
2015-11-18 08:00 | 0 | 0 | 0 | 0 | -19.0163 | -40.6395 | 98.9548 | -8.9548 | -38.5613 | 53.7648 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-11-18 09:00 | 0 | 0 | 0 | 0 | -19.0265 | -25.6418 | 97.2042 | -7.2042 | -24.353 | 43.9424 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-11-18 10:00 | 0 | 0 | 0 | 0 | -19.0366 | -10.644 | 96.2146 | -6.2146 | -10.1158 | 37.4932 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-11-18 11:00 | 0 | 0 | 0 | 0 | -19.0467 | 4.3537 | 96.0488 | -6.0488 | 4.138 | 36.2669 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.5 | -4.5 | 1.118 | 0
2015-11-18 12:00 | 0 | 0 | 0 | 0 | -19.0569 | 19.3514 | 96.7178 | -6.7178 | 18.3829 | 40.7381 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.1 | -4.1 | 1.1164 | 0
2015-11-18 13:00 | 0 | 0 | 0 | 0 | -19.067 | 34.3491 | 98.1799 | -8.1799 | 32.5992 | 49.3809 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.1 | -5.1 | 1.1204 | 0
2015-11-18 14:00 | 0 | 0 | 0 | 0 | -19.0771 | 49.3468 | 100.3446 | -10.3446 | 46.7899 | 60.4275 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.2 | -5.2 | 1.1208 | 0
2015-11-18 15:00 | 0 | 0 | 0 | 0 | -19.0872 | 64.3445 | 103.0799 | -13.0799 | 60.9912 | 72.7872 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.8 | -4.8 | 1.1192 | 0
2015-11-18 16:00 | 0 | 0 | 0 | 0 | -19.0972 | 79.3422 | 106.2203 | -16.2203 | 75.276 | 85.8893 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.1 | -5.1 | 1.1204 | 0
2015-11-18 17:00 | 0 | 0 | 0 | 0 | -19.1073 | 94.3399 | 109.5744 | -19.5744 | 89.7471 | 99.4341 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.3 | -5.3 | 1.1212 | 0
2015-11-18 18:00 | 0 | 0 | 0 | 0 | -19.1174 | 109.3375 | 112.9312 | -22.9312 | 104.5231 | 113.255 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.6 | -6.6 | 1.1264 | 0
2015-11-18 19:00 | 0 | 0 | 0 | 0 | -19.1274 | 124.3352 | 116.066 | -26.066 | 119.7152 | 127.2518 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.5 | -5.5 | 1.122 | 0
2015-11-18 20:00 | 0 | 0 | 0 | 0 | -19.1375 | 139.3329 | 118.7503 | -28.7503 | 135.395 | 141.3584 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.2 | -5.2 | 1.1208 | 0
2015-11-18 21:00 | 0 | 0 | 0 | 0 | -19.1475 | 154.3305 | 120.7683 | -30.7683 | 151.5593 | 155.5194 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-11-18 22:00 | 0 | 0 | 0 | 0 | -19.1575 | 169.3282 | 121.9417 | -31.9417 | 168.1038 | 169.6224 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-11-18 23:00 | 0 | 0 | 0 | 0 | -19.1675 | 184.3258 | 122.1598 | -32.1598 | -175.1723 | 175.3359 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.2 | -4.2 | 1.1168 | 0
2015-11-19 | 0 | 0 | 0 | 0 | -19.1775 | -160.6765 | 121.4018 | -31.4018 | -158.5204 | 161.5071 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.5 | -4.5 | 1.118 | 0
2015-11-19 01:00 | 0 | 0 | 0 | 0 | -19.1875 | -145.6789 | 119.7423 | -29.7423 | -142.1713 | 147.3486 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.5 | -4.5 | 1.118 | 0
2015-11-19 02:00 | 0 | 0 | 0 | 0 | -19.1975 | -130.6812 | 117.3344 | -27.3344 | -126.2741 | 133.217 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.7 | -4.7 | 1.1188 | 0
2015-11-19 03:00 | 0 | 0 | 0 | 0 | -19.2075 | -115.6836 | 114.3817 | -24.3817 | -110.8742 | 119.1741 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1184 | 0
2015-11-19 04:00 | 0 | 0 | 0 | 0 | -19.2174 | -100.686 | 111.1101 | -21.1101 | -95.9283 | 105.2793 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1184 | 0
2015-11-19 05:00 | 0 | 0 | 0 | 0 | -19.2274 | -85.6884 | 107.7477 | -17.7477 | -81.3387 | 91.6161 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.2 | -5.2 | 1.1208 | 0
2015-11-19 06:00 | 0 | 0 | 0 | 0 | -19.2373 | -70.6907 | 104.5122 | -14.5122 | -66.9871 | 78.3188 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.2 | -5.2 | 1.1208 | 0
2015-11-19 07:00 | 0 | 0 | 0 | 0 | -19.2472 | -55.6931 | 101.6042 | -11.6042 | -52.7623 | 65.6214 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.4 | -5.4 | 1.1216 | 0
2015-11-19 08:00 | 0 | 0 | 0 | 0 | -19.2572 | -40.6955 | 99.2008 | -9.2008 | -38.578 | 53.9589 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.4 | -5.4 | 1.1216 | 0
2015-11-19 09:00 | 0 | 0 | 0 | 0 | -19.2671 | -25.6979 | 97.4488 | -7.4488 | -24.3823 | 44.1673 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.7 | -5.7 | 1.1228 | 0
2015-11-19 10:00 | 0 | 0 | 0 | 0 | -19.277 | -10.7003 | 96.457 | -6.457 | -10.1591 | 37.7386 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.4 | -6.4 | 1.1256 | 0
2015-11-19 11:00 | 0 | 0 | 0 | 0 | -19.2869 | 4.2972 | 96.288 | -6.288 | 4.0802 | 36.4987 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.8 | -6.8 | 1.1272 | 0
2015-11-19 12:00 | 0 | 0 | 0 | 0 | -19.2967 | 19.2948 | 96.953 | -6.953 | 18.3111 | 40.9222 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.6 | -6.6 | 1.1264 | 0
2015-11-19 13:00 | 0 | 0 | 0 | 0 | -19.3066 | 34.2924 | 98.4107 | -8.4107 | 32.5145 | 49.5117 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.4 | -6.4 | 1.1256 | 0
2015-11-19 14:00 | 0 | 0 | 0 | 0 | -19.3165 | 49.29 | 100.5711 | -10.5711 | 46.6938 | 60.515 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.5 | -6.5 | 1.126 | 0
2015-11-19 15:00 | 0 | 0 | 0 | 0 | -19.3263 | 64.2875 | 103.3026 | -13.3026 | 60.8859 | 72.8418 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.3 | -7.3 | 1.1292 | 0
2015-11-19 16:00 | 0 | 0 | 0 | 0 | -19.3362 | 79.2851 | 106.4403 | -16.4403 | 75.1639 | 85.9185 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.8 | -7.8 | 1.1312 | 0
2015-11-19 17:00 | 0 | 0 | 0 | 0 | -19.346 | 94.2827 | 109.7933 | -19.7933 | 89.6308 | 99.4428 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.7 | -6.7 | 1.1268 | 0
2015-11-19 18:00 | 0 | 0 | 0 | 0 | -19.3558 | 109.2802 | 113.1506 | -23.1506 | 104.4059 | 113.2463 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.1 | -7.1 | 1.1284 | 0
2015-11-19 19:00 | 0 | 0 | 0 | 0 | -19.3656 | 124.2778 | 116.2877 | -26.2877 | 119.6009 | 127.2273 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.3 | -8.3 | 1.1332 | 0
2015-11-19 20:00 | 0 | 0 | 0 | 0 | -19.3754 | 139.2753 | 118.9758 | -28.9758 | 135.2882 | 141.3179 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.7 | -8.7 | 1.1348 | 0
2015-11-19 21:00 | 0 | 0 | 0 | 0 | -19.3852 | 154.2728 | 120.9983 | -30.9983 | 151.4646 | 155.4598 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.1 | -9.1 | 1.1364 | 0
2015-11-19 22:00 | 0 | 0 | 0 | 0 | -19.395 | 169.2704 | 122.1762 | -32.1762 | 168.0256 | 169.5232 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.6 | -9.6 | 1.1384 | 0
2015-11-19 23:00 | 0 | 0 | 0 | 0 | -19.4047 | 184.2679 | 122.398 | -32.398 | -175.2314 | 175.2692 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.4 | -10.4 | 1.1416 | 0
2015-11-20 | 0 | 0 | 0 | 0 | -19.4145 | -160.7346 | 121.6427 | -31.6427 | -158.5602 | 161.5447 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10 | -10 | 1.14 | 0
2015-11-20 01:00 | 0 | 0 | 0 | 0 | -19.4242 | -145.7371 | 119.9846 | -29.9846 | -142.194 | 147.4097 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.7 | -9.7 | 1.1388 | 0
2015-11-20 02:00 | 0 | 0 | 0 | 0 | -19.434 | -130.7396 | 117.5771 | -27.5771 | -126.2837 | 133.2942 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.2 | -11.2 | 1.1448 | 0
2015-11-20 03:00 | 0 | 0 | 0 | 0 | -19.4437 | -115.7421 | 114.6243 | -24.6243 | -110.8753 | 119.266 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.9 | -9.9 | 1.1396 | 0
2015-11-20 04:00 | 0 | 0 | 0 | 0 | -19.4534 | -100.7446 | 111.3525 | -21.3525 | -95.9258 | 105.3862 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9 | -9 | 1.136 | 0
2015-11-20 05:00 | 0 | 0 | 0 | 0 | -19.4631 | -85.7471 | 107.9898 | -17.9898 | -81.3368 | 91.7395 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.8 | -8.8 | 1.1352 | 0
2015-11-20 06:00 | 0 | 0 | 0 | 0 | -19.4728 | -70.7496 | 104.7542 | -14.7542 | -66.9896 | 78.4613 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.6 | -8.6 | 1.1344 | 0
2015-11-20 07:00 | 0 | 0 | 0 | 0 | -19.4825 | -55.7521 | 101.8458 | -11.8458 | -52.7724 | 65.7868 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.5 | -9.5 | 1.138 | 0
2015-11-20 08:00 | 0 | 0 | 0 | 0 | -19.4922 | -40.7546 | 99.4415 | -9.4415 | -38.5984 | 54.1516 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.5 | -10.5 | 1.142 | 0
2015-11-20 09:00 | 0 | 0 | 0 | 0 | -19.5018 | -25.7572 | 97.688 | -7.688 | -24.415 | 44.3893 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.1 | -9.1 | 1.1364 | 0
2015-11-20 10:00 | 0 | 0 | 0 | 0 | -19.5115 | -10.7597 | 96.6937 | -6.6937 | -10.2054 | 37.9793 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.3 | -9.3 | 1.1372 | 0
2015-11-20 11:00 | 0 | 0 | 0 | 0 | -19.5211 | 4.2378 | 96.5213 | -6.5213 | 4.0198 | 36.7246 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8 | -8 | 1.132 | 0
2015-11-20 12:00 | 0 | 0 | 0 | 0 | -19.5308 | 19.2352 | 97.1822 | -7.1822 | 18.2369 | 41.1003 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.5 | -6.5 | 1.126 | 0
2015-11-20 13:00 | 0 | 0 | 0 | 0 | -19.5404 | 34.2327 | 98.6353 | -8.6353 | 32.4276 | 49.6371 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.6 | -6.6 | 1.1264 | 0
2015-11-20 14:00 | 0 | 0 | 0 | 0 | -19.55 | 49.2301 | 100.7912 | -10.7912 | 46.5959 | 60.5975 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.4 | -6.4 | 1.1256 | 0
2015-11-20 15:00 | 0 | 0 | 0 | 0 | -19.5596 | 64.2275 | 103.5189 | -13.5189 | 60.779 | 72.8917 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8 | -8 | 1.132 | 0
2015-11-20 16:00 | 0 | 0 | 0 | 0 | -19.5692 | 79.225 | 106.654 | -16.654 | 75.0501 | 85.9432 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.6 | -6.6 | 1.1264 | 0
2015-11-20 17:00 | 0 | 0 | 0 | 0 | -19.5788 | 94.2224 | 110.0058 | -20.0058 | 89.5129 | 99.4473 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.8 | -6.8 | 1.1272 | 0
2015-11-20 18:00 | 0 | 0 | 0 | 0 | -19.5884 | 109.2198 | 113.3637 | -23.3637 | 104.287 | 113.2333 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.1 | -7.1 | 1.1284 | 0
2015-11-20 19:00 | 0 | 0 | 0 | 0 | -19.5979 | 124.2172 | 116.5031 | -26.5031 | 119.4847 | 127.1985 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.8 | -6.8 | 1.1272 | 0
2015-11-20 20:00 | 0 | 0 | 0 | 0 | -19.6075 | 139.2147 | 119.1949 | -29.1949 | 135.179 | 141.2732 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.9 | -6.9 | 1.1276 | 0
2015-11-20 21:00 | 0 | 0 | 0 | 0 | -19.617 | 154.2121 | 121.222 | -31.222 | 151.3672 | 155.3956 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9 | -9 | 1.136 | 0
2015-11-20 22:00 | 0 | 0 | 0 | 0 | -19.6265 | 169.2095 | 122.4046 | -32.4046 | 167.9441 | 169.418 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.7 | -8.7 | 1.1348 | 0
2015-11-20 23:00 | 0 | 0 | 0 | 0 | -19.6361 | 184.2069 | 122.6305 | -32.6305 | -175.2941 | 175.1965 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.4 | -9.4 | 1.1376 | 0
2015-11-21 | 0 | 0 | 0 | 0 | -19.6456 | -160.7957 | 121.8779 | -31.8779 | -158.604 | 161.5825 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.4 | -9.4 | 1.1376 | 0
2015-11-21 01:00 | 0 | 0 | 0 | 0 | -19.6551 | -145.7984 | 120.2214 | -30.2214 | -142.2209 | 147.472 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.7 | -8.7 | 1.1348 | 0
2015-11-21 02:00 | 0 | 0 | 0 | 0 | -19.6646 | -130.801 | 117.8145 | -27.8145 | -126.2976 | 133.3727 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.7 | -9.7 | 1.1388 | 0
2015-11-21 03:00 | 0 | 0 | 0 | 0 | -19.674 | -115.8036 | 114.8618 | -24.8618 | -110.8808 | 119.3591 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.6 | -8.6 | 1.1344 | 0
2015-11-21 04:00 | 0 | 0 | 0 | 0 | -19.6835 | -100.8062 | 111.5898 | -21.5898 | -95.9275 | 105.4941 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.7 | -8.7 | 1.1348 | 0
2015-11-21 05:00 | 0 | 0 | 0 | 0 | -19.693 | -85.8089 | 108.2269 | -18.2269 | -81.339 | 91.8637 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.2 | -10.2 | 1.1408 | 0
2015-11-21 06:00 | 0 | 0 | 0 | 0 | -19.7024 | -70.8115 | 104.991 | -14.991 | -66.9961 | 78.6042 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.9 | -9.9 | 1.1396 | 0
2015-11-21 07:00 | 0 | 0 | 0 | 0 | -19.7118 | -55.8141 | 102.0821 | -12.0821 | -52.7863 | 65.9518 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.6 | -11.6 | 1.1464 | 0
2015-11-21 08:00 | 0 | 0 | 0 | 0 | -19.7213 | -40.8168 | 99.6768 | -9.6768 | -38.6223 | 54.3428 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.5 | -11.5 | 1.146 | 0
2015-11-21 09:00 | 0 | 0 | 0 | 0 | -19.7307 | -25.8194 | 97.9215 | -7.9215 | -24.4511 | 44.6082 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.9 | -11.9 | 1.1476 | 0
2015-11-21 10:00 | 0 | 0 | 0 | 0 | -19.7401 | -10.8221 | 96.9246 | -6.9246 | -10.2547 | 38.2151 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.5 | -9.5 | 1.138 | 0
2015-11-21 11:00 | 0 | 0 | 0 | 0 | -19.7495 | 4.1752 | 96.7486 | -6.7486 | 3.9567 | 36.9445 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9 | -9 | 1.136 | 0
2015-11-21 12:00 | 0 | 0 | 0 | 0 | -19.7589 | 19.1726 | 97.4052 | -7.4052 | 18.1604 | 41.2725 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.2 | -9.2 | 1.1368 | 0
2015-11-21 13:00 | 0 | 0 | 0 | 0 | -19.7682 | 34.1699 | 98.8537 | -8.8537 | 32.3387 | 49.757 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.6 | -9.6 | 1.1384 | 0
2015-11-21 14:00 | 0 | 0 | 0 | 0 | -19.7776 | 49.1672 | 101.0051 | -11.0051 | 46.4962 | 60.675 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.7 | -9.7 | 1.1388 | 0
2015-11-21 15:00 | 0 | 0 | 0 | 0 | -19.7869 | 64.1645 | 103.7289 | -13.7289 | 60.6704 | 72.9369 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.3 | -10.3 | 1.1412 | 0
2015-11-21 16:00 | 0 | 0 | 0 | 0 | -19.7963 | 79.1618 | 106.8611 | -16.8611 | 74.9349 | 85.9635 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.2 | -9.2 | 1.1368 | 0
2015-11-21 17:00 | 0 | 0 | 0 | 0 | -19.8056 | 94.1591 | 110.2117 | -20.2117 | 89.3935 | 99.4474 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.6 | -9.6 | 1.1384 | 0
2015-11-21 18:00 | 0 | 0 | 0 | 0 | -19.8149 | 109.1564 | 113.5702 | -23.5702 | 104.1664 | 113.2163 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10 | -10 | 1.14 | 0
2015-11-21 19:00 | 0 | 0 | 0 | 0 | -19.8243 | 124.1537 | 116.712 | -26.712 | 119.3665 | 127.1657 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9 | -9 | 1.136 | 0
2015-11-21 20:00 | 0 | 0 | 0 | 0 | -19.8336 | 139.151 | 119.4076 | -29.4076 | 135.0675 | 141.2244 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.6 | -8.6 | 1.1344 | 0
2015-11-21 21:00 | 0 | 0 | 0 | 0 | -19.8428 | 154.1483 | 121.4394 | -31.4394 | 151.267 | 155.327 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.2 | -8.2 | 1.1328 | 0
2015-11-21 22:00 | 0 | 0 | 0 | 0 | -19.8521 | 169.1456 | 122.6269 | -32.6269 | 167.8595 | 169.3074 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.2 | -9.2 | 1.1368 | 0
2015-11-21 23:00 | 0 | 0 | 0 | 0 | -19.8614 | 184.1429 | 122.8569 | -32.8569 | -175.3605 | 175.1189 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.8 | -10.8 | 1.1432 | 0
2015-11-22 | 0 | 0 | 0 | 0 | -19.8706 | -160.8599 | 122.1074 | -32.1074 | -158.6517 | 161.6206 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.6 | -8.6 | 1.1344 | 0
2015-11-22 01:00 | 0 | 0 | 0 | 0 | -19.8799 | -145.8626 | 120.4526 | -30.4526 | -142.252 | 147.5353 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.6 | -7.6 | 1.1304 | 0
2015-11-22 02:00 | 0 | 0 | 0 | 0 | -19.8891 | -130.8653 | 118.0465 | -28.0465 | -126.3157 | 133.4526 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.3 | -7.3 | 1.1292 | 0
2015-11-22 03:00 | 0 | 0 | 0 | 0 | -19.8983 | -115.8681 | 115.094 | -25.094 | -110.8906 | 119.4534 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.5 | -7.5 | 1.13 | 0
2015-11-22 04:00 | 0 | 0 | 0 | 0 | -19.9076 | -100.8708 | 111.8219 | -21.8219 | -95.9336 | 105.6031 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.2 | -6.2 | 1.1248 | 0
2015-11-22 05:00 | 0 | 0 | 0 | 0 | -19.9168 | -85.8736 | 108.4588 | -18.4588 | -81.3455 | 91.9885 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.5 | -5.5 | 1.122 | 0
2015-11-22 06:00 | 0 | 0 | 0 | 0 | -19.926 | -70.8764 | 105.2225 | -15.2225 | -67.0066 | 78.7472 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-11-22 07:00 | 0 | 0 | 0 | 0 | -19.9351 | -55.8791 | 102.3129 | -12.3129 | -52.8041 | 66.1164 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.7 | -4.7 | 1.1188 | 0
2015-11-22 08:00 | 0 | 0 | 0 | 0 | -19.9443 | -40.8819 | 99.9065 | -9.9065 | -38.6499 | 54.5325 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-11-22 09:00 | 0 | 0 | 0 | 0 | -19.9535 | -25.8847 | 98.1493 | -8.1493 | -24.4904 | 44.824 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.2 | -2.2 | 1.1088 | 0
2015-11-22 10:00 | 0 | 0 | 0 | 0 | -19.9626 | -10.8874 | 97.1496 | -7.1496 | -10.307 | 38.4459 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.4 | -2.4 | 1.1096 | 0
2015-11-22 11:00 | 0 | 0 | 0 | 0 | -19.9718 | 4.1098 | 96.9699 | -6.9699 | 3.891 | 37.1583 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-11-22 12:00 | 0 | 0 | 0 | 0 | -19.9809 | 19.107 | 97.622 | -7.622 | 18.0816 | 41.4387 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.8 | -3.8 | 1.1152 | 0
2015-11-22 13:00 | 0 | 0 | 0 | 0 | -19.99 | 34.1042 | 99.0657 | -9.0657 | 32.2479 | 49.8714 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.3 | -4.3 | 1.1172 | 0
2015-11-22 14:00 | 0 | 0 | 0 | 0 | -19.9991 | 49.1014 | 101.2124 | -11.2124 | 46.3948 | 60.7474 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.4 | -5.4 | 1.1216 | 0
2015-11-22 15:00 | 0 | 0 | 0 | 0 | -20.0082 | 64.0986 | 103.9323 | -13.9323 | 60.5603 | 72.9775 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.3 | -6.3 | 1.1252 | 0
2015-11-22 16:00 | 0 | 0 | 0 | 0 | -20.0173 | 79.0958 | 107.0617 | -17.0617 | 74.8182 | 85.9794 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.9 | -6.9 | 1.1276 | 0
2015-11-22 17:00 | 0 | 0 | 0 | 0 | -20.0264 | 94.0929 | 110.4111 | -20.4111 | 89.2726 | 99.4434 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.9 | -6.9 | 1.1276 | 0
2015-11-22 18:00 | 0 | 0 | 0 | 0 | -20.0354 | 109.0901 | 113.7702 | -23.7702 | 104.0441 | 113.1952 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.5 | -7.5 | 1.13 | 0
2015-11-22 19:00 | 0 | 0 | 0 | 0 | -20.0445 | 124.0873 | 116.9143 | -26.9143 | 119.2464 | 127.1289 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.5 | -6.5 | 1.126 | 0
2015-11-22 20:00 | 0 | 0 | 0 | 0 | -20.0535 | 139.0845 | 119.6138 | -29.6138 | 134.9537 | 141.1716 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.5 | -6.5 | 1.126 | 0
2015-11-22 21:00 | 0 | 0 | 0 | 0 | -20.0626 | 154.0816 | 121.6504 | -31.6504 | 151.1641 | 155.2542 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.5 | -6.5 | 1.126 | 0
2015-11-22 22:00 | 0 | 0 | 0 | 0 | -20.0716 | 169.0788 | 122.8429 | -32.8429 | 167.7717 | 169.192 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.1 | -7.1 | 1.1284 | 0
2015-11-22 23:00 | 0 | 0 | 0 | 0 | -20.0806 | 184.0759 | 123.0773 | -33.0773 | -175.4304 | 175.0374 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.9 | -6.9 | 1.1276 | 0
2015-11-23 | 0 | 0 | 0 | 0 | -20.0896 | -160.9269 | 122.331 | -32.331 | -158.7033 | 161.6592 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.9 | -7.9 | 1.1316 | 0
2015-11-23 01:00 | 0 | 0 | 0 | 0 | -20.0986 | -145.9298 | 120.6782 | -30.6782 | -142.2872 | 147.5999 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.4 | -7.4 | 1.1296 | 0
2015-11-23 02:00 | 0 | 0 | 0 | 0 | -20.1076 | -130.9326 | 118.2731 | -28.2731 | -126.3382 | 133.5337 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.8 | -6.8 | 1.1272 | 0
2015-11-23 03:00 | 0 | 0 | 0 | 0 | -20.1165 | -115.9355 | 115.3208 | -25.3208 | -110.9048 | 119.549 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.5 | -6.5 | 1.126 | 0
2015-11-23 04:00 | 0 | 0 | 0 | 0 | -20.1255 | -100.9384 | 112.0486 | -22.0486 | -95.9439 | 105.713 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.2 | -7.2 | 1.1288 | 0
2015-11-23 05:00 | 0 | 0 | 0 | 0 | -20.1344 | -85.9412 | 108.6853 | -18.6853 | -81.3561 | 92.114 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.8 | -7.8 | 1.1312 | 0
2015-11-23 06:00 | 0 | 0 | 0 | 0 | -20.1434 | -70.9441 | 105.4486 | -15.4486 | -67.0212 | 78.8904 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.9 | -7.9 | 1.1316 | 0
2015-11-23 07:00 | 0 | 0 | 0 | 0 | -20.1523 | -55.947 | 102.5383 | -12.5383 | -52.8257 | 66.2803 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.8 | -6.8 | 1.1272 | 0
2015-11-23 08:00 | 0 | 0 | 0 | 0 | -20.1612 | -40.9499 | 100.1305 | -10.1305 | -38.681 | 54.7204 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.8 | -6.8 | 1.1272 | 0
2015-11-23 09:00 | 0 | 0 | 0 | 0 | -20.1701 | -25.9528 | 98.3712 | -8.3712 | -24.5329 | 45.0365 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.3 | -7.3 | 1.1292 | 0
2015-11-23 10:00 | 0 | 0 | 0 | 0 | -20.179 | -10.9557 | 97.3685 | -7.3685 | -10.3622 | 38.6716 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.2 | -7.2 | 1.1288 | 0
2015-11-23 11:00 | 0 | 0 | 0 | 0 | -20.1879 | 4.0414 | 97.185 | -7.185 | 3.8228 | 37.3658 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.7 | -7.7 | 1.1308 | 0
2015-11-23 12:00 | 0 | 0 | 0 | 0 | -20.1968 | 19.0385 | 97.8325 | -7.8325 | 18.0007 | 41.5987 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.9 | -8.9 | 1.1356 | 0
2015-11-23 13:00 | 0 | 0 | 0 | 0 | -20.2056 | 34.0356 | 99.2713 | -9.2713 | 32.1552 | 49.9802 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.3 | -8.3 | 1.1332 | 0
2015-11-23 14:00 | 0 | 0 | 0 | 0 | -20.2145 | 49.0326 | 101.4133 | -11.4133 | 46.2919 | 60.8148 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.7 | -9.7 | 1.1388 | 0
2015-11-23 15:00 | 0 | 0 | 0 | 0 | -20.2233 | 64.0297 | 104.1291 | -14.1291 | 60.4488 | 73.0133 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.3 | -8.3 | 1.1332 | 0
2015-11-23 16:00 | 0 | 0 | 0 | 0 | -20.2321 | 79.0268 | 107.2557 | -17.2557 | 74.7001 | 85.9909 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.9 | -8.9 | 1.1356 | 0
2015-11-23 17:00 | 0 | 0 | 0 | 0 | -20.241 | 94.0238 | 110.6038 | -20.6038 | 89.1504 | 99.4352 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.5 | -8.5 | 1.134 | 0
2015-11-23 18:00 | 0 | 0 | 0 | 0 | -20.2498 | 109.0209 | 113.9634 | -23.9634 | 103.9204 | 113.1701 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.8 | -9.8 | 1.1392 | 0
2015-11-23 19:00 | 0 | 0 | 0 | 0 | -20.2586 | 124.018 | 117.1099 | -27.1099 | 119.1246 | 127.0882 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.9 | -9.9 | 1.1396 | 0
2015-11-23 20:00 | 0 | 0 | 0 | 0 | -20.2673 | 139.015 | 119.8134 | -29.8134 | 134.8378 | 141.115 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9 | -9 | 1.136 | 0
2015-11-23 21:00 | 0 | 0 | 0 | 0 | -20.2761 | 154.0121 | 121.855 | -31.855 | 151.0587 | 155.1775 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.4 | -9.4 | 1.1376 | 0
2015-11-23 22:00 | 0 | 0 | 0 | 0 | -20.2849 | 169.0091 | 123.0526 | -33.0526 | 167.6809 | 169.0724 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.4 | -11.4 | 1.1456 | 0
2015-11-23 23:00 | 0 | 0 | 0 | 0 | -20.2936 | 184.0061 | 123.2915 | -33.2915 | -175.5039 | 174.9528 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.2 | -10.2 | 1.1408 | 0
2015-11-24 | 0 | 0 | 0 | 0 | -20.3024 | -160.9968 | 122.5487 | -32.5487 | -158.7588 | 161.6984 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9 | -9 | 1.136 | 0
2015-11-24 01:00 | 0 | 0 | 0 | 0 | -20.3111 | -145.9998 | 120.8981 | -30.8981 | -142.3265 | 147.6657 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.3 | -9.3 | 1.1372 | 0
2015-11-24 02:00 | 0 | 0 | 0 | 0 | -20.3198 | -131.0028 | 118.4941 | -28.4941 | -126.3649 | 133.6161 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.1 | -8.1 | 1.1324 | 0
2015-11-24 03:00 | 0 | 0 | 0 | 0 | -20.3285 | -116.0058 | 115.5422 | -25.5422 | -110.9233 | 119.6457 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.3 | -6.3 | 1.1252 | 0
2015-11-24 04:00 | 0 | 0 | 0 | 0 | -20.3372 | -101.0088 | 112.27 | -22.27 | -95.9585 | 105.8239 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.7 | -5.7 | 1.1228 | 0
2015-11-24 05:00 | 0 | 0 | 0 | 0 | -20.3459 | -86.0118 | 108.9064 | -18.9064 | -81.3709 | 92.2401 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.4 | -5.4 | 1.1216 | 0
2015-11-24 06:00 | 0 | 0 | 0 | 0 | -20.3546 | -71.0148 | 105.6692 | -15.6692 | -67.0398 | 79.0336 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.3 | -5.3 | 1.1212 | 0
2015-11-24 07:00 | 0 | 0 | 0 | 0 | -20.3632 | -56.0178 | 102.758 | -12.758 | -52.851 | 66.4434 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.9 | -4.9 | 1.1196 | 0
2015-11-24 08:00 | 0 | 0 | 0 | 0 | -20.3719 | -41.0208 | 100.3488 | -10.3488 | -38.7156 | 54.9065 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.8 | -4.8 | 1.1192 | 0
2015-11-24 09:00 | 0 | 0 | 0 | 0 | -20.3805 | -26.0238 | 98.5872 | -8.5872 | -24.5786 | 45.2456 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1184 | 0
2015-11-24 10:00 | 0 | 0 | 0 | 0 | -20.3892 | -11.0268 | 97.5814 | -7.5814 | -10.4202 | 38.892 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-11-24 11:00 | 0 | 0 | 0 | 0 | -20.3978 | 3.9702 | 97.3938 | -7.3938 | 3.7521 | 37.5671 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.7 | -4.7 | 1.1188 | 0
2015-11-24 12:00 | 0 | 0 | 0 | 0 | -20.4064 | 18.9671 | 98.0366 | -8.0366 | 17.9176 | 41.7526 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-11-24 13:00 | 0 | 0 | 0 | 0 | -20.415 | 33.9641 | 99.4704 | -9.4704 | 32.0608 | 50.0834 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.9 | -4.9 | 1.1196 | 0
2015-11-24 14:00 | 0 | 0 | 0 | 0 | -20.4236 | 48.9611 | 101.6076 | -11.6076 | 46.1873 | 60.877 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.2 | -4.2 | 1.1168 | 0
2015-11-24 15:00 | 0 | 0 | 0 | 0 | -20.4322 | 63.958 | 104.3193 | -14.3193 | 60.3359 | 73.0445 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.1 | -4.1 | 1.1164 | 0
2015-11-24 16:00 | 0 | 0 | 0 | 0 | -20.4407 | 78.955 | 107.443 | -17.443 | 74.5808 | 85.998 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.3 | -4.3 | 1.1172 | 0
2015-11-24 17:00 | 0 | 0 | 0 | 0 | -20.4493 | 93.9519 | 110.7898 | -20.7898 | 89.0268 | 99.4229 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.3 | -4.3 | 1.1172 | 0
2015-11-24 18:00 | 0 | 0 | 0 | 0 | -20.4578 | 108.9489 | 114.15 | -24.15 | 103.7953 | 113.1411 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-11-24 19:00 | 0 | 0 | 0 | 0 | -20.4663 | 123.9458 | 117.2988 | -27.2988 | 119.0011 | 127.0438 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-11-24 20:00 | 0 | 0 | 0 | 0 | -20.4749 | 138.9427 | 120.0063 | -30.0063 | 134.72 | 141.0546 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1184 | 0
2015-11-24 21:00 | 0 | 0 | 0 | 0 | -20.4834 | 153.9397 | 122.0529 | -32.0529 | 150.9508 | 155.0971 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1184 | 0
2015-11-24 22:00 | 0 | 0 | 0 | 0 | -20.4919 | 168.9366 | 123.2558 | -33.2558 | 167.5871 | 168.949 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.7 | -4.7 | 1.1188 | 0
2015-11-24 23:00 | 0 | 0 | 0 | 0 | -20.5004 | 183.9335 | 123.4995 | -33.4995 | -175.5808 | 174.8661 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.5 | -4.5 | 1.118 | 0
2015-11-25 | 0 | 0 | 0 | 0 | -20.5088 | -161.0696 | 122.7603 | -32.7603 | -158.8181 | 161.7384 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-11-25 01:00 | 0 | 0 | 0 | 0 | -20.5173 | -146.0727 | 121.1121 | -31.1121 | -142.37 | 147.7327 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1184 | 0
2015-11-25 02:00 | 0 | 0 | 0 | 0 | -20.5258 | -131.0758 | 118.7094 | -28.7094 | -126.3959 | 133.6997 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.3 | -4.3 | 1.1172 | 0
2015-11-25 03:00 | 0 | 0 | 0 | 0 | -20.5342 | -116.0789 | 115.758 | -25.758 | -110.946 | 119.7434 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.5 | -4.5 | 1.118 | 0
2015-11-25 04:00 | 0 | 0 | 0 | 0 | -20.5426 | -101.082 | 112.4859 | -22.4859 | -95.9774 | 105.9355 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.3 | -4.3 | 1.1172 | 0
2015-11-25 05:00 | 0 | 0 | 0 | 0 | -20.551 | -86.0851 | 109.122 | -19.122 | -81.3899 | 92.3665 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.9 | -3.9 | 1.1156 | 0
2015-11-25 06:00 | 0 | 0 | 0 | 0 | -20.5595 | -71.0882 | 105.8842 | -15.8842 | -67.0623 | 79.1767 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-11-25 07:00 | 0 | 0 | 0 | 0 | -20.5679 | -56.0913 | 102.9721 | -12.9721 | -52.8801 | 66.6057 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-11-25 08:00 | 0 | 0 | 0 | 0 | -20.5762 | -41.0944 | 100.5612 | -10.5612 | -38.7537 | 55.0906 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-11-25 09:00 | 0 | 0 | 0 | 0 | -20.5846 | -26.0976 | 98.7972 | -8.7972 | -24.6275 | 45.4511 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-11-25 10:00 | 0 | 0 | 0 | 0 | -20.593 | -11.1007 | 97.788 | -7.788 | -10.481 | 39.1072 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-11-25 11:00 | 0 | 0 | 0 | 0 | -20.6013 | 3.8962 | 97.5962 | -7.5962 | 3.679 | 37.762 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-11-25 12:00 | 0 | 0 | 0 | 0 | -20.6097 | 18.893 | 98.2342 | -8.2342 | 17.8325 | 41.9002 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-11-25 13:00 | 0 | 0 | 0 | 0 | -20.618 | 33.8899 | 99.6629 | -9.6629 | 31.9645 | 50.1809 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-11-25 14:00 | 0 | 0 | 0 | 0 | -20.6263 | 48.8867 | 101.7952 | -11.7952 | 46.0814 | 60.9341 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-11-25 15:00 | 0 | 0 | 0 | 0 | -20.6346 | 63.8836 | 104.5027 | -14.5027 | 60.2218 | 73.0709 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.112 | 0
2015-11-25 16:00 | 0 | 0 | 0 | 0 | -20.6429 | 78.8804 | 107.6235 | -17.6235 | 74.4604 | 86.0008 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.112 | 0
2015-11-25 17:00 | 0 | 0 | 0 | 0 | -20.6512 | 93.8772 | 110.969 | -20.969 | 88.9021 | 99.4064 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-11-25 18:00 | 0 | 0 | 0 | 0 | -20.6595 | 108.8741 | 114.3297 | -24.3297 | 103.6689 | 113.1082 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.1084 | 0
2015-11-25 19:00 | 0 | 0 | 0 | 0 | -20.6678 | 123.8709 | 117.481 | -27.481 | 118.8761 | 126.9957 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-11-25 20:00 | 0 | 0 | 0 | 0 | -20.676 | 138.8677 | 120.1924 | -30.1924 | 134.6001 | 140.9908 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-11-25 21:00 | 0 | 0 | 0 | 0 | -20.6843 | 153.8645 | 122.2441 | -32.2441 | 150.8405 | 155.0132 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-11-25 22:00 | 0 | 0 | 0 | 0 | -20.6925 | 168.8613 | 123.4525 | -33.4525 | 167.4904 | 168.8224 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-11-25 23:00 | 0 | 0 | 0 | 0 | -20.7007 | 183.8581 | 123.7011 | -33.7011 | -175.661 | 174.7779 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.1048 | 0
2015-11-26 | 0 | 0 | 0 | 0 | -20.7089 | -161.1451 | 122.9658 | -32.9658 | -158.8812 | 161.7793 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-11-26 01:00 | 0 | 0 | 0 | 0 | -20.7171 | -146.1483 | 121.3201 | -31.3201 | -142.4175 | 147.801 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.102 | 0
2015-11-26 02:00 | 0 | 0 | 0 | 0 | -20.7253 | -131.1515 | 118.9188 | -28.9188 | -126.4311 | 133.7846 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-11-26 03:00 | 0 | 0 | 0 | 0 | -20.7335 | -116.1547 | 115.9681 | -25.9681 | -110.973 | 119.8423 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.1032 | 0
2015-11-26 04:00 | 0 | 0 | 0 | 0 | -20.7416 | -101.1579 | 112.6961 | -22.6961 | -96.0004 | 106.048 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-11-26 05:00 | 0 | 0 | 0 | 0 | -20.7498 | -86.1611 | 109.332 | -19.332 | -81.4129 | 92.4933 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-11-26 06:00 | 0 | 0 | 0 | 0 | -20.7579 | -71.1643 | 106.0936 | -16.0936 | -67.0888 | 79.3195 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.1032 | 0
2015-11-26 07:00 | 0 | 0 | 0 | 0 | -20.7661 | -56.1676 | 103.1803 | -13.1803 | -52.9129 | 66.7669 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-11-26 08:00 | 0 | 0 | 0 | 0 | -20.7742 | -41.1708 | 100.7676 | -10.7676 | -38.7952 | 55.2725 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-11-26 09:00 | 0 | 0 | 0 | 0 | -20.7823 | -26.1741 | 99.0011 | -9.0011 | -24.6795 | 45.6529 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.1032 | 0
2015-11-26 10:00 | 0 | 0 | 0 | 0 | -20.7904 | -11.1773 | 97.9883 | -7.9883 | -10.5445 | 39.3169 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.102 | 0
2015-11-26 11:00 | 0 | 0 | 0 | 0 | -20.7985 | 3.8195 | 97.7922 | -7.7922 | 3.6035 | 37.9505 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-11-26 12:00 | 0 | 0 | 0 | 0 | -20.8065 | 18.8162 | 98.4252 | -8.4252 | 17.7454 | 42.0415 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.1032 | 0
2015-11-26 13:00 | 0 | 0 | 0 | 0 | -20.8146 | 33.8129 | 99.8487 | -9.8487 | 31.8667 | 50.2727 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-11-26 14:00 | 0 | 0 | 0 | 0 | -20.8226 | 48.8097 | 101.976 | -11.976 | 45.974 | 60.986 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-11-26 15:00 | 0 | 0 | 0 | 0 | -20.8307 | 63.8064 | 104.6793 | -14.6793 | 60.1065 | 73.0926 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-11-26 16:00 | 0 | 0 | 0 | 0 | -20.8387 | 78.8031 | 107.7971 | -17.7971 | 74.3389 | 85.9992 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-11-26 17:00 | 0 | 0 | 0 | 0 | -20.8467 | 93.7999 | 111.1413 | -21.1413 | 88.7764 | 99.386 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-11-26 18:00 | 0 | 0 | 0 | 0 | -20.8547 | 108.7966 | 114.5024 | -24.5024 | 103.5412 | 113.0716 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-11-26 19:00 | 0 | 0 | 0 | 0 | -20.8627 | 123.7933 | 117.6562 | -27.6562 | 118.7496 | 126.944 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.1048 | 0
2015-11-26 20:00 | 0 | 0 | 0 | 0 | -20.8707 | 138.79 | 120.3717 | -30.3717 | 134.4785 | 140.9236 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-11-26 21:00 | 0 | 0 | 0 | 0 | -20.8787 | 153.7867 | 122.4286 | -32.4286 | 150.7279 | 154.926 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.1056 | 0
2015-11-26 22:00 | 0 | 0 | 0 | 0 | -20.8866 | 168.7834 | 123.6425 | -33.6425 | 167.3908 | 168.6932 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-11-26 23:00 | 0 | 0 | 0 | 0 | -20.8946 | 183.7801 | 123.8963 | -33.8963 | -175.7446 | 174.689 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-11-27 | 0 | 0 | 0 | 0 | -20.9025 | -161.2232 | 123.165 | -33.165 | -158.948 | 161.8212 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.4 | -2.4 | 1.1096 | 0
2015-11-27 01:00 | 0 | 0 | 0 | 0 | -20.9104 | -146.2265 | 121.5221 | -31.5221 | -142.4689 | 147.8707 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-11-27 02:00 | 0 | 0 | 0 | 0 | -20.9183 | -131.2298 | 119.1224 | -29.1224 | -126.4704 | 133.8708 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-11-27 03:00 | 0 | 0 | 0 | 0 | -20.9262 | -116.2332 | 116.1725 | -26.1725 | -111.0042 | 119.9422 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.112 | 0
2015-11-27 04:00 | 0 | 0 | 0 | 0 | -20.9341 | -101.2365 | 112.9006 | -22.9006 | -96.0277 | 106.1611 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-11-27 05:00 | 0 | 0 | 0 | 0 | -20.942 | -86.2398 | 109.5362 | -19.5362 | -81.44 | 92.6204 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.11 | 0
2015-11-27 06:00 | 0 | 0 | 0 | 0 | -20.9499 | -71.2432 | 106.2971 | -16.2971 | -67.1191 | 79.4621 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-11-27 07:00 | 0 | 0 | 0 | 0 | -20.9577 | -56.2465 | 103.3826 | -13.3826 | -52.9493 | 66.927 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-11-27 08:00 | 0 | 0 | 0 | 0 | -20.9656 | -41.2498 | 100.968 | -10.968 | -38.84 | 55.4521 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-11-27 09:00 | 0 | 0 | 0 | 0 | -20.9734 | -26.2532 | 99.1987 | -9.1987 | -24.7344 | 45.8508 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-11-27 10:00 | 0 | 0 | 0 | 0 | -20.9812 | -11.2566 | 98.1823 | -8.1823 | -10.6107 | 39.5211 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-11-27 11:00 | 0 | 0 | 0 | 0 | -20.989 | 3.7401 | 97.9817 | -7.9817 | 3.5258 | 38.1325 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.102 | 0
2015-11-27 12:00 | 0 | 0 | 0 | 0 | -20.9968 | 18.7367 | 98.6096 | -8.6096 | 17.6565 | 42.1765 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.1048 | 0
2015-11-27 13:00 | 0 | 0 | 0 | 0 | -21.0046 | 33.7334 | 100.0277 | -10.0277 | 31.7673 | 50.3587 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.1064 | 0
2015-11-27 14:00 | 0 | 0 | 0 | 0 | -21.0124 | 48.73 | 102.15 | -12.15 | 45.8654 | 61.0328 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-11-27 15:00 | 0 | 0 | 0 | 0 | -21.0202 | 63.7266 | 104.849 | -14.849 | 59.9902 | 73.1097 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.1084 | 0
2015-11-27 16:00 | 0 | 0 | 0 | 0 | -21.0279 | 78.7232 | 107.9638 | -17.9638 | 74.2164 | 85.9934 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-11-27 17:00 | 0 | 0 | 0 | 0 | -21.0357 | 93.7198 | 111.3066 | -21.3066 | 88.6497 | 99.3616 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.2 | -2.2 | 1.1088 | 0
2015-11-27 18:00 | 0 | 0 | 0 | 0 | -21.0434 | 108.7165 | 114.6683 | -24.6683 | 103.4125 | 113.0313 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.7 | -3.7 | 1.1148 | 0
2015-11-27 19:00 | 0 | 0 | 0 | 0 | -21.0511 | 123.7131 | 117.8244 | -27.8244 | 118.6217 | 126.8889 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-11-27 20:00 | 0 | 0 | 0 | 0 | -21.0588 | 138.7097 | 120.5441 | -30.5441 | 134.3551 | 140.8531 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-11-27 21:00 | 0 | 0 | 0 | 0 | -21.0665 | 153.7063 | 122.6063 | -32.6063 | 150.6131 | 154.8359 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-11-27 22:00 | 0 | 0 | 0 | 0 | -21.0742 | 168.7029 | 123.8259 | -33.8259 | 167.2886 | 168.5616 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.11 | 0
2015-11-27 23:00 | 0 | 0 | 0 | 0 | -21.0819 | 183.6994 | 124.0849 | -34.0849 | -175.8314 | 174.6001 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.11 | 0
2015-11-28 | 0 | 0 | 0 | 0 | -21.0895 | -161.304 | 123.3579 | -33.3579 | -159.0184 | 161.8643 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.3 | -3.3 | 1.1132 | 0
2015-11-28 01:00 | 0 | 0 | 0 | 0 | -21.0972 | -146.3074 | 121.7179 | -31.7179 | -142.5244 | 147.9417 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.3 | -3.3 | 1.1132 | 0
2015-11-28 02:00 | 0 | 0 | 0 | 0 | -21.1048 | -131.3108 | 119.32 | -29.32 | -126.5139 | 133.9582 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.8 | -2.8 | 1.1112 | 0
2015-11-28 03:00 | 0 | 0 | 0 | 0 | -21.1124 | -116.3143 | 116.3709 | -26.3709 | -111.0396 | 120.043 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-11-28 04:00 | 0 | 0 | 0 | 0 | -21.1201 | -101.3177 | 113.0993 | -23.0993 | -96.0591 | 106.2749 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.8 | -2.8 | 1.1112 | 0
2015-11-28 05:00 | 0 | 0 | 0 | 0 | -21.1277 | -86.3211 | 109.7346 | -19.7346 | -81.4712 | 92.7477 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.112 | 0
2015-11-28 06:00 | 0 | 0 | 0 | 0 | -21.1352 | -71.3246 | 106.4947 | -16.4947 | -67.1533 | 79.6042 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-11-28 07:00 | 0 | 0 | 0 | 0 | -21.1428 | -56.328 | 103.5789 | -13.5789 | -52.9894 | 67.0858 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-11-28 08:00 | 0 | 0 | 0 | 0 | -21.1504 | -41.3315 | 101.1622 | -11.1622 | -38.8882 | 55.6293 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.8 | -3.8 | 1.1152 | 0
2015-11-28 09:00 | 0 | 0 | 0 | 0 | -21.158 | -26.3349 | 99.39 | -9.39 | -24.7924 | 46.0449 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.1 | -4.1 | 1.1164 | 0
2015-11-28 10:00 | 0 | 0 | 0 | 0 | -21.1655 | -11.3384 | 98.3698 | -8.3698 | -10.6794 | 39.7196 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.7 | -3.7 | 1.1148 | 0
2015-11-28 11:00 | 0 | 0 | 0 | 0 | -21.173 | 3.6582 | 98.1645 | -8.1645 | 3.4459 | 38.308 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.9 | -3.9 | 1.1156 | 0
2015-11-28 12:00 | 0 | 0 | 0 | 0 | -21.1806 | 18.6547 | 98.7872 | -8.7872 | 17.5656 | 42.3051 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1144 | 0
2015-11-28 13:00 | 0 | 0 | 0 | 0 | -21.1881 | 33.6512 | 100.1999 | -10.1999 | 31.6664 | 50.4389 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-11-28 14:00 | 0 | 0 | 0 | 0 | -21.1956 | 48.6477 | 102.317 | -12.317 | 45.7556 | 61.0743 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4 | -4 | 1.116 | 0
2015-11-28 15:00 | 0 | 0 | 0 | 0 | -21.203 | 63.6443 | 105.0118 | -15.0118 | 59.8728 | 73.1221 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.9 | -3.9 | 1.1156 | 0
2015-11-28 16:00 | 0 | 0 | 0 | 0 | -21.2105 | 78.6408 | 108.1235 | -18.1235 | 74.0931 | 85.9833 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.7 | -3.7 | 1.1148 | 0
2015-11-28 17:00 | 0 | 0 | 0 | 0 | -21.218 | 93.6373 | 111.4649 | -21.4649 | 88.5221 | 99.3333 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-11-28 18:00 | 0 | 0 | 0 | 0 | -21.2254 | 108.6338 | 114.8271 | -24.8271 | 103.2829 | 112.9873 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1144 | 0
2015-11-28 19:00 | 0 | 0 | 0 | 0 | -21.2329 | 123.6303 | 117.9856 | -27.9856 | 118.4927 | 126.8305 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-11-28 20:00 | 0 | 0 | 0 | 0 | -21.2403 | 138.6268 | 120.7094 | -30.7094 | 134.2301 | 140.7796 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-11-28 21:00 | 0 | 0 | 0 | 0 | -21.2477 | 153.6233 | 122.777 | -32.777 | 150.4962 | 154.7429 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.8 | -3.8 | 1.1152 | 0
2015-11-28 22:00 | 0 | 0 | 0 | 0 | -21.2551 | 168.6198 | 124.0024 | -34.0024 | 167.1837 | 168.4283 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.9 | -3.9 | 1.1156 | 0
2015-11-28 23:00 | 0 | 0 | 0 | 0 | -21.2625 | 183.6162 | 124.2668 | -34.2668 | -175.9214 | 174.5117 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4 | -4 | 1.116 | 0
2015-11-29 | 0 | 0 | 0 | 0 | -21.2699 | -161.3873 | 123.5443 | -33.5443 | -159.0925 | 161.9086 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.9 | -3.9 | 1.1156 | 0
2015-11-29 01:00 | 0 | 0 | 0 | 0 | -21.2773 | -146.3908 | 121.9075 | -31.9075 | -142.5837 | 148.0141 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.8 | -3.8 | 1.1152 | 0
2015-11-29 02:00 | 0 | 0 | 0 | 0 | -21.2846 | -131.3943 | 119.5116 | -29.5116 | -126.5614 | 134.0468 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.2 | -4.2 | 1.1168 | 0
2015-11-29 03:00 | 0 | 0 | 0 | 0 | -21.292 | -116.3979 | 116.5634 | -26.5634 | -111.0792 | 120.1448 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.7 | -3.7 | 1.1148 | 0
2015-11-29 04:00 | 0 | 0 | 0 | 0 | -21.2993 | -101.4014 | 113.2921 | -23.2921 | -96.0946 | 106.3892 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-11-29 05:00 | 0 | 0 | 0 | 0 | -21.3066 | -86.4049 | 109.9271 | -19.9271 | -81.5063 | 92.875 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-11-29 06:00 | 0 | 0 | 0 | 0 | -21.3139 | -71.4085 | 106.6864 | -16.6864 | -67.1913 | 79.7457 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-11-29 07:00 | 0 | 0 | 0 | 0 | -21.3212 | -56.412 | 103.769 | -13.769 | -53.033 | 67.2433 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-11-29 08:00 | 0 | 0 | 0 | 0 | -21.3285 | -41.4156 | 101.3502 | -11.3502 | -38.9396 | 55.804 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-11-29 09:00 | 0 | 0 | 0 | 0 | -21.3358 | -26.4191 | 99.5749 | -9.5749 | -24.8533 | 46.2348 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-11-29 10:00 | 0 | 0 | 0 | 0 | -21.3431 | -11.4227 | 98.5507 | -8.5507 | -10.7507 | 39.9125 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-11-29 11:00 | 0 | 0 | 0 | 0 | -21.3503 | 3.5737 | 98.3406 | -8.3406 | 3.3638 | 38.4768 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-11-29 12:00 | 0 | 0 | 0 | 0 | -21.3576 | 18.5702 | 98.958 | -8.958 | 17.4731 | 42.4272 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.112 | 0
2015-11-29 13:00 | 0 | 0 | 0 | 0 | -21.3648 | 33.5666 | 100.3652 | -10.3652 | 31.5641 | 50.5133 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-11-29 14:00 | 0 | 0 | 0 | 0 | -21.372 | 48.563 | 102.4771 | -12.4771 | 45.6447 | 61.1107 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.1084 | 0
2015-11-29 15:00 | 0 | 0 | 0 | 0 | -21.3792 | 63.5594 | 105.1675 | -15.1675 | 59.7546 | 73.1298 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-11-29 16:00 | 0 | 0 | 0 | 0 | -21.3864 | 78.5558 | 108.2762 | -18.2762 | 73.9689 | 85.9689 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-11-29 17:00 | 0 | 0 | 0 | 0 | -21.3936 | 93.5522 | 111.6161 | -21.6161 | 88.3937 | 99.3012 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-11-29 18:00 | 0 | 0 | 0 | 0 | -21.4007 | 108.5486 | 114.9787 | -24.9787 | 103.1523 | 112.9399 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.2 | -2.2 | 1.1088 | 0
2015-11-29 19:00 | 0 | 0 | 0 | 0 | -21.4079 | 123.545 | 118.1397 | -28.1397 | 118.3625 | 126.7689 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-11-29 20:00 | 0 | 0 | 0 | 0 | -21.4151 | 138.5414 | 120.8677 | -30.8677 | 134.1037 | 140.7031 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.1048 | 0
2015-11-29 21:00 | 0 | 0 | 0 | 0 | -21.4222 | 153.5378 | 122.9407 | -32.9407 | 150.3773 | 154.6474 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.1032 | 0
2015-11-29 22:00 | 0 | 0 | 0 | 0 | -21.4293 | 168.5342 | 124.172 | -34.172 | 167.0763 | 168.2936 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-11-29 23:00 | 0 | 0 | 0 | 0 | -21.4364 | 183.5306 | 124.4421 | -34.4421 | -176.0144 | 174.4244 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.1032 | 0
2015-11-30 | 0 | 0 | 0 | 0 | -21.4435 | -161.473 | 123.7241 | -33.7241 | -159.1701 | 161.9544 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-11-30 01:00 | 0 | 0 | 0 | 0 | -21.4506 | -146.4767 | 122.0907 | -32.0907 | -142.6469 | 148.0879 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-11-30 02:00 | 0 | 0 | 0 | 0 | -21.4577 | -131.4803 | 119.6969 | -29.6969 | -126.613 | 134.1366 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-11-30 03:00 | 0 | 0 | 0 | 0 | -21.4647 | -116.4839 | 116.7498 | -26.7498 | -111.1229 | 120.2475 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-11-30 04:00 | 0 | 0 | 0 | 0 | -21.4718 | -101.4876 | 113.4788 | -23.4788 | -96.1341 | 106.5041 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-11-30 05:00 | 0 | 0 | 0 | 0 | -21.4788 | -86.4912 | 110.1135 | -20.1135 | -81.5454 | 93.0024 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-11-30 06:00 | 0 | 0 | 0 | 0 | -21.4859 | -71.4948 | 106.8719 | -16.8719 | -67.233 | 79.8867 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-11-30 07:00 | 0 | 0 | 0 | 0 | -21.4929 | -56.4985 | 103.953 | -13.953 | -53.0801 | 67.3993 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-11-30 08:00 | 0 | 0 | 0 | 0 | -21.4999 | -41.5021 | 101.5319 | -11.5319 | -38.9942 | 55.976 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.1032 | 0
2015-11-30 09:00 | 0 | 0 | 0 | 0 | -21.5069 | -26.5058 | 99.7533 | -9.7533 | -24.917 | 46.4206 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-11-30 10:00 | 0 | 0 | 0 | 0 | -21.5139 | -11.5095 | 98.725 | -8.725 | -10.8245 | 40.0995 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-11-30 11:00 | 0 | 0 | 0 | 0 | -21.5208 | 3.4869 | 98.51 | -8.51 | 3.2797 | 38.6389 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.1032 | 0
2015-11-30 12:00 | 0 | 0 | 0 | 0 | -21.5278 | 18.4832 | 99.1219 | -9.1219 | 17.3788 | 42.5428 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-11-30 13:00 | 0 | 0 | 0 | 0 | -21.5347 | 33.4795 | 100.5235 | -10.5235 | 31.4605 | 50.5818 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-11-30 14:00 | 0 | 0 | 0 | 0 | -21.5417 | 48.4758 | 102.6302 | -12.6302 | 45.5328 | 61.1418 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-11-30 15:00 | 0 | 0 | 0 | 0 | -21.5486 | 63.4722 | 105.3161 | -15.3161 | 59.6356 | 73.1328 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-11-30 16:00 | 0 | 0 | 0 | 0 | -21.5555 | 78.4685 | 108.4217 | -18.4217 | 73.8442 | 85.9504 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-11-30 17:00 | 0 | 0 | 0 | 0 | -21.5624 | 93.4648 | 111.7601 | -21.7601 | 88.2648 | 99.2653 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-11-30 18:00 | 0 | 0 | 0 | 0 | -21.5693 | 108.4611 | 115.1233 | -25.1233 | 103.021 | 112.889 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.1032 | 0
2015-11-30 19:00 | 0 | 0 | 0 | 0 | -21.5761 | 123.4574 | 118.2867 | -28.2867 | 118.2314 | 126.7041 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-11-30 20:00 | 0 | 0 | 0 | 0 | -21.583 | 138.4537 | 121.0189 | -31.0189 | 133.9758 | 140.6238 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-11-30 21:00 | 0 | 0 | 0 | 0 | -21.5898 | 153.45 | 123.0973 | -33.0973 | 150.2565 | 154.5496 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-11-30 22:00 | 0 | 0 | 0 | 0 | -21.5967 | 168.4463 | 124.3347 | -34.3347 | 166.9664 | 168.1578 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-11-30 23:00 | 0 | 0 | 0 | 0 | -21.6035 | 183.4426 | 124.6105 | -34.6105 | -176.1104 | 174.3387 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-12-01 | 0 | 0 | 0 | 0 | -21.6103 | -161.5612 | 123.8974 | -33.8974 | -159.2511 | 162.0016 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.0948 | 0
2015-12-01 01:00 | 0 | 0 | 0 | 0 | -21.6171 | -146.5649 | 122.2675 | -32.2675 | -142.7139 | 148.1632 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.9 | 1.9 | 1.0924 | 0
2015-12-01 02:00 | 0 | 0 | 0 | 0 | -21.6239 | -131.5686 | 119.8759 | -29.8759 | -126.6686 | 134.2276 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-12-01 03:00 | 0 | 0 | 0 | 0 | -21.6307 | -116.5723 | 116.9301 | -26.9301 | -111.1706 | 120.3511 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0912 | 0
2015-12-01 04:00 | 0 | 0 | 0 | 0 | -21.6374 | -101.5761 | 113.6594 | -23.6594 | -96.1777 | 106.6193 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0928 | 0
2015-12-01 05:00 | 0 | 0 | 0 | 0 | -21.6442 | -86.5798 | 110.2938 | -20.2938 | -81.5884 | 93.1296 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0916 | 0
2015-12-01 06:00 | 0 | 0 | 0 | 0 | -21.6509 | -71.5836 | 107.0513 | -17.0513 | -67.2785 | 80.0268 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0916 | 0
2015-12-01 07:00 | 0 | 0 | 0 | 0 | -21.6577 | -56.5873 | 104.1307 | -14.1307 | -53.1307 | 67.5536 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0916 | 0
2015-12-01 08:00 | 0 | 0 | 0 | 0 | -21.6644 | -41.591 | 101.7071 | -11.7071 | -39.052 | 56.1453 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.09 | 0
2015-12-01 09:00 | 0 | 0 | 0 | 0 | -21.6711 | -26.5948 | 99.9251 | -9.9251 | -24.9835 | 46.602 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0888 | 0
2015-12-01 10:00 | 0 | 0 | 0 | 0 | -21.6778 | -11.5986 | 98.8925 | -8.8925 | -10.9007 | 40.2807 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-12-01 11:00 | 0 | 0 | 0 | 0 | -21.6845 | 3.3977 | 98.6725 | -8.6725 | 3.1935 | 38.7942 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.0948 | 0
2015-12-01 12:00 | 0 | 0 | 0 | 0 | -21.6911 | 18.3939 | 99.2788 | -9.2788 | 17.283 | 42.6518 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-12-01 13:00 | 0 | 0 | 0 | 0 | -21.6978 | 33.3901 | 100.6747 | -10.6747 | 31.3557 | 50.6445 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-12-01 14:00 | 0 | 0 | 0 | 0 | -21.7044 | 48.3864 | 102.7761 | -12.7761 | 45.4199 | 61.1677 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-12-01 15:00 | 0 | 0 | 0 | 0 | -21.7111 | 63.3826 | 105.4576 | -15.4576 | 59.5158 | 73.1312 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0932 | 0
2015-12-01 16:00 | 0 | 0 | 0 | 0 | -21.7177 | 78.3788 | 108.56 | -18.56 | 73.7189 | 85.9277 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0968 | 0
2015-12-01 17:00 | 0 | 0 | 0 | 0 | -21.7243 | 93.375 | 111.897 | -21.897 | 88.1353 | 99.2256 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-12-01 18:00 | 0 | 0 | 0 | 0 | -21.7309 | 108.3712 | 115.2606 | -25.2606 | 102.8891 | 112.8348 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-12-01 19:00 | 0 | 0 | 0 | 0 | -21.7375 | 123.3674 | 118.4264 | -28.4264 | 118.0994 | 126.6363 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-12-01 20:00 | 0 | 0 | 0 | 0 | -21.744 | 138.3636 | 121.1628 | -31.1628 | 133.8467 | 140.542 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.096 | 0
2015-12-01 21:00 | 0 | 0 | 0 | 0 | -21.7506 | 153.3598 | 123.2468 | -33.2468 | 150.134 | 154.4496 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-12-01 22:00 | 0 | 0 | 0 | 0 | -21.7572 | 168.356 | 124.4903 | -34.4903 | 166.8543 | 168.0214 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0972 | 0
2015-12-01 23:00 | 0 | 0 | 0 | 0 | -21.7637 | 183.3522 | 124.772 | -34.772 | -176.2093 | 174.255 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0932 | 0
2015-12-02 | 0 | 0 | 0 | 0 | -21.7702 | -161.6516 | 124.0639 | -34.0639 | -159.3355 | 162.0505 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0932 | 0
2015-12-02 01:00 | 0 | 0 | 0 | 0 | -21.7767 | -146.6554 | 122.4377 | -32.4377 | -142.7847 | 148.2399 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-12-02 02:00 | 0 | 0 | 0 | 0 | -21.7832 | -131.6592 | 120.0486 | -30.0486 | -126.7282 | 134.3197 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0932 | 0
2015-12-02 03:00 | 0 | 0 | 0 | 0 | -21.7897 | -116.663 | 117.104 | -27.104 | -111.2223 | 120.4554 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.4 | 1.4 | 1.0944 | 0
2015-12-02 04:00 | 0 | 0 | 0 | 0 | -21.7962 | -101.6669 | 113.8338 | -23.8338 | -96.2253 | 106.7349 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-12-02 05:00 | 0 | 0 | 0 | 0 | -21.8026 | -86.6707 | 110.4679 | -20.4679 | -81.6352 | 93.2567 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2 | 2 | 1.092 | 0
2015-12-02 06:00 | 0 | 0 | 0 | 0 | -21.8091 | -71.6745 | 107.2243 | -17.2243 | -67.3276 | 80.1662 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.0948 | 0
2015-12-02 07:00 | 0 | 0 | 0 | 0 | -21.8155 | -56.6784 | 104.302 | -14.302 | -53.1846 | 67.7062 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-12-02 08:00 | 0 | 0 | 0 | 0 | -21.822 | -41.6822 | 101.8757 | -11.8757 | -39.1128 | 56.3116 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.0948 | 0
2015-12-02 09:00 | 0 | 0 | 0 | 0 | -21.8284 | -26.6861 | 100.0903 | -10.0903 | -25.0527 | 46.779 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-12-02 10:00 | 0 | 0 | 0 | 0 | -21.8348 | -11.6899 | 99.0533 | -9.0533 | -10.9792 | 40.4558 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0936 | 0
2015-12-02 11:00 | 0 | 0 | 0 | 0 | -21.8412 | 3.3062 | 98.828 | -8.828 | 3.1055 | 38.9427 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0936 | 0
2015-12-02 12:00 | 0 | 0 | 0 | 0 | -21.8475 | 18.3024 | 99.4287 | -9.4287 | 17.1856 | 42.7543 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-12-02 13:00 | 0 | 0 | 0 | 0 | -21.8539 | 33.2985 | 100.8189 | -10.8189 | 31.2497 | 50.7011 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0968 | 0
2015-12-02 14:00 | 0 | 0 | 0 | 0 | -21.8603 | 48.2946 | 102.9149 | -12.9149 | 45.3062 | 61.1884 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-12-02 15:00 | 0 | 0 | 0 | 0 | -21.8666 | 63.2908 | 105.5919 | -15.5919 | 59.3955 | 73.125 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-12-02 16:00 | 0 | 0 | 0 | 0 | -21.8729 | 78.2869 | 108.6911 | -18.6911 | 73.5931 | 85.9009 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-12-02 17:00 | 0 | 0 | 0 | 0 | -21.8793 | 93.283 | 112.0266 | -22.0266 | 88.0054 | 99.1823 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-12-02 18:00 | 0 | 0 | 0 | 0 | -21.8856 | 108.2791 | 115.3906 | -25.3906 | 102.7567 | 112.7773 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-12-02 19:00 | 0 | 0 | 0 | 0 | -21.8918 | 123.2753 | 118.5589 | -28.5589 | 117.9666 | 126.5657 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-12-02 20:00 | 0 | 0 | 0 | 0 | -21.8981 | 138.2714 | 121.2995 | -31.2995 | 133.7165 | 140.4576 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-12-02 21:00 | 0 | 0 | 0 | 0 | -21.9044 | 153.2675 | 123.3891 | -33.3891 | 150.0098 | 154.3477 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-12-02 22:00 | 0 | 0 | 0 | 0 | -21.9107 | 168.2636 | 124.6388 | -34.6388 | 166.7398 | 167.8848 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.0948 | 0
2015-12-02 23:00 | 0 | 0 | 0 | 0 | -21.9169 | 183.2597 | 124.9266 | -34.9266 | -176.311 | 174.1738 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.8 | 0.8 | 1.0968 | 0
2015-12-03 | 0 | 0 | 0 | 0 | -21.9231 | -161.7442 | 124.2236 | -34.2236 | -159.4232 | 162.1011 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-12-03 01:00 | 0 | 0 | 0 | 0 | -21.9293 | -146.7481 | 122.6013 | -32.6013 | -142.859 | 148.3181 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-12-03 02:00 | 0 | 0 | 0 | 0 | -21.9356 | -131.752 | 120.2147 | -30.2147 | -126.7916 | 134.413 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-12-03 03:00 | 0 | 0 | 0 | 0 | -21.9417 | -116.756 | 117.2717 | -27.2717 | -111.278 | 120.5604 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-12-03 04:00 | 0 | 0 | 0 | 0 | -21.9479 | -101.7599 | 114.0019 | -24.0019 | -96.2768 | 106.8508 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.096 | 0
2015-12-03 05:00 | 0 | 0 | 0 | 0 | -21.9541 | -86.7638 | 110.6357 | -20.6357 | -81.6859 | 93.3835 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0972 | 0
2015-12-03 06:00 | 0 | 0 | 0 | 0 | -21.9603 | -71.7677 | 107.391 | -17.391 | -67.3804 | 80.3045 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-12-03 07:00 | 0 | 0 | 0 | 0 | -21.9664 | -56.7717 | 104.4668 | -14.4668 | -53.242 | 67.857 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-12-03 08:00 | 0 | 0 | 0 | 0 | -21.9725 | -41.7756 | 102.0378 | -12.0378 | -39.1767 | 56.4749 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-12-03 09:00 | 0 | 0 | 0 | 0 | -21.9787 | -26.7795 | 100.2487 | -10.2487 | -25.1246 | 46.9515 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-12-03 10:00 | 0 | 0 | 0 | 0 | -21.9848 | -11.7835 | 99.2071 | -9.2071 | -11.0599 | 40.6249 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.3 | 0.3 | 1.0988 | 0
2015-12-03 11:00 | 0 | 0 | 0 | 0 | -21.9909 | 3.2126 | 98.9766 | -8.9766 | 3.0156 | 39.0844 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.5 | 0.5 | 1.098 | 0
2015-12-03 12:00 | 0 | 0 | 0 | 0 | -21.9969 | 18.2086 | 99.5715 | -9.5715 | 17.0869 | 42.85 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-12-03 13:00 | 0 | 0 | 0 | 0 | -22.003 | 33.2047 | 100.9558 | -10.9558 | 31.1427 | 50.7519 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.102 | 0
2015-12-03 14:00 | 0 | 0 | 0 | 0 | -22.0091 | 48.2007 | 103.0464 | -13.0464 | 45.1918 | 61.2039 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-12-03 15:00 | 0 | 0 | 0 | 0 | -22.0151 | 63.1968 | 105.7189 | -15.7189 | 59.2748 | 73.1142 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-12-03 16:00 | 0 | 0 | 0 | 0 | -22.0212 | 78.1928 | 108.8149 | -18.8149 | 73.467 | 85.8701 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-12-03 17:00 | 0 | 0 | 0 | 0 | -22.0272 | 93.1889 | 112.1489 | -22.1489 | 87.8751 | 99.1353 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-12-03 18:00 | 0 | 0 | 0 | 0 | -22.0332 | 108.1849 | 115.5133 | -25.5133 | 102.6239 | 112.7166 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-12-03 19:00 | 0 | 0 | 0 | 0 | -22.0392 | 123.1809 | 118.6839 | -28.6839 | 117.8332 | 126.4922 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-12-03 20:00 | 0 | 0 | 0 | 0 | -22.0452 | 138.1769 | 121.4288 | -31.4288 | 133.5852 | 140.3709 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-12-03 21:00 | 0 | 0 | 0 | 0 | -22.0511 | 153.173 | 123.5241 | -33.5241 | 149.8842 | 154.244 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.1056 | 0
2015-12-03 22:00 | 0 | 0 | 0 | 0 | -22.0571 | 168.169 | 124.7801 | -34.7801 | 166.6233 | 167.7481 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-12-03 23:00 | 0 | 0 | 0 | 0 | -22.0631 | 183.165 | 125.0741 | -35.0741 | -176.4154 | 174.0954 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-12-04 | 0 | 0 | 0 | 0 | -22.069 | -161.839 | 124.3764 | -34.3764 | -159.5141 | 162.1535 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-12-04 01:00 | 0 | 0 | 0 | 0 | -22.0749 | -146.843 | 122.7582 | -32.7582 | -142.937 | 148.3978 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-12-04 02:00 | 0 | 0 | 0 | 0 | -22.0808 | -131.847 | 120.3744 | -30.3744 | -126.8588 | 134.5074 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.2 | -2.2 | 1.1088 | 0
2015-12-04 03:00 | 0 | 0 | 0 | 0 | -22.0867 | -116.851 | 117.4328 | -27.4328 | -111.3377 | 120.6662 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-12-04 04:00 | 0 | 0 | 0 | 0 | -22.0926 | -101.855 | 114.1636 | -24.1636 | -96.3322 | 106.9669 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.4 | -2.4 | 1.1096 | 0
2015-12-04 05:00 | 0 | 0 | 0 | 0 | -22.0985 | -86.859 | 110.7971 | -20.7971 | -81.7403 | 93.51 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.4 | -2.4 | 1.1096 | 0
2015-12-04 06:00 | 0 | 0 | 0 | 0 | -22.1043 | -71.863 | 107.5513 | -17.5513 | -67.4367 | 80.4418 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-12-04 07:00 | 0 | 0 | 0 | 0 | -22.1102 | -56.867 | 104.6251 | -14.6251 | -53.3026 | 68.0058 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-12-04 08:00 | 0 | 0 | 0 | 0 | -22.116 | -41.871 | 102.1932 | -12.1932 | -39.2436 | 56.635 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.1064 | 0
2015-12-04 09:00 | 0 | 0 | 0 | 0 | -22.1219 | -26.8751 | 100.4003 | -10.4003 | -25.199 | 47.1194 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-12-04 10:00 | 0 | 0 | 0 | 0 | -22.1277 | -11.8791 | 99.354 | -9.354 | -11.1428 | 40.7878 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-12-04 11:00 | 0 | 0 | 0 | 0 | -22.1335 | 3.1169 | 99.1181 | -9.1181 | 2.924 | 39.2191 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-12-04 12:00 | 0 | 0 | 0 | 0 | -22.1393 | 18.1129 | 99.7071 | -9.7071 | 16.9868 | 42.9391 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.1056 | 0
2015-12-04 13:00 | 0 | 0 | 0 | 0 | -22.145 | 33.1088 | 101.0856 | -11.0856 | 31.0347 | 50.7966 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-12-04 14:00 | 0 | 0 | 0 | 0 | -22.1508 | 48.1048 | 103.1707 | -13.1707 | 45.0768 | 61.2141 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-12-04 15:00 | 0 | 0 | 0 | 0 | -22.1565 | 63.1007 | 105.8386 | -15.8386 | 59.1536 | 73.0988 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-12-04 16:00 | 0 | 0 | 0 | 0 | -22.1623 | 78.0967 | 108.9313 | -18.9313 | 73.3407 | 85.8352 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-12-04 17:00 | 0 | 0 | 0 | 0 | -22.168 | 93.0926 | 112.2638 | -22.2638 | 87.7447 | 99.0848 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-12-04 18:00 | 0 | 0 | 0 | 0 | -22.1737 | 108.0886 | 115.6286 | -25.6286 | 102.4908 | 112.6528 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-12-04 19:00 | 0 | 0 | 0 | 0 | -22.1794 | 123.0845 | 118.8017 | -28.8017 | 117.6993 | 126.4161 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.11 | 0
2015-12-04 20:00 | 0 | 0 | 0 | 0 | -22.1851 | 138.0805 | 121.5508 | -31.5508 | 133.4531 | 140.282 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-12-04 21:00 | 0 | 0 | 0 | 0 | -22.1908 | 153.0764 | 123.6517 | -33.6517 | 149.7571 | 154.1389 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.4 | -2.4 | 1.1096 | 0
2015-12-04 22:00 | 0 | 0 | 0 | 0 | -22.1964 | 168.0723 | 124.9142 | -34.9142 | 166.5048 | 167.6118 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-12-04 23:00 | 0 | 0 | 0 | 0 | -22.2021 | 183.0683 | 125.2144 | -35.2144 | -176.5224 | 174.0202 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-12-05 | 0 | 0 | 0 | 0 | -22.2077 | -161.9358 | 124.5223 | -34.5223 | -159.6082 | 162.2079 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1144 | 0
2015-12-05 01:00 | 0 | 0 | 0 | 0 | -22.2134 | -146.9399 | 122.9083 | -32.9083 | -143.0185 | 148.479 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.8 | -3.8 | 1.1152 | 0
2015-12-05 02:00 | 0 | 0 | 0 | 0 | -22.219 | -131.944 | 120.5274 | -30.5274 | -126.9298 | 134.6028 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-12-05 03:00 | 0 | 0 | 0 | 0 | -22.2246 | -116.948 | 117.5875 | -27.5875 | -111.4011 | 120.7725 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.5 | -4.5 | 1.118 | 0
2015-12-05 04:00 | 0 | 0 | 0 | 0 | -22.2302 | -101.9521 | 114.3188 | -24.3188 | -96.3915 | 107.0832 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.1 | -5.1 | 1.1204 | 0
2015-12-05 05:00 | 0 | 0 | 0 | 0 | -22.2357 | -86.9562 | 110.952 | -20.952 | -81.7984 | 93.636 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.4 | -5.4 | 1.1216 | 0
2015-12-05 06:00 | 0 | 0 | 0 | 0 | -22.2413 | -71.9603 | 107.705 | -17.705 | -67.4965 | 80.578 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.3 | -5.3 | 1.1212 | 0
2015-12-05 07:00 | 0 | 0 | 0 | 0 | -22.2468 | -56.9644 | 104.7767 | -14.7767 | -53.3664 | 68.1526 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.9 | -6.9 | 1.1276 | 0
2015-12-05 08:00 | 0 | 0 | 0 | 0 | -22.2524 | -41.9685 | 102.3419 | -12.3419 | -39.3133 | 56.7919 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.7 | -6.7 | 1.1268 | 0
2015-12-05 09:00 | 0 | 0 | 0 | 0 | -22.2579 | -26.9726 | 100.545 | -10.545 | -25.276 | 47.2825 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.4 | -5.4 | 1.1216 | 0
2015-12-05 10:00 | 0 | 0 | 0 | 0 | -22.2634 | -11.9767 | 99.4939 | -9.4939 | -11.2279 | 40.9446 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-12-05 11:00 | 0 | 0 | 0 | 0 | -22.2689 | 3.0192 | 99.2524 | -9.2524 | 2.8307 | 39.3467 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-12-05 12:00 | 0 | 0 | 0 | 0 | -22.2744 | 18.0151 | 99.8355 | -9.8355 | 16.8854 | 43.0214 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.9 | -5.9 | 1.1236 | 0
2015-12-05 13:00 | 0 | 0 | 0 | 0 | -22.2799 | 33.0109 | 101.208 | -11.208 | 30.9258 | 50.8353 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.9 | -6.9 | 1.1276 | 0
2015-12-05 14:00 | 0 | 0 | 0 | 0 | -22.2853 | 48.0068 | 103.2876 | -13.2876 | 44.9612 | 61.2191 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.7 | -6.7 | 1.1268 | 0
2015-12-05 15:00 | 0 | 0 | 0 | 0 | -22.2908 | 63.0027 | 105.9509 | -15.9509 | 59.0321 | 73.0788 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.3 | -6.3 | 1.1252 | 0
2015-12-05 16:00 | 0 | 0 | 0 | 0 | -22.2962 | 77.9986 | 109.0404 | -19.0404 | 73.2142 | 85.7963 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.1 | -5.1 | 1.1204 | 0
2015-12-05 17:00 | 0 | 0 | 0 | 0 | -22.3017 | 92.9944 | 112.3713 | -22.3713 | 87.6143 | 99.0309 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.3 | -4.3 | 1.1172 | 0
2015-12-05 18:00 | 0 | 0 | 0 | 0 | -22.3071 | 107.9903 | 115.7365 | -25.7365 | 102.3575 | 112.586 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.2 | -4.2 | 1.1168 | 0
2015-12-05 19:00 | 0 | 0 | 0 | 0 | -22.3125 | 122.9862 | 118.9119 | -28.9119 | 117.565 | 126.3375 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4 | -4 | 1.116 | 0
2015-12-05 20:00 | 0 | 0 | 0 | 0 | -22.3179 | 137.982 | 121.6653 | -31.6653 | 133.3202 | 140.1911 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.1064 | 0
2015-12-05 21:00 | 0 | 0 | 0 | 0 | -22.3232 | 152.9779 | 123.7719 | -33.7719 | 149.6287 | 154.0323 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.1 | 1.1 | 1.0956 | 0
2015-12-05 22:00 | 0 | 0 | 0 | 0 | -22.3286 | 167.9737 | 125.0409 | -35.0409 | 166.3844 | 167.4761 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.096 | 0
2015-12-05 23:00 | 0 | 0 | 0 | 0 | -22.3339 | 182.9696 | 125.3476 | -35.3476 | -176.6319 | 173.9485 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-12-06 | 0 | 0 | 0 | 0 | -22.3393 | -162.0346 | 124.6611 | -34.6611 | -159.7052 | 162.2643 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-12-06 01:00 | 0 | 0 | 0 | 0 | -22.3446 | -147.0387 | 123.0515 | -33.0515 | -143.1034 | 148.5617 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.7 | 0.7 | 1.0972 | 0
2015-12-06 02:00 | 0 | 0 | 0 | 0 | -22.3499 | -132.0429 | 120.6736 | -30.6736 | -127.0045 | 134.6993 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.6 | 0.6 | 1.0976 | 0
2015-12-06 03:00 | 0 | 0 | 0 | 0 | -22.3552 | -117.047 | 117.7355 | -27.7355 | -111.4684 | 120.8794 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-12-06 04:00 | 0 | 0 | 0 | 0 | -22.3605 | -102.0512 | 114.4675 | -24.4675 | -96.4545 | 107.1994 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-12-06 05:00 | 0 | 0 | 0 | 0 | -22.3658 | -87.0554 | 111.1003 | -21.1003 | -81.8602 | 93.7614 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-12-06 06:00 | 0 | 0 | 0 | 0 | -22.371 | -72.0595 | 107.8521 | -17.8521 | -67.5597 | 80.7129 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-12-06 07:00 | 0 | 0 | 0 | 0 | -22.3763 | -57.0637 | 104.9216 | -14.9216 | -53.4334 | 68.2971 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.1048 | 0
2015-12-06 08:00 | 0 | 0 | 0 | 0 | -22.3815 | -42.0679 | 102.4837 | -12.4837 | -39.3859 | 56.9455 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.1056 | 0
2015-12-06 09:00 | 0 | 0 | 0 | 0 | -22.3867 | -27.0721 | 100.6827 | -10.6827 | -25.3555 | 47.4408 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.1056 | 0
2015-12-06 10:00 | 0 | 0 | 0 | 0 | -22.392 | -12.0763 | 99.6267 | -9.6267 | -11.3149 | 41.095 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-12-06 11:00 | 0 | 0 | 0 | 0 | -22.3972 | 2.9196 | 99.3795 | -9.3795 | 2.7358 | 39.4674 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-12-06 12:00 | 0 | 0 | 0 | 0 | -22.4023 | 17.9154 | 99.9566 | -9.9566 | 16.7829 | 43.0969 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-12-06 13:00 | 0 | 0 | 0 | 0 | -22.4075 | 32.9112 | 101.3231 | -11.3231 | 30.8162 | 50.868 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.102 | 0
2015-12-06 14:00 | 0 | 0 | 0 | 0 | -22.4127 | 47.907 | 103.3971 | -13.3971 | 44.8452 | 61.2188 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-12-06 15:00 | 0 | 0 | 0 | 0 | -22.4178 | 62.9028 | 106.0558 | -16.0558 | 58.9105 | 73.0543 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-12-06 16:00 | 0 | 0 | 0 | 0 | -22.423 | 77.8986 | 109.142 | -19.142 | 73.0878 | 85.7535 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-12-06 17:00 | 0 | 0 | 0 | 0 | -22.4281 | 92.8944 | 112.4713 | -22.4713 | 87.4839 | 98.9735 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-12-06 18:00 | 0 | 0 | 0 | 0 | -22.4332 | 107.8902 | 115.8369 | -25.8369 | 102.2242 | 112.5163 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-12-06 19:00 | 0 | 0 | 0 | 0 | -22.4383 | 122.8859 | 119.0147 | -29.0147 | 117.4304 | 126.2564 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-12-06 20:00 | 0 | 0 | 0 | 0 | -22.4434 | 137.8817 | 121.7724 | -31.7724 | 133.1867 | 140.0982 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-12-06 21:00 | 0 | 0 | 0 | 0 | -22.4484 | 152.8775 | 123.8847 | -33.8847 | 149.4992 | 153.9247 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.1032 | 0
2015-12-06 22:00 | 0 | 0 | 0 | 0 | -22.4535 | 167.8733 | 125.1602 | -35.1602 | 166.2623 | 167.3413 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.102 | 0
2015-12-06 23:00 | 0 | 0 | 0 | 0 | -22.4585 | 182.8691 | 125.4735 | -35.4735 | -176.7438 | 173.8805 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-12-07 | 0 | 0 | 0 | 0 | -22.4636 | -162.1352 | 124.7928 | -34.7928 | -159.8053 | 162.3228 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-12-07 01:00 | 0 | 0 | 0 | 0 | -22.4686 | -147.1394 | 123.1878 | -33.1878 | -143.1917 | 148.6459 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-12-07 02:00 | 0 | 0 | 0 | 0 | -22.4736 | -132.1436 | 120.8131 | -30.8131 | -127.0828 | 134.7968 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-12-07 03:00 | 0 | 0 | 0 | 0 | -22.4786 | -117.1479 | 117.8768 | -27.8768 | -111.5393 | 120.9869 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-12-07 04:00 | 0 | 0 | 0 | 0 | -22.4836 | -102.1521 | 114.6095 | -24.6095 | -96.5211 | 107.3157 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-12-07 05:00 | 0 | 0 | 0 | 0 | -22.4886 | -87.1563 | 111.242 | -21.242 | -81.9255 | 93.8863 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-12-07 06:00 | 0 | 0 | 0 | 0 | -22.4935 | -72.1606 | 107.9925 | -17.9925 | -67.6263 | 80.8464 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-12-07 07:00 | 0 | 0 | 0 | 0 | -22.4985 | -57.1648 | 105.0598 | -15.0598 | -53.5035 | 68.4394 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-12-07 08:00 | 0 | 0 | 0 | 0 | -22.5034 | -42.1691 | 102.6185 | -12.6185 | -39.4612 | 57.0955 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-12-07 09:00 | 0 | 0 | 0 | 0 | -22.5083 | -27.1734 | 100.8134 | -10.8134 | -25.4373 | 47.5942 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-12-07 10:00 | 0 | 0 | 0 | 0 | -22.5132 | -12.1776 | 99.7523 | -9.7523 | -11.4039 | 41.239 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-12-07 11:00 | 0 | 0 | 0 | 0 | -22.5181 | 2.8181 | 99.4994 | -9.4994 | 2.6393 | 39.581 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-12-07 12:00 | 0 | 0 | 0 | 0 | -22.523 | 17.8139 | 100.0703 | -10.0703 | 16.6792 | 43.1656 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-12-07 13:00 | 0 | 0 | 0 | 0 | -22.5279 | 32.8096 | 101.4308 | -11.4308 | 30.7059 | 50.8947 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.1084 | 0
2015-12-07 14:00 | 0 | 0 | 0 | 0 | -22.5327 | 47.8053 | 103.4992 | -13.4992 | 44.7288 | 61.2133 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.1084 | 0
2015-12-07 15:00 | 0 | 0 | 0 | 0 | -22.5376 | 62.8011 | 106.1532 | -16.1532 | 58.7888 | 73.0253 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.4 | -2.4 | 1.1096 | 0
2015-12-07 16:00 | 0 | 0 | 0 | 0 | -22.5424 | 77.7968 | 109.2362 | -19.2362 | 72.9614 | 85.7068 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-12-07 17:00 | 0 | 0 | 0 | 0 | -22.5472 | 92.7925 | 112.5639 | -22.5639 | 87.3536 | 98.9128 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-12-07 18:00 | 0 | 0 | 0 | 0 | -22.552 | 107.7882 | 115.9298 | -25.9298 | 102.0911 | 112.4437 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.112 | 0
2015-12-07 19:00 | 0 | 0 | 0 | 0 | -22.5568 | 122.7839 | 119.11 | -29.11 | 117.2958 | 126.173 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-12-07 20:00 | 0 | 0 | 0 | 0 | -22.5616 | 137.7796 | 121.8719 | -31.8719 | 133.0527 | 140.0036 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-12-07 21:00 | 0 | 0 | 0 | 0 | -22.5663 | 152.7754 | 123.99 | -33.99 | 149.3687 | 153.8161 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-12-07 22:00 | 0 | 0 | 0 | 0 | -22.5711 | 167.7711 | 125.2721 | -35.2721 | 166.1385 | 167.2076 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1144 | 0
2015-12-07 23:00 | 0 | 0 | 0 | 0 | -22.5758 | 182.7668 | 125.5921 | -35.5921 | -176.858 | 173.8166 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-12-08 | 0 | 0 | 0 | 0 | -22.5806 | -162.2375 | 124.9173 | -34.9173 | -159.9081 | 162.3835 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.8 | -3.8 | 1.1152 | 0
2015-12-08 01:00 | 0 | 0 | 0 | 0 | -22.5853 | -147.2418 | 123.3171 | -33.3171 | -143.2833 | 148.7317 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.9 | -3.9 | 1.1156 | 0
2015-12-08 02:00 | 0 | 0 | 0 | 0 | -22.59 | -132.2461 | 120.9457 | -30.9457 | -127.1646 | 134.8953 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.9 | -3.9 | 1.1156 | 0
2015-12-08 03:00 | 0 | 0 | 0 | 0 | -22.5947 | -117.2504 | 118.0113 | -28.0113 | -111.614 | 121.0948 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.5 | -4.5 | 1.118 | 0
2015-12-08 04:00 | 0 | 0 | 0 | 0 | -22.5993 | -102.2548 | 114.7448 | -24.7448 | -96.5915 | 107.4319 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1184 | 0
2015-12-08 05:00 | 0 | 0 | 0 | 0 | -22.604 | -87.2591 | 111.377 | -21.377 | -81.9943 | 94.0104 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.9 | -4.9 | 1.1196 | 0
2015-12-08 06:00 | 0 | 0 | 0 | 0 | -22.6087 | -72.2634 | 108.1261 | -18.1261 | -67.6963 | 80.9784 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.5 | -5.5 | 1.122 | 0
2015-12-08 07:00 | 0 | 0 | 0 | 0 | -22.6133 | -57.2677 | 105.191 | -15.191 | -53.5766 | 68.5793 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.6 | -5.6 | 1.1224 | 0
2015-12-08 08:00 | 0 | 0 | 0 | 0 | -22.6179 | -42.272 | 102.7464 | -12.7464 | -39.5392 | 57.242 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.8 | -5.8 | 1.1232 | 0
2015-12-08 09:00 | 0 | 0 | 0 | 0 | -22.6225 | -27.2764 | 100.937 | -10.937 | -25.5214 | 47.7426 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.5 | -7.5 | 1.13 | 0
2015-12-08 10:00 | 0 | 0 | 0 | 0 | -22.6271 | -12.2807 | 99.8707 | -9.8707 | -11.4948 | 41.3767 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.2 | -7.2 | 1.1288 | 0
2015-12-08 11:00 | 0 | 0 | 0 | 0 | -22.6317 | 2.715 | 99.612 | -9.612 | 2.5415 | 39.6874 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8 | -8 | 1.132 | 0
2015-12-08 12:00 | 0 | 0 | 0 | 0 | -22.6363 | 17.7107 | 100.1767 | -10.1767 | 16.5746 | 43.2275 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.5 | -7.5 | 1.13 | 0
2015-12-08 13:00 | 0 | 0 | 0 | 0 | -22.6408 | 32.7063 | 101.531 | -11.531 | 30.5949 | 50.9153 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.5 | -8.5 | 1.134 | 0
2015-12-08 14:00 | 0 | 0 | 0 | 0 | -22.6454 | 47.702 | 103.5939 | -13.5939 | 44.6122 | 61.2027 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.3 | -8.3 | 1.1332 | 0
2015-12-08 15:00 | 0 | 0 | 0 | 0 | -22.6499 | 62.6976 | 106.2432 | -16.2432 | 58.6671 | 72.9919 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.9 | -8.9 | 1.1356 | 0
2015-12-08 16:00 | 0 | 0 | 0 | 0 | -22.6545 | 77.6933 | 109.3229 | -19.3229 | 72.8353 | 85.6563 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.7 | -7.7 | 1.1308 | 0
2015-12-08 17:00 | 0 | 0 | 0 | 0 | -22.659 | 92.6889 | 112.649 | -22.649 | 87.2236 | 98.8489 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.9 | -8.9 | 1.1356 | 0
2015-12-08 18:00 | 0 | 0 | 0 | 0 | -22.6635 | 107.6846 | 116.0151 | -26.0151 | 101.9581 | 112.3684 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.4 | -8.4 | 1.1336 | 0
2015-12-08 19:00 | 0 | 0 | 0 | 0 | -22.6679 | 122.6802 | 119.1977 | -29.1977 | 117.1612 | 126.0873 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.1 | -7.1 | 1.1284 | 0
2015-12-08 20:00 | 0 | 0 | 0 | 0 | -22.6724 | 137.6759 | 121.9638 | -31.9638 | 132.9183 | 139.9073 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.8 | -7.8 | 1.1312 | 0
2015-12-08 21:00 | 0 | 0 | 0 | 0 | -22.6769 | 152.6715 | 124.0877 | -34.0877 | 149.2373 | 153.7066 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.2 | -6.2 | 1.1248 | 0
2015-12-08 22:00 | 0 | 0 | 0 | 0 | -22.6813 | 167.6672 | 125.3765 | -35.3765 | 166.0132 | 167.0753 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.3 | -7.3 | 1.1292 | 0
2015-12-08 23:00 | 0 | 0 | 0 | 0 | -22.6857 | 182.6628 | 125.7032 | -35.7032 | -176.9743 | 173.757 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.5 | -8.5 | 1.134 | 0
2015-12-09 | 0 | 0 | 0 | 0 | -22.6902 | -162.3416 | 125.0346 | -35.0346 | -160.0137 | 162.4464 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.5 | -8.5 | 1.134 | 0
2015-12-09 01:00 | 0 | 0 | 0 | 0 | -22.6946 | -147.3459 | 123.4392 | -33.4392 | -143.378 | 148.8189 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.5 | -6.5 | 1.126 | 0
2015-12-09 02:00 | 0 | 0 | 0 | 0 | -22.699 | -132.3503 | 121.0713 | -31.0713 | -127.2499 | 134.9947 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6 | -6 | 1.124 | 0
2015-12-09 03:00 | 0 | 0 | 0 | 0 | -22.7033 | -117.3547 | 118.139 | -28.139 | -111.6922 | 121.203 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.1 | -7.1 | 1.1284 | 0
2015-12-09 04:00 | 0 | 0 | 0 | 0 | -22.7077 | -102.3591 | 114.8733 | -24.8733 | -96.6654 | 107.5478 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.8 | -5.8 | 1.1232 | 0
2015-12-09 05:00 | 0 | 0 | 0 | 0 | -22.7121 | -87.3634 | 111.5051 | -21.5051 | -82.0666 | 94.1337 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.9 | -5.9 | 1.1236 | 0
2015-12-09 06:00 | 0 | 0 | 0 | 0 | -22.7164 | -72.3678 | 108.2528 | -18.2528 | -67.7694 | 81.1089 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.5 | -5.5 | 1.122 | 0
2015-12-09 07:00 | 0 | 0 | 0 | 0 | -22.7207 | -57.3722 | 105.3153 | -15.3153 | -53.6527 | 68.7166 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.1 | -6.1 | 1.1244 | 0
2015-12-09 08:00 | 0 | 0 | 0 | 0 | -22.7251 | -42.3766 | 102.8673 | -12.8673 | -39.6199 | 57.3848 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.3 | -6.3 | 1.1252 | 0
2015-12-09 09:00 | 0 | 0 | 0 | 0 | -22.7294 | -27.381 | 101.0534 | -11.0534 | -25.6077 | 47.8858 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.1 | -5.1 | 1.1204 | 0
2015-12-09 10:00 | 0 | 0 | 0 | 0 | -22.7336 | -12.3854 | 99.9818 | -9.9818 | -11.5875 | 41.5078 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.9 | -4.9 | 1.1196 | 0
2015-12-09 11:00 | 0 | 0 | 0 | 0 | -22.7379 | 2.6102 | 99.7171 | -9.7171 | 2.4423 | 39.7866 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.4 | -5.4 | 1.1216 | 0
2015-12-09 12:00 | 0 | 0 | 0 | 0 | -22.7422 | 17.6058 | 100.2756 | -10.2756 | 16.4691 | 43.2825 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-12-09 13:00 | 0 | 0 | 0 | 0 | -22.7464 | 32.6014 | 101.6238 | -11.6238 | 30.4835 | 50.9299 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.2 | -5.2 | 1.1208 | 0
2015-12-09 14:00 | 0 | 0 | 0 | 0 | -22.7507 | 47.597 | 103.681 | -13.681 | 44.4955 | 61.1868 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.4 | -5.4 | 1.1216 | 0
2015-12-09 15:00 | 0 | 0 | 0 | 0 | -22.7549 | 62.5926 | 106.3256 | -16.3256 | 58.5456 | 72.954 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.1 | -5.1 | 1.1204 | 0
2015-12-09 16:00 | 0 | 0 | 0 | 0 | -22.7591 | 77.5882 | 109.402 | -19.402 | 72.7094 | 85.602 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.5 | -5.5 | 1.122 | 0
2015-12-09 17:00 | 0 | 0 | 0 | 0 | -22.7633 | 92.5838 | 112.7265 | -22.7265 | 87.0941 | 98.7817 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.7 | -5.7 | 1.1228 | 0
2015-12-09 18:00 | 0 | 0 | 0 | 0 | -22.7675 | 107.5794 | 116.0929 | -26.0929 | 101.8255 | 112.2905 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.9 | -5.9 | 1.1236 | 0
2015-12-09 19:00 | 0 | 0 | 0 | 0 | -22.7717 | 122.575 | 119.2778 | -29.2778 | 117.0267 | 125.9996 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7 | -7 | 1.128 | 0
2015-12-09 20:00 | 0 | 0 | 0 | 0 | -22.7758 | 137.5705 | 122.0481 | -32.0481 | 132.7837 | 139.8096 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.3 | -7.3 | 1.1292 | 0
2015-12-09 21:00 | 0 | 0 | 0 | 0 | -22.78 | 152.5661 | 124.1778 | -34.1778 | 149.1052 | 153.5966 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.7 | -7.7 | 1.1308 | 0
2015-12-09 22:00 | 0 | 0 | 0 | 0 | -22.7841 | 167.5617 | 125.4734 | -35.4734 | 165.8866 | 166.9445 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.4 | -7.4 | 1.1296 | 0
2015-12-09 23:00 | 0 | 0 | 0 | 0 | -22.7882 | 182.5573 | 125.8069 | -35.8069 | -177.0926 | 173.7018 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.3 | -8.3 | 1.1332 | 0
2015-12-10 | 0 | 0 | 0 | 0 | -22.7923 | -162.4472 | 125.1445 | -35.1445 | -160.1219 | 162.5118 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9 | -9 | 1.136 | 0
2015-12-10 01:00 | 0 | 0 | 0 | 0 | -22.7964 | -147.4516 | 123.5542 | -33.5542 | -143.4758 | 148.9077 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.8 | -8.8 | 1.1352 | 0
2015-12-10 02:00 | 0 | 0 | 0 | 0 | -22.8005 | -132.456 | 121.1899 | -31.1899 | -127.3385 | 135.095 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.5 | -9.5 | 1.138 | 0
2015-12-10 03:00 | 0 | 0 | 0 | 0 | -22.8046 | -117.4605 | 118.2598 | -28.2598 | -111.7739 | 121.3116 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.9 | -9.9 | 1.1396 | 0
2015-12-10 04:00 | 0 | 0 | 0 | 0 | -22.8086 | -102.4649 | 114.9949 | -24.9949 | -96.7427 | 107.6636 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.8 | -8.8 | 1.1352 | 0
2015-12-10 05:00 | 0 | 0 | 0 | 0 | -22.8127 | -87.4694 | 111.6264 | -21.6264 | -82.1423 | 94.2561 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.8 | -8.8 | 1.1352 | 0
2015-12-10 06:00 | 0 | 0 | 0 | 0 | -22.8167 | -72.4738 | 108.3727 | -18.3727 | -67.8457 | 81.2378 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.2 | -8.2 | 1.1328 | 0
2015-12-10 07:00 | 0 | 0 | 0 | 0 | -22.8207 | -57.4782 | 105.4327 | -15.4327 | -53.7317 | 68.8514 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.1 | -7.1 | 1.1284 | 0
2015-12-10 08:00 | 0 | 0 | 0 | 0 | -22.8247 | -42.4827 | 102.981 | -12.981 | -39.703 | 57.5238 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.3 | -7.3 | 1.1292 | 0
2015-12-10 09:00 | 0 | 0 | 0 | 0 | -22.8287 | -27.4872 | 101.1626 | -11.1626 | -25.6962 | 48.0239 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.3 | -6.3 | 1.1252 | 0
2015-12-10 10:00 | 0 | 0 | 0 | 0 | -22.8327 | -12.4916 | 100.0856 | -10.0856 | -11.6818 | 41.6324 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.2 | -5.2 | 1.1208 | 0
2015-12-10 11:00 | 0 | 0 | 0 | 0 | -22.8367 | 2.5039 | 99.8149 | -9.8149 | 2.3418 | 39.8786 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.1 | -5.1 | 1.1204 | 0
2015-12-10 12:00 | 0 | 0 | 0 | 0 | -22.8406 | 17.4995 | 100.3671 | -10.3671 | 16.3628 | 43.3305 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-12-10 13:00 | 0 | 0 | 0 | 0 | -22.8446 | 32.495 | 101.709 | -11.709 | 30.3717 | 50.9383 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-12-10 14:00 | 0 | 0 | 0 | 0 | -22.8485 | 47.4905 | 103.7605 | -13.7605 | 44.3787 | 61.1657 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-12-10 15:00 | 0 | 0 | 0 | 0 | -22.8524 | 62.4861 | 106.4005 | -16.4005 | 58.4243 | 72.9117 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1144 | 0
2015-12-10 16:00 | 0 | 0 | 0 | 0 | -22.8563 | 77.4816 | 109.4736 | -19.4736 | 72.5841 | 85.544 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.7 | -3.7 | 1.1148 | 0
2015-12-10 17:00 | 0 | 0 | 0 | 0 | -22.8602 | 92.4771 | 112.7964 | -22.7964 | 86.965 | 98.7114 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1184 | 0
2015-12-10 18:00 | 0 | 0 | 0 | 0 | -22.8641 | 107.4727 | 116.1631 | -26.1631 | 101.6934 | 112.21 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.4 | -5.4 | 1.1216 | 0
2015-12-10 19:00 | 0 | 0 | 0 | 0 | -22.8679 | 122.4682 | 119.3502 | -29.3502 | 116.8924 | 125.9098 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.5 | -6.5 | 1.126 | 0
2015-12-10 20:00 | 0 | 0 | 0 | 0 | -22.8718 | 137.4637 | 122.1248 | -32.1248 | 132.6491 | 139.7104 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.2 | -7.2 | 1.1288 | 0
2015-12-10 21:00 | 0 | 0 | 0 | 0 | -22.8756 | 152.4592 | 124.2603 | -34.2603 | 148.9724 | 153.486 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.7 | -7.7 | 1.1308 | 0
2015-12-10 22:00 | 0 | 0 | 0 | 0 | -22.8794 | 167.4547 | 125.5626 | -35.5626 | 165.7587 | 166.8154 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.5 | -7.5 | 1.13 | 0
2015-12-10 23:00 | 0 | 0 | 0 | 0 | -22.8832 | 182.4503 | 125.9031 | -35.9031 | -177.2128 | 173.6513 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.8 | -7.8 | 1.1312 | 0
2015-12-11 | 0 | 0 | 0 | 0 | -22.887 | -162.5542 | 125.2471 | -35.2471 | -160.2326 | 162.5795 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.7 | -7.7 | 1.1308 | 0
2015-12-11 01:00 | 0 | 0 | 0 | 0 | -22.8908 | -147.5587 | 123.6619 | -33.6619 | -143.5766 | 148.9979 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.6 | -7.6 | 1.1304 | 0
2015-12-11 02:00 | 0 | 0 | 0 | 0 | -22.8946 | -132.5632 | 121.3013 | -31.3013 | -127.4304 | 135.1961 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.4 | -7.4 | 1.1296 | 0
2015-12-11 03:00 | 0 | 0 | 0 | 0 | -22.8984 | -117.5677 | 118.3736 | -28.3736 | -111.859 | 121.4205 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8 | -8 | 1.132 | 0
2015-12-11 04:00 | 0 | 0 | 0 | 0 | -22.9021 | -102.5722 | 115.1096 | -25.1096 | -96.8235 | 107.779 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.8 | -8.8 | 1.1352 | 0
2015-12-11 05:00 | 0 | 0 | 0 | 0 | -22.9058 | -87.5767 | 111.7408 | -21.7408 | -82.2213 | 94.3775 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.6 | -9.6 | 1.1384 | 0
2015-12-11 06:00 | 0 | 0 | 0 | 0 | -22.9095 | -72.5812 | 108.4855 | -18.4855 | -67.9252 | 81.3648 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.5 | -10.5 | 1.142 | 0
2015-12-11 07:00 | 0 | 0 | 0 | 0 | -22.9132 | -57.5857 | 105.5429 | -15.5429 | -53.8135 | 68.9835 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.1 | -11.1 | 1.1444 | 0
2015-12-11 08:00 | 0 | 0 | 0 | 0 | -22.9169 | -42.5902 | 103.0876 | -13.0876 | -39.7887 | 57.659 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.7 | -10.7 | 1.1428 | 0
2015-12-11 09:00 | 0 | 0 | 0 | 0 | -22.9206 | -27.5947 | 101.2645 | -11.2645 | -25.7867 | 48.1567 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10 | -10 | 1.14 | 0
2015-12-11 10:00 | 0 | 0 | 0 | 0 | -22.9243 | -12.5993 | 100.182 | -10.182 | -11.7778 | 41.7504 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.7 | -10.7 | 1.1428 | 0
2015-12-11 11:00 | 0 | 0 | 0 | 0 | -22.9279 | 2.3962 | 99.9052 | -9.9052 | 2.2402 | 39.9634 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.8 | -9.8 | 1.1392 | 0
2015-12-11 12:00 | 0 | 0 | 0 | 0 | -22.9316 | 17.3917 | 100.451 | -10.451 | 16.2557 | 43.3717 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.5 | -9.5 | 1.138 | 0
2015-12-11 13:00 | 0 | 0 | 0 | 0 | -22.9352 | 32.3872 | 101.7866 | -11.7866 | 30.2596 | 50.9407 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10 | -10 | 1.14 | 0
2015-12-11 14:00 | 0 | 0 | 0 | 0 | -22.9388 | 47.3827 | 103.8325 | -13.8325 | 44.262 | 61.1394 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.4 | -10.4 | 1.1416 | 0
2015-12-11 15:00 | 0 | 0 | 0 | 0 | -22.9424 | 62.3782 | 106.4678 | -16.4678 | 58.3034 | 72.865 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.6 | -10.6 | 1.1424 | 0
2015-12-11 16:00 | 0 | 0 | 0 | 0 | -22.946 | 77.3736 | 109.5375 | -19.5375 | 72.4592 | 85.4823 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.3 | -10.3 | 1.1412 | 0
2015-12-11 17:00 | 0 | 0 | 0 | 0 | -22.9496 | 92.3691 | 112.8587 | -22.8587 | 86.8366 | 98.6381 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12.2 | -12.2 | 1.1488 | 0
2015-12-11 18:00 | 0 | 0 | 0 | 0 | -22.9531 | 107.3646 | 116.2257 | -26.2257 | 101.5619 | 112.127 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.6 | -11.6 | 1.1464 | 0
2015-12-11 19:00 | 0 | 0 | 0 | 0 | -22.9567 | 122.36 | 119.4151 | -29.4151 | 116.7586 | 125.8181 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12.2 | -12.2 | 1.1488 | 0
2015-12-11 20:00 | 0 | 0 | 0 | 0 | -22.9602 | 137.3555 | 122.1938 | -32.1938 | 132.5144 | 139.61 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.7 | -11.7 | 1.1468 | 0
2015-12-11 21:00 | 0 | 0 | 0 | 0 | -22.9637 | 152.351 | 124.3351 | -34.3351 | 148.8392 | 153.3752 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12 | -12 | 1.148 | 0
2015-12-11 22:00 | 0 | 0 | 0 | 0 | -22.9672 | 167.3464 | 125.6442 | -35.6442 | 165.6297 | 166.6883 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12 | -12 | 1.148 | 0
2015-12-11 23:00 | 0 | 0 | 0 | 0 | -22.9707 | 182.3419 | 125.9918 | -35.9918 | -177.3349 | 173.6057 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.8 | -11.8 | 1.1472 | 0
2015-12-12 | 0 | 0 | 0 | 0 | -22.9742 | -162.6627 | 125.3422 | -35.3422 | -160.3457 | 162.6497 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.7 | -11.7 | 1.1468 | 0
2015-12-12 01:00 | 0 | 0 | 0 | 0 | -22.9777 | -147.6672 | 123.7624 | -33.7624 | -143.6803 | 149.0897 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.8 | -11.8 | 1.1472 | 0
2015-12-12 02:00 | 0 | 0 | 0 | 0 | -22.9811 | -132.6718 | 121.4057 | -31.4057 | -127.5256 | 135.2981 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12.8 | -12.8 | 1.1512 | 0
2015-12-12 03:00 | 0 | 0 | 0 | 0 | -22.9846 | -117.6763 | 118.4803 | -28.4803 | -111.9475 | 121.5296 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.5 | -11.5 | 1.146 | 0
2015-12-12 04:00 | 0 | 0 | 0 | 0 | -22.988 | -102.6809 | 115.2173 | -25.2173 | -96.9077 | 107.894 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12.8 | -12.8 | 1.1512 | 0
2015-12-12 05:00 | 0 | 0 | 0 | 0 | -22.9914 | -87.6854 | 111.8481 | -21.8481 | -82.3035 | 94.4978 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12.9 | -12.9 | 1.1516 | 0
2015-12-12 06:00 | 0 | 0 | 0 | 0 | -22.9948 | -72.69 | 108.5913 | -18.5913 | -68.0076 | 81.4901 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12.8 | -12.8 | 1.1512 | 0
2015-12-12 07:00 | 0 | 0 | 0 | 0 | -22.9982 | -57.6945 | 105.646 | -15.646 | -53.898 | 69.1128 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12.4 | -12.4 | 1.1496 | 0
2015-12-12 08:00 | 0 | 0 | 0 | 0 | -23.0016 | -42.6991 | 103.1869 | -13.1869 | -39.8767 | 57.7902 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.1 | -13.1 | 1.1524 | 0
2015-12-12 09:00 | 0 | 0 | 0 | 0 | -23.005 | -27.7037 | 101.3591 | -11.3591 | -25.8792 | 48.2842 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13 | -13 | 1.152 | 0
2015-12-12 10:00 | 0 | 0 | 0 | 0 | -23.0083 | -12.7082 | 100.2709 | -10.2709 | -11.8754 | 41.8616 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.3 | -13.3 | 1.1532 | 0
2015-12-12 11:00 | 0 | 0 | 0 | 0 | -23.0116 | 2.2872 | 99.9879 | -9.9879 | 2.1375 | 40.0408 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.2 | -13.2 | 1.1528 | 0
2015-12-12 12:00 | 0 | 0 | 0 | 0 | -23.015 | 17.2826 | 100.5273 | -10.5273 | 16.148 | 43.4059 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12.8 | -12.8 | 1.1512 | 0
2015-12-12 13:00 | 0 | 0 | 0 | 0 | -23.0183 | 32.2781 | 101.8567 | -11.8567 | 30.1473 | 50.937 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12.7 | -12.7 | 1.1508 | 0
2015-12-12 14:00 | 0 | 0 | 0 | 0 | -23.0216 | 47.2735 | 103.8969 | -13.8969 | 44.1454 | 61.108 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.1 | -13.1 | 1.1524 | 0
2015-12-12 15:00 | 0 | 0 | 0 | 0 | -23.0249 | 62.2689 | 106.5275 | -16.5275 | 58.1829 | 72.814 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.1 | -13.1 | 1.1524 | 0
2015-12-12 16:00 | 0 | 0 | 0 | 0 | -23.0281 | 77.2643 | 109.5939 | -19.5939 | 72.3351 | 85.4171 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.7 | -13.7 | 1.1548 | 0
2015-12-12 17:00 | 0 | 0 | 0 | 0 | -23.0314 | 92.2598 | 112.9134 | -22.9134 | 86.709 | 98.5618 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.5 | -13.5 | 1.154 | 0
2015-12-12 18:00 | 0 | 0 | 0 | 0 | -23.0346 | 107.2552 | 116.2807 | -26.2807 | 101.431 | 112.0416 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.9 | -13.9 | 1.1556 | 0
2015-12-12 19:00 | 0 | 0 | 0 | 0 | -23.0379 | 122.2506 | 119.4722 | -29.4722 | 116.6253 | 125.7246 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.1 | -13.1 | 1.1524 | 0
2015-12-12 20:00 | 0 | 0 | 0 | 0 | -23.0411 | 137.246 | 122.2551 | -32.2551 | 132.38 | 139.5085 | 0 | 0 | 0.2 | 0 | 0 | 0 | -14.9 | -14.9 | 1.1596 | 0
2015-12-12 21:00 | 0 | 0 | 0 | 0 | -23.0443 | 152.2414 | 124.4022 | -34.4022 | 148.7056 | 153.2641 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.4 | -15.4 | 1.1616 | 0
2015-12-12 22:00 | 0 | 0 | 0 | 0 | -23.0475 | 167.2368 | 125.7181 | -35.7181 | 165.4997 | 166.5632 | 0 | 0 | 0.2 | 0 | 0 | 0 | -14.2 | -14.2 | 1.1568 | 0
2015-12-12 23:00 | 0 | 0 | 0 | 0 | -23.0506 | 182.2322 | 126.0728 | -36.0728 | -177.4586 | 173.5651 | 0 | 0 | 0.2 | 0 | 0 | 0 | -14.6 | -14.6 | 1.1584 | 0
2015-12-13 | 0 | 0 | 0 | 0 | -23.0538 | -162.7724 | 125.4298 | -35.4298 | -160.4611 | 162.7224 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.3 | -15.3 | 1.1612 | 0
2015-12-13 01:00 | 0 | 0 | 0 | 0 | -23.057 | -147.777 | 123.8555 | -33.8555 | -143.7867 | 149.1829 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.8 | -15.8 | 1.1632 | 0
2015-12-13 02:00 | 0 | 0 | 0 | 0 | -23.0601 | -132.7816 | 121.5028 | -31.5028 | -127.6238 | 135.4008 | 0 | 0 | 0.2 | 0 | 0 | 0 | -16.3 | -16.3 | 1.1652 | 0
2015-12-13 03:00 | 0 | 0 | 0 | 0 | -23.0632 | -117.7862 | 118.5798 | -28.5798 | -112.0392 | 121.6388 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.1 | -15.1 | 1.1604 | 0
2015-12-13 04:00 | 0 | 0 | 0 | 0 | -23.0663 | -102.7908 | 115.3179 | -25.3179 | -96.9951 | 108.0085 | 0 | 0 | 0.2 | 0 | 0 | 0 | -16.2 | -16.2 | 1.1648 | 0
2015-12-13 05:00 | 0 | 0 | 0 | 0 | -23.0694 | -87.7954 | 111.9483 | -21.9483 | -82.3889 | 94.617 | 0 | 0 | 0.2 | 0 | 0 | 0 | -16 | -16 | 1.164 | 0
2015-12-13 06:00 | 0 | 0 | 0 | 0 | -23.0725 | -72.8 | 108.69 | -18.69 | -68.093 | 81.6134 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.7 | -15.7 | 1.1628 | 0
2015-12-13 07:00 | 0 | 0 | 0 | 0 | -23.0756 | -57.8046 | 105.7419 | -15.7419 | -53.9852 | 69.2392 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.5 | -15.5 | 1.162 | 0
2015-12-13 08:00 | 0 | 0 | 0 | 0 | -23.0787 | -42.8092 | 103.279 | -13.279 | -39.967 | 57.9174 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.4 | -15.4 | 1.1616 | 0
2015-12-13 09:00 | 0 | 0 | 0 | 0 | -23.0817 | -27.8138 | 101.4462 | -11.4462 | -25.9736 | 48.4062 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.1 | -15.1 | 1.1604 | 0
2015-12-13 10:00 | 0 | 0 | 0 | 0 | -23.0847 | -12.8184 | 100.3524 | -10.3524 | -11.9744 | 41.9662 | 0 | 0 | 0.2 | 0 | 0 | 0 | -16.3 | -16.3 | 1.1652 | 0
2015-12-13 11:00 | 0 | 0 | 0 | 0 | -23.0878 | 2.177 | 100.0631 | -10.0631 | 2.0338 | 40.1109 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.6 | -15.6 | 1.1624 | 0
2015-12-13 12:00 | 0 | 0 | 0 | 0 | -23.0908 | 17.1724 | 100.596 | -10.596 | 16.0398 | 43.4331 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.8 | -15.8 | 1.1632 | 0
2015-12-13 13:00 | 0 | 0 | 0 | 0 | -23.0938 | 32.1677 | 101.9191 | -11.9191 | 30.0349 | 50.9272 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.9 | -15.9 | 1.1636 | 0
2015-12-13 14:00 | 0 | 0 | 0 | 0 | -23.0967 | 47.1631 | 103.9537 | -13.9537 | 44.0291 | 61.0715 | 0 | 0 | 0.2 | 0 | 0 | 0 | -16.3 | -16.3 | 1.1652 | 0
2015-12-13 15:00 | 0 | 0 | 0 | 0 | -23.0997 | 62.1585 | 106.5796 | -16.5796 | 58.0629 | 72.7587 | 0 | 0 | 0.2 | 0 | 0 | 0 | -16 | -16 | 1.164 | 0
2015-12-13 16:00 | 0 | 0 | 0 | 0 | -23.1027 | 77.1539 | 109.6426 | -19.6426 | 72.2117 | 85.3482 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.1 | -15.1 | 1.1604 | 0
2015-12-13 17:00 | 0 | 0 | 0 | 0 | -23.1056 | 92.1492 | 112.9605 | -22.9605 | 86.5822 | 98.4826 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.9 | -15.9 | 1.1636 | 0
2015-12-13 18:00 | 0 | 0 | 0 | 0 | -23.1085 | 107.1446 | 116.3279 | -26.3279 | 101.3011 | 111.9539 | 0 | 0 | 0.2 | 0 | 0 | 0 | -16.8 | -16.8 | 1.1672 | 0
2015-12-13 19:00 | 0 | 0 | 0 | 0 | -23.1114 | 122.14 | 119.5217 | -29.5217 | 116.4927 | 125.6294 | 0 | 0 | 0.2 | 0 | 0 | 0 | -16.3 | -16.3 | 1.1652 | 0
2015-12-13 20:00 | 0 | 0 | 0 | 0 | -23.1143 | 137.1353 | 122.3087 | -32.3087 | 132.2458 | 139.4059 | 0 | 0 | 0.2 | 0 | 0 | 0 | -16.1 | -16.1 | 1.1644 | 0
2015-12-13 21:00 | 0 | 0 | 0 | 0 | -23.1172 | 152.1307 | 124.4615 | -34.4615 | 148.5719 | 153.1531 | 0 | 0 | 0.2 | 0 | 0 | 0 | -16 | -16 | 1.164 | 0
2015-12-13 22:00 | 0 | 0 | 0 | 0 | -23.1201 | 167.1261 | 125.7843 | -35.7843 | 165.3688 | 166.4403 | 0 | 0 | 0.2 | 0 | 0 | 0 | -16.1 | -16.1 | 1.1644 | 0
2015-12-13 23:00 | 0 | 0 | 0 | 0 | -23.123 | 182.1214 | 126.1462 | -36.1462 | -177.5838 | 173.5296 | 0 | 0 | 0.2 | 0 | 0 | 0 | -16.2 | -16.2 | 1.1648 | 0
2015-12-14 | 0 | 0 | 0 | 0 | -23.1258 | -162.8832 | 125.5099 | -35.5099 | -160.5786 | 162.7977 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.9 | -15.9 | 1.1636 | 0
2015-12-14 01:00 | 0 | 0 | 0 | 0 | -23.1286 | -147.8878 | 123.9411 | -33.9411 | -143.8958 | 149.2775 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.6 | -15.6 | 1.1624 | 0
2015-12-14 02:00 | 0 | 0 | 0 | 0 | -23.1315 | -132.8925 | 121.5926 | -31.5926 | -127.725 | 135.5042 | 0 | 0 | 0.2 | 0 | 0 | 0 | -16 | -16 | 1.164 | 0
2015-12-14 03:00 | 0 | 0 | 0 | 0 | -23.1343 | -117.8971 | 118.6722 | -28.6722 | -112.1341 | 121.748 | 0 | 0 | 0.2 | 0 | 0 | 0 | -16.1 | -16.1 | 1.1644 | 0
2015-12-14 04:00 | 0 | 0 | 0 | 0 | -23.1371 | -102.9018 | 115.4113 | -25.4113 | -97.0857 | 108.1224 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.5 | -15.5 | 1.162 | 0
2015-12-14 05:00 | 0 | 0 | 0 | 0 | -23.1398 | -87.9064 | 112.0415 | -22.0415 | -82.4773 | 94.7349 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.7 | -15.7 | 1.1628 | 0
2015-12-14 06:00 | 0 | 0 | 0 | 0 | -23.1426 | -72.9111 | 108.7815 | -18.7815 | -68.1813 | 81.7346 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.6 | -15.6 | 1.1624 | 0
2015-12-14 07:00 | 0 | 0 | 0 | 0 | -23.1454 | -57.9157 | 105.8306 | -15.8306 | -54.0749 | 69.3626 | 0 | 0 | 0.2 | 0 | 0 | 0 | -14.5 | -14.5 | 1.158 | 0
2015-12-14 08:00 | 0 | 0 | 0 | 0 | -23.1481 | -42.9204 | 103.3637 | -13.3637 | -40.0596 | 58.0404 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15 | -15 | 1.16 | 0
2015-12-14 09:00 | 0 | 0 | 0 | 0 | -23.1508 | -27.9251 | 101.526 | -11.526 | -26.0698 | 48.5228 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15 | -15 | 1.16 | 0
2015-12-14 10:00 | 0 | 0 | 0 | 0 | -23.1535 | -12.9297 | 100.4263 | -10.4263 | -12.0747 | 42.064 | 0 | 0 | 0.2 | 0 | 0 | 0 | -14.2 | -14.2 | 1.1568 | 0
2015-12-14 11:00 | 0 | 0 | 0 | 0 | -23.1562 | 2.0656 | 100.1307 | -10.1307 | 1.9292 | 40.1737 | 0 | 0 | 0.2 | 0 | 0 | 0 | -16.2 | -16.2 | 1.1648 | 0
2015-12-14 12:00 | 0 | 0 | 0 | 0 | -23.1589 | 17.061 | 100.6571 | -10.6571 | 15.9311 | 43.4534 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.4 | -15.4 | 1.1616 | 0
2015-12-14 13:00 | 0 | 0 | 0 | 0 | -23.1616 | 32.0563 | 101.9739 | -11.9739 | 29.9224 | 50.9114 | 0 | 0 | 0.2 | 0 | 0 | 0 | -14.8 | -14.8 | 1.1592 | 0
2015-12-14 14:00 | 0 | 0 | 0 | 0 | -23.1643 | 47.0516 | 104.0027 | -14.0027 | 43.9132 | 61.0298 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.8 | -13.8 | 1.1552 | 0
2015-12-14 15:00 | 0 | 0 | 0 | 0 | -23.1669 | 62.047 | 106.624 | -16.624 | 57.9437 | 72.6992 | 0 | 0 | 0.2 | 0 | 0 | 0 | -14.5 | -14.5 | 1.158 | 0
2015-12-14 16:00 | 0 | 0 | 0 | 0 | -23.1695 | 77.0423 | 109.6837 | -19.6837 | 72.0891 | 85.2759 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.9 | -13.9 | 1.1556 | 0
2015-12-14 17:00 | 0 | 0 | 0 | 0 | -23.1722 | 92.0376 | 112.9999 | -22.9999 | 86.4564 | 98.4006 | 0 | 0 | 0.2 | 0 | 0 | 0 | -14.4 | -14.4 | 1.1576 | 0
2015-12-14 18:00 | 0 | 0 | 0 | 0 | -23.1748 | 107.033 | 116.3676 | -26.3676 | 101.1721 | 111.864 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.1 | -13.1 | 1.1524 | 0
2015-12-14 19:00 | 0 | 0 | 0 | 0 | -23.1774 | 122.0283 | 119.5635 | -29.5635 | 116.3609 | 125.5327 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.6 | -11.6 | 1.1464 | 0
2015-12-14 20:00 | 0 | 0 | 0 | 0 | -23.1799 | 137.0236 | 122.3546 | -32.3546 | 132.1122 | 139.3025 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.3 | -10.3 | 1.1412 | 0
2015-12-14 21:00 | 0 | 0 | 0 | 0 | -23.1825 | 152.0189 | 124.5131 | -34.5131 | 148.4381 | 153.0421 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.5 | -10.5 | 1.142 | 0
2015-12-14 22:00 | 0 | 0 | 0 | 0 | -23.1851 | 167.0143 | 125.8428 | -35.8428 | 165.2373 | 166.3198 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.1 | -11.1 | 1.1444 | 0
2015-12-14 23:00 | 0 | 0 | 0 | 0 | -23.1876 | 182.0096 | 126.2119 | -36.2119 | -177.7104 | 173.4994 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.3 | -13.3 | 1.1532 | 0
2015-12-15 | 0 | 0 | 0 | 0 | -23.1901 | -162.9951 | 125.5824 | -35.5824 | -160.6983 | 162.8757 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13 | -13 | 1.152 | 0
2015-12-15 01:00 | 0 | 0 | 0 | 0 | -23.1926 | -147.9998 | 124.0193 | -34.0193 | -144.0075 | 149.3736 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.7 | -13.7 | 1.1548 | 0
2015-12-15 02:00 | 0 | 0 | 0 | 0 | -23.1951 | -133.0045 | 121.675 | -31.675 | -127.8291 | 135.6082 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.2 | -11.2 | 1.1448 | 0
2015-12-15 03:00 | 0 | 0 | 0 | 0 | -23.1976 | -118.0092 | 118.7573 | -28.7573 | -112.232 | 121.8573 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.7 | -10.7 | 1.1428 | 0
2015-12-15 04:00 | 0 | 0 | 0 | 0 | -23.2001 | -103.0139 | 115.4975 | -25.4975 | -97.1794 | 108.2357 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.1 | -10.1 | 1.1404 | 0
2015-12-15 05:00 | 0 | 0 | 0 | 0 | -23.2026 | -88.0185 | 112.1274 | -22.1274 | -82.5687 | 94.8515 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.3 | -10.3 | 1.1412 | 0
2015-12-15 06:00 | 0 | 0 | 0 | 0 | -23.205 | -73.0232 | 108.8657 | -18.8657 | -68.2723 | 81.8538 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.3 | -10.3 | 1.1412 | 0
2015-12-15 07:00 | 0 | 0 | 0 | 0 | -23.2075 | -58.0279 | 105.9119 | -15.9119 | -54.1672 | 69.483 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.3 | -11.3 | 1.1452 | 0
2015-12-15 08:00 | 0 | 0 | 0 | 0 | -23.2099 | -43.0326 | 103.441 | -13.441 | -40.1542 | 58.1592 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.2 | -11.2 | 1.1448 | 0
2015-12-15 09:00 | 0 | 0 | 0 | 0 | -23.2123 | -28.0373 | 101.5982 | -11.5982 | -26.1678 | 48.6338 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.4 | -10.4 | 1.1416 | 0
2015-12-15 10:00 | 0 | 0 | 0 | 0 | -23.2147 | -13.042 | 100.4927 | -10.4927 | -12.1764 | 42.155 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.5 | -10.5 | 1.142 | 0
2015-12-15 11:00 | 0 | 0 | 0 | 0 | -23.2171 | 1.9533 | 100.1907 | -10.1907 | 1.8238 | 40.2291 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.3 | -11.3 | 1.1452 | 0
2015-12-15 12:00 | 0 | 0 | 0 | 0 | -23.2194 | 16.9486 | 100.7105 | -10.7105 | 15.8221 | 43.4667 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.7 | -11.7 | 1.1468 | 0
2015-12-15 13:00 | 0 | 0 | 0 | 0 | -23.2218 | 31.9439 | 102.021 | -12.021 | 29.81 | 50.8895 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.9 | -11.9 | 1.1476 | 0
2015-12-15 14:00 | 0 | 0 | 0 | 0 | -23.2241 | 46.9392 | 104.0442 | -14.0442 | 43.7977 | 60.9831 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12.4 | -12.4 | 1.1496 | 0
2015-12-15 15:00 | 0 | 0 | 0 | 0 | -23.2264 | 61.9345 | 106.6607 | -16.6607 | 57.8252 | 72.6355 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12.7 | -12.7 | 1.1508 | 0
2015-12-15 16:00 | 0 | 0 | 0 | 0 | -23.2288 | 76.9298 | 109.7172 | -19.7172 | 71.9676 | 85.2001 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12.6 | -12.6 | 1.1504 | 0
2015-12-15 17:00 | 0 | 0 | 0 | 0 | -23.2311 | 91.925 | 113.0317 | -23.0317 | 86.3317 | 98.3158 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.1 | -10.1 | 1.1404 | 0
2015-12-15 18:00 | 0 | 0 | 0 | 0 | -23.2333 | 106.9203 | 116.3995 | -26.3995 | 101.0442 | 111.772 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.2 | -9.2 | 1.1368 | 0
2015-12-15 19:00 | 0 | 0 | 0 | 0 | -23.2356 | 121.9156 | 119.5975 | -29.5975 | 116.23 | 125.4344 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.6 | -8.6 | 1.1344 | 0
2015-12-15 20:00 | 0 | 0 | 0 | 0 | -23.2379 | 136.9109 | 122.3927 | -32.3927 | 131.9791 | 139.1983 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.5 | -8.5 | 1.134 | 0
2015-12-15 21:00 | 0 | 0 | 0 | 0 | -23.2401 | 151.9062 | 124.5569 | -34.5569 | 148.3043 | 152.9313 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.4 | -8.4 | 1.1336 | 0
2015-12-15 22:00 | 0 | 0 | 0 | 0 | -23.2424 | 166.9015 | 125.8935 | -35.8935 | 165.1052 | 166.2017 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.7 | -8.7 | 1.1348 | 0
2015-12-15 23:00 | 0 | 0 | 0 | 0 | -23.2446 | 181.8968 | 126.2698 | -36.2698 | -177.8382 | 173.4746 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.6 | -8.6 | 1.1344 | 0
2015-12-16 | 0 | 0 | 0 | 0 | -23.2468 | -163.108 | 125.6472 | -35.6472 | -160.8198 | 162.9563 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9 | -9 | 1.136 | 0
2015-12-16 01:00 | 0 | 0 | 0 | 0 | -23.249 | -148.1127 | 124.09 | -34.09 | -144.1216 | 149.4711 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.9 | -8.9 | 1.1356 | 0
2015-12-16 02:00 | 0 | 0 | 0 | 0 | -23.2512 | -133.1174 | 121.7501 | -31.7501 | -127.9361 | 135.7128 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9 | -9 | 1.136 | 0
2015-12-16 03:00 | 0 | 0 | 0 | 0 | -23.2533 | -118.1221 | 118.8351 | -28.8351 | -112.3329 | 121.9664 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9 | -9 | 1.136 | 0
2015-12-16 04:00 | 0 | 0 | 0 | 0 | -23.2555 | -103.1268 | 115.5765 | -25.5765 | -97.276 | 108.3483 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.9 | -8.9 | 1.1356 | 0
2015-12-16 05:00 | 0 | 0 | 0 | 0 | -23.2576 | -88.1316 | 112.2061 | -22.2061 | -82.663 | 94.9667 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.2 | -9.2 | 1.1368 | 0
2015-12-16 06:00 | 0 | 0 | 0 | 0 | -23.2597 | -73.1363 | 108.9427 | -18.9427 | -68.366 | 81.9707 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.3 | -9.3 | 1.1372 | 0
2015-12-16 07:00 | 0 | 0 | 0 | 0 | -23.2619 | -58.141 | 105.9859 | -15.9859 | -54.2618 | 69.6002 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.7 | -9.7 | 1.1388 | 0
2015-12-16 08:00 | 0 | 0 | 0 | 0 | -23.264 | -43.1458 | 103.5108 | -13.5108 | -40.251 | 58.2737 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.7 | -9.7 | 1.1388 | 0
2015-12-16 09:00 | 0 | 0 | 0 | 0 | -23.266 | -28.1505 | 101.6629 | -11.6629 | -26.2674 | 48.7392 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10 | -10 | 1.14 | 0
2015-12-16 10:00 | 0 | 0 | 0 | 0 | -23.2681 | -13.1552 | 100.5515 | -10.5515 | -12.2792 | 42.2392 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.3 | -10.3 | 1.1412 | 0
2015-12-16 11:00 | 0 | 0 | 0 | 0 | -23.2702 | 1.84 | 100.2431 | -10.2431 | 1.7177 | 40.277 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.3 | -10.3 | 1.1412 | 0
2015-12-16 12:00 | 0 | 0 | 0 | 0 | -23.2722 | 16.8353 | 100.7563 | -10.7563 | 15.7128 | 43.4729 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.6 | -10.6 | 1.1424 | 0
2015-12-16 13:00 | 0 | 0 | 0 | 0 | -23.2743 | 31.8306 | 102.0604 | -12.0604 | 29.6978 | 50.8615 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.1 | -11.1 | 1.1444 | 0
2015-12-16 14:00 | 0 | 0 | 0 | 0 | -23.2763 | 46.8258 | 104.0779 | -14.0779 | 43.6827 | 60.9313 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11 | -11 | 1.144 | 0
2015-12-16 15:00 | 0 | 0 | 0 | 0 | -23.2783 | 61.8211 | 106.6898 | -16.6898 | 57.7076 | 72.5676 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.3 | -11.3 | 1.1452 | 0
2015-12-16 16:00 | 0 | 0 | 0 | 0 | -23.2803 | 76.8163 | 109.7429 | -19.7429 | 71.8472 | 85.121 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.6 | -11.6 | 1.1464 | 0
2015-12-16 17:00 | 0 | 0 | 0 | 0 | -23.2823 | 91.8116 | 113.0558 | -23.0558 | 86.2083 | 98.2283 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.7 | -11.7 | 1.1468 | 0
2015-12-16 18:00 | 0 | 0 | 0 | 0 | -23.2842 | 106.8069 | 116.4237 | -26.4237 | 100.9175 | 111.6779 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.1 | -11.1 | 1.1444 | 0
2015-12-16 19:00 | 0 | 0 | 0 | 0 | -23.2862 | 121.8021 | 119.6239 | -29.6239 | 116.1002 | 125.3347 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.7 | -10.7 | 1.1428 | 0
2015-12-16 20:00 | 0 | 0 | 0 | 0 | -23.2881 | 136.7974 | 122.423 | -32.423 | 131.8467 | 139.0934 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.8 | -10.8 | 1.1432 | 0
2015-12-16 21:00 | 0 | 0 | 0 | 0 | -23.29 | 151.7926 | 124.5929 | -34.5929 | 148.1708 | 152.8209 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.5 | -10.5 | 1.142 | 0
2015-12-16 22:00 | 0 | 0 | 0 | 0 | -23.2919 | 166.7879 | 125.9363 | -35.9363 | 164.9727 | 166.0861 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.4 | -10.4 | 1.1416 | 0
2015-12-16 23:00 | 0 | 0 | 0 | 0 | -23.2938 | 181.7831 | 126.32 | -36.32 | -177.9672 | 173.4554 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.8 | -10.8 | 1.1432 | 0
2015-12-17 | 0 | 0 | 0 | 0 | -23.2957 | -163.2216 | 125.7044 | -35.7044 | -160.9431 | 163.0395 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.3 | -10.3 | 1.1412 | 0
2015-12-17 01:00 | 0 | 0 | 0 | 0 | -23.2976 | -148.2264 | 124.1531 | -34.1531 | -144.2381 | 149.5699 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.3 | -10.3 | 1.1412 | 0
2015-12-17 02:00 | 0 | 0 | 0 | 0 | -23.2995 | -133.2312 | 121.8177 | -31.8177 | -128.0457 | 135.8179 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.1 | -10.1 | 1.1404 | 0
2015-12-17 03:00 | 0 | 0 | 0 | 0 | -23.3013 | -118.2359 | 118.9056 | -28.9056 | -112.4367 | 122.0754 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.1 | -10.1 | 1.1404 | 0
2015-12-17 04:00 | 0 | 0 | 0 | 0 | -23.3031 | -103.2407 | 115.6482 | -25.6482 | -97.3756 | 108.46 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.7 | -9.7 | 1.1388 | 0
2015-12-17 05:00 | 0 | 0 | 0 | 0 | -23.305 | -88.2454 | 112.2774 | -22.2774 | -82.7602 | 95.0804 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9 | -9 | 1.136 | 0
2015-12-17 06:00 | 0 | 0 | 0 | 0 | -23.3068 | -73.2502 | 109.0124 | -19.0124 | -68.4624 | 82.0853 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.9 | -8.9 | 1.1356 | 0
2015-12-17 07:00 | 0 | 0 | 0 | 0 | -23.3085 | -58.2549 | 106.0526 | -16.0526 | -54.3588 | 69.7142 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.7 | -8.7 | 1.1348 | 0
2015-12-17 08:00 | 0 | 0 | 0 | 0 | -23.3103 | -43.2597 | 103.5732 | -13.5732 | -40.3497 | 58.3838 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.6 | -8.6 | 1.1344 | 0
2015-12-17 09:00 | 0 | 0 | 0 | 0 | -23.3121 | -28.2645 | 101.7201 | -11.7201 | -26.3685 | 48.8389 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.5 | -8.5 | 1.134 | 0
2015-12-17 10:00 | 0 | 0 | 0 | 0 | -23.3138 | -13.2692 | 100.6026 | -10.6026 | -12.3831 | 42.3165 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.9 | -8.9 | 1.1356 | 0
2015-12-17 11:00 | 0 | 0 | 0 | 0 | -23.3156 | 1.726 | 100.2877 | -10.2877 | 1.6109 | 40.3175 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.9 | -8.9 | 1.1356 | 0
2015-12-17 12:00 | 0 | 0 | 0 | 0 | -23.3173 | 16.7212 | 100.7943 | -10.7943 | 15.6034 | 43.4722 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.7 | -8.7 | 1.1348 | 0
2015-12-17 13:00 | 0 | 0 | 0 | 0 | -23.319 | 31.7165 | 102.0921 | -12.0921 | 29.5859 | 50.8274 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.8 | -8.8 | 1.1352 | 0
2015-12-17 14:00 | 0 | 0 | 0 | 0 | -23.3207 | 46.7117 | 104.1039 | -14.1039 | 43.5685 | 60.8745 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.5 | -8.5 | 1.134 | 0
2015-12-17 15:00 | 0 | 0 | 0 | 0 | -23.3224 | 61.7069 | 106.7112 | -16.7112 | 57.5909 | 72.4957 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.2 | -8.2 | 1.1328 | 0
2015-12-17 16:00 | 0 | 0 | 0 | 0 | -23.3241 | 76.7022 | 109.7611 | -19.7611 | 71.728 | 85.0386 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8 | -8 | 1.132 | 0
2015-12-17 17:00 | 0 | 0 | 0 | 0 | -23.3257 | 91.6974 | 113.0722 | -23.0722 | 86.0862 | 98.1383 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8 | -8 | 1.132 | 0
2015-12-17 18:00 | 0 | 0 | 0 | 0 | -23.3274 | 106.6926 | 116.4403 | -26.4403 | 100.7922 | 111.5819 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.4 | -7.4 | 1.1296 | 0
2015-12-17 19:00 | 0 | 0 | 0 | 0 | -23.329 | 121.6878 | 119.6425 | -29.6425 | 115.9716 | 125.2338 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.3 | -7.3 | 1.1292 | 0
2015-12-17 20:00 | 0 | 0 | 0 | 0 | -23.3306 | 136.6831 | 122.4455 | -32.4455 | 131.7152 | 138.9879 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.8 | -6.8 | 1.1272 | 0
2015-12-17 21:00 | 0 | 0 | 0 | 0 | -23.3322 | 151.6783 | 124.6211 | -34.6211 | 148.0377 | 152.711 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.3 | -6.3 | 1.1252 | 0
2015-12-17 22:00 | 0 | 0 | 0 | 0 | -23.3338 | 166.6735 | 125.9714 | -35.9714 | 164.8399 | 165.9732 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6 | -6 | 1.124 | 0
2015-12-17 23:00 | 0 | 0 | 0 | 0 | -23.3354 | 181.6687 | 126.3625 | -36.3625 | -178.0972 | 173.4417 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.8 | -5.8 | 1.1232 | 0
2015-12-18 | 0 | 0 | 0 | 0 | -23.3369 | -163.3361 | 125.7539 | -35.7539 | -161.068 | 163.1255 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.4 | -5.4 | 1.1216 | 0
2015-12-18 01:00 | 0 | 0 | 0 | 0 | -23.3385 | -148.3408 | 124.2087 | -34.2087 | -144.3567 | 149.67 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.1 | -5.1 | 1.1204 | 0
2015-12-18 02:00 | 0 | 0 | 0 | 0 | -23.34 | -133.3456 | 121.8778 | -31.8778 | -128.1579 | 135.9235 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.5 | -4.5 | 1.118 | 0
2015-12-18 03:00 | 0 | 0 | 0 | 0 | -23.3415 | -118.3504 | 118.9686 | -28.9686 | -112.5433 | 122.1842 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.8 | -3.8 | 1.1152 | 0
2015-12-18 04:00 | 0 | 0 | 0 | 0 | -23.343 | -103.3552 | 115.7125 | -25.7125 | -97.478 | 108.5709 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.3 | -4.3 | 1.1172 | 0
2015-12-18 05:00 | 0 | 0 | 0 | 0 | -23.3445 | -88.36 | 112.3414 | -22.3414 | -82.86 | 95.1924 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-12-18 06:00 | 0 | 0 | 0 | 0 | -23.346 | -73.3648 | 109.0746 | -19.0746 | -68.5613 | 82.1975 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-12-18 07:00 | 0 | 0 | 0 | 0 | -23.3475 | -58.3696 | 106.1117 | -16.1117 | -54.458 | 69.8249 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.112 | 0
2015-12-18 08:00 | 0 | 0 | 0 | 0 | -23.3489 | -43.3743 | 103.6281 | -13.6281 | -40.4503 | 58.4895 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-12-18 09:00 | 0 | 0 | 0 | 0 | -23.3504 | -28.3791 | 101.7697 | -11.7697 | -26.4712 | 48.9329 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-12-18 10:00 | 0 | 0 | 0 | 0 | -23.3518 | -13.3839 | 100.6461 | -10.6461 | -12.4881 | 42.3868 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-12-18 11:00 | 0 | 0 | 0 | 0 | -23.3532 | 1.6113 | 100.3247 | -10.3247 | 1.5036 | 40.3506 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-12-18 12:00 | 0 | 0 | 0 | 0 | -23.3546 | 16.6065 | 100.8246 | -10.8246 | 15.4938 | 43.4644 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.1056 | 0
2015-12-18 13:00 | 0 | 0 | 0 | 0 | -23.356 | 31.6017 | 102.1161 | -12.1161 | 29.4743 | 50.7874 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-12-18 14:00 | 0 | 0 | 0 | 0 | -23.3574 | 46.5969 | 104.1222 | -14.1222 | 43.455 | 60.8127 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-12-18 15:00 | 0 | 0 | 0 | 0 | -23.3587 | 61.5921 | 106.7249 | -16.7249 | 57.4754 | 72.4197 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-12-18 16:00 | 0 | 0 | 0 | 0 | -23.3601 | 76.5873 | 109.7715 | -19.7715 | 71.6101 | 84.953 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.1048 | 0
2015-12-18 17:00 | 0 | 0 | 0 | 0 | -23.3614 | 91.5825 | 113.081 | -23.081 | 85.9655 | 98.0457 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-12-18 18:00 | 0 | 0 | 0 | 0 | -23.3627 | 106.5777 | 116.4492 | -26.4492 | 100.6683 | 111.4841 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-12-18 19:00 | 0 | 0 | 0 | 0 | -23.364 | 121.5729 | 119.6533 | -29.6533 | 115.8443 | 125.1316 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-12-18 20:00 | 0 | 0 | 0 | 0 | -23.3653 | 136.5681 | 122.4603 | -32.4603 | 131.5847 | 138.882 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.1048 | 0
2015-12-18 21:00 | 0 | 0 | 0 | 0 | -23.3666 | 151.5633 | 124.6415 | -34.6415 | 147.9051 | 152.6016 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-12-18 22:00 | 0 | 0 | 0 | 0 | -23.3679 | 166.5585 | 125.9986 | -35.9986 | 164.707 | 165.863 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.8 | -0.8 | 1.1032 | 0
2015-12-18 23:00 | 0 | 0 | 0 | 0 | -23.3691 | 181.5537 | 126.397 | -36.397 | -178.228 | 173.4338 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-12-19 | 0 | 0 | 0 | 0 | -23.3704 | -163.4511 | 125.7956 | -35.7956 | -161.1945 | 163.2142 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-12-19 01:00 | 0 | 0 | 0 | 0 | -23.3716 | -148.4559 | 124.2565 | -34.2565 | -144.4775 | 149.7714 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-12-19 02:00 | 0 | 0 | 0 | 0 | -23.3728 | -133.4607 | 121.9303 | -31.9303 | -128.2725 | 136.0295 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-12-19 03:00 | 0 | 0 | 0 | 0 | -23.374 | -118.4655 | 119.0242 | -29.0242 | -112.6526 | 122.2927 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-12-19 04:00 | 0 | 0 | 0 | 0 | -23.3752 | -103.4703 | 115.7694 | -25.7694 | -97.5831 | 108.6807 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.1 | -2.1 | 1.1084 | 0
2015-12-19 05:00 | 0 | 0 | 0 | 0 | -23.3764 | -88.4751 | 112.3981 | -22.3981 | -82.9625 | 95.3028 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.11 | 0
2015-12-19 06:00 | 0 | 0 | 0 | 0 | -23.3775 | -73.4799 | 109.1295 | -19.1295 | -68.6626 | 82.3073 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-12-19 07:00 | 0 | 0 | 0 | 0 | -23.3787 | -58.4848 | 106.1634 | -16.1634 | -54.5594 | 69.9321 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-12-19 08:00 | 0 | 0 | 0 | 0 | -23.3798 | -43.4896 | 103.6754 | -13.6754 | -40.5527 | 58.5907 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-12-19 09:00 | 0 | 0 | 0 | 0 | -23.3809 | -28.4944 | 101.8116 | -11.8116 | -26.5752 | 49.0211 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-12-19 10:00 | 0 | 0 | 0 | 0 | -23.382 | -13.4992 | 100.6819 | -10.6819 | -12.594 | 42.4502 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.11 | 0
2015-12-19 11:00 | 0 | 0 | 0 | 0 | -23.3831 | 1.496 | 100.3539 | -10.3539 | 1.3958 | 40.3762 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-12-19 12:00 | 0 | 0 | 0 | 0 | -23.3842 | 16.4912 | 100.8472 | -10.8472 | 15.3843 | 43.4496 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-12-19 13:00 | 0 | 0 | 0 | 0 | -23.3852 | 31.4864 | 102.1323 | -12.1323 | 29.3632 | 50.7413 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.1056 | 0
2015-12-19 14:00 | 0 | 0 | 0 | 0 | -23.3863 | 46.4815 | 104.1328 | -14.1328 | 43.3423 | 60.746 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-12-19 15:00 | 0 | 0 | 0 | 0 | -23.3873 | 61.4767 | 106.731 | -16.731 | 57.361 | 72.3397 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-12-19 16:00 | 0 | 0 | 0 | 0 | -23.3883 | 76.4719 | 109.7743 | -19.7743 | 71.4937 | 84.8641 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-12-19 17:00 | 0 | 0 | 0 | 0 | -23.3893 | 91.4671 | 113.0821 | -23.0821 | 85.8464 | 97.9507 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.8 | -1.8 | 1.1072 | 0
2015-12-19 18:00 | 0 | 0 | 0 | 0 | -23.3903 | 106.4623 | 116.4504 | -26.4504 | 100.546 | 111.3844 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-12-19 19:00 | 0 | 0 | 0 | 0 | -23.3913 | 121.4575 | 119.6565 | -29.6565 | 115.7184 | 125.0283 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-12-19 20:00 | 0 | 0 | 0 | 0 | -23.3923 | 136.4526 | 122.4673 | -32.4673 | 131.4554 | 138.7757 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-12-19 21:00 | 0 | 0 | 0 | 0 | -23.3932 | 151.4478 | 124.654 | -34.654 | 147.7731 | 152.4929 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-12-19 22:00 | 0 | 0 | 0 | 0 | -23.3942 | 166.443 | 126.0179 | -36.0179 | 164.5741 | 165.7556 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-12-19 23:00 | 0 | 0 | 0 | 0 | -23.3951 | 181.4382 | 126.4238 | -36.4238 | -178.3596 | 173.4316 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-12-20 | 0 | 0 | 0 | 0 | -23.396 | -163.5667 | 125.8296 | -35.8296 | -161.3224 | 163.3056 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-12-20 01:00 | 0 | 0 | 0 | 0 | -23.3969 | -148.5715 | 124.2967 | -34.2967 | -144.6002 | 149.874 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-12-20 02:00 | 0 | 0 | 0 | 0 | -23.3978 | -133.5763 | 121.9753 | -31.9753 | -128.3895 | 136.1359 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.7 | -0.7 | 1.1028 | 0
2015-12-20 03:00 | 0 | 0 | 0 | 0 | -23.3987 | -118.5811 | 119.0723 | -29.0723 | -112.7644 | 122.4008 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 | 0.1 | 1.0996 | 0
2015-12-20 04:00 | 0 | 0 | 0 | 0 | -23.3995 | -103.586 | 115.8189 | -25.8189 | -97.6909 | 108.7896 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0
2015-12-20 05:00 | 0 | 0 | 0 | 0 | -23.4004 | -88.5908 | 112.4473 | -22.4473 | -83.0675 | 95.4115 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-12-20 06:00 | 0 | 0 | 0 | 0 | -23.4012 | -73.5956 | 109.1769 | -19.1769 | -68.7662 | 82.4146 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.102 | 0
2015-12-20 07:00 | 0 | 0 | 0 | 0 | -23.402 | -58.6004 | 106.2076 | -16.2076 | -54.6629 | 70.0359 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-12-20 08:00 | 0 | 0 | 0 | 0 | -23.4028 | -43.6053 | 103.7152 | -13.7152 | -40.6568 | 58.6873 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-12-20 09:00 | 0 | 0 | 0 | 0 | -23.4036 | -28.6101 | 101.8459 | -11.8459 | -26.6804 | 49.1034 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-12-20 10:00 | 0 | 0 | 0 | 0 | -23.4044 | -13.6149 | 100.71 | -10.71 | -12.7007 | 42.5066 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-12-20 11:00 | 0 | 0 | 0 | 0 | -23.4052 | 1.3802 | 100.3753 | -10.3753 | 1.2877 | 40.3944 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-12-20 12:00 | 0 | 0 | 0 | 0 | -23.4059 | 16.3754 | 100.862 | -10.862 | 15.2749 | 43.4278 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-12-20 13:00 | 0 | 0 | 0 | 0 | -23.4067 | 31.3706 | 102.1408 | -12.1408 | 29.2527 | 50.6892 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-12-20 14:00 | 0 | 0 | 0 | 0 | -23.4074 | 46.3657 | 104.1357 | -14.1357 | 43.2306 | 60.6744 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-12-20 15:00 | 0 | 0 | 0 | 0 | -23.4081 | 61.3609 | 106.7293 | -16.7293 | 57.2479 | 72.2558 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.112 | 0
2015-12-20 16:00 | 0 | 0 | 0 | 0 | -23.4088 | 76.3561 | 109.7694 | -19.7694 | 71.3787 | 84.7722 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-12-20 17:00 | 0 | 0 | 0 | 0 | -23.4095 | 91.3512 | 113.0756 | -23.0756 | 85.729 | 97.8533 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-12-20 18:00 | 0 | 0 | 0 | 0 | -23.4102 | 106.3464 | 116.4439 | -26.4439 | 100.4254 | 111.2831 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.11 | 0
2015-12-20 19:00 | 0 | 0 | 0 | 0 | -23.4108 | 121.3416 | 119.652 | -29.652 | 115.5941 | 124.924 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-12-20 20:00 | 0 | 0 | 0 | 0 | -23.4115 | 136.3367 | 122.4665 | -32.4665 | 131.3273 | 138.6691 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-12-20 21:00 | 0 | 0 | 0 | 0 | -23.4121 | 151.3319 | 124.6587 | -34.6587 | 147.6419 | 152.3849 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3 | -3 | 1.112 | 0
2015-12-20 22:00 | 0 | 0 | 0 | 0 | -23.4127 | 166.3271 | 126.0294 | -36.0294 | 164.4414 | 165.651 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.2 | -2.2 | 1.1088 | 0
2015-12-20 23:00 | 0 | 0 | 0 | 0 | -23.4133 | 181.3222 | 126.4427 | -36.4427 | -178.4917 | 173.4352 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.8 | -2.8 | 1.1112 | 0
2015-12-21 | 0 | 0 | 0 | 0 | -23.4139 | -163.6826 | 125.8557 | -35.8557 | -161.4516 | 163.3997 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-12-21 01:00 | 0 | 0 | 0 | 0 | -23.4145 | -148.6874 | 124.3292 | -34.3292 | -144.7247 | 149.9778 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-12-21 02:00 | 0 | 0 | 0 | 0 | -23.415 | -133.6923 | 122.0127 | -32.0127 | -128.5088 | 136.2424 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-12-21 03:00 | 0 | 0 | 0 | 0 | -23.4156 | -118.6971 | 119.1128 | -29.1128 | -112.8787 | 122.5084 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.1048 | 0
2015-12-21 04:00 | 0 | 0 | 0 | 0 | -23.4161 | -103.702 | 115.8609 | -25.8609 | -97.8011 | 108.8972 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.2 | -2.2 | 1.1088 | 0
2015-12-21 05:00 | 0 | 0 | 0 | 0 | -23.4166 | -88.7068 | 112.489 | -22.489 | -83.175 | 95.5183 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-12-21 06:00 | 0 | 0 | 0 | 0 | -23.4171 | -73.7116 | 109.2167 | -19.2167 | -68.8721 | 82.5192 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.4 | -1.4 | 1.1056 | 0
2015-12-21 07:00 | 0 | 0 | 0 | 0 | -23.4176 | -58.7165 | 106.2442 | -16.2442 | -54.7683 | 70.1362 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.11 | 0
2015-12-21 08:00 | 0 | 0 | 0 | 0 | -23.4181 | -43.7213 | 103.7473 | -13.7473 | -40.7625 | 58.7793 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.5 | -2.5 | 1.11 | 0
2015-12-21 09:00 | 0 | 0 | 0 | 0 | -23.4186 | -28.7262 | 101.8725 | -11.8725 | -26.7869 | 49.1799 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-12-21 10:00 | 0 | 0 | 0 | 0 | -23.419 | -13.731 | 100.7304 | -10.7304 | -12.8081 | 42.556 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-12-21 11:00 | 0 | 0 | 0 | 0 | -23.4195 | 1.2641 | 100.3891 | -10.3891 | 1.1793 | 40.405 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.8 | -5.8 | 1.1232 | 0
2015-12-21 12:00 | 0 | 0 | 0 | 0 | -23.4199 | 16.2593 | 100.8691 | -10.8691 | 15.1657 | 43.399 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.8 | -5.8 | 1.1232 | 0
2015-12-21 13:00 | 0 | 0 | 0 | 0 | -23.4203 | 31.2545 | 102.1416 | -12.1416 | 29.1428 | 50.6312 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.9 | -6.9 | 1.1276 | 0
2015-12-21 14:00 | 0 | 0 | 0 | 0 | -23.4207 | 46.2496 | 104.1309 | -14.1309 | 43.12 | 60.5979 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.7 | -7.7 | 1.1308 | 0
2015-12-21 15:00 | 0 | 0 | 0 | 0 | -23.4211 | 61.2448 | 106.72 | -16.72 | 57.1363 | 72.168 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.2 | -8.2 | 1.1328 | 0
2015-12-21 16:00 | 0 | 0 | 0 | 0 | -23.4215 | 76.2399 | 109.7569 | -19.7569 | 71.2654 | 84.6773 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.2 | -8.2 | 1.1328 | 0
2015-12-21 17:00 | 0 | 0 | 0 | 0 | -23.4218 | 91.2351 | 113.0614 | -23.0614 | 85.6134 | 97.7536 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.2 | -7.2 | 1.1288 | 0
2015-12-21 18:00 | 0 | 0 | 0 | 0 | -23.4222 | 106.2302 | 116.4298 | -26.4298 | 100.3067 | 111.1802 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.5 | -8.5 | 1.134 | 0
2015-12-21 19:00 | 0 | 0 | 0 | 0 | -23.4225 | 121.2254 | 119.6397 | -29.6397 | 115.4715 | 124.8188 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.3 | -7.3 | 1.1292 | 0
2015-12-21 20:00 | 0 | 0 | 0 | 0 | -23.4228 | 136.2205 | 122.458 | -32.458 | 131.2006 | 138.5624 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.6 | -7.6 | 1.1304 | 0
2015-12-21 21:00 | 0 | 0 | 0 | 0 | -23.4231 | 151.2157 | 124.6556 | -34.6556 | 147.5116 | 152.2778 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.5 | -7.5 | 1.13 | 0
2015-12-21 22:00 | 0 | 0 | 0 | 0 | -23.4234 | 166.2108 | 126.033 | -36.033 | 164.3089 | 165.5493 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.8 | -6.8 | 1.1272 | 0
2015-12-21 23:00 | 0 | 0 | 0 | 0 | -23.4237 | 181.206 | 126.4537 | -36.4537 | -178.6242 | 173.4447 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.5 | -7.5 | 1.13 | 0
2015-12-22 | 0 | 0 | 0 | 0 | -23.4239 | -163.7989 | 125.8741 | -35.8741 | -161.5818 | 163.4966 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.1 | -7.1 | 1.1284 | 0
2015-12-22 01:00 | 0 | 0 | 0 | 0 | -23.4242 | -148.8037 | 124.354 | -34.354 | -144.8509 | 150.0826 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.4 | -8.4 | 1.1336 | 0
2015-12-22 02:00 | 0 | 0 | 0 | 0 | -23.4244 | -133.8086 | 122.0424 | -32.0424 | -128.6302 | 136.3492 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.7 | -4.7 | 1.1188 | 0
2015-12-22 03:00 | 0 | 0 | 0 | 0 | -23.4246 | -118.8134 | 119.1458 | -29.1458 | -112.9953 | 122.6154 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.2 | -4.2 | 1.1168 | 0
2015-12-22 04:00 | 0 | 0 | 0 | 0 | -23.4249 | -103.8183 | 115.8954 | -25.8954 | -97.9138 | 109.0037 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.5 | -4.5 | 1.118 | 0
2015-12-22 05:00 | 0 | 0 | 0 | 0 | -23.4251 | -88.8231 | 112.5232 | -22.5232 | -83.2848 | 95.6231 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-12-22 06:00 | 0 | 0 | 0 | 0 | -23.4252 | -73.828 | 109.2491 | -19.2491 | -68.9802 | 82.621 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4 | -4 | 1.116 | 0
2015-12-22 07:00 | 0 | 0 | 0 | 0 | -23.4254 | -58.8328 | 106.2733 | -16.2733 | -54.8756 | 70.2328 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4 | -4 | 1.116 | 0
2015-12-22 08:00 | 0 | 0 | 0 | 0 | -23.4256 | -43.8377 | 103.7718 | -13.7718 | -40.8697 | 58.8666 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.9 | -3.9 | 1.1156 | 0
2015-12-22 09:00 | 0 | 0 | 0 | 0 | -23.4257 | -28.8425 | 101.8914 | -11.8914 | -26.8945 | 49.2505 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.3 | -4.3 | 1.1172 | 0
2015-12-22 10:00 | 0 | 0 | 0 | 0 | -23.4258 | -13.8474 | 100.743 | -10.743 | -12.9162 | 42.5984 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.9 | -4.9 | 1.1196 | 0
2015-12-22 11:00 | 0 | 0 | 0 | 0 | -23.4259 | 1.1478 | 100.395 | -10.395 | 1.0708 | 40.4082 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.8 | -4.8 | 1.1192 | 0
2015-12-22 12:00 | 0 | 0 | 0 | 0 | -23.426 | 16.1429 | 100.8683 | -10.8683 | 15.0568 | 43.3631 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.7 | -5.7 | 1.1228 | 0
2015-12-22 13:00 | 0 | 0 | 0 | 0 | -23.4261 | 31.1381 | 102.1346 | -12.1346 | 29.0337 | 50.5672 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.5 | -5.5 | 1.122 | 0
2015-12-22 14:00 | 0 | 0 | 0 | 0 | -23.4262 | 46.1332 | 104.1184 | -14.1184 | 43.0105 | 60.5166 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.1 | -6.1 | 1.1244 | 0
2015-12-22 15:00 | 0 | 0 | 0 | 0 | -23.4263 | 61.1284 | 106.703 | -16.703 | 57.026 | 72.0764 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.1 | -7.1 | 1.1284 | 0
2015-12-22 16:00 | 0 | 0 | 0 | 0 | -23.4263 | 76.1235 | 109.7368 | -19.7368 | 71.1539 | 84.5794 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.9 | -8.9 | 1.1356 | 0
2015-12-22 17:00 | 0 | 0 | 0 | 0 | -23.4263 | 91.1187 | 113.0396 | -23.0396 | 85.4997 | 97.6517 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8 | -8 | 1.132 | 0
2015-12-22 18:00 | 0 | 0 | 0 | 0 | -23.4264 | 106.1138 | 116.408 | -26.408 | 100.1898 | 111.0757 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.8 | -7.8 | 1.1312 | 0
2015-12-22 19:00 | 0 | 0 | 0 | 0 | -23.4264 | 121.109 | 119.6198 | -29.6198 | 115.3507 | 124.7127 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.7 | -7.7 | 1.1308 | 0
2015-12-22 20:00 | 0 | 0 | 0 | 0 | -23.4264 | 136.1041 | 122.4417 | -32.4417 | 131.0754 | 138.4555 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.8 | -6.8 | 1.1272 | 0
2015-12-22 21:00 | 0 | 0 | 0 | 0 | -23.4263 | 151.0993 | 124.6447 | -34.6447 | 147.3824 | 152.1716 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.8 | -6.8 | 1.1272 | 0
2015-12-22 22:00 | 0 | 0 | 0 | 0 | -23.4263 | 166.0944 | 126.0288 | -36.0288 | 164.1768 | 165.4504 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.9 | -5.9 | 1.1236 | 0
2015-12-22 23:00 | 0 | 0 | 0 | 0 | -23.4262 | 181.0896 | 126.4569 | -36.4569 | -178.757 | 173.4601 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6 | -6 | 1.124 | 0
2015-12-23 | 0 | 0 | 0 | 0 | -23.4262 | -163.9153 | 125.8846 | -35.8846 | -161.7131 | 163.5961 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.1 | -5.1 | 1.1204 | 0
2015-12-23 01:00 | 0 | 0 | 0 | 0 | -23.4261 | -148.9201 | 124.371 | -34.371 | -144.9787 | 150.1885 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.8 | -4.8 | 1.1192 | 0
2015-12-23 02:00 | 0 | 0 | 0 | 0 | -23.426 | -133.925 | 122.0645 | -32.0645 | -128.7535 | 136.456 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.5 | -4.5 | 1.118 | 0
2015-12-23 03:00 | 0 | 0 | 0 | 0 | -23.4259 | -118.9298 | 119.1712 | -29.1712 | -113.1142 | 122.7219 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.2 | -4.2 | 1.1168 | 0
2015-12-23 04:00 | 0 | 0 | 0 | 0 | -23.4258 | -103.9347 | 115.9223 | -25.9223 | -98.0287 | 109.1088 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-12-23 05:00 | 0 | 0 | 0 | 0 | -23.4257 | -88.9396 | 112.5499 | -22.5499 | -83.3968 | 95.726 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.1 | -4.1 | 1.1164 | 0
2015-12-23 06:00 | 0 | 0 | 0 | 0 | -23.4255 | -73.9444 | 109.2739 | -19.2739 | -69.0903 | 82.7202 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1144 | 0
2015-12-23 07:00 | 0 | 0 | 0 | 0 | -23.4254 | -58.9493 | 106.2947 | -16.2947 | -54.9846 | 70.3258 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.1 | -3.1 | 1.1124 | 0
2015-12-23 08:00 | 0 | 0 | 0 | 0 | -23.4252 | -43.9541 | 103.7887 | -13.7887 | -40.9784 | 58.9491 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-12-23 09:00 | 0 | 0 | 0 | 0 | -23.425 | -28.959 | 101.9027 | -11.9027 | -27.0031 | 49.3152 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-12-23 10:00 | 0 | 0 | 0 | 0 | -23.4248 | -13.9638 | 100.7479 | -10.7479 | -13.0249 | 42.6337 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.1064 | 0
2015-12-23 11:00 | 0 | 0 | 0 | 0 | -23.4246 | 1.0313 | 100.3932 | -10.3932 | 0.9621 | 40.4038 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-12-23 12:00 | 0 | 0 | 0 | 0 | -23.4244 | 16.0265 | 100.8599 | -10.8599 | 14.9483 | 43.3203 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1 | -1 | 1.104 | 0
2015-12-23 13:00 | 0 | 0 | 0 | 0 | -23.4241 | 31.0216 | 102.1199 | -12.1199 | 28.9254 | 50.4973 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.102 | 0
2015-12-23 14:00 | 0 | 0 | 0 | 0 | -23.4239 | 46.0168 | 104.0983 | -14.0983 | 42.9022 | 60.4306 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-12-23 15:00 | 0 | 0 | 0 | 0 | -23.4236 | 61.0119 | 106.6784 | -16.6784 | 56.9174 | 71.9811 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-12-23 16:00 | 0 | 0 | 0 | 0 | -23.4233 | 76.007 | 109.7091 | -19.7091 | 71.0442 | 84.4787 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.9 | -0.9 | 1.1036 | 0
2015-12-23 17:00 | 0 | 0 | 0 | 0 | -23.423 | 91.0022 | 113.0103 | -23.0103 | 85.3879 | 97.5477 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-12-23 18:00 | 0 | 0 | 0 | 0 | -23.4227 | 105.9973 | 116.3786 | -26.3786 | 100.075 | 110.9698 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.1064 | 0
2015-12-23 19:00 | 0 | 0 | 0 | 0 | -23.4224 | 120.9925 | 119.5922 | -29.5922 | 115.2318 | 124.6059 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-12-23 20:00 | 0 | 0 | 0 | 0 | -23.4221 | 135.9876 | 122.4177 | -32.4177 | 130.9519 | 138.3487 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.2 | -1.2 | 1.1048 | 0
2015-12-23 21:00 | 0 | 0 | 0 | 0 | -23.4217 | 150.9828 | 124.6259 | -34.6259 | 147.2543 | 152.0663 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-12-23 22:00 | 0 | 0 | 0 | 0 | -23.4214 | 165.9779 | 126.0167 | -36.0167 | 164.0454 | 165.3545 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.102 | 0
2015-12-23 23:00 | 0 | 0 | 0 | 0 | -23.421 | 180.9731 | 126.4522 | -36.4522 | -178.8899 | 173.4815 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.5 | -0.5 | 1.102 | 0
2015-12-24 | 0 | 0 | 0 | 0 | -23.4206 | -164.0318 | 125.8872 | -35.8872 | -161.8451 | 163.6983 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.3 | -0.3 | 1.1012 | 0
2015-12-24 01:00 | 0 | 0 | 0 | 0 | -23.4202 | -149.0366 | 124.3802 | -34.3802 | -145.1079 | 150.2954 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.2 | -0.2 | 1.1008 | 0
2015-12-24 02:00 | 0 | 0 | 0 | 0 | -23.4198 | -134.0415 | 122.0788 | -32.0788 | -128.8787 | 136.5629 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.4 | -0.4 | 1.1016 | 0
2015-12-24 03:00 | 0 | 0 | 0 | 0 | -23.4194 | -119.0463 | 119.189 | -29.189 | -113.2351 | 122.8276 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.6 | -0.6 | 1.1024 | 0
2015-12-24 04:00 | 0 | 0 | 0 | 0 | -23.4189 | -104.0512 | 115.9416 | -25.9416 | -98.1459 | 109.2126 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.7 | -1.7 | 1.1068 | 0
2015-12-24 05:00 | 0 | 0 | 0 | 0 | -23.4185 | -89.0561 | 112.569 | -22.569 | -83.511 | 95.8268 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.4 | -2.4 | 1.1096 | 0
2015-12-24 06:00 | 0 | 0 | 0 | 0 | -23.418 | -74.0609 | 109.2911 | -19.2911 | -69.2023 | 82.8164 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.6 | -1.6 | 1.1064 | 0
2015-12-24 07:00 | 0 | 0 | 0 | 0 | -23.4175 | -59.0658 | 106.3086 | -16.3086 | -55.0954 | 70.4149 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-12-24 08:00 | 0 | 0 | 0 | 0 | -23.417 | -44.0706 | 103.7978 | -13.7978 | -41.0884 | 59.0268 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-12-24 09:00 | 0 | 0 | 0 | 0 | -23.4165 | -29.0755 | 101.9061 | -11.9061 | -27.1127 | 49.3738 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.4 | -2.4 | 1.1096 | 0
2015-12-24 10:00 | 0 | 0 | 0 | 0 | -23.416 | -14.0803 | 100.745 | -10.745 | -13.1341 | 42.662 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-12-24 11:00 | 0 | 0 | 0 | 0 | -23.4154 | 0.91483 | 100.3836 | -10.3836 | 0.85346 | 40.392 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-12-24 12:00 | 0 | 0 | 0 | 0 | -23.4149 | 15.91 | 100.8437 | -10.8437 | 14.8403 | 43.2706 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.7 | -2.7 | 1.1108 | 0
2015-12-24 13:00 | 0 | 0 | 0 | 0 | -23.4143 | 30.9051 | 102.0975 | -12.0975 | 28.818 | 50.4215 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.8 | -2.8 | 1.1112 | 0
2015-12-24 14:00 | 0 | 0 | 0 | 0 | -23.4137 | 45.9003 | 104.0704 | -14.0704 | 42.7953 | 60.3399 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1144 | 0
2015-12-24 15:00 | 0 | 0 | 0 | 0 | -23.4132 | 60.8954 | 106.6462 | -16.6462 | 56.8105 | 71.8821 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.4 | -4.4 | 1.1176 | 0
2015-12-24 16:00 | 0 | 0 | 0 | 0 | -23.4125 | 75.8906 | 109.6737 | -19.6737 | 70.9364 | 84.3751 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.1 | -4.1 | 1.1164 | 0
2015-12-24 17:00 | 0 | 0 | 0 | 0 | -23.4119 | 90.8857 | 112.9733 | -22.9733 | 85.2783 | 97.4417 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4 | -4 | 1.116 | 0
2015-12-24 18:00 | 0 | 0 | 0 | 0 | -23.4113 | 105.8809 | 116.3417 | -26.3417 | 99.9624 | 110.8626 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.3 | -3.3 | 1.1132 | 0
2015-12-24 19:00 | 0 | 0 | 0 | 0 | -23.4106 | 120.876 | 119.5569 | -29.5569 | 115.115 | 124.4984 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.7 | -3.7 | 1.1148 | 0
2015-12-24 20:00 | 0 | 0 | 0 | 0 | -23.41 | 135.8712 | 122.386 | -32.386 | 130.8302 | 138.2419 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.3 | -4.3 | 1.1172 | 0
2015-12-24 21:00 | 0 | 0 | 0 | 0 | -23.4093 | 150.8663 | 124.5994 | -34.5994 | 147.1276 | 151.9622 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.1 | -5.1 | 1.1204 | 0
2015-12-24 22:00 | 0 | 0 | 0 | 0 | -23.4086 | 165.8615 | 125.9967 | -35.9967 | 163.9146 | 165.2615 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.9 | -4.9 | 1.1196 | 0
2015-12-24 23:00 | 0 | 0 | 0 | 0 | -23.4079 | 180.8566 | 126.4396 | -36.4396 | -179.0228 | 173.5088 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-12-25 | 0 | 0 | 0 | 0 | -23.4072 | -164.1482 | 125.882 | -35.882 | -161.9779 | 163.8031 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.7 | -4.7 | 1.1188 | 0
2015-12-25 01:00 | 0 | 0 | 0 | 0 | -23.4065 | -149.1531 | 124.3816 | -34.3816 | -145.2385 | 150.4031 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.8 | -3.8 | 1.1152 | 0
2015-12-25 02:00 | 0 | 0 | 0 | 0 | -23.4057 | -134.1579 | 122.0855 | -32.0855 | -129.0057 | 136.6697 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.7 | -3.7 | 1.1148 | 0
2015-12-25 03:00 | 0 | 0 | 0 | 0 | -23.405 | -119.1628 | 119.1991 | -29.1991 | -113.3581 | 122.9325 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1144 | 0
2015-12-25 04:00 | 0 | 0 | 0 | 0 | -23.4042 | -104.1676 | 115.9533 | -25.9533 | -98.2651 | 109.3149 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.5 | -3.5 | 1.114 | 0
2015-12-25 05:00 | 0 | 0 | 0 | 0 | -23.4034 | -89.1725 | 112.5805 | -22.5805 | -83.6272 | 95.9254 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.2 | -3.2 | 1.1128 | 0
2015-12-25 06:00 | 0 | 0 | 0 | 0 | -23.4026 | -74.1773 | 109.3007 | -19.3007 | -69.3162 | 82.9097 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-12-25 07:00 | 0 | 0 | 0 | 0 | -23.4018 | -59.1822 | 106.3148 | -16.3148 | -55.2077 | 70.5003 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.1 | -4.1 | 1.1164 | 0
2015-12-25 08:00 | 0 | 0 | 0 | 0 | -23.401 | -44.187 | 103.7993 | -13.7993 | -41.1996 | 59.0997 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.4 | -3.4 | 1.1136 | 0
2015-12-25 09:00 | 0 | 0 | 0 | 0 | -23.4002 | -29.1919 | 101.9019 | -11.9019 | -27.2231 | 49.4264 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.1 | -4.1 | 1.1164 | 0
2015-12-25 10:00 | 0 | 0 | 0 | 0 | -23.3993 | -14.1967 | 100.7344 | -10.7344 | -13.2436 | 42.6832 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.7 | -3.7 | 1.1148 | 0
2015-12-25 11:00 | 0 | 0 | 0 | 0 | -23.3985 | 0.79842 | 100.3663 | -10.3663 | 0.74492 | 40.3727 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4 | -4 | 1.116 | 0
2015-12-25 12:00 | 0 | 0 | 0 | 0 | -23.3976 | 15.7936 | 100.8197 | -10.8197 | 14.7329 | 43.2138 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.2 | -5.2 | 1.1208 | 0
2015-12-25 13:00 | 0 | 0 | 0 | 0 | -23.3967 | 30.7887 | 102.0673 | -12.0673 | 28.7117 | 50.3399 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.9 | -4.9 | 1.1196 | 0
2015-12-25 14:00 | 0 | 0 | 0 | 0 | -23.3958 | 45.7839 | 104.0349 | -14.0349 | 42.6898 | 60.2445 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5.7 | -5.7 | 1.1228 | 0
2015-12-25 15:00 | 0 | 0 | 0 | 0 | -23.3949 | 60.779 | 106.6064 | -16.6064 | 56.7053 | 71.7795 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.2 | -6.2 | 1.1248 | 0
2015-12-25 16:00 | 0 | 0 | 0 | 0 | -23.3939 | 75.7742 | 109.6308 | -19.6308 | 70.8307 | 84.2688 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.7 | -6.7 | 1.1268 | 0
2015-12-25 17:00 | 0 | 0 | 0 | 0 | -23.393 | 90.7693 | 112.9288 | -22.9288 | 85.1709 | 97.3337 | 0 | 0 | 0.2 | 0 | 0 | 0 | -6.9 | -6.9 | 1.1276 | 0
2015-12-25 18:00 | 0 | 0 | 0 | 0 | -23.392 | 105.7645 | 116.2971 | -26.2971 | 99.852 | 110.7541 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.2 | -7.2 | 1.1288 | 0
2015-12-25 19:00 | 0 | 0 | 0 | 0 | -23.3911 | 120.7597 | 119.5141 | -29.5141 | 115.0004 | 124.3903 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.7 | -7.7 | 1.1308 | 0
2015-12-25 20:00 | 0 | 0 | 0 | 0 | -23.3901 | 135.7548 | 122.3465 | -32.3465 | 130.7104 | 138.1353 | 0 | 0 | 0.2 | 0 | 0 | 0 | -7.9 | -7.9 | 1.1316 | 0
2015-12-25 21:00 | 0 | 0 | 0 | 0 | -23.3891 | 150.75 | 124.5651 | -34.5651 | 147.0024 | 151.8591 | 0 | 0 | 0.2 | 0 | 0 | 0 | -8.6 | -8.6 | 1.1344 | 0
2015-12-25 22:00 | 0 | 0 | 0 | 0 | -23.3881 | 165.7451 | 125.9689 | -35.9689 | 163.7847 | 165.1715 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.4 | -9.4 | 1.1376 | 0
2015-12-25 23:00 | 0 | 0 | 0 | 0 | -23.387 | 180.7403 | 126.4191 | -36.4191 | -179.1556 | 173.5422 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.6 | -9.6 | 1.1384 | 0
2015-12-26 | 0 | 0 | 0 | 0 | -23.386 | -164.2646 | 125.869 | -35.869 | -162.1113 | 163.9105 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.2 | -10.2 | 1.1408 | 0
2015-12-26 01:00 | 0 | 0 | 0 | 0 | -23.385 | -149.2694 | 124.3752 | -34.3752 | -145.3702 | 150.5117 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.6 | -10.6 | 1.1424 | 0
2015-12-26 02:00 | 0 | 0 | 0 | 0 | -23.3839 | -134.2742 | 122.0844 | -32.0844 | -129.1343 | 136.7763 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.7 | -10.7 | 1.1428 | 0
2015-12-26 03:00 | 0 | 0 | 0 | 0 | -23.3828 | -119.2791 | 119.2016 | -29.2016 | -113.4829 | 123.0366 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.8 | -10.8 | 1.1432 | 0
2015-12-26 04:00 | 0 | 0 | 0 | 0 | -23.3817 | -104.2839 | 115.9575 | -25.9575 | -98.3864 | 109.4156 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.6 | -11.6 | 1.1464 | 0
2015-12-26 05:00 | 0 | 0 | 0 | 0 | -23.3806 | -89.2888 | 112.5844 | -22.5844 | -83.7453 | 96.0217 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.8 | -11.8 | 1.1472 | 0
2015-12-26 06:00 | 0 | 0 | 0 | 0 | -23.3795 | -74.2936 | 109.3027 | -19.3027 | -69.4319 | 83 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12.5 | -12.5 | 1.15 | 0
2015-12-26 07:00 | 0 | 0 | 0 | 0 | -23.3783 | -59.2984 | 106.3133 | -16.3133 | -55.3215 | 70.5818 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.4 | -13.4 | 1.1536 | 0
2015-12-26 08:00 | 0 | 0 | 0 | 0 | -23.3772 | -44.3033 | 103.7931 | -13.7931 | -41.312 | 59.1677 | 0 | 0 | 0.2 | 0 | 0 | 0 | -14.8 | -14.8 | 1.1592 | 0
2015-12-26 09:00 | 0 | 0 | 0 | 0 | -23.376 | -29.3081 | 101.8899 | -11.8899 | -27.3342 | 49.473 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.5 | -15.5 | 1.162 | 0
2015-12-26 10:00 | 0 | 0 | 0 | 0 | -23.3749 | -14.313 | 100.716 | -10.716 | -13.3534 | 42.6973 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15 | -15 | 1.16 | 0
2015-12-26 11:00 | 0 | 0 | 0 | 0 | -23.3737 | 0.68221 | 100.3412 | -10.3412 | 0.63657 | 40.3458 | 0 | 0 | 0.2 | 0 | 0 | 0 | -17.7 | -17.7 | 1.1708 | 0
2015-12-26 12:00 | 0 | 0 | 0 | 0 | -23.3725 | 15.6774 | 100.788 | -10.788 | 14.6261 | 43.1502 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.1 | -15.1 | 1.1604 | 0
2015-12-26 13:00 | 0 | 0 | 0 | 0 | -23.3713 | 30.6725 | 102.0295 | -12.0295 | 28.6064 | 50.2525 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.9 | -15.9 | 1.1636 | 0
2015-12-26 14:00 | 0 | 0 | 0 | 0 | -23.37 | 45.6677 | 103.9917 | -13.9917 | 42.5859 | 60.1445 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.8 | -15.8 | 1.1632 | 0
2015-12-26 15:00 | 0 | 0 | 0 | 0 | -23.3688 | 60.6629 | 106.5589 | -16.5589 | 56.602 | 71.6734 | 0 | 0 | 0.2 | 0 | 0 | 0 | -14.8 | -14.8 | 1.1592 | 0
2015-12-26 16:00 | 0 | 0 | 0 | 0 | -23.3675 | 75.658 | 109.5804 | -19.5804 | 70.7271 | 84.1599 | 0 | 0 | 0.2 | 0 | 0 | 0 | -14.8 | -14.8 | 1.1592 | 0
2015-12-26 17:00 | 0 | 0 | 0 | 0 | -23.3663 | 90.6532 | 112.8768 | -22.8768 | 85.0658 | 97.2238 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.2 | -15.2 | 1.1608 | 0
2015-12-26 18:00 | 0 | 0 | 0 | 0 | -23.365 | 105.6484 | 116.2451 | -26.2451 | 99.7439 | 110.6444 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.8 | -15.8 | 1.1632 | 0
2015-12-26 19:00 | 0 | 0 | 0 | 0 | -23.3637 | 120.6435 | 119.4636 | -29.4636 | 114.888 | 124.2817 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15 | -15 | 1.16 | 0
2015-12-26 20:00 | 0 | 0 | 0 | 0 | -23.3624 | 135.6387 | 122.2994 | -32.2994 | 130.5926 | 138.0288 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.9 | -13.9 | 1.1556 | 0
2015-12-26 21:00 | 0 | 0 | 0 | 0 | -23.361 | 150.6339 | 124.523 | -34.523 | 146.8787 | 151.7573 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.6 | -13.6 | 1.1544 | 0
2015-12-26 22:00 | 0 | 0 | 0 | 0 | -23.3597 | 165.629 | 125.9333 | -35.9333 | 163.6558 | 165.0843 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.6 | -13.6 | 1.1544 | 0
2015-12-26 23:00 | 0 | 0 | 0 | 0 | -23.3584 | 180.6242 | 126.3908 | -36.3908 | -179.2881 | 173.5815 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.3 | -13.3 | 1.1532 | 0
2015-12-27 | 0 | 0 | 0 | 0 | -23.357 | -164.3806 | 125.848 | -35.848 | -162.245 | 164.0205 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12.9 | -12.9 | 1.1516 | 0
2015-12-27 01:00 | 0 | 0 | 0 | 0 | -23.3556 | -149.3854 | 124.361 | -34.361 | -145.5029 | 150.6209 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12.5 | -12.5 | 1.15 | 0
2015-12-27 02:00 | 0 | 0 | 0 | 0 | -23.3542 | -134.3903 | 122.0755 | -32.0755 | -129.2644 | 136.8827 | 0 | 0 | 0.2 | 0 | 0 | 0 | -14.3 | -14.3 | 1.1572 | 0
2015-12-27 03:00 | 0 | 0 | 0 | 0 | -23.3528 | -119.3951 | 119.1963 | -29.1963 | -113.6095 | 123.1396 | 0 | 0 | 0.2 | 0 | 0 | 0 | -14.7 | -14.7 | 1.1588 | 0
2015-12-27 04:00 | 0 | 0 | 0 | 0 | -23.3514 | -104.3999 | 115.9539 | -25.9539 | -98.5094 | 109.5146 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.9 | -13.9 | 1.1556 | 0
2015-12-27 05:00 | 0 | 0 | 0 | 0 | -23.35 | -89.4047 | 112.5807 | -22.5807 | -83.8652 | 96.1157 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.5 | -13.5 | 1.154 | 0
2015-12-27 06:00 | 0 | 0 | 0 | 0 | -23.3485 | -74.4096 | 109.2971 | -19.2971 | -69.5492 | 83.0873 | 0 | 0 | 0.2 | 0 | 0 | 0 | -14.6 | -14.6 | 1.1584 | 0
2015-12-27 07:00 | 0 | 0 | 0 | 0 | -23.3471 | -59.4144 | 106.3042 | -16.3042 | -55.4367 | 70.6594 | 0 | 0 | 0.2 | 0 | 0 | 0 | -14 | -14 | 1.156 | 0
2015-12-27 08:00 | 0 | 0 | 0 | 0 | -23.3456 | -44.4192 | 103.7792 | -13.7792 | -41.4254 | 59.2307 | 0 | 0 | 0.2 | 0 | 0 | 0 | -14 | -14 | 1.156 | 0
2015-12-27 09:00 | 0 | 0 | 0 | 0 | -23.3441 | -29.424 | 101.8702 | -11.8702 | -27.4459 | 49.5135 | 0 | 0 | 0.2 | 0 | 0 | 0 | -16.3 | -16.3 | 1.1652 | 0
2015-12-27 10:00 | 0 | 0 | 0 | 0 | -23.3426 | -14.4289 | 100.6898 | -10.6898 | -13.4634 | 42.7043 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15.6 | -15.6 | 1.1624 | 0
2015-12-27 11:00 | 0 | 0 | 0 | 0 | -23.3411 | 0.56632 | 100.3083 | -10.3083 | 0.5285 | 40.3116 | 0 | 0 | 0.2 | 0 | 0 | 0 | -16.4 | -16.4 | 1.1656 | 0
2015-12-27 12:00 | 0 | 0 | 0 | 0 | -23.3396 | 15.5615 | 100.7486 | -10.7486 | 14.5201 | 43.0796 | 0 | 0 | 0.2 | 0 | 0 | 0 | -15 | -15 | 1.16 | 0
2015-12-27 13:00 | 0 | 0 | 0 | 0 | -23.338 | 30.5567 | 101.984 | -11.984 | 28.5024 | 50.1594 | 0 | 0 | 0.2 | 0 | 0 | 0 | -13.8 | -13.8 | 1.1552 | 0
2015-12-27 14:00 | 0 | 0 | 0 | 0 | -23.3365 | 45.5519 | 103.941 | -13.941 | 42.4835 | 60.04 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12.8 | -12.8 | 1.1512 | 0
2015-12-27 15:00 | 0 | 0 | 0 | 0 | -23.3349 | 60.547 | 106.504 | -16.504 | 56.5007 | 71.5638 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12.5 | -12.5 | 1.15 | 0
2015-12-27 16:00 | 0 | 0 | 0 | 0 | -23.3333 | 75.5422 | 109.5225 | -19.5225 | 70.6258 | 84.0484 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12.4 | -12.4 | 1.1496 | 0
2015-12-27 17:00 | 0 | 0 | 0 | 0 | -23.3317 | 90.5374 | 112.8173 | -22.8173 | 84.9631 | 97.1122 | 0 | 0 | 0.2 | 0 | 0 | 0 | -12 | -12 | 1.148 | 0
2015-12-27 18:00 | 0 | 0 | 0 | 0 | -23.3301 | 105.5326 | 116.1855 | -26.1855 | 99.6384 | 110.5336 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.9 | -11.9 | 1.1476 | 0
2015-12-27 19:00 | 0 | 0 | 0 | 0 | -23.3285 | 120.5278 | 119.4056 | -29.4056 | 114.778 | 124.1726 | 0 | 0 | 0.2 | 0 | 0 | 0 | -11.4 | -11.4 | 1.1456 | 0
2015-12-27 20:00 | 0 | 0 | 0 | 0 | -23.3269 | 135.523 | 122.2447 | -32.2447 | 130.4769 | 137.9227 | 0 | 0 | 0.2 | 0 | 0 | 0 | -10.3 | -10.3 | 1.1412 | 0
2015-12-27 21:00 | 0 | 0 | 0 | 0 | -23.3252 | 150.5181 | 124.4732 | -34.4732 | 146.7568 | 151.6566 | 0 | 0 | 0.2 | 0 | 0 | 0 | -9.4 | -9.4 | 1.1376 | 0
2015-12-27 22:00 | 0 | 0 | 0 | 0 | -23.3236 | 165.5133 | 125.8898 | -35.8898 | 163.5281 | 165.0001 | 0 | 0 | 0.2 | 0 | 0 | 0 | -5 | -5 | 1.12 | 0
2015-12-27 23:00 | 0 | 0 | 0 | 0 | -23.3219 | 180.5085 | 126.3546 | -36.3546 | -179.4202 | 173.6269 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.3 | -4.3 | 1.1172 | 0
2015-12-28 | 0 | 0 | 0 | 0 | -23.3202 | -164.4963 | 125.8193 | -35.8193 | -162.3791 | 164.1328 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.1 | -4.1 | 1.1164 | 0
2015-12-28 01:00 | 0 | 0 | 0 | 0 | -23.3185 | -149.5011 | 124.339 | -34.339 | -145.6366 | 150.7308 | 0 | 0 | 0.2 | 0 | 0 | 0 | -4.6 | -4.6 | 1.1184 | 0
2015-12-28 02:00 | 0 | 0 | 0 | 0 | -23.3168 | -134.5059 | 122.0589 | -32.0589 | -129.3958 | 136.9888 | 0 | 0 | 0.2 | 0 | 0 | 0 | -3.6 | -3.6 | 1.1144 | 0
2015-12-28 03:00 | 0 | 0 | 0 | 0 | -23.315 | -119.5107 | 119.1834 | -29.1834 | -113.7378 | 123.2416 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.9 | -2.9 | 1.1116 | 0
2015-12-28 04:00 | 0 | 0 | 0 | 0 | -23.3133 | -104.5155 | 115.9428 | -25.9428 | -98.6342 | 109.612 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.3 | -2.3 | 1.1092 | 0
2015-12-28 05:00 | 0 | 0 | 0 | 0 | -23.3115 | -89.5203 | 112.5694 | -22.5694 | -83.9868 | 96.2073 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-12-28 06:00 | 0 | 0 | 0 | 0 | -23.3098 | -74.5251 | 109.2838 | -19.2838 | -69.6681 | 83.1714 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.5 | -1.5 | 1.106 | 0
2015-12-28 07:00 | 0 | 0 | 0 | 0 | -23.308 | -59.5299 | 106.2874 | -16.2874 | -55.5532 | 70.7329 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-12-28 08:00 | 0 | 0 | 0 | 0 | -23.3062 | -44.5348 | 103.7576 | -13.7576 | -41.5398 | 59.2887 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-12-28 09:00 | 0 | 0 | 0 | 0 | -23.3044 | -29.5396 | 101.8428 | -11.8428 | -27.5582 | 49.548 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.9 | -1.9 | 1.1076 | 0
2015-12-28 10:00 | 0 | 0 | 0 | 0 | -23.3026 | -14.5444 | 100.656 | -10.656 | -13.5735 | 42.7042 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2 | -2 | 1.108 | 0
2015-12-28 11:00 | 0 | 0 | 0 | 0 | -23.3007 | 0.45084 | 100.2678 | -10.2678 | 0.42081 | 40.2698 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.4 | -2.4 | 1.1096 | 0
2015-12-28 12:00 | 0 | 0 | 0 | 0 | -23.2989 | 15.446 | 100.7014 | -10.7014 | 14.4149 | 43.0021 | 0 | 0 | 0.2 | 0 | 0 | 0 | -2.6 | -2.6 | 1.1104 | 0
2015-12-28 13:00 | 0 | 0 | 0 | 0 | -23.297 | 30.4412 | 101.9309 | -11.9309 | 28.3997 | 50.0605 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.3 | -1.3 | 1.1052 | 0
2015-12-28 14:00 | 0 | 0 | 0 | 0 | -23.2951 | 45.4364 | 103.8826 | -13.8826 | 42.3829 | 59.931 | 0 | 0 | 0.2 | 0 | 0 | 0 | -1.1 | -1.1 | 1.1044 | 0
2015-12-28 15:00 | 0 | 0 | 0 | 0 | -23.2932 | 60.4316 | 106.4415 | -16.4415 | 56.4014 | 71.4508 | 0 | 0 | 0.2 | 0 | 0 | 0 | -0.1 | -0.1 | 1.1004 | 0
2015-12-28 16:00 | 0 | 0 | 0 | 0 | -23.2913 | 75.4268 | 109.4571 | -19.4571 | 70.5268 | 83.9345 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 0.2 | 1.0992 | 0
2015-12-28 17:00 | 0 | 0 | 0 | 0 | -23.2894 | 90.422 | 112.7503 | -22.7503 | 84.8629 | 96.9988 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.4 | 0.4 | 1.0984 | 0
2015-12-28 18:00 | 0 | 0 | 0 | 0 | -23.2875 | 105.4173 | 116.1185 | -26.1185 | 99.5354 | 110.4218 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.6 | 1.6 | 1.0936 | 0
2015-12-28 19:00 | 0 | 0 | 0 | 0 | -23.2855 | 120.4125 | 119.3401 | -29.3401 | 114.6706 | 124.0632 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.0948 | 0
2015-12-28 20:00 | 0 | 0 | 0 | 0 | -23.2836 | 135.4077 | 122.1824 | -32.1824 | 130.3636 | 137.8169 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.5 | 1.5 | 1.094 | 0
2015-12-28 21:00 | 0 | 0 | 0 | 0 | -23.2816 | 150.4029 | 124.4157 | -34.4157 | 146.6368 | 151.5572 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-12-28 22:00 | 0 | 0 | 0 | 0 | -23.2796 | 165.3981 | 125.8386 | -35.8386 | 163.4016 | 164.9188 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.0948 | 0
2015-12-28 23:00 | 0 | 0 | 0 | 0 | -23.2776 | 180.3933 | 126.3106 | -36.3106 | -179.5517 | 173.6783 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.9 | 0.9 | 1.0964 | 0
2015-12-29 | 0 | 0 | 0 | 0 | -23.2756 | -164.6115 | 125.7826 | -35.7826 | -162.5132 | 164.2476 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 1 | 1.096 | 0
2015-12-29 01:00 | 0 | 0 | 0 | 0 | -23.2736 | -149.6163 | 124.3091 | -34.3091 | -145.771 | 150.8412 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.2 | 1.2 | 1.0952 | 0
2015-12-29 02:00 | 0 | 0 | 0 | 0 | -23.2715 | -134.6211 | 122.0346 | -32.0346 | -129.5284 | 137.0944 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0932 | 0
2015-12-29 03:00 | 0 | 0 | 0 | 0 | -23.2695 | -119.6259 | 119.1628 | -29.1628 | -113.8675 | 123.3424 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0912 | 0
2015-12-29 04:00 | 0 | 0 | 0 | 0 | -23.2674 | -104.6306 | 115.9239 | -25.9239 | -98.7607 | 109.7075 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.0892 | 0
2015-12-29 05:00 | 0 | 0 | 0 | 0 | -23.2653 | -89.6354 | 112.5504 | -22.5504 | -84.11 | 96.2965 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.8 | 2.8 | 1.0888 | 0
2015-12-29 06:00 | 0 | 0 | 0 | 0 | -23.2632 | -74.6402 | 109.2629 | -19.2629 | -69.7884 | 83.2522 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0896 | 0
2015-12-29 07:00 | 0 | 0 | 0 | 0 | -23.2611 | -59.645 | 106.2629 | -16.2629 | -55.6709 | 70.8025 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0912 | 0
2015-12-29 08:00 | 0 | 0 | 0 | 0 | -23.259 | -44.6498 | 103.7283 | -13.7283 | -41.655 | 59.3418 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0896 | 0
2015-12-29 09:00 | 0 | 0 | 0 | 0 | -23.2569 | -29.6546 | 101.8076 | -11.8076 | -27.6709 | 49.5763 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0896 | 0
2015-12-29 10:00 | 0 | 0 | 0 | 0 | -23.2547 | -14.6593 | 100.6143 | -10.6143 | -13.6835 | 42.6971 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.1 | 3.1 | 1.0876 | 0
2015-12-29 11:00 | 0 | 0 | 0 | 0 | -23.2526 | 0.33589 | 100.2194 | -10.2194 | 0.31358 | 40.2206 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.9 | 2.9 | 1.0884 | 0
2015-12-29 12:00 | 0 | 0 | 0 | 0 | -23.2504 | 15.3311 | 100.6466 | -10.6466 | 14.3107 | 42.9178 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0868 | 0
2015-12-29 13:00 | 0 | 0 | 0 | 0 | -23.2482 | 30.3263 | 101.8701 | -11.8701 | 28.2984 | 49.9561 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0896 | 0
2015-12-29 14:00 | 0 | 0 | 0 | 0 | -23.246 | 45.3216 | 103.8168 | -13.8168 | 42.2841 | 59.8177 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.0892 | 0
2015-12-29 15:00 | 0 | 0 | 0 | 0 | -23.2438 | 60.3168 | 106.3715 | -16.3715 | 56.3043 | 71.3345 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.088 | 0
2015-12-29 16:00 | 0 | 0 | 0 | 0 | -23.2416 | 75.312 | 109.3843 | -19.3843 | 70.4302 | 83.8181 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0868 | 0
2015-12-29 17:00 | 0 | 0 | 0 | 0 | -23.2393 | 90.3073 | 112.676 | -22.676 | 84.7653 | 96.8838 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.086 | 0
2015-12-29 18:00 | 0 | 0 | 0 | 0 | -23.2371 | 105.3025 | 116.0441 | -26.0441 | 99.4351 | 110.309 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.4 | 3.4 | 1.0864 | 0
2015-12-29 19:00 | 0 | 0 | 0 | 0 | -23.2348 | 120.2977 | 119.2671 | -29.2671 | 114.5657 | 123.9535 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.086 | 0
2015-12-29 20:00 | 0 | 0 | 0 | 0 | -23.2325 | 135.2929 | 122.1125 | -32.1125 | 130.2526 | 137.7116 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.8 | 3.8 | 1.0848 | 0
2015-12-29 21:00 | 0 | 0 | 0 | 0 | -23.2302 | 150.2882 | 124.3506 | -34.3506 | 146.5187 | 151.4592 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.1 | 4.1 | 1.0836 | 0
2015-12-29 22:00 | 0 | 0 | 0 | 0 | -23.2279 | 165.2834 | 125.7796 | -35.7796 | 163.2765 | 164.8403 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.8 | 3.8 | 1.0848 | 0
2015-12-29 23:00 | 0 | 0 | 0 | 0 | -23.2256 | 180.2787 | 126.2588 | -36.2588 | -179.6824 | 173.7356 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0852 | 0
2015-12-30 | 0 | 0 | 0 | 0 | -23.2233 | -164.7261 | 125.7382 | -35.7382 | -162.6474 | 164.3646 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.6 | 3.6 | 1.0856 | 0
2015-12-30 01:00 | 0 | 0 | 0 | 0 | -23.2209 | -149.7309 | 124.2715 | -34.2715 | -145.906 | 150.952 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.4 | 3.4 | 1.0864 | 0
2015-12-30 02:00 | 0 | 0 | 0 | 0 | -23.2186 | -134.7356 | 122.0024 | -32.0024 | -129.6622 | 137.1994 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.086 | 0
2015-12-30 03:00 | 0 | 0 | 0 | 0 | -23.2162 | -119.7404 | 119.1344 | -29.1344 | -113.9986 | 123.442 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0844 | 0
2015-12-30 04:00 | 0 | 0 | 0 | 0 | -23.2138 | -104.7451 | 115.8974 | -25.8974 | -98.8886 | 109.8011 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.8 | 3.8 | 1.0848 | 0
2015-12-30 05:00 | 0 | 0 | 0 | 0 | -23.2114 | -89.7499 | 112.5238 | -22.5238 | -84.2347 | 96.383 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.7 | 3.7 | 1.0852 | 0
2015-12-30 06:00 | 0 | 0 | 0 | 0 | -23.209 | -74.7547 | 109.2343 | -19.2343 | -69.9101 | 83.3298 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.8 | 3.8 | 1.0848 | 0
2015-12-30 07:00 | 0 | 0 | 0 | 0 | -23.2065 | -59.7594 | 106.2308 | -16.2308 | -55.7897 | 70.8679 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.084 | 0
2015-12-30 08:00 | 0 | 0 | 0 | 0 | -23.2041 | -44.7642 | 103.6913 | -13.6913 | -41.771 | 59.3897 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.6 | 3.6 | 1.0856 | 0
2015-12-30 09:00 | 0 | 0 | 0 | 0 | -23.2016 | -29.7689 | 101.7648 | -11.7648 | -27.784 | 49.5985 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.4 | 3.4 | 1.0864 | 0
2015-12-30 10:00 | 0 | 0 | 0 | 0 | -23.1992 | -14.7737 | 100.565 | -10.565 | -13.7935 | 42.6829 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.6 | 3.6 | 1.0856 | 0
2015-12-30 11:00 | 0 | 0 | 0 | 0 | -23.1967 | 0.22158 | 100.1634 | -10.1634 | 0.20692 | 40.1639 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0868 | 0
2015-12-30 12:00 | 0 | 0 | 0 | 0 | -23.1942 | 15.2168 | 100.5842 | -10.5842 | 14.2075 | 42.8267 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.4 | 2.4 | 1.0904 | 0
2015-12-30 13:00 | 0 | 0 | 0 | 0 | -23.1917 | 30.2121 | 101.8018 | -11.8018 | 28.1986 | 49.846 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.09 | 0
2015-12-30 14:00 | 0 | 0 | 0 | 0 | -23.1892 | 45.2073 | 103.7434 | -13.7434 | 42.1871 | 59.7 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.088 | 0
2015-12-30 15:00 | 0 | 0 | 0 | 0 | -23.1866 | 60.2026 | 106.2942 | -16.2942 | 56.2094 | 71.215 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.0892 | 0
2015-12-30 16:00 | 0 | 0 | 0 | 0 | -23.1841 | 75.1979 | 109.3041 | -19.3041 | 70.3361 | 83.6994 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0908 | 0
2015-12-30 17:00 | 0 | 0 | 0 | 0 | -23.1815 | 90.1931 | 112.5943 | -22.5943 | 84.6704 | 96.7672 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.6 | 2.6 | 1.0896 | 0
2015-12-30 18:00 | 0 | 0 | 0 | 0 | -23.1789 | 105.1884 | 115.9623 | -25.9623 | 99.3375 | 110.1954 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.5 | 2.5 | 1.09 | 0
2015-12-30 19:00 | 0 | 0 | 0 | 0 | -23.1763 | 120.1836 | 119.1867 | -29.1867 | 114.4636 | 123.8436 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0908 | 0
2015-12-30 20:00 | 0 | 0 | 0 | 0 | -23.1737 | 135.1789 | 122.0351 | -32.0351 | 130.1441 | 137.6067 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.1 | 2.1 | 1.0916 | 0
2015-12-30 21:00 | 0 | 0 | 0 | 0 | -23.1711 | 150.1742 | 124.2778 | -34.2778 | 146.4027 | 151.3624 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.088 | 0
2015-12-30 22:00 | 0 | 0 | 0 | 0 | -23.1685 | 165.1694 | 125.7129 | -35.7129 | 163.1529 | 164.7646 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0844 | 0
2015-12-30 23:00 | 0 | 0 | 0 | 0 | -23.1658 | 180.1647 | 126.1991 | -36.1991 | -179.8124 | 173.7989 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.084 | 0
2015-12-31 | 0 | 0 | 0 | 0 | -23.1632 | -164.84 | 125.6859 | -35.6859 | -162.7814 | 164.4838 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.084 | 0
2015-12-31 01:00 | 0 | 0 | 0 | 0 | -23.1605 | -149.8448 | 124.226 | -34.226 | -146.0414 | 151.063 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5 | 4.5 | 1.082 | 0
2015-12-31 02:00 | 0 | 0 | 0 | 0 | -23.1578 | -134.8495 | 121.9626 | -31.9626 | -129.7968 | 137.3038 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4 | 4 | 1.084 | 0
2015-12-31 03:00 | 0 | 0 | 0 | 0 | -23.1551 | -119.8542 | 119.0984 | -29.0984 | -114.131 | 123.5402 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0844 | 0
2015-12-31 04:00 | 0 | 0 | 0 | 0 | -23.1524 | -104.8589 | 115.8632 | -25.8632 | -99.018 | 109.8927 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.4 | 3.4 | 1.0864 | 0
2015-12-31 05:00 | 0 | 0 | 0 | 0 | -23.1497 | -89.8637 | 112.4895 | -22.4895 | -84.3608 | 96.467 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.086 | 0
2015-12-31 06:00 | 0 | 0 | 0 | 0 | -23.147 | -74.8684 | 109.1981 | -19.1981 | -70.0329 | 83.4041 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.9 | 3.9 | 1.0844 | 0
2015-12-31 07:00 | 0 | 0 | 0 | 0 | -23.1442 | -59.8731 | 106.191 | -16.191 | -55.9095 | 70.9292 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0816 | 0
2015-12-31 08:00 | 0 | 0 | 0 | 0 | -23.1414 | -44.8778 | 103.6465 | -13.6465 | -41.8876 | 59.4326 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.6 | 4.6 | 1.0816 | 0
2015-12-31 09:00 | 0 | 0 | 0 | 0 | -23.1387 | -29.8826 | 101.7142 | -11.7142 | -27.8974 | 49.6146 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5 | 4.5 | 1.082 | 0
2015-12-31 10:00 | 0 | 0 | 0 | 0 | -23.1359 | -14.8873 | 100.5079 | -10.5079 | -13.9034 | 42.6616 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.8 | 3.8 | 1.0848 | 0
2015-12-31 11:00 | 0 | 0 | 0 | 0 | -23.1331 | 0.10802 | 100.0998 | -10.0998 | 0.10089 | 40.0999 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.086 | 0
2015-12-31 12:00 | 0 | 0 | 0 | 0 | -23.1303 | 15.1033 | 100.5141 | -10.5141 | 14.1054 | 42.7289 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0868 | 0
2015-12-31 13:00 | 0 | 0 | 0 | 0 | -23.1274 | 30.0986 | 101.7259 | -11.7259 | 28.1003 | 49.7304 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.5 | 3.5 | 1.086 | 0
2015-12-31 14:00 | 0 | 0 | 0 | 0 | -23.1246 | 45.0939 | 103.6625 | -13.6625 | 42.0922 | 59.5781 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.6 | 3.6 | 1.0856 | 0
2015-12-31 15:00 | 0 | 0 | 0 | 0 | -23.1217 | 60.0892 | 106.2094 | -16.2094 | 56.1168 | 71.0923 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3.3 | 3.3 | 1.0868 | 0
2015-12-31 16:00 | 0 | 0 | 0 | 0 | -23.1189 | 75.0845 | 109.2166 | -19.2166 | 70.2445 | 83.5785 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.3 | 2.3 | 1.0908 | 0
2015-12-31 17:00 | 0 | 0 | 0 | 0 | -23.116 | 90.0798 | 112.5053 | -22.5053 | 84.5783 | 96.6491 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.7 | 2.7 | 1.0892 | 0
2015-12-31 18:00 | 0 | 0 | 0 | 0 | -23.1131 | 105.075 | 115.8731 | -25.8731 | 99.2428 | 110.0809 | 0 | 0 | 0.2 | 0 | 0 | 0 | 2.2 | 2.2 | 1.0912 | 0
2015-12-31 19:00 | 0 | 0 | 0 | 0 | -23.1102 | 120.0703 | 119.099 | -29.099 | 114.3642 | 123.7336 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0928 | 0
2015-12-31 20:00 | 0 | 0 | 0 | 0 | -23.1072 | 135.0656 | 121.9503 | -31.9503 | 130.0381 | 137.5024 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.3 | 1.3 | 1.0948 | 0
2015-12-31 21:00 | 0 | 0 | 0 | 0 | -23.1043 | 150.0609 | 124.1975 | -34.1975 | 146.2889 | 151.2671 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.0928 | 0
2015-12-31 22:00 | 0 | 0 | 0 | 0 | -23.1013 | 165.0562 | 125.6385 | -35.6385 | 163.031 | 164.6916 | 0 | 0 | 0.2 | 0 | 0 | 0 | 3 | 3 | 1.088 | 0
2015-12-31 23:00 | 0 | 0 | 0 | 0 | -23.0984 | 180.0515 | 126.1317 | -36.1317 | -179.9413 | 173.8681 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1.7 | 1.7 | 1.0932 | 0